## ndashboard
| Fetch Date | FV Engine Count |  |  | Cache Time [s] |  |  | T |  |  |  | FV Start Date |  | FV cum hours |  | FV days | FV oph/day | [38 empty] | Pn | 1013 | mbar | Tn | 0 | °C | Hu | 9.8 | kWh / mn3
| 2020-12-27 08:15 | 32 |  |  | 0 |  |  | 30000 |  |  |  | 2020-02-07 |  | 78686 |  | 324 | 562.99 | [47 empty] | ETAMOT not plausible ? | [9 empty] | Knock Noise | [23 empty] | Mechanical Valve Noise | [23 empty] | Exhaust Valve, Close Crank Angle | [23 empty] | Inlet Valve, Close Crank Angle
| v | p | p | p | p | p | c | p | d | d | c | v | d | c , v | c | c | c | c | c | c | d | d | d | d | d | d | d | d | d | d | d | d | p | d | d | c | d | d | d | d | d | d | d | d | c | c | d | d | d | d | d | d | d | d | c | d | d | d | d | d | d | d | d | c | c | d | d | d |  | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d | d
| Validation Engine | Engine ID | Country | Design Number | Engine Type | Engine Version | #parts | Serial Number | oph | Starts | oph/start | val start | LOC Avg | oph @v al | starts @val | oph/start @val | opd/day | 2000 | 4000 | 6000 | Status | oph | Starts | Status No | OP on | OP Switch on | OP NetP | Wanrning ? | Alarm ? | Slow Down Time | h since Start | E since Start | Orig Commissioning | P nom | N nom | BMEP | P red Act | Pred ext | Pred Bus | Pred knock | Pred misfire | Pred mixtemp | P Act | N Act | BMEP Act | oph parts | LOC Avg | Crankcase Pressure | Oil P limit | DP Oilfilter | T2' | P2' | LambdaTJ | LoadRamp | Load Ramp to 100% | TJ Vol Eff | BP pos | DK pos | TJ pos | TJ Gas Flow | TJ Gas T | TJ Gas P | TJ Gas DP | Qn | ETAmot | Q Gas B/N | Q Gas P | Q Gas T | Qn | T11 A | P11 A | T11 B | P11 B | Safi Temp | Safi W1 Z01 | Safi W1 Z02 | Safi W1 Z03 | Safi W1 Z04 | Safi W1 Z05 | Safi W1 Z06 | Safi W1 Z07 | Safi W1 Z08 | Safi W1 Z09 | Safi W1 Z10 | Safi W1 Z11 | Safi W1 Z12 | Safi W1 Z13 | Safi W1 Z14 | Safi W1 Z15 | Safi W1 Z16 | Safi W1 Z17 | Safi W1 Z18 | Safi W1 Z19 | Safi W1 Z20 | Safi W1 Z21 | Safi W1 Z22 | Safi W1 Z23 | Safi W1 Z24 | Safi W2 Z01 | Safi W2 Z02 | Safi W2 Z03 | Safi W2 Z04 | Safi W2 Z05 | Safi W2 Z06 | Safi W2 Z07 | Safi W2 Z08 | Safi W2 Z09 | Safi W2 Z10 | Safi W2 Z11 | Safi W2 Z12 | Safi W2 Z13 | Safi W2 Z14 | Safi W2 Z15 | Safi W2 Z16 | Safi W2 Z17 | Safi W2 Z18 | Safi W2 Z19 | Safi W2 Z20 | Safi W2 Z21 | Safi W2 Z22 | Safi W2 Z23 | Safi W2 Z24 | Safi W3 Z1 | Safi W3 Z2 | Safi W3 Z3 | Safi W3 Z4 | Safi W3 Z5 | Safi W3 Z6 | Safi W3 Z7 | Safi W3 Z8 | Safi W3 Z9 | Safi W3 Z10 | Safi W3 Z11 | Safi W3 Z12 | Safi W3 Z13 | Safi W3 Z14 | Safi W3 Z15 | Safi W3 Z16 | Safi W3 Z17 | Safi W3 Z18 | Safi W3 Z19 | Safi W3 Z20 | Safi W3 Z21 | Safi W3 Z22 | Safi W3 Z23 | Safi W3 Z24 | Safi W4 Z1 | Safi W4 Z2 | Safi W4 Z3 | Safi W4 Z4 | Safi W4 Z5 | Safi W4 Z6 | Safi W4 Z7 | Safi W4 Z8 | Safi W4 Z9 | Safi W4 Z10 | Safi W4 Z11 | Safi W4 Z12 | Safi W4 Z13 | Safi W4 Z14 | Safi W4 Z15 | Safi W4 Z16 | Safi W4 Z17 | Safi W4 Z18 | Safi W4 Z19 | Safi W4 Z20 | Safi W4 Z21 | Safi W4 Z22 | Safi W4 Z23 | Safi W4 Z24
27 | ABINSK | M09 | CH | Y203 | 624 | H01 | 24 | 1386177 | 8221 | 224 | 36.7009 | 2020-03-02 |  | 6376 | 169 | 37.7278 | 21.2533 | done | done | done | Running | 8221 | 224 | 17 | 1 | 1 | 1 | 0 | 0 | 40 | 18.5 | 175 | 2019-09-03 | 4397 | 1500 | 23.9523 | 4397 | 0 | 0 | 0 | 0 | 0 | 4191 | #N/A | 0 | 6376 |  | -40.09 | 3.99 | 0.70855 | #N/A | #N/A | 2.001 | 0.56 | 178.5714 | 0.58 | 8.3 | 98.8 | 29.7 | 253.4 | 15.7 | 1090 | 70 | 928.2287 | 45.2% | 0 | 0 | 0 |  | 67.4 | 2.7 |  |  | 69.55 | 300 | 174 | 126 | 189 | 141 | 253 | 126 | 174 | 141 | 79 | 141 | 158 | 174 | 110 | 141 | 300 | 174 | 126 | 205 | 189 | 332 | 110 | 126 | 126 | 268 | 317 | 268 | 268 | 402 | 329 | 341 | 354 | 610 | 244 | 427 | 488 | 207 | 329 | 329 | 402 | 427 | 317 | 317 | 366 | 244 | 378 | 305 | 341 | 366 | 371 |  |  | 370 | 362 | 370 | 365 | 371 | 365 |  | 372 | 374 | 370 | 370 | 367 | 372 | 368 | 370 | 370 | 368 | 371 | 366 | 374 | 494 | 496 | 495 | 496 | 496 | 493 | 496 | 495 | 500 | 495 | 495 | 496 | 495 | 496 | 497 | 496 | 497 | 495 | 497 | 496 | 496 | 497 | 496 | 496
29 | BLESSED TEXTILE | M01 | PK | Y386 | 620 | J101 | 20 | 1393153 | 13528 | 370 | 36.5622 | 2020-03-23 | 0.1315 | 6213 | 127 | 48.9213 | 22.2688 | done | done | done | Running | 13528 | 370 | 26 | 1 | 1 | 0 | 0 | 0 | 43 | 9.1 | 290.2 | 2019-04-08 | 3356 | 1500 | 21.9602 | 3356 | 0 | 0 | 0 | 0 | 0 | 2856 | #N/A | 0 | 6213 | 0.1315 | -18.16 | 4.119 | 0.83245 | #N/A | #N/A | 1.885 | 0.63 | 158.7302 | 0.74 | 34.4 | 100 | 52.7 | 168.2 | 14.9 | 1176 | 210 | 666.5914 | 42.84% | 377 | 1887 | 16.2 | [5 empty] | 50.73 | 141 | 110 | 189 | 110 | 62 | 94 | 94 | 126 | 94 | 62 | 126 | 141 | 141 | 110 | 126 | 110 | 189 | 110 | 141 | 94 |  |  |  |  | 231 | 231 | 219 | 244 | 305 | 293 | 280 | 268 | 256 | 293 | 378 | 293 | 280 | 354 | 219 | 231 | 268 | 305 | 231 | 329 |  |  |  |  | 400 | 390 | 384 | 383 | 396 | 390 | 384 | 389 | 387 | 392 | 383 | 390 | 390 | 390 |  | 377 | 383 | 389 | 382 | 389 | [5 empty] | 523 |  | 516 | 520 | 520 | 521 |  | 518 | 522 | 521 | 523 | 517 | 524 | 524 | 517 | 518 | 522 | 520 | 527
16 | BMW LANDSHUT 4.10 | M04 | DE | U781 | 624 | H01 | 24 | 1320072 | 11542 | 1130 | 10.2142 | 2020-02-07 | 0.074 | 5226 | 362 | 14.4365 | 16.1296 | done | done | 2021-02-13 07:55 | Not Available | 11542 | 1130 | 19 | 0 | 0 | 1 | 1 | 0 | 45 | 0 | 0 | 2019-01-09 | 4500 | 1500 | 24.5133 | 4500 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | 0 | 5226 | 0.074 | -46.17 | 3.993 | 0.91291 | #N/A | #N/A | 1.45 | 0.72 | 138.8889 | 0.59 | 0 | 1.9 | 0 | 0 | 27.9 | 963 | -1 | 0 |  | 0 | 0 | 0 |  | 30.4 | 0.97 | 30.5 | 0.97 | 67.31 | [48 empty] | 361 | 364 | 362 | 361 | 364 | 360 | 363 | 356 | 358 | 361 | 361 | 360 | 362 | 362 | 362 | 363 | 363 | 362 | 362 | 362 | 360 | 362 | 356 | 360 | 492 | 494 | 495 | 495 | 495 | 494 | 494 | 491 | 493 | 492 | 490 | 494 | 494 | 494 | 492 | 495 | 495 | 497 | 494 | 493 | 493 | 495 | 491 | 492
2 | ROCHE PENZBERG KWKK | M01 | DE | U233 | 624 | H02 | 24 | 1184199 | 30314 | 811 | 37.3785 | 2020-04-27 | 0.027 | 5106 | 62 | 82.3548 | 20.9262 | done | done | 2021-02-08 01:34 | Running | 30314 | 811 | 17 | 1 | 1 | 1 | 0 | 0 | 59 | 0.1 | 0 | 2016-12-22 | 4404 | 1500 | 23.9904 | 4404 | 0 | 0 | 0 | 0 | 0 | 4435 | #N/A | 0 | 5106 | 0.027 | -52.36 | 4.5 | 0.81373 | #N/A | #N/A | 1.883 | 0.58 | 172.4138 | 0.6 | 16.7 | 100 | 31.7 | 299.5 | 10.4 | 1017 | 91 | 1042.7553 | 42.57% | 0 | 0 | 0 |  | 68 | 3.14 | 69.6 | 3.14 | 58.02 | 253 | 174 | 110 | 205 | 174 | 126 | 189 | 269 | 189 | 220 | 174 | 174 | 158 | 220 | 126 | 174 | 158 | 141 | 220 | 110 | 174 | 237 | 189 | 189 | 415 | 317 | 378 | 402 | 402 | 305 | 305 | 390 | 231 | 317 | 366 | 293 | 549 | 341 | 305 | 329 | 329 | 366 | 268 | 366 | 231 | 244 | 402 | 329 | 371 | 374 | 370 | 370 | 373 | 367 | 370 | 368 | 369 | 369 | 370 | 377 | 381 | 370 | 369 | 369 | 367 | 367 |  | 383 | 373 | 369 | 368 |  | 495 |  | 496 | 498 |  | 488 | 488 | 492 | 495 | 495 | 496 | 495 | 489 |  | 505 | 503 |  | 491 | 502 | 497 | 508 | 507 | 501 | 508
22 | BMW DINGOLFING 2.4 | M06 | DE | X263 | 624 | H01 | 24 | 1352268 | 9496 | 643 | 14.7683 | 2020-05-04 | 0.056 | 3740 | 199 | 18.794 | 15.7806 | done | 2021-01-12 19:40 | 2021-05-19 13:23 | Running | 9496 | 643 | 17 | 1 | 1 | 1 | 0 | 0 | 45 | 21.6 | 405.9 | 2019-10-11 | 4500 | 1501 | 24.497 | 4500 | 0 | 0 | 0 | 0 | 0 | 4391 | #N/A | 0 | 3740 | 0.056 | -43.86 | 3.911 | 0.733 | #N/A | #N/A | 2.058 | 1 | 100 | 0.58 | 9.7 | 100 | 31.7 | 261.4 | -1.2 | 1025 | 70 | 956.3892 | 45.96% | 928 | 0 | 0 |  | 72 | 2.75 | 72 | 2.76 | 76.32 | 284 | 269 | 126 | 141 | 220 | 79 | 126 | 158 | 220 | 141 | 317 | 110 | 141 | 189 | 189 | 237 | 126 | 110 | 141 | 237 | 364 | 205 | 189 | 189 | 354 | 329 | 341 | 439 | 366 | 341 | 634 | 354 | 402 | 341 | 390 | 427 | 341 | 476 | 427 | 549 | 561 | 390 | 341 | 427 | 427 | 525 | 341 | 305 | 365 | 367 | 368 | 368 | 369 | 368 | 369 | 365 | 365 | 366 | 365 | 367 | 367 | 365 | 363 | 367 | 362 | 368 | 367 | 365 | 365 | 365 | 364 | 366 | 494 | 495 | 496 | 497 | 496 | 495 | 497 | 492 | 495 | 496 | 494 | 496 | 495 | 495 | 497 | 496 | 496 | 497 | 495 | 495 | 495 | 496 | 494 | 494
14 | BMW MÜNCHEN | M01 | DE | U779 | 624 | H01 | 24 | 1320022 | 7521 | 1700 | 4.4241 | 2020-06-08 | 0.04 | 3536 | 836 | 4.2297 | 17.505 | done | 2021-01-22 20:25 | 2021-05-17 02:30 | Running | 7521 | 1700 | 17 | 1 | 1 | 1 | 1 | 0 | 47 | 18.1 | 1036.3 | 2019-09-16 | 4500 | 1500 | 24.5133 | 4500 | 0 | 0 | 0 | 0 | 0 | 4501 | #N/A | 0 | 3536 | 0.04 | -43.41 | 4.054 | 0.75164 | #N/A | #N/A | 2.046 | 0.72 | 138.8889 | 0.59 | 9 | 100 | 36.7 | 277.2 | 4.9 | 1004 | 57 | 971.6241 | 46.37% | 962 | 0 | 0 |  | 68 | 2.99 | 67.8 | 2.99 | 65.97 | 141 | 205 | 284 | 269 | 189 | 126 | 158 | 220 | 110 | 126 | 332 | 220 | 189 | 189 | 158 | 205 | 158 | 158 | 141 | 141 | 189 | 158 | 237 | 126 | 402 | 366 | 561 | 439 | 378 | 390 | 488 | 500 | 451 | 390 | 378 | 366 | 329 | 525 | 463 | 402 | 390 | 439 | 329 | 439 | 415 | 354 | 390 | 366 | 364 | 367 | 366 | 367 | 369 | 367 | 367 | 366 | 366 | 366 | 365 | 366 | 366 | 366 | 364 | 365 | 366 | 366 | 367 | 366 | 365 | 366 | 365 | 365 | 495 | 493 | 495 | 493 | 494 | 494 | 493 | 495 | 494 | 496 | 494 | 496 | 493 | 494 | 492 | 495 | 494 | 494 | 494 | 496 | 494 | 494 | 496 | 495
6 | ABINSK | M01 | RU | Y199 | 624 | K01 | 24 | 1250575 | 4134 | 147 | 28.1224 | 2020-06-15 |  | 3376 | 147 | 22.966 | 17.3128 | done | 2021-02-01 09:16 | 2021-05-27 21:47 | Running | 4134 | 147 | 17 | 1 | 1 | 1 | 1 | 0 | 42 | 21.2 | 185 | 2019-09-03 | 4397 | 1500 | 23.9523 | 4397 | 0 | 0 | 0 | 0 | 0 | 4188 | #N/A | 0 | 3376 |  | -44.52 | 4.012 | 0.841 | #N/A | #N/A | 1.949 | 0.56 | 178.5714 | 0.6 | 17.4 | 98.8 | 28.7 | 240.4 | 10.4 | 1091 | 68 | 897.8914 | 46.69% | 0 | 0 | 0 |  | 66.6 | 2.63 |  |  | 66.74 | 220 | 205 | 220 | 79 | 141 | 189 | 174 | 205 | 189 | 126 | 189 | 205 | 174 | 205 | 158 | 253 | 253 | 141 | 110 | 174 | 237 | 110 | 189 | 189 | 305 | 402 | 537 | 378 | 378 | 317 | 268 | 476 | 305 | 317 | 378 | 451 | 329 | 378 | 341 | 317 | 390 | 390 | 378 | 293 | 317 | 256 | 329 | 549 | 383 | 384 | 383 | 369 | 384 | 384 | 374 | 369 | 363 | 370 |  | 372 | 386 |  |  |  | 383 | 385 |  |  | 369 | 367 | 382 |  |  | 493 | 504 | 504 |  | 488 |  | 495 | 497 | 501 | 493 |  | 493 | 493 | 497 | 500 | 492 |  | 495 | 492 | 496 | 496 | 492 | 497
28 | ABINSK | M10 | CH | Y204 | 624 | H01 | 24 | 1386260 | 9560 | 253 | 37.7866 | 2020-07-13 |  | 3320 | 61 | 54.4262 | 19.8802 | done | 2021-01-30 13:10 | 2021-05-11 03:37 | Running | 9560 | 253 | 17 | 1 | 1 | 1 | 1 | 0 | 42 | 20.9 | 183.7 | 2019-09-03 | 4397 | 1500 | 23.9523 | 4397 | 0 | 0 | 0 | 0 | 0 | 4202 | #N/A | 0 | 3320 |  | -37.5 | 3.997 | 0.74136 | #N/A | #N/A | 1.928 | 0.56 | 178.5714 | 0.58 | 12 | 98 | 28.7 | 249.5 | 16.1 | 1095 | 76 | 916.8654 | 45.88% | 0 | 0 | 0 |  | 68.1 | 2.6 |  |  | 70.98 | 317 | 158 | 253 | 174 | 220 | 220 | 174 | 158 | 158 | 126 | 189 | 126 | 205 | 220 | 94 | 284 | 189 | 141 | 284 | 220 | 237 | 158 | 110 | 174 | 378 | 415 | 317 | 415 | 512 | 622 | 341 | 378 | 378 | 476 | 329 | 439 | 573 | 402 | 402 | 378 | 390 | 500 | 341 | 317 | 500 | 525 | 366 | 512 | 373 | 373 | 371 | 372 | 372 | 372 | 372 |  | 368 | 371 |  | 375 | 373 | 371 | 372 | 374 | 372 | 375 | 374 | 370 | 372 | 378 | 370 | 373 | 497 | 495 | 496 | 496 | 497 | 496 | 497 | 494 | 496 | 496 | 494 | 496 | 497 | 496 | 496 | 496 | 496 | 496 | 496 | 494 | 497 | 496 | 495 | 496
18 | BMW LANDSHUT 4.10 | M03 | DE | U781 | 624 | H01 | 24 | 1320114 | 9481 | 1147 | 8.2659 | 2020-02-24 | 0.052 | 2987 | 545 | 5.4807 | 9.7296 | done | 2021-04-10 11:00 | 2021-11-02 00:23 | Not Available | 9481 | 1147 | 19 | 0 | 0 | 1 | 1 | 0 | 46 | 0.1 | 0.1 | 2019-01-09 | 4500 | 1500 | 24.5133 | 4500 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | 0 | 2987 | 0.052 | -43.24 | 4.003 | 0.68345 | #N/A | #N/A | 1.45 | 0.72 | 138.8889 | 0.59 | 0 | 1.9 | 0 | 0 | 29.4 | 958 | 0 | 0 |  | 0 | 0 | 0 |  | 32.1 | 0.97 | 32 | 0.97 | 68.57 | [48 empty] | 364 | 364 | 363 | 363 | 366 | 365 | 366 | 360 | 363 | 362 | 362 | 361 | 365 | 363 | 364 | 366 | 366 | 365 | 365 | 363 | 363 | 363 | 359 | 359 | 495 | 493 | 494 | 494 | 497 | 492 | 501 | 493 | 494 | 495 | 492 | 494 | 494 | 493 | 495 | 494 | 495 | 499 | 496 | 495 | 494 | 494 | 491 | 492
23 | BMW DINGOLFING 2.4 | M07 | DE | X263 | 624 | H01 | 24 | 1352323 | 9308 | 634 | 14.6814 | 2020-06-22 | 0.0445 | 3046 | 100 | 30.46 | 16.2021 | done | 2021-02-24 05:24 | 2021-06-27 15:58 | Available | 9308 | 634 | 5 | 0 | 0 | 1 | 0 | 0 | 45 | 4.9 | 15.8 | 2019-10-10 | 4500 | 1501 | 24.497 | 4500 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | 0 | 3046 | 0.0445 | -49.97 | 3.927 | 0.74909 | #N/A | #N/A | 1.45 | 0.5 | 200 | 0.58 | 0 | 1.9 | 0 | 0 | 29.9 | 969 | -1 | 0 |  | 0 | 0 | 0 |  | 30.4 | 0.97 | 30.3 | 0.97 | 81.37 | [48 empty] | 362 | 364 | 363 | 366 | 365 | 365 | 363 | 360 | 361 | 361 | 362 | 362 | 363 | 362 | 362 | 363 | 362 | 364 | 363 | 361 | 362 | 362 | 361 | 361 | 490 | 496 | 493 | 493 | 496 | 495 | 496 | 493 | 493 | 496 | 494 | 490 | 495 | 492 | 494 | 494 | 493 | 493 | 491 | 493 | 494 | 491 | 491 | 493
4 | BMW REGENSBURG M3 | M03 | DE | I448 | 616 | J01 | 16 | 1243360 | 66470 | 2183 | 30.4489 | 2020-08-17 |  | 2577 | 167 | 15.4311 | 19.5227 | done | 2021-03-10 05:36 | 2021-06-20 16:16 | Not Available | 66470 | 2183 | 19 | 0 | 0 | 1 | 1 | 0 | 44 | 5 | 208 | 2012-10-28 | 2679 | 1500 | 21.9995 | 2679 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | 0 | 2577 |  | -28.46 | 4.108 | 0.67655 | #N/A | #N/A | 1.38 | 0.63 | 158.7302 | 0.74 | 0 | 0 | 0 | 0 | 32.5 | 967 | 23 | 0 |  | 0 | 0 | 0 | [5 empty] | 38.76 | [48 empty] | 389 | 391 | 386 | 389 | 394 | 393 | 390 | 385 | 390 | 402 | 391 | 392 | 401 | 392 | 397 | 394 | [8 empty] | 527 | 527 | 522 | 521 | 523 | 526 | 523 | 524 | 524 | 527 | 526 | 530 | 528 | 528 | 531 | 532
13 | BMW MÜNCHEN | M02 | DE | U779 | 624 | H01 | 24 | 1319997 | 7511 | 1732 | 4.3366 | 2020-08-24 | 0.0515 | 2519 | 353 | 7.136 | 20.152 | done | 2021-03-10 20:03 | 2021-06-18 01:56 | Running | 7511 | 1732 | 17 | 1 | 1 | 1 | 1 | 0 | 45 | 12.7 | 366.5 | 2019-09-16 | 4500 | 1500 | 24.5133 | 4500 | 0 | 0 | 0 | 0 | 0 | 4489 | #N/A | 0 | 2519 | 0.0515 | -45.47 | 4.13 | 0.939 | #N/A | #N/A | 2.05 | 0.72 | 138.8889 | 0.59 | 8.2 | 99.9 | 24.7 | 263.5 | 5.9 | 1059 | 113 | 970.7085 | 46.29% | 969 | 0 | 0 |  | 67.6 | 3 | 67.7 | 3 | 68.76 | 174 | 174 | 189 | 174 | 110 | 205 | 174 | 158 | 220 | 189 | 158 | 158 | 253 | 205 | 126 | 141 | 174 | 126 | 174 | 158 | 158 | 126 | 158 | 126 | 366 | 378 | 463 | 305 | 378 | 305 | 402 | 317 | 378 | 341 | 537 | 329 | 280 | 598 | 317 | 305 | 427 | 512 | 341 | 317 | 378 | 378 | 488 | 488 | 363 | 367 | 366 | 365 | 364 | 365 | 366 | 364 | 364 | 364 | 364 | 366 | 367 | 364 | 364 | 365 | 366 | 365 | 365 | 365 | 366 | 366 | 363 | 365 | 493 | 495 | 496 | 496 | 495 | 495 | 495 | 493 | 495 | 496 | 495 | 495 | 495 | 496 | 496 | 494 | 496 | 495 | 496 | 495 | 495 | 496 | 494 | 495
11 | BMW MÜNCHEN | M01 | DE | V008 | 620 | F01 | 20 | 1319151 | 6427 | 913 | 7.0394 | 2020-07-06 | 0.1105 | 2319 | 187 | 12.4011 | 13.3276 | done | 2021-05-02 11:21 | 2021-09-29 12:54 | Available | 6427 | 913 | 5 | 0 | 0 | 1 | 1 | 0 | 48 | 0 | 0 | 2020-08-25 | 3356 | 1500 | 21.9602 | 3356 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | 0 | 2319 | 0.1105 | -20.11 | 4.119 | 1.2056 | #N/A | #N/A | 1.307 | 0 |  | 0.74 | 0 | 0 | 0 | 0 | 24.7 | 950 | 3 | 0 |  | 0 | 0 | 0 | [5 empty] | 76.17 | [48 empty] | 368 | 371 | 369 | 368 | 371 | 366 | 372 | 366 | 370 | 384 | 367 | 364 | 365 | 364 | 358 | 370 | 373 | 369 | 360 | 359 |  |  |  |  | 523 | 520 | 520 | 520 | 520 | 518 | 519 | 516 | 518 | 522 | 519 | 519 | 520 | 520 | 518 | 522 | 520 | 520 | 523 | 518
15 | BMW MÜNCHEN | M03 | DE | U779 | 624 | H01 | 24 | 1320030 | 7641 | 1415 | 5.4 | 2020-08-03 | 0.0805 | 2163 | 373 | 5.7989 | 14.8151 | done | 2021-04-30 08:08 | 2021-09-12 08:05 | Not Available | 7641 | 1415 | 19 | 0 | 0 | 1 | 1 | 0 | 45 | 0 | 0 | 2019-09-16 | 4500 | 1500 | 24.5133 | 4274 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | 0 | 2163 | 0.0805 | -39.15 | 3.996 | 0.80082 | #N/A | #N/A | 1.2 | 0.72 | 138.8889 | 0.59 | 0 | 1.9 | 0 | 0 | 19.8 | 948 | -1 | 0 |  | 0 | 0 | 0 |  | 21.5 | 0.95 | 21.4 | 0.95 | 73.93 | [48 empty] | 363 | 367 | 363 | 363 | 366 | 366 | 365 | 363 | 364 | 360 | 364 | 365 | 368 | 367 | 366 | 367 | 362 | 365 | 367 | 359 | 367 | 365 | 363 | 362 | 494 | 494 | 495 | 494 | 495 | 495 | 497 | 493 | 495 | 495 | 495 | 496 | 494 | 496 | 496 | 496 | 495 | 497 | 494 | 495 | 496 | 496 | 493 | 495
10 | BMW MÜNCHEN | M02 | DE | V008 | 620 | F01 | 20 | 1319138 | 6427 | 734 | 8.7561 | 2020-07-20 | 0.0925 | 2135 | 177 | 12.0621 | 13.3438 | done | 2021-05-16 02:38 | 2021-10-12 23:49 | Not Available | 6427 | 734 | 19 | 0 | 0 | 1 | 0 | 0 | 48 | 0 | 0 | 2020-01-01 | 3356 | 1500 | 21.9602 | 3356 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | 0 | 2135 | 0.0925 | -14.75 | 4.043 | 1.2295 | #N/A | #N/A | 1.307 | 0 |  | 0.74 | 0 | 0 | 0 | 0 | 27 | 943 | 1 | 0 |  | 0 | 0 | 0 | [5 empty] | 73.29 | [48 empty] | 366 | 366 | 365 | 370 | 366 | 368 | 366 | 369 | 363 | 364 | 362 | 378 | 371 | 367 | 366 | 376 | 366 | 375 | 368 | 374 |  |  |  |  | 518 | 517 | 517 | 522 | 517 | 517 | 517 | 517 | 516 | 517 | 517 | 518 | 516 | 519 | 520 | 524 | 521 | 522 | 521 | 520
12 | BMW MÜNCHEN | M03 | DE | V008 | 620 | F01 | 20 | 1319157 | 6462 | 737 | 8.768 | 2020-08-17 | 0.076 | 2046 | 158 | 12.9494 | 15.5 | done | 2021-05-02 09:48 | 2021-09-08 10:34 | Running | 6462 | 737 | 17 | 1 | 1 | 1 | 0 | 0 | 47 | 0 | 0 | 2020-01-01 | 3356 | 1500 | 21.9602 | 3356 | 0 | 0 | 0 | 0 | 0 | 3354 | #N/A | 0 | 2046 | 0.076 | -30.17 | 3.947 | 1.0385 | #N/A | #N/A | 2.096 | 0 |  | 0.74 | 24.9 | 100 | 66.1 | 199.6 | 4.1 | 1076 | 157 | 751.9613 | 44.6% | 740 | 0 | 0 | [5 empty] | 68.07 | 174 | 174 | 94 | 269 | 126 | 158 | 141 | 237 | 79 | 110 | 126 | 141 | 141 | 126 | 110 | 205 | 141 | 126 | 110 | 126 |  |  |  |  | 341 | 317 | 268 | 366 | 402 | 268 | 402 | 378 | 256 | 305 | 244 | 329 | 317 | 439 | 378 | 415 | 329 | 256 | 256 | 305 |  |  |  |  | 363 | 369 | 368 | 367 | 364 | 367 | 365 | 366 | 362 | 368 | 375 | 368 | 365 | 367 | 367 | 369 | 365 | 374 | 370 | 367 |  |  |  |  | 514 | 517 | 515 | 517 | 514 | 516 | 514 | 515 | 512 | 515 | 515 | 516 | 518 | 516 | 516 | 517 | 517 | 518 | 515 | 518
9 | BMW MÜNCHEN | M04 | DE | V008 | 620 | F01 | 20 | 1319133 | 6428 | 719 | 8.9402 | 2020-08-31 | 0.1 | 1896 | 138 | 13.7391 | 16.0678 | 2021-01-02 19:35 | 2021-05-07 06:56 | 2021-09-08 18:16 | Available | 6428 | 719 | 5 | 0 | 0 | 1 | 1 | 0 | 47 | 0 | 0 | 2020-08-25 | 3356 | 1500 | 21.9602 | 3356 | 0 | 100 | 100 | 0 | 100 | 0 | #N/A | 0 | 1896 | 0.1 | -18.4 | 4.059 | 0.98909 | #N/A | #N/A | 1.307 | 0 |  | 0.74 | 0 | 0 | 0 | 0 | 25.7 | 946 | 1 | 0 |  | 0 | 0 | 0 | [5 empty] | 71.67 | [48 empty] | 361 | 360 | 363 | 362 | 361 | 360 | 362 | 362 | 359 | 363 | 365 | 364 | 365 | 361 | 360 | 363 | 360 | 362 | 367 | 364 |  |  |  |  | 518 | 516 | 515 | 516 | 516 | 515 | 517 | 515 | 516 | 515 | 519 | 520 | 520 | 519 | 518 | 516 | 517 | 521 | 522 | 521
5 | REGENSBURG | M02 | DE | I448 | 616 | J01 | 16 | 1243362 | 64726 | 1476 | 43.8523 | 2020-09-07 |  | 1961 | 1476 | 1.3286 | 17.6667 | 2020-12-29 13:14 | 2021-04-21 18:13 | 2021-08-12 23:12 | Not Available | 64726 | 1476 | 19 | 0 | 0 | 1 | 0 | 0 | 45 | 13.8 | 347.8 | 2011-07-04 | 2679 | 1500 | 21.9995 | 2679 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | 0 | 1961 |  | -23.9 | 4.054 | 0.97091 | #N/A | #N/A | 1.287 | 0.63 | 158.7302 | 0.74 | 0 | 0 | 0 | 0 | 36.1 | 964 | 2 | 0 |  | 0 | 0 | 0 | [5 empty] | 39.64 | [48 empty] | 391 | 394 | 393 | 396 | 389 | 392 | 394 | 396 | 393 | 393 | 392 | 399 | 396 | 389 | 391 | 394 | [8 empty] | 529 | 525 | 527 | 527 | 525 | 527 | 525 | 527 | 523 | 526 | 526 | 527 | 527 | 527 | 529 | 529
1 | REGENSBURG | M05 | DE | T966 | 616 | F01 | 16 | 1175579 | 32288 | 1485 | 21.7428 | 2020-09-14 |  | 1886 | 134 | 14.0746 | 18.1346 | 2021-01-02 15:07 | 2021-04-22 22:00 | 2021-08-11 04:52 | Running | 32288 | 1485 | 17 | 1 | 1 | 1 | 1 | 0 | 41 | 11.6 | 31.2 | 2016-08-22 | 2679 | 1500 | 21.9995 | 2679 | 0 | 0 | 0 | 0 | 0 | 2681 | #N/A | 0 | 1886 |  | -28.33 | 4.449 | 0.86909 | #N/A | #N/A | 1.848 | 0.55 | 181.8182 | 0.74 | 37.8 | 100 | 67.2 | 162.3 | 8.3 | 1119 | 152 | 626.3854 | 42.63% | 0 | 0 | 0 | [5 empty] | 73.63 | 158 | 110 | 126 | 110 | 126 | 94 | 174 | 110 | 126 | 205 | 126 | 110 | 141 | 174 | 158 | 94 | [8 empty] | 390 | 305 | 476 | 231 | 586 | 256 | 402 | 378 | 573 | 293 | 500 | 366 | 280 | 329 | 305 | 317 | [8 empty] | 369 | 378 | 376 | 380 | 378 | 379 | 380 | 376 | 383 | 366 | 380 | 379 | 381 | 378 | 378 | 380 | [8 empty] | 526 | 523 |  | 524 | 523 |  | 521 | 523 | 528 | 524 |  | 529 | 525 | 527 | 528 | 526
31 | Salmmeir 2 | M02 | BE | Y809 | 624 | K01 | 24 | 1415410 | 8405 | 793 | 10.599 | 2020-10-02 | 0.0115 | 1825 | 119 | 15.3361 | 21.2209 | 2021-01-04 14:10 | 2021-04-08 20:05 | 2021-07-12 02:00 | Running | 8405 | 793 | 17 | 1 | 1 | 1 | 1 | 0 | 61 | 9.8 | 44.1 | 2019-09-15 | 4497 | 1502 | 24.4644 | 4497 | 0 | 0 | 0 | 0 | 0 | 4505 | #N/A | 0 | 1825 | 0.0115 | -43.79 | 4.022 | 0.73 | #N/A | #N/A | 1.86 | 0.3 | 333.3333 | 0.61 | 12.6 | 99.9 | 59.3 | 291.8 | 8.3 | 1024 | 25 | 1030.5718 | 43.76% | 0 | 0 | 0 |  | 78.5 | 2.67 |  |  | 77.39 | 174 | 126 | 237 | 158 | 189 | 126 | 269 | 141 | 237 | 237 | 110 | 94 | 189 | 174 | 174 | 110 | 141 | 141 | 126 | 110 | 126 | 141 | 158 | 94 | 415 | 402 | 402 | 378 | 476 | 512 | 463 | 341 | 500 | 329 | 341 | 354 | 293 | 378 | 256 | 341 | 476 | 476 | 341 | 366 | 366 | 366 | 329 | 415 | 385 | 390 | 387 |  | 389 | 370 |  |  | 379 | 373 | 390 | 388 | 387 | 385 | 379 | 390 | 384 | 382 | 387 |  | 382 | 387 | 376 | 387 | 487 | 494 | 506 | 508 |  |  | 509 | 487 | 499 | 506 | 511 | 493 | 508 | 509 | 508 | 507 | 509 | 509 | 496 | 496 | 507 | 509 | 496 | 508
0 | POLYNT - 2 (1145166-T241) --> Sept | M02 | IT | T241 | 624 | H01 | 24 | 1145166 | 33030 | 390 | 84.6923 | 2020-10-12 | 0.027768 | 1739 | 12 | 144.9167 | 22.8816 | 2021-01-07 18:00 | 2021-04-05 03:46 | 2021-07-01 13:31 | Running | 33030 | 390 | 17 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2016-12-09 | 4401 | 1500 | 23.974 | 0 | 0 | 0 | 0 | 0 | 0 | 4400 | #N/A | 0 | 1739 | 0.027768 | -46.1 | 3.967 | 0.88309 | #N/A | #N/A | 1.956 | 0 |  | 0.59 | 9.8 | 98.8 | 25.7 | 258.944 | 2.1 | 1070.4 | 112.2 | 977.5048 | 45.06% | 0 | 0 | 0 | [5 empty] | 51.59 | 207 | 269 | 176 | 191 | 127 | 176 | 159 | 221 | 143 | 191 | 111 | 159 | 207 | 127 | 191 | 191 | 221 | 176 | 269 | 143 | 143 | 143 | 127 | 111 | 1423 | 1420 | 866 | 1295 | 927 | 1700 | 1377 | 1422 | 1210 | 1975 | 2201 | 2410 | 1850 | 1341 | 2183 | 1405 | 1239 | 1487 | 1525 | 1768 | 1848 | 1449 | 1534 | 1887
7 | PROSPERITY WEAVING MILLS LTD - 1 (1351388-X243) | M01 | PK | X243 | 624 | K505 | 24 | 1250578 | 1723 | 391 | 4.4066 | 2020-10-12 |  | 1723 | 39 | 44.1795 | 22.6711 | 2021-01-08 13:29 | 2021-04-06 18:43 | 2021-07-03 23:58 | Running | 1723 | 391 | 27 | 1 | 1 | 0 | 0 | 0 | 43 | 5.4 | 1593.3 | 2018-10-15 | 4200 | 1500 | 22.8791 | 4200 | 0 | 0 | 0 | 0 | 0 | 3972 | #N/A | 0 | 1723 |  | -33.78 | 4.127 | 0.939 | #N/A | #N/A | 1.88 | 0.72 | 138.8889 | 0.6 | 21.1 | 100 | 28.7 | 230.9 | 13 | 1078 | 78 | 844.3902 | 47.09% | 546 | 755 | 12.7 |  | 71.6 | 2.71 |  |  | 49.32 | 237 | 220 | 110 | 110 | 110 | 189 | 110 | 126 | 94 | 126 | 158 | 94 | 126 | 174 | 284 | 174 | 189 | 94 | 94 | 62 | 253 | 141 | 110 | 174 | 341 | 329 | 219 | 219 | 317 | 305 | 207 | 244 | 219 | 256 | 231 | 439 | 451 | 354 | 219 | 317 | 268 | 268 | 305 | 293 | 341 | 219 | 415 | 293 | 384 | 379 | 384 | 382 | 384 | 382 | 373 | 370 | 381 | 370 | 371 | 376 | 384 | 377 | 376 | 372 | 382 | 385 | 386 | 380 | 375 | 373 | 371 | 370 | 507 | 507 | 503 | 503 | 506 | 504 | 505 | 494 | 505 | 504 | 493 | 493 | 502 | 500 | 505 | 504 | 501 | 506 | 502 | 495 | 496 | 498 | 493 | 497
3 | ECOGEN ENERGY SYSTEMS BVBA | M02 | BE | U658 | 616 | F12 | 16 | 1198719 | 30241 | 771 | 39.2231 | 2020-10-15 | 0.0795 | 1658 | 60 | 27.6333 | 22.7123 | 2021-01-11 09:38 | 2021-04-09 11:02 | 2021-07-06 12:25 | Running | 30241 | 771 | 17 | 1 | 1 | 1 | 1 | 0 | 43 | 1.8 | 135.6 | 2017-03-31 | 2679 | 1500 | 21.9995 | 2679 | 0 | 0 | 0 | 0 | 0 | 2675 | #N/A | 0 | 1658 | 0.0795 | -25.64 | 4.032 | 0.70418 | #N/A | #N/A | 1.555 | 0.35 | 285.7143 | 0.74 | 36.1 | 100 | 80.7 | 170.6 | 9.3 | 1088 | 101 | 637.9118 | 41.77% | 0 | 0 | 0 | 0 |  |  |  |  | 67.12 | 94 | 126 | 174 | 141 | 110 | 158 | 141 | 126 | 94 | 94 | 141 | 141 | 94 | 126 | 174 | 189 | [8 empty] | 1587 | 1391 | 732 | 1123 | 1355 | 1050 | 1880 | 1465 | 1575 | 439 | 695 | 1111 | 1196 | 757 | 1037 | 1013
21 | GAZ DE LACQ | M03 | FR | X077 | 616 | J12 | 16 | 1345851 | 8792 | 126 | 69.7778 | 2020-10-22 |  | 1540 | 7 | 220 | 23.3333 | 2021-01-16 01:24 | 2021-04-11 18:32 | 2021-07-06 11:41 | Running | 8792 | 126 | 17 | 1 | 1 | 1 | 0 | 0 | 38 | 20.2 | 684.2 | 2018-10-31 | 2679 | 1500 | 21.9995 | 2679 | 0 | 0 | 0 | 0 | 0 | 2679 | #N/A | 0 | 1540 |  | -26.79 | 3.995 | 0.71 | #N/A | #N/A | 2.044 | 0.2 | 500 | 0.74 | 30.2 | 100 | 53.7 | 167.4 | 38.6 | 1153 | 149 | 600.9974 | 44.4% | 0 | 0 | 0 | [5 empty] | 62.67 | 95 | 127 | 111 | 207 | 176 | 111 | 191 | 95 | 78 | 176 | 111 | 159 | 176 | 191 | 127 | 78 | [8 empty] | 386 | 399 | 612 | 732 | 519 | 615 | 596 | 453 | 315 | 418 | 433 | 444 | 414 | 371 | 394 | 483
30 | Salmmeir 1 | M01 | BE | Y809 | 624 | K01 | 24 | 1415409 | 8306 | 1110 | 7.4829 | 2020-10-21 | 0.016 | 1435 | 99 | 14.4949 | 21.4179 | 2021-01-22 17:22 | 2021-04-26 02:29 | 2021-07-28 11:36 | Running | 8306 | 1110 | 17 | 1 | 1 | 1 | 1 | 0 | 62 | 9.8 | 44.1 | 2019-09-15 | 4497 | 1500 | 24.497 | 4497 | 0 | 0 | 0 | 0 | 0 | 4480 | #N/A | 0 | 1435 | 0.016 | -45.23 | 4.006 | 0.831 | #N/A | #N/A | 1.912 | 0.3 | 333.3333 | 0.61 | 12.1 | 100 | 57 | 286.9 | 6.8 | 1031 | 24 | 1025.659 | 43.72% | 0 | 0 | 0 |  | 77.7 | 2.75 |  |  | 75.71 | 237 | 220 | 189 | 253 | 141 | 141 | 237 | 412 | 126 | 79 | 158 | 94 | 269 | 332 | 205 | 110 | 205 | 126 | 189 | 220 | 126 | 253 | 62 | 126 | 256 | 329 | 378 | 329 | 354 | 293 | 305 | 305 | 305 | 293 | 378 | 390 | 244 | 317 | 305 | 402 | 317 | 512 | 329 | 366 | 280 | 463 | 305 | 329 | 387 | 387 | 386 | 385 | 390 | 385 | 382 | 372 | 381 | 382 | 382 | 388 | 383 | 384 | 380 | 386 | 380 | 383 | 386 | 384 | 378 | 385 | 380 |  | 507 | 507 | 506 | 505 |  | 506 | 508 | 504 | 505 | 507 | 503 | 508 | 507 | 507 | 508 | 508 | 506 | 510 | 507 | 496 | 508 | 509 | 500 | 506
8 | SOTERNIX RENOVE | M01 | PT | U763 | 616 | F11 | 16 | 1310773 | 19731 | 1280 | 15.4148 | 2020-09-25 |  | 1292 | 62 | 20.8387 | 13.8925 | 2021-02-16 07:21 | 2021-07-10 06:28 | 2021-12-01 05:34 | Available | 19731 | 1280 | 5 | 0 | 0 | 1 | 1 | 0 | 40 | 0.2 | 197.6 | 2017-04-12 | 2683 | 1500 | 22.0323 | 2683 | 0 | 100 | 100 | 0 | 100 | 0 | #N/A | 0 | 1292 |  | -26.23 | 4.11 | 0.74636 | #N/A | #N/A | 1.1 | 0.56 | 178.5714 | 0.72 | 0 | 0 | 0 | 0 | 17.7 | 1020 | 13 | 0 |  | 0 | 0 | 0 | [5 empty] | 73.2
19 | LES COURONNERIES | M01 | FR | V229 | 624 | H12 | 24 | 1325927 | 11165 | 267 | 41.8165 | 2020-09-09 | 0.079 | 1361 | 12 | 113.4167 | 12.4862 | 2021-02-16 12:29 | 2021-07-26 16:43 | 2022-01-02 20:57 | Running | 11165 | 267 | 12 | 1 | 1 | 1 | 1 | 0 | 46 | 21.3 | 1273.7 | 2017-11-02 | 4499 | 1500 | 24.5079 | 4499 | 0 | 0 | 0 | 0 | 0 | 4504 | #N/A | 0 | 1361 | 0.079 | -50.32 | 3.975 | 0.96555 | #N/A | #N/A | 1.954 | 0.2 | 500 | 0.59 | 16.6 | 100 | 23.7 | 273.2 | 23.4 | 1134 | 133 | 1014.1217 | 44.46% | 0 | 0 | 0 |  | 72.4 | 2.92 | 72.4 | 2.91 | 69.35 | 220 | 237 | 174 | 126 | 141 | 79 | 220 | 300 | 94 | 141 | 141 | 205 | 126 | 220 | 110 | 189 | 253 | 158 | 110 | 284 | 205 | 141 | 110 | 79 | 329 | 476 | 390 | 378 | 549 | 317 | 305 | 451 | 463 | 366 | 415 | 488 | 451 | 366 | 378 | 512 | 415 | 354 | 378 | 476 | 683 | 366 | 463 | 512 | 362 | 367 | 366 | 367 | 367 | 369 | 368 | 366 | 368 | 366 | 366 | 367 | 373 | 367 | 366 | 369 | 367 | 368 | 370 | 366 | 368 | 368 | 364 | 367 | 495 | 495 | 495 | 493 | 495 | 495 | 496 | 495 | 497 | 493 | 498 | 495 | 494 | 495 | 496 | 495 | 496 | 495 | 495 | 495 | 496 | 495 | 494 | 491
17 | BMW LANDSHUT M1 | M01 | DE | U781 | 624 | H01 | 24 | 1320090 | 9224 | 1331 | 6.9301 | 2020-10-12 | 0.0495 | 1148 | 107 | 10.729 | 15.1053 | 2021-02-21 17:57 | 2021-07-04 03:39 | 2021-11-13 13:21 | Not Available | 9224 | 1331 | 19 | 0 | 0 | 1 | 1 | 0 | 45 | 0.3 | 0.8 | 2019-01-07 | 4500 | 1500 | 24.5133 | 3004 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | 0 | 1148 | 0.0495 | -38.01 | 4 | 0.673 | #N/A | #N/A | 1.55 | 0.72 | 138.8889 | 0.59 | 0 | 1.9 | 0 | 0 | 28.5 | 963 | 0 | 0 |  | 0 | 0 | 0 |  | 30.7 | 0.97 | 30.4 | 0.97 | 64.96 | [48 empty] | 362 | 366 | 364 | 363 | 368 | 365 | 368 | 361 | 361 | 361 | 363 | 366 | 367 | 364 | 362 | 363 | 362 | 366 | 362 | 360 | 364 | 363 | 360 | 361 | 492 | 496 | 495 | 495 | 497 | 493 | 496 | 493 | 493 | 494 | 493 | 496 | 496 | 497 | 495 | 497 | 495 | 495 | 494 | 492 | 493 | 494 | 492 | 492
25 | TOM VILLE | M01 | FR | X684 | 620 | J12 | 20 | 1364066 | 780 | 40 | 19.5 | 2020-09-25 |  | 780 | 26 | 30 | 8.3871 | 2021-05-21 19:20 | 2022-01-15 06:24 | 2022-09-10 17:29 | Available | 780 | 40 | 4 | 0 | 0 | 0 | 1 | 0 | 47 | 6.7 | 2097.1 | 0 | 3356 | 1500 | 21.9602 | 1678 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | 0 | 780 |  | -29.83 | 4.248 | 1.0102 | #N/A | #N/A | 1.45 | 0.56 | 178.5714 | 0.74 | 0 | 0 | 0 | 0 | 24.1 | 1006 | 2 | 0 |  | 0 | 0 | 0 | [5 empty] | 66.96
24 | FRONERI - FERENTINO | M01 | IT | X580 | 616 | J11 | 16 | 1361965 | 8003 | 316 | 25.3259 | 2020-11-18 01:00 | 0.1355 | 774 | 11 | 70.3636 | 19.8462 | 2021-02-27 02:51 | 2021-06-07 21:27 | 2021-09-16 16:04 | Available | 8003 | 316 | 5 | 0 | 0 | 1 | 1 | 0 | 47 | 5.8 | 169 | 2019-07-19 | 2678 | 1500 | 21.9913 | 2678 | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | 0 | 774 | 0.1355 | -7.93 | 4.238 | 0.52455 | #N/A | #N/A | 1.25 | 0.63 | 158.7302 | 0.74 | 0 | 0 | 0 | 0 | 23.8 | 982 | 0 | 0 |  | 0 | 0 | 0 | [5 empty] | 61.1
20 | DALOMA | M01 | FR | V624 | 612 | J12 | 12 | 1339812 | 5878 | 119 | 49.395 | 2020-11-02 |  | 630 | 8 | 78.75 | 11.4545 | 2021-04-25 22:44 | 2021-10-17 13:12 | 2022-04-10 03:41 | Running | 5878 | 119 | 17 | 1 | 1 | 1 | 0 | 0 | 44 | 23 | 301.8 | 2018-11-23 | 2029 | 1500 | 21.9996 | 2029 | 0 | 0 | 0 | 0 | 0 | 2034 | #N/A | 0 | 630 |  | -22.84 | 4.058 | 0.39827 | #N/A | #N/A | 2.018 | 0.48 | 208.3333 | 0.74 | 36.5 | 100 | 38.7 | 117.7 | 17.4 | 1161 | 174 | 456.5434 | 44.81% | 0 | 0 | 0 | [5 empty] | 65.21 | 110 | 158 | 141 | 220 | 141 | 110 | 79 | 110 | 237 | 126 | 79 | 126 | [12 empty] | 1196 | 622 | 671 | 2002 | 1355 | 2759 | 610 | 659 | 671 | 415 | 647 | 390
26 | ABINSK | M06 | RU | Y202 | 624 | H01 | 24 | 1386147 | 9273 | 165 | 56.2 | 2020-12-11 |  | 353 | 20 | 17.65 | 22.0625 | 2021-03-11 23:53 | 2021-06-10 15:31 | 2021-09-09 07:10 | Running | 9273 | 165 | 17 | 1 | 1 | 1 | 0 | 0 | 40 | 21.1 | 185.1 | 2019-09-03 | 4397 | 1500 | 23.9523 | 4397 | 0 | 0 | 0 | 0 | 0 | 4207 | #N/A | 0 | 353 |  | -38.75 | 4.052 | 0.725 | #N/A | #N/A | 1.891 | 0.56 | 178.5714 | 0.58 | 14.1 | 98 | 32.7 | 251.6 | 12.5 | 1080 | 62 | 923.4097 | 45.61% | 0 | 0 | 0 |  | 68.1 | 2.76 |  |  | 72.38 | 348 | 284 | 269 | 141 | 189 | 189 | 141 | 174 | 237 | 174 | 126 | 205 | 269 | 174 | 110 | 126 | 174 | 158 | 110 | 110 | 189 | 189 | 174 | 110 | 256 | 427 | 402 | 329 | 341 | 256 | 378 | 317 | 329 | 427 | 280 | 586 | 293 | 293 | 317 | 427 | 402 | 280 | 244 | 341 | 268 | 390 | 329 | 390 | 367 | 374 | 371 | 369 | 375 | 370 | 373 | 368 | 363 | 367 | 368 | 375 | 382 | 371 | 370 | 371 | 371 | 372 | 369 | 371 | 370 | 371 | 367 | 371 |  |  | 498 | 499 |  | 503 | 496 |  | 497 | 504 | 496 | 489 | 493 | 495 | 496 | 505 | 494 | 491 | 500 | 495 | 506 | 500 | 494 | 493
Formulas:
FV days = DAYS([Fetch Date],[FV Start Date])
FV oph/day = [FV cum hours]/(DAYS(B2,[FV Start Date]))

## summary
[7 empty] | Pn | 1013 | mbar | Tn | 0 | °C | 9.8 | kWh / mn3
Validation Fleet Status |  | Date | 2020-12-27 08:15 |  |  |  | ETAMOT not fully plausible ?
624 | 18 |  | Cum hours | 78686
620 | 6 |  | Fl Leader | 6376
616 | 7 |  | Avg hours | 2458.9375 | [9 empty] | 0
612 | 1 |  | 2000 | 16 | [9 empty] | 0
Sum Engines | 32 |  | 4000 | 4 | [9 empty] | 0
Sum PU's | 676 |  | 6000 | 2 | [9 empty] | 0
0
Beta | Running | Available | Not Available | Error | [9 empty] | 0
1.21 | 19 | 6 | 7 | 0 | [9 empty] | 0
0
| T | CL | BETA | R | [9 empty] | 0
R1 | 30000 | 50% | 1.21 | 98.08% | [9 empty] | 0
R2 | 30000 | 90% | 1.21 | 93.76% | [9 empty] | 0
R3 | 30000 | 10% | 1.21 | 99.71% | [9 empty] | 0
0
Field Validation Results vs. CTQ's |  |  |  | CTQ | [9 empty] | 0
1. R(CL 50%) > 97% @ß = |  | 1.21 | 98.08% | 97% | [9 empty] | 0
2. R(CL 90%) > 90% @ß = |  | 1.21 | 93.76% | 90% | [9 empty] | 0
3. 4 Engines > 6000 oph |  |  | 2 | 4 | [9 empty] | 0
[5 empty] | 1.21 | 1.21 | [7 empty] | 0
| BR6 |  | hours s. VS | 7776 | 6376 | 6376 | [7 empty] | 0
Bohrung [mm] | 190 |  | pess PU F | 7.798% | 232.8296 | 232.8296 | [7 empty] | 0
Hub [mm] | 220 |  | pess PU F | 52.7151 | 99.42% | [8 empty] | 0
VH zyl [dm3] | 6.2376 |  | like PU F | 1.92% | 449084.5698 | 1410295.1741 | [7 empty] | 0
|  |  | like PU F | 12.9821 | 96.29% | [8 empty] | 0
|  |  |  | 2310.8824 | 3.714% | 0.1454% | [7 empty] | 0
[5 empty] | 8.6466 | 0.98281 | [7 empty] | 0
Engines | ~ BMP Avg | z | VH [dm3] | etael | [9 empty] | 0
624 | 24.2331 | 24 | 149.7032 | 98.1% | [9 empty] | 0
620 | 21.9602 | 20 | 124.7526 | 98% | [9 empty] | 0
616 | 22.003 | 16 | 99.8021 | 97.61% | [9 empty] | 0
612 | 21.9996 | 12 | 74.8516 | 98.57% | [9 empty] | 0
0
BMEP Avg | BMEP Min | BMEP Max | NOX | MN | Version | #
24.3045 | 23.9523 | 24.497 | 500 | 80 | K01 | 3
24.3254 | 23.9523 | 24.5133 | 500 | 80 | H01 | 12
23.9904 | 23.9904 | 23.9904 | 250 | 80 | H02 | 1
| 0 | 0 | 500 | 70 | H101 | 0
24.5079 | 24.5079 | 24.5079 | 250 | 70 | H12 | 1
21.968 | 21.9602 | 21.9995 | 500 | 80 | F01 | 5
21.9995 | 21.9995 | 21.9995 | 500 | 80 | J01 | 2
21.9602 | 21.9602 | 21.9602 | 500 | 70 | J101 | 1
21.9913 | 21.9913 | 21.9913 | 500 | 70 | J11 | 1
22.0323 | 22.0323 | 22.0323 | 500 | 70 | F11 | 1
21.9995 | 21.9995 | 21.9995 | 250 | 70 | F12 | 1
21.9864 | 21.9602 | 21.9996 | 250 | 70 | J12 | 3
22.8791 | 22.8791 | 22.8791 | 500 | 80 | K505 | 1
32

## MP Bench
Myplant Diagnostic Worbench
2020-12-27
|  | whole Val Period |  |  | last 7 days | Val Start + 7 days
|  | Validation Engine | Val Start | AssetNumber | 7 | 7 | Dataset | Data Items
27 | Running | ABINSK | 2020-03-02 | 130891 | Diagnostic | workbench | Overview V1 | Various_Values_PressBoost,Various_Values_TempMixture,Various_Values_PosTurboBypass,Hyd_TempWatRet,Hyd_PressCoolWat,Hyd_TempCoolWat,Power_PowerAct,Aux_RoomTemp
29 | Running | BLESSED TEXTILE | 2020-03-23 | 129039 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct
16 | Not Available | BMW LANDSHUT 4.10 | 2020-02-07 | 117617 | Diagnostic | workbench | Overview V1 | Various_Values_PressBoost,Various_Values_TempMixture,Various_Values_PosTurboBypass,Hyd_TempWatRet,Hyd_PressCoolWat,Hyd_TempCoolWat,Power_PowerAct,Aux_RoomTemp
2 | Running | ROCHE PENZBERG KWKK | 2020-04-27 | 108532 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct
22 | Running | BMW DINGOLFING 2.4 | 2020-05-04 | 118223 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct
14 | Running | BMW MÜNCHEN | 2020-06-08 | 117551 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct
6 | Running | ABINSK | 2020-06-15 | 156120 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct
28 | Running | ABINSK | 2020-07-13 | 130893 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct
18 | Not Available | BMW LANDSHUT 4.10 | 2020-02-24 | 117547 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct
23 | Available | BMW DINGOLFING 2.4 | 2020-06-22 | 126032 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct
4 | Not Available | BMW REGENSBURG M3 | 2020-08-17 | 157181 | Diagnostic | workbench | Overview V1 | Various_Values_PressBoost,Various_Values_TempMixture,Various_Values_PosTurboBypass,Hyd_TempWatRet,Hyd_PressCoolWat,Hyd_TempCoolWat,Power_PowerAct,Aux_RoomTemp
13 | Running | BMW MÜNCHEN | 2020-08-24 | 117598 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct
11 | Available | BMW MÜNCHEN | 2020-07-06 | 126448 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct
15 | Not Available | BMW MÜNCHEN | 2020-08-03 | 117550 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct
10 | Not Available | BMW MÜNCHEN | 2020-07-20 | 126449 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct
12 | Running | BMW MÜNCHEN | 2020-08-17 | 126402 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct
9 | Available | BMW MÜNCHEN | 2020-08-31 | 126399 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct
5 | Not Available | REGENSBURG | 2020-09-07 | 157701 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct
1 | Running | REGENSBURG | 2020-09-14 | 106622 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct
31 | Running | Salmmeir 2 | 2020-10-02 | 133858 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct
0 | Running | POLYNT - 2 (1145166-T241) --> Sept | 2020-10-12 | 103791 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct
7 | Running | PROSPERITY WEAVING MILLS LTD - 1 (1351388-X243) | 2020-10-12 | 158705 | Diagnostic | workbench | Overview V1 | Various_Values_PressBoost,Various_Values_TempMixture,Various_Values_PosTurboBypass,Hyd_TempWatRet,Hyd_PressCoolWat,Hyd_TempCoolWat,Power_PowerAct,Aux_RoomTemp
3 | Running | ECOGEN ENERGY SYSTEMS BVBA | 2020-10-15 | 110311 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct
21 | Running | GAZ DE LACQ | 2020-10-22 | 117227 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct
30 | Running | Salmmeir 1 | 2020-10-21 | 133716 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct
8 | Available | SOTERNIX RENOVE | 2020-09-25 | 109063 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct
19 | Running | LES COURONNERIES | 2020-09-09 | 113808 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct
17 | Not Available | BMW LANDSHUT M1 | 2020-10-12 | 117510 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct
25 | Available | TOM VILLE | 2020-09-25 | 123220 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct
24 | Available | FRONERI - FERENTINO | 2020-11-18 01:00 | 126008 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct
20 | Running | DALOMA | 2020-11-02 | 116255 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct
26 | Running | ABINSK | 2020-12-11 | 123269 | Diagnostic | workbench | oph, power | Count_OpHour,Power_PowerAct

## MP Datasets
No | Name | Copy Myplant Link into this list
1 | oph, power | https://myplant.io/app/#/fleet/workbench?q=1607492609986-1608097409986¦129512-Count_OpHour,Power_PowerAct
2 | Overview V1 | https://myplant.io/app/#/fleet/workbench?q=1606912163519-1607516963519¦130891-Various_Values_PressBoost,Various_Values_TempMixture,Various_Values_PosTurboBypass,Hyd_TempWatRet,Hyd_PressCoolWat,Hyd_TempCoolWat,Power_PowerAct,Aux_RoomTemp
3 | Oil Sensor | https://myplant.io/app/#/fleet/workbench?q=1606867200000-1608076800000¦117547-Various_Values_PressBoost,Various_Values_TempMixture,Various_Values_PosTurboBypass,Hyd_TempWatRet,Hyd_PressCoolWat,Hyd_TempCoolWat,Power_PowerAct

## validation
n | Validation Engine | serialNumber | val start | oph@start | starts@start | Asset ID
0 | POLYNT - 2 (1145166-T241) --> Sept | 1145166 | 2020-10-12 | 31291 | 378 | 103791
1 | REGENSBURG | 1175579 | 2020-09-14 | 30402 | 1351 | 106622
2 | ROCHE PENZBERG KWKK | 1184199 | 2020-04-27 | 25208 | 749 | 108532
3 | ECOGEN ENERGY SYSTEMS BVBA | 1198719 | 2020-10-15 | 28583 | 711 | 110311
4 | BMW REGENSBURG M3 | 1243360 | 2020-08-17 | 63893 | 2016 | 157181
5 | REGENSBURG | 1243362 | 2020-09-07 | 62765 |  | 157701
6 | ABINSK | 1250575 | 2020-06-15 | 758 |  | 156120
7 | PROSPERITY WEAVING MILLS LTD - 1 (1351388-X243) | 1250578 | 2020-10-12 | 0 | 352 | 158705
8 | SOTERNIX RENOVE | 1310773 | 2020-09-25 | 18439 | 1218 | 109063
9 | BMW MÜNCHEN | 1319133 | 2020-08-31 | 4532 | 581 | 126399
10 | BMW MÜNCHEN | 1319138 | 2020-07-20 | 4292 | 557 | 126449
11 | BMW MÜNCHEN | 1319151 | 2020-07-06 | 4108 | 726 | 126448
12 | BMW MÜNCHEN | 1319157 | 2020-08-17 | 4416 | 579 | 126402
13 | BMW MÜNCHEN | 1319997 | 2020-08-24 | 4992 | 1379 | 117598
14 | BMW MÜNCHEN | 1320022 | 2020-06-08 | 3985 | 864 | 117551
15 | BMW MÜNCHEN | 1320030 | 2020-08-03 | 5478 | 1042 | 117550
16 | BMW LANDSHUT 4.10 | 1320072 | 2020-02-07 | 6316 | 768 | 117617
17 | BMW LANDSHUT M1 | 1320090 | 2020-10-12 | 8076 | 1224 | 117510
18 | BMW LANDSHUT 4.10 | 1320114 | 2020-02-24 | 6494 | 602 | 117547
19 | LES COURONNERIES | 1325927 | 2020-09-09 | 9804 | 255 | 113808
20 | DALOMA | 1339812 | 2020-11-02 | 5248 | 111 | 116255
21 | GAZ DE LACQ | 1345851 | 2020-10-22 | 7252 | 119 | 117227
22 | BMW DINGOLFING 2.4 | 1352268 | 2020-05-04 | 5756 | 444 | 118223
23 | BMW DINGOLFING 2.4 | 1352323 | 2020-06-22 | 6262 | 534 | 126032
24 | FRONERI - FERENTINO | 1361965 | 2020-11-18 01:00 | 7229 | 305 | 126008
25 | TOM VILLE | 1364066 | 2020-09-25 | 0 | 14 | 123220
26 | ABINSK | 1386147 | 2020-12-11 | 8920 | 145 | 123269
27 | ABINSK | 1386177 | 2020-03-02 | 1845 | 55 | 130891
28 | ABINSK | 1386260 | 2020-07-13 | 6240 | 192 | 130893
29 | BLESSED TEXTILE | 1393153 | 2020-03-23 | 7315 | 243 | 129039
30 | Salmmeir 1 | 1415409 | 2020-10-21 | 6871 | 1011 | 133716
31 | Salmmeir 2 | 1415410 | 2020-10-02 | 6580 | 674 | 133858

## validation2
n | Validation Engine | serialNumber | val start | oph@start | starts@start | Asset ID
0 | POLYNT - 2 (1145166-T241) --> Sept | 1145166 | 2019-09-03 | 0 | 0 | 103791
1 | REGENSBURG | 1175579 | 2019-04-08 | 0 | 0 | 106622
2 | ROCHE PENZBERG KWKK | 1184199 | 2019-01-09 | 0 | 0 | 108532
3 | ECOGEN ENERGY SYSTEMS BVBA | 1198719 | 2016-12-22 | 0 | 0 | 110311
4 | BMW REGENSBURG M3 | 1243360 | 2019-10-11 | 0 | 0 | 157181
5 | REGENSBURG | 1243362 | 2019-09-16 | 0 | 0 | 157701
6 | ABINSK | 1250575 | 2019-09-03 | 0 | 0 | 156120
7 | PROSPERITY WEAVING MILLS LTD - 1 (1351388-X243) | 1250578 | 2019-09-03 | 0 | 0 | 158705
8 | SOTERNIX RENOVE | 1310773 | 2019-01-09 | 0 | 0 | 109063
9 | BMW MÜNCHEN | 1319133 | 2019-10-10 | 0 | 0 | 126399
10 | BMW MÜNCHEN | 1319138 | 2012-10-28 | 0 | 0 | 126449
11 | BMW MÜNCHEN | 1319151 | 2019-09-16 | 0 | 0 | 126448
12 | BMW MÜNCHEN | 1319157 | 2020-08-25 | 0 | 0 | 126402
13 | BMW MÜNCHEN | 1319997 | 2019-09-16 | 0 | 0 | 117598
14 | BMW MÜNCHEN | 1320022 | 2020-01-01 | 0 | 0 | 117551
15 | BMW MÜNCHEN | 1320030 | 2020-01-01 | 0 | 0 | 117550
16 | BMW LANDSHUT 4.10 | 1320072 | 2020-08-25 | 0 | 0 | 117617
17 | BMW LANDSHUT M1 | 1320090 | 2011-07-04 | 0 | 0 | 117510
18 | BMW LANDSHUT 4.10 | 1320114 | 2016-08-22 | 0 | 0 | 117547
19 | LES COURONNERIES | 1325927 | 2019-09-15 | 0 | 0 | 113808
20 | DALOMA | 1339812 | 2016-12-09 | 0 | 0 | 116255
21 | GAZ DE LACQ | 1345851 | 2018-10-15 | 0 | 0 | 117227
22 | BMW DINGOLFING 2.4 | 1352268 | 2017-03-31 | 0 | 0 | 118223
23 | BMW DINGOLFING 2.4 | 1352323 | 2018-10-31 | 0 | 0 | 126032
24 | FRONERI - FERENTINO | 1361965 | 2019-09-15 | 0 | 0 | 126008
25 | TOM VILLE | 1364066 | 2017-04-12 | 0 | 0 | 123220
26 | ABINSK | 1386147 | 2017-11-02 | 0 | 0 | 123269
27 | ABINSK | 1386177 | 2019-01-07 | 0 | 0 | 130891
28 | ABINSK | 1386260 | 0 | 0 | 0 | 130893
29 | BLESSED TEXTILE | 1393153 | 2019-07-19 | 0 | 0 | 129039
30 | Salmmeir 1 | 1415409 | 2018-11-23 | 0 | 0 | 133716
31 | Salmmeir 2 | 1415410 | 2019-09-03 | 0 | 0 | 133858

## failures
| Sum | 0 | 0
failurs |  |  | 4
f1 | 2020-12-17 08:15 | 0 | 6
f2 | 2021-01-26 08:15 | 0
f3 | 2020-11-26 08:15 | 0
f4 | 2020-08-25 08:15 | 0
f5 | 2021-04-30 08:15 | 0
f6 | 2021-07-01 08:15 | 0
f7
f8
f9
f10
f11
f12
f13
f14
f15
f16
f17
f18
f19
f20
f21
f22
f23
f24
f25

## ndReliaCalc2
| Data Date | 2020-12-27 08:15
| Val Start | 2020-02-07
| Val Period (days) | 324
| Beta (R2) | 1.21
|  |  |  | 2000h line | 2000 | 2000
[5 empty] | 2019-05-01 | 2021-12-31
|  |  |  | 6000h line | 6000 | 6000
[5 empty] | 2019-05-01 | 2021-12-31
[8 empty] | R1 failures | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | R2 failures | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | f1 | 2020-12-17 08:15 | 0 | 96.91% | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | f2 | 2021-01-26 08:15 | 0 | 109.3% | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | f3 | 2020-11-26 08:15 | 0 | 90.43% | 293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | f4 | 2020-08-25 08:15 | 0 | 61.73% | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | f5 | 2021-04-30 08:15 | 0 | 138.3% | 448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | f6 | 2021-07-01 08:15 | 0 | 157.4% | 510 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | f7 | 0 | 0 | -13540% | -43868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | f8 | 0 | 0 | -13540% | -43868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | f9 | 0 | 0 | -13540% | -43868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | f10 | 0 | 0 | -13540% | -43868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | f11 | 0 | 0 | -13540% | -43868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | f12 | 0 | 0 | -13540% | -43868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | f13 | 0 | 0 | -13540% | -43868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | f14 | 0 | 0 | -13540% | -43868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | f15 | 0 | 0 | -13540% | -43868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | f16 | 0 | 0 | -13540% | -43868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | f17 | 0 | 0 | -13540% | -43868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | f18 | 0 | 0 | -13540% | -43868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | f19 | 0 | 0 | -13540% | -43868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | f20 | 0 | 0 | -13540% | -43868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | f21 | 0 | 0 | -13540% | -43868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | f22 | 0 | 0 | -13540% | -43868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | f23 | 0 | 0 | -13540% | -43868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | f24 | 0 | 0 | -13540% | -43868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | f25 | 0 | 0 | -13540% | -43868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | Sum failures |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | Input |  |  | 0% | 3% | 8% | 15% | 20% | 25% | 30% | 35% | 40% | 45% | 50% | 55% | 60% | 65% | 70% | 75% | 80% | 85% | 90% | 95% | 100% | 105% | 110% | 115% | 120% | 125% | 130% | 135% | 140% | 145% | 150% | 155% | 160% | 165% | 170% | 175% | 180% | 185% | 190% | 195% | 200%
[6 empty] | calc % for diagram (failures) |  |  | 0% | 3% | 8% | 15% | 20% | 25% | 30% | 35% | 40% | 45% | 50% | 55% | 60% | 65% | 70% | 75% | 80% | 85% | 90% | 95% | 100% | 105% | 110% | 115% | 120% | 125% | 130% | 135% | 140% | 145% | 150% | 155% | 160% | 165% | 170% | 175% | 180% | 185% | 190% | 195% | 200%
[6 empty] | Val test Time % |  |  | 0% | 3% | 8% | 15% | 20% | 25% | 30% | 35% | 40% | 45% | 50% | 55% | 60% | 65% | 70% | 75% | 80% | 85% | 90% | 95% | 100% | 105% | 110% | 115% | 120% | 125% | 130% | 135% | 140% | 145% | 150% | 155% | 160% | 165% | 170% | 175% | 180% | 185% | 190% | 195% | 200%
[6 empty] | days |  |  | 0 | 9.72 | 25.92 | 48.6 | 64.8 | 81 | 97.2 | 113.4 | 129.6 | 145.8 | 162 | 178.2 | 194.4 | 210.6 | 226.8 | 243 | 259.2 | 275.4 | 291.6 | 307.8 | 324 | 340.2 | 356.4 | 372.6 | 388.8 | 405 | 421.2 | 437.4 | 453.6 | 469.8 | 486 | 502.2 | 518.4 | 534.6 | 550.8 | 567 | 583.2 | 599.4 | 615.6 | 631.8 | 648
[9 empty] | 0 | 1 |  | R Ref | 93.76% |  | R HRS | 6376
[8 empty] | today | 0% 0% 0%: 7776; 3% 3% 3%: 7776; 15% 15% 15%: 2020-12-27; 20% 20% 20%: 7776; 30% 30% 30%: 2020-12-27; 35% 35% 35%: 7776
[6 empty] | CLB 90% - 10% |  |  | 71.51% | 71.51% | 71.51% | 71.51% | 71.51% | 71.51% | 60.48% | 50.57% | 42.51% | 35.24% | 29.3% | 24.42% | 20.56% | 17.33% | 14.65% | 12.48% | 10.6% | 9.003% | 7.749% | 6.755% | 5.944% | 5.287% | 4.747% | 4.297% | 3.919% | 3.596% | 3.318% | 3.076% | 2.865% | 2.678% | 2.512% | 2.364% | 2.231% | 2.111% | 2.003% | 1.904% | 1.813% | 1.73% | 1.654% | 1.583% | 1.518%
[7 empty] | R | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97% | 97%
[7 empty] | R | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95% | 95%
[5 empty] | Weibull G3, b 0,97 | R | alpha | beta
[5 empty] | R | 85% | 195372 | 0.97 | 100% | 99.85% | 99.62% | 99.31% | 99.08% | 98.86% | 98.65% | 98.43% | 98.21% | 98% | 97.79% | 97.57% | 97.36% | 97.15% | 96.95% | 96.74% | 96.53% | 96.32% | 96.12% | 95.91% | 95.71% | 95.51% | 95.3% | 95.1% | 94.9% | 94.7% | 94.5% | 94.3% | 94.1% | 93.91% | 93.71% | 93.51% | 93.32% | 93.12% | 92.93% | 92.73% | 92.54% | 92.35% | 92.15% | 91.96% | 91.77%
[5 empty] | Weibull, b = 1,21 | R | alpha | beta
[5 empty] | 30000 | 98.08% | 780418.137 | 1.21 | 100% | 99.99% | 99.98% | 99.96% | 99.95% | 99.93% | 99.91% | 99.89% | 99.88% | 99.86% | 99.84% | 99.82% | 99.8% | 99.78% | 99.75% | 99.73% | 99.71% | 99.69% | 99.67% | 99.64% | 99.62% | 99.6% | 99.58% | 99.55% | 99.53% | 99.51% | 99.48% | 99.46% | 99.43% | 99.41% | 99.38% | 99.36% | 99.33% | 99.31% | 99.28% | 99.26% | 99.23% | 99.21% | 99.18% | 99.15% | 99.13%
[5 empty] | R1 | 30000 | 50% | 1.21 |  | 5.827e-06% | 1.492% | 30.26% | 50.65% | 63.18% | 72.78% | 79.12% | 83.42% | 86.87% | 89.44% | 91.42% | 92.91% | 94.11% | 95.08% | 95.85% | 96.51% | 97.05% | 97.48% | 97.81% | 98.08% | 98.3% | 98.47% | 98.62% | 98.74% | 98.85% | 98.94% | 99.02% | 99.09% | 99.15% | 99.2% | 99.25% | 99.29% | 99.33% | 99.36% | 99.39% | 99.42% | 99.45% | 99.47% | 99.5% | 99.52%
[5 empty] | R2 | 30000 | 90% | 1.21 |  | 9.273e-23% | 8.585e-05% | 1.885% | 10.44% | 21.75% | 34.81% | 45.94% | 54.77% | 62.65% | 69.02% | 74.22% | 78.33% | 81.75% | 84.58% | 86.88% | 88.86% | 90.54% | 91.86% | 92.91% | 93.76% | 94.45% | 95.02% | 95.49% | 95.89% | 96.23% | 96.52% | 96.77% | 97% | 97.19% | 97.37% | 97.52% | 97.66% | 97.79% | 97.9% | 98% | 98.1% | 98.19% | 98.27% | 98.34% | 98.41%
[5 empty] | R3 | 30000 | 10% | 1.21 |  | 7.949% | 52.77% | 83.38% | 90.18% | 93.26% | 95.29% | 96.5% | 97.28% | 97.88% | 98.32% | 98.65% | 98.89% | 99.08% | 99.24% | 99.36% | 99.46% | 99.55% | 99.61% | 99.66% | 99.71% | 99.74% | 99.77% | 99.79% | 99.81% | 99.82% | 99.84% | 99.85% | 99.86% | 99.87% | 99.88% | 99.89% | 99.89% | 99.9% | 99.9% | 99.91% | 99.91% | 99.92% | 99.92% | 99.92% | 99.93%
[5 empty] | R4 | 30000 | 90% | 1.21 |  | 9.273e-23% | 8.585e-05% | 1.885% | 10.44% | 21.75% | 34.81% | 45.94% | 54.77% | 62.65% | 69.02% | 74.22% | 78.33% | 81.75% | 84.58% | 86.88% | 88.86% | 90.54% | 91.86% | 92.91% | 93.76% | 94.45% | 95.02% | 95.49% | 95.89% | 96.23% | 96.52% | 96.77% | 97% | 97.19% | 97.37% | 97.52% | 97.66% | 97.79% | 97.9% | 98% | 98.1% | 98.19% | 98.27% | 98.34% | 98.41%
[5 empty] | nL |  |  | 1.21 |  | 24 | 29.0182 | 47.7025 | 59.1931 | 66.931 | 77.5927 | 83.4231 | 88.1249 | 95.447 | 103.4923 | 112.5544 | 121.7201 | 132.1966 | 143.8705 | 156.0674 | 170.4082 | 186.9655 | 202.9361 | 218.0962 | 232.8296 | 246.5903 | 259.3278 | 271.1086 | 282.0138 | 292.1241 | 301.5148 | 310.2542 | 318.4037 | 326.0183 | 333.0849 | 339.1076 | 344.7484 | 350.0419 | 355.0184 | 359.7051 | 364.1264 | 368.3037 | 372.2565 | 376.0022 | 379.5566
[9 empty] | 0 | 233.28 | 622.08 | 1166.4 | 1555.2 | 1944 | 2332.8 | 2721.6 | 3110.4 | 3499.2 | 3888 | 4276.8 | 4665.6 | 5054.4 | 5443.2 | 5832 | 6220.8 | 6609.6 | 6998.4 | 7387.2 | 7776 | 8164.8 | 8553.6 | 8942.4 | 9331.2 | 9720 | 10108.8 | 10497.6 | 10886.4 | 11275.2 | 11664 | 12052.8 | 12441.6 | 12830.4 | 13219.2 | 13608 | 13996.8 | 14385.6 | 14774.4 | 15163.2 | 15552
[8 empty] | Date line | 0% 0% 0%: 0; 3% 3% 3%: 6376; 15% 15% 15%: Date; 20% 20% 20%: 6376; 35% 35% 35%: 2000; 40% 40% 40%: 2000; 45% 45% 45%: 2000; 55% 55% 55%: 6000; 60% 60% 60%: 6000; 65% 65% 65%: 6000
[9 empty] | 2020-12-27 | 2020-12-27 |  |  | 2020-12-27 |  |  |  | 2020-02-07 | 2021-11-16 |  |  | 2020-02-07 | 2021-11-16
Serial Number | Name | Engine ID | Val Start | Part hrs | parts | h / day | Engine | Version | 2020-02-07 | 2020-02-16 17:17 | 2020-03-03 22:05 | 2020-03-26 14:24 | 2020-04-11 19:12 | 2020-04-28 | 2020-05-14 04:48 | 2020-05-30 09:36 | 2020-06-15 14:24 | 2020-07-01 19:12 | 2020-07-18 | 2020-08-03 04:48 | 2020-08-19 09:36 | 2020-09-04 14:24 | 2020-09-20 19:12 | 2020-10-07 | 2020-10-23 04:48 | 2020-11-08 09:36 | 2020-11-24 14:24 | 2020-12-10 19:12 | 2020-12-27 | 2021-01-12 04:48 | 2021-01-28 09:36 | 2021-02-13 14:24 | 2021-03-01 19:12 | 2021-03-18 | 2021-04-03 04:48 | 2021-04-19 09:36 | 2021-05-05 14:24 | 2021-05-21 19:12 | 2021-06-07 | 2021-06-23 04:48 | 2021-07-09 09:36 | 2021-07-25 14:24 | 2021-08-10 19:12 | 2021-08-27 | 2021-09-12 04:48 | 2021-09-28 09:36 | 2021-10-14 14:24 | 2021-10-30 19:12 | 2021-11-16
1386177 | ABINSK | M09 | 2020-03-02 | 6376 | 24 | 21.2533 | 624 | H01 | 0 | 0 | 40.8064 | 522.832 | 867.136 | 1211.44 | 1555.744 | 1900.048 | 2244.352 | 2588.656 | 2932.96 | 3277.264 | 3621.568 | 3965.872 | 4310.176 | 4654.48 | 4998.784 | 5343.088 | 5687.392 | 6031.696 | 6376 | 6720.304 | 7064.608 | 7408.912 | 7753.216 | 8097.52 | 8441.824 | 8786.128 | 9130.432 | 9474.736 | 9819.04 | 10163.344 | 10507.648 | 10851.952 | 11196.256 | 11540.56 | 11884.864 | 12229.168 | 12573.472 | 12917.776 | 13262.08
1393153 | BLESSED TEXTILE | M01 | 2020-03-23 | 6213 | 20 | 22.2688 | 620 | J101 | 0 | 0 | 0 | 80.1677 | 440.9226 | 801.6774 | 1162.4323 | 1523.1871 | 1883.9419 | 2244.6968 | 2605.4516 | 2966.2065 | 3326.9613 | 3687.7161 | 4048.471 | 4409.2258 | 4769.9806 | 5130.7355 | 5491.4903 | 5852.2452 | 6213 | 6573.7548 | 6934.5097 | 7295.2645 | 7656.0194 | 8016.7742 | 8377.529 | 8738.2839 | 9099.0387 | 9459.7935 | 9820.5484 | 10181.3032 | 10542.0581 | 10902.8129 | 11263.5677 | 11624.3226 | 11985.0774 | 12345.8323 | 12706.5871 | 13067.3419 | 13428.0968
1320072 | BMW LANDSHUT 4.10 | M04 | 2020-02-07 | 5226 | 24 | 16.1296 | 624 | H01 | 0 | 156.78 | 418.08 | 783.9 | 1045.2 | 1306.5 | 1567.8 | 1829.1 | 2090.4 | 2351.7 | 2613 | 2874.3 | 3135.6 | 3396.9 | 3658.2 | 3919.5 | 4180.8 | 4442.1 | 4703.4 | 4964.7 | 5226 | 5487.3 | 5748.6 | 6009.9 | 6271.2 | 6532.5 | 6793.8 | 7055.1 | 7316.4 | 7577.7 | 7839 | 8100.3 | 8361.6 | 8622.9 | 8884.2 | 9145.5 | 9406.8 | 9668.1 | 9929.4 | 10190.7 | 10452
1184199 | ROCHE PENZBERG KWKK | M01 | 2020-04-27 | 5106 | 24 | 20.9262 | 624 | H02 | 0 | 0 | 0 | 0 | 0 | 20.9262 | 359.9311 | 698.9361 | 1037.941 | 1376.9459 | 1715.9508 | 2054.9557 | 2393.9607 | 2732.9656 | 3071.9705 | 3410.9754 | 3749.9803 | 4088.9852 | 4427.9902 | 4766.9951 | 5106 | 5445.0049 | 5784.0098 | 6123.0148 | 6462.0197 | 6801.0246 | 7140.0295 | 7479.0344 | 7818.0393 | 8157.0443 | 8496.0492 | 8835.0541 | 9174.059 | 9513.0639 | 9852.0689 | 10191.0738 | 10530.0787 | 10869.0836 | 11208.0885 | 11547.0934 | 11886.0984
1352268 | BMW DINGOLFING 2.4 | M06 | 2020-05-04 | 3740 | 24 | 15.7806 | 624 | H01 | 0 | 0 | 0 | 0 | 0 | 0 | 160.962 | 416.6076 | 672.2532 | 927.8987 | 1183.5443 | 1439.1899 | 1694.8354 | 1950.481 | 2206.1266 | 2461.7722 | 2717.4177 | 2973.0633 | 3228.7089 | 3484.3544 | 3740 | 3995.6456 | 4251.2911 | 4506.9367 | 4762.5823 | 5018.2278 | 5273.8734 | 5529.519 | 5785.1646 | 6040.8101 | 6296.4557 | 6552.1013 | 6807.7468 | 7063.3924 | 7319.038 | 7574.6835 | 7830.3291 | 8085.9747 | 8341.6203 | 8597.2658 | 8852.9114
1320022 | BMW MÜNCHEN | M01 | 2020-06-08 | 3536 | 24 | 17.505 | 624 | H01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133.0376 | 416.6178 | 700.198 | 983.7782 | 1267.3584 | 1550.9386 | 1834.5188 | 2118.099 | 2401.6792 | 2685.2594 | 2968.8396 | 3252.4198 | 3536 | 3819.5802 | 4103.1604 | 4386.7406 | 4670.3208 | 4953.901 | 5237.4812 | 5521.0614 | 5804.6416 | 6088.2218 | 6371.802 | 6655.3822 | 6938.9624 | 7222.5426 | 7506.1228 | 7789.703 | 8073.2832 | 8356.8634 | 8640.4436 | 8924.0238 | 9207.604
1250575 | ABINSK | M01 | 2020-06-15 | 3376 | 24 | 17.3128 | 624 | K01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3877 | 290.8554 | 571.3231 | 851.7908 | 1132.2585 | 1412.7262 | 1693.1938 | 1973.6615 | 2254.1292 | 2534.5969 | 2815.0646 | 3095.5323 | 3376 | 3656.4677 | 3936.9354 | 4217.4031 | 4497.8708 | 4778.3385 | 5058.8062 | 5339.2738 | 5619.7415 | 5900.2092 | 6180.6769 | 6461.1446 | 6741.6123 | 7022.08 | 7302.5477 | 7583.0154 | 7863.4831 | 8143.9508 | 8424.4185 | 8704.8862 | 8985.3538
1386260 | ABINSK | M10 | 2020-07-13 | 3320 | 24 | 19.8802 | 624 | H01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.4012 | 421.4611 | 743.521 | 1065.5808 | 1387.6407 | 1709.7006 | 2031.7605 | 2353.8204 | 2675.8802 | 2997.9401 | 3320 | 3642.0599 | 3964.1198 | 4286.1796 | 4608.2395 | 4930.2994 | 5252.3593 | 5574.4192 | 5896.479 | 6218.5389 | 6540.5988 | 6862.6587 | 7184.7186 | 7506.7784 | 7828.8383 | 8150.8982 | 8472.9581 | 8795.018 | 9117.0778 | 9439.1377 | 9761.1976
1320114 | BMW LANDSHUT 4.10 | M03 | 2020-02-24 | 2987 | 24 | 9.7296 | 624 | H01 | 0 | 0 | 86.7884 | 307.4567 | 465.0769 | 622.6971 | 780.3173 | 937.9375 | 1095.5577 | 1253.1779 | 1410.798 | 1568.4182 | 1726.0384 | 1883.6586 | 2041.2788 | 2198.899 | 2356.5192 | 2514.1394 | 2671.7596 | 2829.3798 | 2987 | 3144.6202 | 3302.2404 | 3459.8606 | 3617.4808 | 3775.101 | 3932.7212 | 4090.3414 | 4247.9616 | 4405.5818 | 4563.202 | 4720.8221 | 4878.4423 | 5036.0625 | 5193.6827 | 5351.3029 | 5508.9231 | 5666.5433 | 5824.1635 | 5981.7837 | 6139.4039
1352323 | BMW DINGOLFING 2.4 | M07 | 2020-06-22 | 3046 | 24 | 16.2021 | 624 | H01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158.7809 | 421.2553 | 683.7298 | 946.2043 | 1208.6787 | 1471.1532 | 1733.6277 | 1996.1021 | 2258.5766 | 2521.0511 | 2783.5255 | 3046 | 3308.4745 | 3570.9489 | 3833.4234 | 4095.8979 | 4358.3723 | 4620.8468 | 4883.3213 | 5145.7957 | 5408.2702 | 5670.7447 | 5933.2191 | 6195.6936 | 6458.1681 | 6720.6426 | 6983.117 | 7245.5915 | 7508.066 | 7770.5404 | 8033.0149 | 8295.4894
1243360 | BMW REGENSBURG M3 | M03 | 2020-08-17 | 2577 | 16 | 19.5227 | 616 | J01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46.8545 | 363.1227 | 679.3909 | 995.6591 | 1311.9273 | 1628.1955 | 1944.4636 | 2260.7318 | 2577 | 2893.2682 | 3209.5364 | 3525.8045 | 3842.0727 | 4158.3409 | 4474.6091 | 4790.8773 | 5107.1455 | 5423.4136 | 5739.6818 | 6055.95 | 6372.2182 | 6688.4864 | 7004.7545 | 7321.0227 | 7637.2909 | 7953.5591 | 8269.8273 | 8586.0955 | 8902.3636
1319997 | BMW MÜNCHEN | M02 | 2020-08-24 | 2519 | 24 | 20.152 | 624 | H01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233.7632 | 560.2256 | 886.688 | 1213.1504 | 1539.6128 | 1866.0752 | 2192.5376 | 2519 | 2845.4624 | 3171.9248 | 3498.3872 | 3824.8496 | 4151.312 | 4477.7744 | 4804.2368 | 5130.6992 | 5457.1616 | 5783.624 | 6110.0864 | 6436.5488 | 6763.0112 | 7089.4736 | 7415.936 | 7742.3984 | 8068.8608 | 8395.3232 | 8721.7856 | 9048.248
1319151 | BMW MÜNCHEN | M01 | 2020-07-06 | 2319 | 20 | 13.3276 | 620 | F01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159.931 | 375.8379 | 591.7448 | 807.6517 | 1023.5586 | 1239.4655 | 1455.3724 | 1671.2793 | 1887.1862 | 2103.0931 | 2319 | 2534.9069 | 2750.8138 | 2966.7207 | 3182.6276 | 3398.5345 | 3614.4414 | 3830.3483 | 4046.2552 | 4262.1621 | 4478.069 | 4693.9759 | 4909.8828 | 5125.7897 | 5341.6966 | 5557.6034 | 5773.5103 | 5989.4172 | 6205.3241 | 6421.231 | 6637.1379
1320030 | BMW MÜNCHEN | M03 | 2020-08-03 | 2163 | 24 | 14.8151 | 624 | H01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.963 | 242.9671 | 482.9712 | 722.9753 | 962.9795 | 1202.9836 | 1442.9877 | 1682.9918 | 1922.9959 | 2163 | 2403.0041 | 2643.0082 | 2883.0123 | 3123.0164 | 3363.0205 | 3603.0247 | 3843.0288 | 4083.0329 | 4323.037 | 4563.0411 | 4803.0452 | 5043.0493 | 5283.0534 | 5523.0575 | 5763.0616 | 6003.0658 | 6243.0699 | 6483.074 | 6723.0781 | 6963.0822
1319138 | BMW MÜNCHEN | M02 | 2020-07-20 | 2135 | 20 | 13.3438 | 620 | F01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189.4813 | 405.65 | 621.8187 | 837.9875 | 1054.1562 | 1270.325 | 1486.4937 | 1702.6625 | 1918.8312 | 2135 | 2351.1687 | 2567.3375 | 2783.5062 | 2999.675 | 3215.8438 | 3432.0125 | 3648.1813 | 3864.35 | 4080.5188 | 4296.6875 | 4512.8562 | 4729.025 | 4945.1938 | 5161.3625 | 5377.5312 | 5593.7 | 5809.8687 | 6026.0375 | 6242.2062 | 6458.375
1319157 | BMW MÜNCHEN | M03 | 2020-08-17 | 2046 | 20 | 15.5 | 620 | F01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.2 | 288.3 | 539.4 | 790.5 | 1041.6 | 1292.7 | 1543.8 | 1794.9 | 2046 | 2297.1 | 2548.2 | 2799.3 | 3050.4 | 3301.5 | 3552.6 | 3803.7 | 4054.8 | 4305.9 | 4557 | 4808.1 | 5059.2 | 5310.3 | 5561.4 | 5812.5 | 6063.6 | 6314.7 | 6565.8 | 6816.9 | 7068
1319133 | BMW MÜNCHEN | M04 | 2020-08-31 | 1896 | 20 | 16.0678 | 620 | F01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.9119 | 334.2102 | 594.5085 | 854.8068 | 1115.1051 | 1375.4034 | 1635.7017 | 1896 | 2156.2983 | 2416.5966 | 2676.8949 | 2937.1932 | 3197.4915 | 3457.7898 | 3718.0881 | 3978.3864 | 4238.6847 | 4498.9831 | 4759.2814 | 5019.5797 | 5279.878 | 5540.1763 | 5800.4746 | 6060.7729 | 6321.0712 | 6581.3695 | 6841.6678 | 7101.9661
1243362 | REGENSBURG | M02 | 2020-09-07 | 1961 | 16 | 17.6667 | 616 | J01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243.8 | 530 | 816.2 | 1102.4 | 1388.6 | 1674.8 | 1961 | 2247.2 | 2533.4 | 2819.6 | 3105.8 | 3392 | 3678.2 | 3964.4 | 4250.6 | 4536.8 | 4823 | 5109.2 | 5395.4 | 5681.6 | 5967.8 | 6254 | 6540.2 | 6826.4 | 7112.6 | 7398.8 | 7685
1175579 | REGENSBURG | M05 | 2020-09-14 | 1886 | 16 | 18.1346 | 616 | F01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.3154 | 417.0962 | 710.8769 | 1004.6577 | 1298.4385 | 1592.2192 | 1886 | 2179.7808 | 2473.5615 | 2767.3423 | 3061.1231 | 3354.9038 | 3648.6846 | 3942.4654 | 4236.2462 | 4530.0269 | 4823.8077 | 5117.5885 | 5411.3692 | 5705.15 | 5998.9308 | 6292.7115 | 6586.4923 | 6880.2731 | 7174.0538 | 7467.8346 | 7761.6154
1415410 | Salmmeir 2 | M02 | 2020-10-02 | 1825 | 24 | 21.2209 | 624 | K01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.1047 | 449.8837 | 793.6628 | 1137.4419 | 1481.2209 | 1825 | 2168.7791 | 2512.5581 | 2856.3372 | 3200.1163 | 3543.8953 | 3887.6744 | 4231.4535 | 4575.2326 | 4919.0116 | 5262.7907 | 5606.5698 | 5950.3488 | 6294.1279 | 6637.907 | 6981.686 | 7325.4651 | 7669.2442 | 8013.0233 | 8356.8023 | 8700.5814
1145166 | POLYNT - 2 (1145166-T241) --> Sept | M02 | 2020-10-12 | 1739 | 24 | 22.8816 | 624 | H01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256.2737 | 626.9553 | 997.6368 | 1368.3184 | 1739 | 2109.6816 | 2480.3632 | 2851.0447 | 3221.7263 | 3592.4079 | 3963.0895 | 4333.7711 | 4704.4526 | 5075.1342 | 5445.8158 | 5816.4974 | 6187.1789 | 6557.8605 | 6928.5421 | 7299.2237 | 7669.9053 | 8040.5868 | 8411.2684 | 8781.95 | 9152.6316
1250578 | PROSPERITY WEAVING MILLS LTD - 1 (1351388-X243) | M01 | 2020-10-12 | 1723 | 24 | 22.6711 | 624 | K505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.9158 | 621.1868 | 988.4579 | 1355.7289 | 1723 | 2090.2711 | 2457.5421 | 2824.8132 | 3192.0842 | 3559.3553 | 3926.6263 | 4293.8974 | 4661.1684 | 5028.4395 | 5395.7105 | 5762.9816 | 6130.2526 | 6497.5237 | 6864.7947 | 7232.0658 | 7599.3368 | 7966.6079 | 8333.8789 | 8701.15 | 9068.4211
1198719 | ECOGEN ENERGY SYSTEMS BVBA | M02 | 2020-10-15 | 1658 | 16 | 22.7123 | 616 | F12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186.2411 | 554.1808 | 922.1205 | 1290.0603 | 1658 | 2025.9397 | 2393.8795 | 2761.8192 | 3129.7589 | 3497.6986 | 3865.6384 | 4233.5781 | 4601.5178 | 4969.4575 | 5337.3973 | 5705.337 | 6073.2767 | 6441.2164 | 6809.1562 | 7177.0959 | 7545.0356 | 7912.9753 | 8280.9151 | 8648.8548 | 9016.7945
1345851 | GAZ DE LACQ | M03 | 2020-10-22 | 1540 | 16 | 23.3333 | 616 | J12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 406 | 784 | 1162 | 1540 | 1918 | 2296 | 2674 | 3052 | 3430 | 3808 | 4186 | 4564 | 4942 | 5320 | 5698 | 6076 | 6454 | 6832 | 7210 | 7588 | 7966 | 8344 | 8722 | 9100
1415409 | Salmmeir 1 | M01 | 2020-10-21 | 1435 | 24 | 21.4179 | 624 | K01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47.1194 | 394.0896 | 741.0597 | 1088.0299 | 1435 | 1781.9701 | 2128.9403 | 2475.9104 | 2822.8806 | 3169.8507 | 3516.8209 | 3863.791 | 4210.7612 | 4557.7313 | 4904.7015 | 5251.6716 | 5598.6418 | 5945.6119 | 6292.5821 | 6639.5522 | 6986.5224 | 7333.4925 | 7680.4627 | 8027.4328 | 8374.403
1310773 | SOTERNIX RENOVE | M01 | 2020-09-25 | 1292 | 16 | 13.8925 | 616 | F11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166.7097 | 391.7677 | 616.8258 | 841.8839 | 1066.9419 | 1292 | 1517.0581 | 1742.1161 | 1967.1742 | 2192.2323 | 2417.2903 | 2642.3484 | 2867.4065 | 3092.4645 | 3317.5226 | 3542.5806 | 3767.6387 | 3992.6968 | 4217.7548 | 4442.8129 | 4667.871 | 4892.929 | 5117.9871 | 5343.0452 | 5568.1032 | 5793.1613
1325927 | LES COURONNERIES | M01 | 2020-09-09 | 1361 | 24 | 12.4862 | 624 | H12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147.3376 | 349.6147 | 551.8917 | 754.1688 | 956.4459 | 1158.7229 | 1361 | 1563.2771 | 1765.5541 | 1967.8312 | 2170.1083 | 2372.3853 | 2574.6624 | 2776.9394 | 2979.2165 | 3181.4936 | 3383.7706 | 3586.0477 | 3788.3248 | 3990.6018 | 4192.8789 | 4395.156 | 4597.433 | 4799.7101 | 5001.9872 | 5204.2642 | 5406.5413
1320090 | BMW LANDSHUT M1 | M01 | 2020-10-12 | 1148 | 24 | 15.1053 | 624 | H01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169.1789 | 413.8842 | 658.5895 | 903.2947 | 1148 | 1392.7053 | 1637.4105 | 1882.1158 | 2126.8211 | 2371.5263 | 2616.2316 | 2860.9368 | 3105.6421 | 3350.3474 | 3595.0526 | 3839.7579 | 4084.4632 | 4329.1684 | 4573.8737 | 4818.5789 | 5063.2842 | 5307.9895 | 5552.6947 | 5797.4 | 6042.1053
1364066 | TOM VILLE | M01 | 2020-09-25 | 780 | 20 | 8.3871 | 620 | J12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.6452 | 236.5161 | 372.3871 | 508.2581 | 644.129 | 780 | 915.871 | 1051.7419 | 1187.6129 | 1323.4839 | 1459.3548 | 1595.2258 | 1731.0968 | 1866.9677 | 2002.8387 | 2138.7097 | 2274.5806 | 2410.4516 | 2546.3226 | 2682.1935 | 2818.0645 | 2953.9355 | 3089.8065 | 3225.6774 | 3361.5484 | 3497.4194
1361965 | FRONERI - FERENTINO | M01 | 2020-11-18 01:00 | 774 | 16 | 19.8462 | 616 | J11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130.9846 | 452.4923 | 774 | 1095.5077 | 1417.0154 | 1738.5231 | 2060.0308 | 2381.5385 | 2703.0462 | 3024.5538 | 3346.0615 | 3667.5692 | 3989.0769 | 4310.5846 | 4632.0923 | 4953.6 | 5275.1077 | 5596.6154 | 5918.1231 | 6239.6308 | 6561.1385 | 6882.6462 | 7204.1538
1339812 | DALOMA | M01 | 2020-11-02 | 630 | 12 | 11.4545 | 612 | J12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.3091 | 258.8727 | 444.4364 | 630 | 815.5636 | 1001.1273 | 1186.6909 | 1372.2545 | 1557.8182 | 1743.3818 | 1928.9455 | 2114.5091 | 2300.0727 | 2485.6364 | 2671.2 | 2856.7636 | 3042.3273 | 3227.8909 | 3413.4545 | 3599.0182 | 3784.5818 | 3970.1455 | 4155.7091 | 4341.2727
1386147 | ABINSK | M06 | 2020-12-11 | 353 | 24 | 22.0625 | 624 | H01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 710.4125 | 1067.825 | 1425.2375 | 1782.65 | 2140.0625 | 2497.475 | 2854.8875 | 3212.3 | 3569.7125 | 3927.125 | 4284.5375 | 4641.95 | 4999.3625 | 5356.775 | 5714.1875 | 6071.6 | 6429.0125 | 6786.425 | 7143.8375 | 7501.25
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## dictionary
conversion table |  | properties reference |  |  | properties raw |  |  | dataItems reference |  |  | dataItems raw
name | shortname | id | name | shortname |  |  |  | id | name | shortname
IB ItemNumber Engine | Serial Number | id | Name | name |  | name | id | id | name | name |  | name | unit | id
RMD_ListAvgCCP_CCPSensor | Crankcase Pressure | 62 | Application Type | Application Type | 0 | Application Type | 62 | 13051 | Activation Status | Activation Status | 0 | Activation Status | . | 13051
RMD_ListBuffMAvgOilDiffPress_OilDiffPress | DP Oilfilter | 20 | Asset Type | Asset Type | 1 | Asset Type | 20 | 1040109 | AGG_AssetAvailability | AGG_AssetAvailability | 1 | AGG_AssetAvailability | % | 1040109
RMD_ListBuffMAvgOilConsume_OilConsumption | LOC Avg | 1397 | AssetStatusOracle | AssetStatusOracle | 2 | AssetStatusOracle | 1397 | 1040110 | AGG_AssetPerformanceRate | AGG_AssetPerformanceRate | 2 | AGG_AssetPerformanceRate | % | 1040110
opd/day | opd / day | 1106 | Catalyst Model | Catalyst Model | 3 | Catalyst Model | 1106 | 1040111 | AGG_AssetReliabilityRate | AGG_AssetReliabilityRate | 3 | AGG_AssetReliabilityRate | % | 1040111
Count_OpHour | oph | 19 | Commissioning Date | Commissioning Date | 4 | Commissioning Date | 19 | 19884 | asset_status | asset_status | 4 | asset_status |  | 19884
oph/start | oph / start | 1108 | Contract Organization Unit | Contract Organization Unit | 5 | Contract Organization Unit | 1108 | 10009029 | ATD1 | ATD1 | 5 | ATD1 |  | 10009029
Power_PowerAct | P Act | 1312 | Contract.Service Contract End Counter | Contract.Service Contract End Counter | 6 | Contract.Service Contract End Counter | 1312 | 10009028 | ATD2 | ATD2 | 6 | ATD2 |  | 10009028
Count_Start | Starts | 24 | Contract.Service Contract End Date | Contract.Service Contract End Date | 7 | Contract.Service Contract End Date | 24 | 127 | Aux_CH4Cont | Aux_CH4Cont | 7 | Aux_CH4Cont | % | 127
Para_Leanox_Comp_ITPPower1 | Power SetVal | 1448 | Contract.Service Contract Start Counter | Contract.Service Contract Start Counter | 8 | Contract.Service Contract Start Counter | 1448 | 111 | Aux_GasPress | Q Gas P | 8 | Aux_GasPress | mbar | 111
Various_Values_SpeedAct | N Act | 444 | Contract.Service Contract Start Date | Contract.Service Contract Start Date | 9 | Contract.Service Contract Start Date | 444 | 20287 | Aux_GasRail_rDPr_SetAct | Aux_GasRail_rDPr_SetAct | 9 | Aux_GasRail_rDPr_SetAct |  | 20287
Various_Values_TempMixture | T2' | 23 | Contract.Service Contract Type | Contract.Service Contract Type | 10 | Contract.Service Contract Type | 23 | 20284 | Aux_GasRail_rPr_a_Filt | Aux_GasRail_rPr_a_Filt | 10 | Aux_GasRail_rPr_a_Filt |  | 20284
Various_Values_PressBoost | P2' | 18 | Contract.Warranty End Date | Contract.Warranty End Date | 11 | Contract.Warranty End Date | 18 | 20286 | Aux_GasRail_rPr_Out_Calc | Aux_GasRail_rPr_Out_Calc | 11 | Aux_GasRail_rPr_Out_Calc |  | 20286
TecJet_Lambda1 | LambdaTJ | 443 | Contract.Warranty Start Date | Contract.Warranty Start Date | 12 | Contract.Warranty Start Date | 443 | 20285 | Aux_GasRail_rPr_sp | Aux_GasRail_rPr_sp | 12 | Aux_GasRail_rPr_sp |  | 20285
TecJet_GasTemp1 | TJ Gas T | 342 | Contract.Warranty Type | Contract.Warranty Type | 13 | Contract.Warranty Type | 342 | 199 | Aux_GasTemp | Q Gas T | 13 | Aux_GasTemp | C | 199
TecJet_GasPress1 | TJ Gas P | 17 | Control System Type | Control System Type | 14 | Control System Type | 17 | 197 | Aux_GasVol | Q Gas B/N | 14 | Aux_GasVol | m3/h | 197
TecJet_GasFlow1 | TJ Gas Flow | 16 | Country | Country | 15 | Country | 16 | 213 | Aux_O2Cont | Aux_O2Cont | 15 | Aux_O2Cont | % | 213
TecJet_ValvePos1 | TJ pos | 1311 | CSA Region | CSA Region | 16 | CSA Region | 1311 | 112 | Aux_PreChambDifPress | Aux_PreChambDifPress | 16 | Aux_PreChambDifPress | mbar | 112
TecJet_GasDiffPress | TJ Gas DP | 15 | Customer Engine Number | Customer Engine Number | 17 | Customer Engine Number | 15 | 20290 | Aux_PreChambGasTrain_rDPr_SetAct | Aux_PreChambGasTrain_rDPr_SetAct | 17 | Aux_PreChambGasTrain_rDPr_SetAct |  | 20290
Power_RedPowerAct | P red Act | 21 | Design Number | Design Number | 18 | Design Number | 21 | 20291 | Aux_PreChambGasTrain_rPr_a_Filt | Aux_PreChambGasTrain_rPr_a_Filt | 18 | Aux_PreChambGasTrain_rPr_a_Filt |  | 20291
Power_PowerNominal | P nom | 1337 | End Customer | End Customer | 19 | End Customer | 1337 | 20288 | Aux_PreChambGasTrain_rPr_Out | Aux_PreChambGasTrain_rPr_Out | 19 | Aux_PreChambGasTrain_rPr_Out |  | 20288
OperationalCondition | Status | 643 | Engine ID | Engine ID | 20 | Engine ID | 643 | 20289 | Aux_PreChambGasTrain_rPr_sp | Aux_PreChambGasTrain_rPr_sp | 20 | Aux_PreChambGasTrain_rPr_sp | bar | 20289
Para_Speed_Nominal | N nom | 13 | Engine Series | Engine Series | 21 | Engine Series | 13 | 202 | Aux_PreChambGasTrainPress | Aux_PreChambGasTrainPress | 21 | Aux_PreChambGasTrainPress | bar | 202
Various_Values_PosTurboBypass | BP pos | 12 | Engine Type | Engine Type | 22 | Engine Type | 12 | 21 | Aux_RoomTemp | Aux_RoomTemp | 22 | Aux_RoomTemp | °C | 21
Various_Values_PosThrottle | DK pos | 11 | Engine Version | Engine Version | 23 | Engine Version | 11 | 20292 | Aux_rPr_Baro | Aux_rPr_Baro | 23 | Aux_rPr_Baro | bar | 20292
Various_EngineStatus | Status No | 623 | EngineSerialNumberOracle | EngineSerialNumberOracle | 24 | EngineSerialNumberOracle | 623 | 19284 | Aux_StarterPressInlet | Aux_StarterPressInlet | 24 | Aux_StarterPressInlet | bar | 19284
Various_Bits_OperationOn | OP on | 1107 | Exhaust After-Treatment System Model | Exhaust After-Treatment System Model | 25 | Exhaust After-Treatment System Model | 1107 | 19285 | Aux_StarterPressTank | Aux_StarterPressTank | 25 | Aux_StarterPressTank | bar | 19285
Various_Bits_GenSwitchOn | OP Switch on | 1344 | Field Validation - Additional Details | Field Validation - Additional Details | 26 | Field Validation - Additional Details | 1344 | 19286 | Aux_StarterSpeed | Aux_StarterSpeed | 26 | Aux_StarterSpeed | 1/min | 19286
synchronization_bmcb_on | OP NetP | 1342 | Field Validation - Contact Person | Field Validation - Contact Person | 27 | Field Validation - Contact Person | 1342 | 219 | Aux_SucPress | Aux_SucPress | 27 | Aux_SucPress | mbar | 219
Various_Bits_CollWarning | Wanrning ? | 1341 | Field Validation - Description | Field Validation - Description | 28 | Field Validation - Description | 1341 | 16587 | Aux_TempOutDoor | Aux_TempOutDoor | 28 | Aux_TempOutDoor | °C | 16587
Various_Bits_CollAlarm | Alarm ? | 1340 | Field Validation - Flag | Field Validation - Flag | 29 | Field Validation - Flag | 1340 | 10049859 | auxiliariesgeneral_rdpr_ofu_filt | auxiliariesgeneral_rdpr_ofu_filt | 29 | auxiliariesgeneral_rdpr_ofu_filt |  | 10049859
t_ch_t1hp_a | T11 A | 1343 | Field Validation - Start Date | Field Validation - Start Date | 30 | Field Validation - Start Date | 1343 | 10049862 | auxiliariesgeneral_reo_level | auxiliariesgeneral_reo_level | 30 | auxiliariesgeneral_reo_level |  | 10049862
t_ch_t1hp_b | T11 B | 10 | Gas Type | Gas Type | 31 | Gas Type | 10 | 10049863 | auxiliariesgeneral_rpr_eo_diff_f | auxiliariesgeneral_rpr_eo_diff_f | 31 | auxiliariesgeneral_rpr_eo_diff_f |  | 10049863
pr_ch_p1hp_a | P11 A | 9 | Gas Type2 | Gas Type2 | 32 | Gas Type2 | 9 | 10049864 | auxiliariesgeneral_rpr_eoap | auxiliariesgeneral_rpr_eoap | 32 | auxiliariesgeneral_rpr_eoap | bar | 10049864
pr_ch_p1hp_b | P11 B | 8 | Generator Model | Generator Model | 33 | Generator Model | 8 | 10049865 | auxiliariesgeneral_rpr_eof_diffmon | auxiliariesgeneral_rpr_eof_diffmon | 33 | auxiliariesgeneral_rpr_eof_diffmon |  | 10049865
SlowDownTime00 | Slow Down Time | 7 | Generator Serial Number | Generator Serial Number | 34 | Generator Serial Number | 7 | 10049860 | auxiliariesgeneral_rpr_ofuafilt | auxiliariesgeneral_rpr_ofuafilt | 34 | auxiliariesgeneral_rpr_ofuafilt |  | 10049860
safi_win3_1 | Safi W3 Z1 | 727 | IB Alternator Item Number | IB Alternator Item Number | 35 | IB Alternator Item Number | 727 | 10049861 | auxiliariesgeneral_rpr_ofubcentrifuge | auxiliariesgeneral_rpr_ofubcentrifuge | 35 | auxiliariesgeneral_rpr_ofubcentrifuge |  | 10049861
safi_win3_2 | Safi W3 Z2 | 719 | IB Alternator Manufacturer | IB Alternator Manufacturer | 36 | IB Alternator Manufacturer | 719 | 10049858 | auxiliariesgeneral_rpr_ofubfilt | auxiliariesgeneral_rpr_ofubfilt | 36 | auxiliariesgeneral_rpr_ofubfilt |  | 10049858
safi_win3_3 | Safi W3 Z3 | 728 | IB Cat2 | IB Cat2 | 37 | IB Cat2 | 728 | 20643 | BaseProg_Vers | BaseProg_Vers | 37 | BaseProg_Vers | float | 20643
safi_win3_4 | Safi W3 Z4 | 732 | IB City | IB City | 38 | IB City | 732 | 1000081 | BBFRULABS_RUL | BBFRULABS_RUL | 38 | BBFRULABS_RUL | oph | 1000081
safi_win3_5 | Safi W3 Z5 | 721 | IB Control Software | IB Control Software | 39 | IB Control Software | 721 | 19109 | Bear_Conrod_Temp01 | Bear_Conrod_Temp01 | 39 | Bear_Conrod_Temp01 | °C | 19109
safi_win3_6 | Safi W3 Z6 | 1356 | IB Customer Service Manager | IB Customer Service Manager | 40 | IB Customer Service Manager | 1356 | 19110 | Bear_Conrod_Temp02 | Bear_Conrod_Temp02 | 40 | Bear_Conrod_Temp02 | °C | 19110
safi_win3_7 | Safi W3 Z7 | 729 | IB Distribution Channel | IB Distribution Channel | 41 | IB Distribution Channel | 729 | 19111 | Bear_Conrod_Temp03 | Bear_Conrod_Temp03 | 41 | Bear_Conrod_Temp03 | °C | 19111
safi_win3_8 | Safi W3 Z8 | 730 | IB Frequency | IB Frequency | 42 | IB Frequency | 730 | 19112 | Bear_Conrod_Temp04 | Bear_Conrod_Temp04 | 42 | Bear_Conrod_Temp04 | °C | 19112
safi_win3_9 | Safi W3 Z9 | 731 | IB HQ Duns Number | IB HQ Duns Number | 43 | IB HQ Duns Number | 731 | 19113 | Bear_Conrod_Temp05 | Bear_Conrod_Temp05 | 43 | Bear_Conrod_Temp05 | °C | 19113
safi_win3_10 | Safi W3 Z10 | 736 | IB Item Description Engine | IB Item Description Engine | 44 | IB Item Description Engine | 736 | 19114 | Bear_Conrod_Temp06 | Bear_Conrod_Temp06 | 44 | Bear_Conrod_Temp06 | °C | 19114
safi_win3_11 | Safi W3 Z11 | 737 | IB ItemInstance Unit | IB ItemInstance Unit | 45 | IB ItemInstance Unit | 737 | 19115 | Bear_Conrod_Temp07 | Bear_Conrod_Temp07 | 45 | Bear_Conrod_Temp07 | °C | 19115
safi_win3_12 | Safi W3 Z12 | 738 | IB ItemNumber Engine | Serial Number | 46 | IB ItemNumber Engine | 738 | 19116 | Bear_Conrod_Temp08 | Bear_Conrod_Temp08 | 46 | Bear_Conrod_Temp08 | °C | 19116
safi_win3_13 | Safi W3 Z13 | 744 | IB ItemNumber Unit | IB ItemNumber Unit | 47 | IB ItemNumber Unit | 744 | 19117 | Bear_Conrod_Temp09 | Bear_Conrod_Temp09 | 47 | Bear_Conrod_Temp09 | °C | 19117
safi_win3_14 | Safi W3 Z14 | 739 | IB Leanox | IB Leanox | 48 | IB Leanox | 739 | 19118 | Bear_Conrod_Temp10 | Bear_Conrod_Temp10 | 48 | Bear_Conrod_Temp10 | °C | 19118
safi_win3_15 | Safi W3 Z15 | 718 | IB NOX | IB NOX | 49 | IB NOX | 718 | 19119 | Bear_Conrod_Temp11 | Bear_Conrod_Temp11 | 49 | Bear_Conrod_Temp11 | °C | 19119
safi_win3_16 | Safi W3 Z16 | 740 | IB Operating Unit | IB Operating Unit | 50 | IB Operating Unit | 740 | 19120 | Bear_Conrod_Temp12 | Bear_Conrod_Temp12 | 50 | Bear_Conrod_Temp12 | °C | 19120
safi_win3_17 | Safi W3 Z17 | 746 | IB Party Name Owner | IB Party Name Owner | 51 | IB Party Name Owner | 746 | 19121 | Bear_Conrod_Temp13 | Bear_Conrod_Temp13 | 51 | Bear_Conrod_Temp13 | °C | 19121
safi_win3_18 | Safi W3 Z18 | 733 | IB Postal code | IB Postal code | 52 | IB Postal code | 733 | 19122 | Bear_Conrod_Temp14 | Bear_Conrod_Temp14 | 52 | Bear_Conrod_Temp14 | °C | 19122
safi_win3_19 | Safi W3 Z19 | 783 | IB Project Name | IB Project Name | 53 | IB Project Name | 783 | 19123 | Bear_Conrod_Temp15 | Bear_Conrod_Temp15 | 53 | Bear_Conrod_Temp15 | °C | 19123
safi_win3_20 | Safi W3 Z20 | 734 | IB Region | IB Region | 54 | IB Region | 734 | 19124 | Bear_Conrod_Temp16 | Bear_Conrod_Temp16 | 54 | Bear_Conrod_Temp16 | °C | 19124
safi_win3_21 | Safi W3 Z21 | 741 | IB Service Region | IB Service Region | 55 | IB Service Region | 741 | 19125 | Bear_Conrod_Temp17 | Bear_Conrod_Temp17 | 55 | Bear_Conrod_Temp17 | °C | 19125
safi_win3_22 | Safi W3 Z22 | 1457 | IB Site Customer Name | IB Site Customer Name | 56 | IB Site Customer Name | 1457 | 19126 | Bear_Conrod_Temp18 | Bear_Conrod_Temp18 | 56 | Bear_Conrod_Temp18 | °C | 19126
safi_win3_23 | Safi W3 Z23 | 742 | IB Site Name | IB Site Name | 57 | IB Site Name | 742 | 19127 | Bear_Conrod_Temp19 | Bear_Conrod_Temp19 | 57 | Bear_Conrod_Temp19 | °C | 19127
safi_win3_24 | Safi W3 Z24 | 743 | IB Status | IB Status | 58 | IB Status | 743 | 19128 | Bear_Conrod_Temp20 | Bear_Conrod_Temp20 | 58 | Bear_Conrod_Temp20 | °C | 19128
safi_win4_1 | Safi W4 Z1 | 717 | IB Unit Commissioning Date | Orig Commissioning | 59 | IB Unit Commissioning Date | 717 | 19129 | Bear_Conrod_Temp21 | Bear_Conrod_Temp21 | 59 | Bear_Conrod_Temp21 | °C | 19129
safi_win4_2 | Safi W4 Z2 | 745 | IB Unit Item Instance Type2 | IB Unit Item Instance Type2 | 60 | IB Unit Item Instance Type2 | 745 | 19130 | Bear_Conrod_Temp22 | Bear_Conrod_Temp22 | 60 | Bear_Conrod_Temp22 | °C | 19130
safi_win4_3 | Safi W4 Z3 | 543 | Party Number Owner | Party Number Owner | 61 | Party Number Owner | 543 | 19131 | Bear_Conrod_Temp23 | Bear_Conrod_Temp23 | 61 | Bear_Conrod_Temp23 | °C | 19131
safi_win4_4 | Safi W4 Z4 | 142 | Piston Type | Piston Type | 62 | Piston Type | 142 | 19132 | Bear_Conrod_Temp24 | Bear_Conrod_Temp24 | 62 | Bear_Conrod_Temp24 | °C | 19132
safi_win4_5 | Safi W4 Z5 | 684 | PM Schedule Category | PM Schedule Category | 63 | PM Schedule Category | 684 | 19944 | Bear_Conrod_TempMax | Bear_Conrod_TempMax | 63 | Bear_Conrod_TempMax | °C | 19944
safi_win4_6 | Safi W4 Z6 | 1101 | Product Program | Product Program | 64 | Product Program | 1101 | 19287 | Bear_Main_Temp01 | Bear_Main_Temp01 | 64 | Bear_Main_Temp01 | °C | 19287
safi_win4_7 | Safi W4 Z7 | 5 | Remote Monitored | Remote Monitored | 65 | Remote Monitored | 5 | 19288 | Bear_Main_Temp02 | Bear_Main_Temp02 | 65 | Bear_Main_Temp02 | °C | 19288
safi_win4_8 | Safi W4 Z8 | 1336 | Service Area | Service Area | 66 | Service Area | 1336 | 19289 | Bear_Main_Temp03 | Bear_Main_Temp03 | 66 | Bear_Main_Temp03 | °C | 19289
safi_win4_9 | Safi W4 Z9 | 1441 | Territory | Territory | 67 | Territory | 1441 | 19290 | Bear_Main_Temp04 | Bear_Main_Temp04 | 67 | Bear_Main_Temp04 | °C | 19290
safi_win4_10 | Safi W4 Z10 | 1102 | Turbocharger 1 Model | Turbocharger 1 Model | 68 | Turbocharger 1 Model | 1102 | 19291 | Bear_Main_Temp05 | Bear_Main_Temp05 | 68 | Bear_Main_Temp05 | °C | 19291
safi_win4_11 | Safi W4 Z11 | 3 | Turbocharger 1 Serial Number | Turbocharger 1 Serial Number | 69 | Turbocharger 1 Serial Number | 3 | 19092 | Bear_Main_Temp06 | Bear_Main_Temp06 | 69 | Bear_Main_Temp06 | °C | 19092
safi_win4_12 | Safi W4 Z12 | 1103 | Turbocharger 2 Model | Turbocharger 2 Model | 70 | Turbocharger 2 Model | 1103 | 19292 | Bear_Main_Temp07 | Bear_Main_Temp07 | 70 | Bear_Main_Temp07 | °C | 19292
safi_win4_13 | Safi W4 Z13 | 1450 | Turbocharger 2 Serial Number | Turbocharger 2 Serial Number | 71 | Turbocharger 2 Serial Number | 1450 | 19293 | Bear_Main_Temp08 | Bear_Main_Temp08 | 71 | Bear_Main_Temp08 | °C | 19293
safi_win4_14 | Safi W4 Z14 | 1104 | Turbocharger 3 Model | Turbocharger 3 Model | 72 | Turbocharger 3 Model | 1104 | 19294 | Bear_Main_Temp09 | Bear_Main_Temp09 | 72 | Bear_Main_Temp09 | °C | 19294
safi_win4_15 | Safi W4 Z15 | 1451 | Turbocharger 3 Serial Number | Turbocharger 3 Serial Number | 73 | Turbocharger 3 Serial Number | 1451 | 19295 | Bear_Main_Temp10 | Bear_Main_Temp10 | 73 | Bear_Main_Temp10 | °C | 19295
safi_win4_16 | Safi W4 Z16 | 1105 | Turbocharger 4 Model | Turbocharger 4 Model | 74 | Turbocharger 4 Model | 1105 | 19296 | Bear_Main_Temp11 | Bear_Main_Temp11 | 74 | Bear_Main_Temp11 | °C | 19296
safi_win4_17 | Safi W4 Z17 | 1452 | Turbocharger 4 Serial Number | Turbocharger 4 Serial Number | 75 | Turbocharger 4 Serial Number | 1452 | 19297 | Bear_Main_TempMax | Bear_Main_TempMax | 75 | Bear_Main_TempMax | °C | 19297
safi_win4_18 | Safi W4 Z18 | 2 | Unit Serial Number | Unit Serial Number | 76 | Unit Serial Number | 2 | 10009048 | bFS_Req | bFS_Req | 76 | bFS_Req |  | 10009048
safi_win4_19 | Safi W4 Z19 | 1 | Unit Type | Unit Type | 77 | Unit Type | 1 | 10008983 | bLoad | bLoad | 77 | bLoad |  | 10008983
safi_win4_20 | Safi W4 Z20 | 624 | UnitSerialNumberOracle | UnitSerialNumberOracle | 78 | UnitSerialNumberOracle | 624 | 10049326 | bp_red_active | bp_red_active | 78 | bp_red_active |  | 10049326
safi_win4_21 | Safi W4 Z21 | [6 empty] | 10009024 | bScavDone | bScavDone | 79 | bScavDone |  | 10009024
safi_win4_22 | Safi W4 Z22 | [6 empty] | 10008981 | bSync | bSync | 80 | bSync |  | 10008981
safi_win4_23 | Safi W4 Z23 | [6 empty] | 10009026 | bT_ECW_Ok | bT_ECW_Ok | 81 | bT_ECW_Ok |  | 10009026
safi_win4_24 | Safi W4 Z24 | [6 empty] | 10009025 | bT_EO_Ok | bT_EO_Ok | 82 | bT_EO_Ok |  | 10009025
SAFI_Electronic_Temp_Average | Safi Temp | [6 empty] | 19317 | ChannelPartnerRegion | ChannelPartnerRegion | 83 | ChannelPartnerRegion |  | 19317
rP_Ramp_Set | LoadRamp | [6 empty] | 10044849 | chargingunit_rvol_ch_engine_norm | chargingunit_rvol_ch_engine_norm | 84 | chargingunit_rvol_ch_engine_norm | m3N/h | 10044849
RMD_ListAvgOilPress_OilPressureLimit | Oil P limit | [6 empty] | 10008980 | CMU_rDPr_AirFilt_A | CMU_rDPr_AirFilt_A | 85 | CMU_rDPr_AirFilt_A |  | 10008980
rHours_SinceStart | h since Start | [6 empty] | 10008982 | CMU_rDPr_AirFilt_B | CMU_rDPr_AirFilt_B | 86 | CMU_rDPr_AirFilt_B |  | 10008982
rE_SinceStart | E since Start | [6 empty] | 10046604 | CMU_rDPr_BbFilt | CMU_rDPr_BbFilt | 87 | CMU_rDPr_BbFilt |  | 10046604
Power_RedExt | Pred ext | [6 empty] | 20068 | CMU_rDPr_Ch_AirFilt | CMU_rDPr_Ch_AirFilt | 88 | CMU_rDPr_Ch_AirFilt | mbar | 20068
Power_RedExtBus | Pred Bus | [6 empty] | 10008979 | CMU_rDPr_Ch_FA | CMU_rDPr_Ch_FA | 89 | CMU_rDPr_Ch_FA |  | 10008979
Power_RedKnock | Pred knock | [6 empty] | 10008976 | CMU_rDPr_Ch_HPCooler | CMU_rDPr_Ch_HPCooler | 90 | CMU_rDPr_Ch_HPCooler |  | 10008976
Power_RedMisfire | Pred misfire | [6 empty] | 10008977 | CMU_rDPr_Ch_LPCooler | CMU_rDPr_Ch_LPCooler | 91 | CMU_rDPr_Ch_LPCooler |  | 10008977
Power_RedMixTemp | Pred mixtemp | [6 empty] | 10009076 | CMU_rPr_a_BbFilt | CMU_rPr_a_BbFilt | 92 | CMU_rPr_a_BbFilt |  | 10009076
Para_Tecjet_VolumEffic | TJ Vol Eff | [6 empty] | 20066 | CMU_rPr_a_BbFilt_A | CMU_rPr_a_BbFilt_A | 93 | CMU_rPr_a_BbFilt_A | mbar | 20066
Aux_GasVol | Q Gas B/N | [6 empty] | 20067 | CMU_rPr_a_BbFilt_B | CMU_rPr_a_BbFilt_B | 94 | CMU_rPr_a_BbFilt_B | mbar | 20067
Aux_GasPress | Q Gas P | [6 empty] | 20070 | CMU_rPr_Ch_P2bFA | CMU_rPr_Ch_P2bFA | 95 | CMU_rPr_Ch_P2bFA | bar | 20070
Aux_GasTemp | Q Gas T | [6 empty] | 20069 | CMU_rPr_Ch_P2HP | CMU_rPr_Ch_P2HP | 96 | CMU_rPr_Ch_P2HP | bar | 20069
Knock_Valve_Noise_Cyl01 | Safi W2 Z01 | [6 empty] | 20074 | CMU_rPr_Ch_P2LP | CMU_rPr_Ch_P2LP | 97 | CMU_rPr_Ch_P2LP | bar | 20074
Knock_Valve_Noise_Cyl02 | Safi W2 Z02 | [6 empty] | 10009075 | CMU_rPr_f_BbFilt | CMU_rPr_f_BbFilt | 98 | CMU_rPr_f_BbFilt |  | 10009075
Knock_Valve_Noise_Cyl03 | Safi W2 Z03 | [6 empty] | 20064 | CMU_rPr_f_BbFilt_A | CMU_rPr_f_BbFilt_A | 99 | CMU_rPr_f_BbFilt_A | mbar | 20064
Knock_Valve_Noise_Cyl04 | Safi W2 Z04 | [6 empty] | 20065 | CMU_rPr_f_BbFilt_B | CMU_rPr_f_BbFilt_B | 100 | CMU_rPr_f_BbFilt_B | mbar | 20065
Knock_Valve_Noise_Cyl05 | Safi W2 Z05 | [6 empty] | 20399 | Combustion_Quality_Cyl01 | Combustion_Quality_Cyl01 | 101 | Combustion_Quality_Cyl01 | % | 20399
Knock_Valve_Noise_Cyl06 | Safi W2 Z06 | [6 empty] | 20400 | Combustion_Quality_Cyl02 | Combustion_Quality_Cyl02 | 102 | Combustion_Quality_Cyl02 | % | 20400
Knock_Valve_Noise_Cyl07 | Safi W2 Z07 | [6 empty] | 20401 | Combustion_Quality_Cyl03 | Combustion_Quality_Cyl03 | 103 | Combustion_Quality_Cyl03 | % | 20401
Knock_Valve_Noise_Cyl08 | Safi W2 Z08 | [6 empty] | 20402 | Combustion_Quality_Cyl04 | Combustion_Quality_Cyl04 | 104 | Combustion_Quality_Cyl04 | % | 20402
Knock_Valve_Noise_Cyl09 | Safi W2 Z09 | [6 empty] | 20403 | Combustion_Quality_Cyl05 | Combustion_Quality_Cyl05 | 105 | Combustion_Quality_Cyl05 | % | 20403
Knock_Valve_Noise_Cyl10 | Safi W2 Z10 | [6 empty] | 20404 | Combustion_Quality_Cyl06 | Combustion_Quality_Cyl06 | 106 | Combustion_Quality_Cyl06 | % | 20404
Knock_Valve_Noise_Cyl11 | Safi W2 Z11 | [6 empty] | 20405 | Combustion_Quality_Cyl07 | Combustion_Quality_Cyl07 | 107 | Combustion_Quality_Cyl07 | % | 20405
Knock_Valve_Noise_Cyl12 | Safi W2 Z12 | [6 empty] | 20406 | Combustion_Quality_Cyl08 | Combustion_Quality_Cyl08 | 108 | Combustion_Quality_Cyl08 | % | 20406
Knock_Valve_Noise_Cyl13 | Safi W2 Z13 | [6 empty] | 20407 | Combustion_Quality_Cyl09 | Combustion_Quality_Cyl09 | 109 | Combustion_Quality_Cyl09 | % | 20407
Knock_Valve_Noise_Cyl14 | Safi W2 Z14 | [6 empty] | 20408 | Combustion_Quality_Cyl10 | Combustion_Quality_Cyl10 | 110 | Combustion_Quality_Cyl10 | % | 20408
Knock_Valve_Noise_Cyl15 | Safi W2 Z15 | [6 empty] | 20409 | Combustion_Quality_Cyl11 | Combustion_Quality_Cyl11 | 111 | Combustion_Quality_Cyl11 | % | 20409
Knock_Valve_Noise_Cyl16 | Safi W2 Z16 | [6 empty] | 20410 | Combustion_Quality_Cyl12 | Combustion_Quality_Cyl12 | 112 | Combustion_Quality_Cyl12 | % | 20410
Knock_Valve_Noise_Cyl17 | Safi W2 Z17 | [6 empty] | 20411 | Combustion_Quality_Cyl13 | Combustion_Quality_Cyl13 | 113 | Combustion_Quality_Cyl13 | % | 20411
Knock_Valve_Noise_Cyl18 | Safi W2 Z18 | [6 empty] | 20412 | Combustion_Quality_Cyl14 | Combustion_Quality_Cyl14 | 114 | Combustion_Quality_Cyl14 | % | 20412
Knock_Valve_Noise_Cyl19 | Safi W2 Z19 | [6 empty] | 20413 | Combustion_Quality_Cyl15 | Combustion_Quality_Cyl15 | 115 | Combustion_Quality_Cyl15 | % | 20413
Knock_Valve_Noise_Cyl20 | Safi W2 Z20 | [6 empty] | 20414 | Combustion_Quality_Cyl16 | Combustion_Quality_Cyl16 | 116 | Combustion_Quality_Cyl16 | % | 20414
Knock_Valve_Noise_Cyl21 | Safi W2 Z21 | [6 empty] | 20415 | Combustion_Quality_Cyl17 | Combustion_Quality_Cyl17 | 117 | Combustion_Quality_Cyl17 | % | 20415
Knock_Valve_Noise_Cyl22 | Safi W2 Z22 | [6 empty] | 20416 | Combustion_Quality_Cyl18 | Combustion_Quality_Cyl18 | 118 | Combustion_Quality_Cyl18 | % | 20416
Knock_Valve_Noise_Cyl23 | Safi W2 Z23 | [6 empty] | 20417 | Combustion_Quality_Cyl19 | Combustion_Quality_Cyl19 | 119 | Combustion_Quality_Cyl19 | % | 20417
Knock_Valve_Noise_Cyl24 | Safi W2 Z24 | [6 empty] | 20418 | Combustion_Quality_Cyl20 | Combustion_Quality_Cyl20 | 120 | Combustion_Quality_Cyl20 | % | 20418
Knock_KLS98_Knock_Cyl01 | Safi W1 Z01 | [6 empty] | 20419 | Combustion_Quality_Cyl21 | Combustion_Quality_Cyl21 | 121 | Combustion_Quality_Cyl21 | % | 20419
Knock_KLS98_Knock_Cyl02 | Safi W1 Z02 | [6 empty] | 20420 | Combustion_Quality_Cyl22 | Combustion_Quality_Cyl22 | 122 | Combustion_Quality_Cyl22 | % | 20420
Knock_KLS98_Knock_Cyl03 | Safi W1 Z03 | [6 empty] | 20421 | Combustion_Quality_Cyl23 | Combustion_Quality_Cyl23 | 123 | Combustion_Quality_Cyl23 | % | 20421
Knock_KLS98_Knock_Cyl04 | Safi W1 Z04 | [6 empty] | 20422 | Combustion_Quality_Cyl24 | Combustion_Quality_Cyl24 | 124 | Combustion_Quality_Cyl24 | % | 20422
Knock_KLS98_Knock_Cyl05 | Safi W1 Z05 | [6 empty] | 20375 | Combustion_Quality_Max_Cyl01 | Combustion_Quality_Max_Cyl01 | 125 | Combustion_Quality_Max_Cyl01 | % | 20375
Knock_KLS98_Knock_Cyl06 | Safi W1 Z06 | [6 empty] | 20376 | Combustion_Quality_Max_Cyl02 | Combustion_Quality_Max_Cyl02 | 126 | Combustion_Quality_Max_Cyl02 | % | 20376
Knock_KLS98_Knock_Cyl07 | Safi W1 Z07 | [6 empty] | 20377 | Combustion_Quality_Max_Cyl03 | Combustion_Quality_Max_Cyl03 | 127 | Combustion_Quality_Max_Cyl03 | % | 20377
Knock_KLS98_Knock_Cyl08 | Safi W1 Z08 | [6 empty] | 20378 | Combustion_Quality_Max_Cyl04 | Combustion_Quality_Max_Cyl04 | 128 | Combustion_Quality_Max_Cyl04 | % | 20378
Knock_KLS98_Knock_Cyl09 | Safi W1 Z09 | [6 empty] | 20379 | Combustion_Quality_Max_Cyl05 | Combustion_Quality_Max_Cyl05 | 129 | Combustion_Quality_Max_Cyl05 | % | 20379
Knock_KLS98_Knock_Cyl10 | Safi W1 Z10 | [6 empty] | 20380 | Combustion_Quality_Max_Cyl06 | Combustion_Quality_Max_Cyl06 | 130 | Combustion_Quality_Max_Cyl06 | % | 20380
Knock_KLS98_Knock_Cyl11 | Safi W1 Z11 | [6 empty] | 20381 | Combustion_Quality_Max_Cyl07 | Combustion_Quality_Max_Cyl07 | 131 | Combustion_Quality_Max_Cyl07 | % | 20381
Knock_KLS98_Knock_Cyl12 | Safi W1 Z12 | [6 empty] | 20382 | Combustion_Quality_Max_Cyl08 | Combustion_Quality_Max_Cyl08 | 132 | Combustion_Quality_Max_Cyl08 | % | 20382
Knock_KLS98_Knock_Cyl13 | Safi W1 Z13 | [6 empty] | 20383 | Combustion_Quality_Max_Cyl09 | Combustion_Quality_Max_Cyl09 | 133 | Combustion_Quality_Max_Cyl09 | % | 20383
Knock_KLS98_Knock_Cyl14 | Safi W1 Z14 | [6 empty] | 20384 | Combustion_Quality_Max_Cyl10 | Combustion_Quality_Max_Cyl10 | 134 | Combustion_Quality_Max_Cyl10 | % | 20384
Knock_KLS98_Knock_Cyl15 | Safi W1 Z15 | [6 empty] | 20385 | Combustion_Quality_Max_Cyl11 | Combustion_Quality_Max_Cyl11 | 135 | Combustion_Quality_Max_Cyl11 | % | 20385
Knock_KLS98_Knock_Cyl16 | Safi W1 Z16 | [6 empty] | 20386 | Combustion_Quality_Max_Cyl12 | Combustion_Quality_Max_Cyl12 | 136 | Combustion_Quality_Max_Cyl12 | % | 20386
Knock_KLS98_Knock_Cyl17 | Safi W1 Z17 | [6 empty] | 20387 | Combustion_Quality_Max_Cyl13 | Combustion_Quality_Max_Cyl13 | 137 | Combustion_Quality_Max_Cyl13 | % | 20387
Knock_KLS98_Knock_Cyl18 | Safi W1 Z18 | [6 empty] | 20388 | Combustion_Quality_Max_Cyl14 | Combustion_Quality_Max_Cyl14 | 138 | Combustion_Quality_Max_Cyl14 | % | 20388
Knock_KLS98_Knock_Cyl19 | Safi W1 Z19 | [6 empty] | 20389 | Combustion_Quality_Max_Cyl15 | Combustion_Quality_Max_Cyl15 | 139 | Combustion_Quality_Max_Cyl15 | % | 20389
Knock_KLS98_Knock_Cyl20 | Safi W1 Z20 | [6 empty] | 20390 | Combustion_Quality_Max_Cyl16 | Combustion_Quality_Max_Cyl16 | 140 | Combustion_Quality_Max_Cyl16 | % | 20390
Knock_KLS98_Knock_Cyl21 | Safi W1 Z21 | [6 empty] | 20391 | Combustion_Quality_Max_Cyl17 | Combustion_Quality_Max_Cyl17 | 141 | Combustion_Quality_Max_Cyl17 | % | 20391
Knock_KLS98_Knock_Cyl22 | Safi W1 Z22 | [6 empty] | 20392 | Combustion_Quality_Max_Cyl18 | Combustion_Quality_Max_Cyl18 | 142 | Combustion_Quality_Max_Cyl18 | % | 20392
Knock_KLS98_Knock_Cyl23 | Safi W1 Z23 | [6 empty] | 20393 | Combustion_Quality_Max_Cyl19 | Combustion_Quality_Max_Cyl19 | 143 | Combustion_Quality_Max_Cyl19 | % | 20393
Knock_KLS98_Knock_Cyl24 | Safi W1 Z24 | [6 empty] | 20394 | Combustion_Quality_Max_Cyl20 | Combustion_Quality_Max_Cyl20 | 144 | Combustion_Quality_Max_Cyl20 | % | 20394
IB Unit Commissioning Date | Orig Commissioning | [6 empty] | 20395 | Combustion_Quality_Max_Cyl21 | Combustion_Quality_Max_Cyl21 | 145 | Combustion_Quality_Max_Cyl21 | % | 20395
[8 empty] | 20396 | Combustion_Quality_Max_Cyl22 | Combustion_Quality_Max_Cyl22 | 146 | Combustion_Quality_Max_Cyl22 | % | 20396
[8 empty] | 20397 | Combustion_Quality_Max_Cyl23 | Combustion_Quality_Max_Cyl23 | 147 | Combustion_Quality_Max_Cyl23 | % | 20397
[8 empty] | 20398 | Combustion_Quality_Max_Cyl24 | Combustion_Quality_Max_Cyl24 | 148 | Combustion_Quality_Max_Cyl24 | % | 20398
[8 empty] | 1000644 | Cooling_Water_Degassing | Cooling_Water_Degassing | 149 | Cooling_Water_Degassing | bar | 1000644
[8 empty] | 1000645 | Cooling_Water_TopUp | Cooling_Water_TopUp | 150 | Cooling_Water_TopUp | bar | 1000645
[8 empty] | 132 | Count_Count1 | Count_Count1 | 151 | Count_Count1 | h | 132
[8 empty] | 150 | Count_Count2 | Count_Count2 | 152 | Count_Count2 |  | 150
[8 empty] | 144 | Count_Count3 | Count_Count3 | 153 | Count_Count3 | h | 144
[8 empty] | 149 | Count_Count4 | Count_Count4 | 154 | Count_Count4 | h | 149
[8 empty] | 19885 | Count_Counter1 | Count_Counter1 | 155 | Count_Counter1 |  | 19885
[8 empty] | 10046533 | Count_Counter10 | Count_Counter10 | 156 | Count_Counter10 |  | 10046533
[8 empty] | 19886 | Count_Counter2 | Count_Counter2 | 157 | Count_Counter2 |  | 19886
[8 empty] | 19924 | Count_Counter3 | Count_Counter3 | 158 | Count_Counter3 |  | 19924
[8 empty] | 19925 | Count_Counter4 | Count_Counter4 | 159 | Count_Counter4 |  | 19925
[8 empty] | 10046532 | Count_Counter5 | Count_Counter5 | 160 | Count_Counter5 |  | 10046532
[8 empty] | 10046531 | Count_Counter6 | Count_Counter6 | 161 | Count_Counter6 |  | 10046531
[8 empty] | 10046529 | Count_Counter7 | Count_Counter7 | 162 | Count_Counter7 |  | 10046529
[8 empty] | 10046530 | Count_Counter8 | Count_Counter8 | 163 | Count_Counter8 |  | 10046530
[8 empty] | 10046528 | Count_Counter9 | Count_Counter9 | 164 | Count_Counter9 |  | 10046528
[8 empty] | 157 | Count_Maintenance1 | Count_Maintenance1 | 165 | Count_Maintenance1 | h | 157
[8 empty] | 158 | Count_Maintenance2 | Count_Maintenance2 | 166 | Count_Maintenance2 | h | 158
[8 empty] | 159 | Count_Maintenance3 | Count_Maintenance3 | 167 | Count_Maintenance3 | h | 159
[8 empty] | 160 | Count_Maintenance4 | Count_Maintenance4 | 168 | Count_Maintenance4 | h | 160
[8 empty] | 10046363 | Count_Maintenance5 | Count_Maintenance5 | 169 | Count_Maintenance5 |  | 10046363
[8 empty] | 10046364 | Count_Maintenance6 | Count_Maintenance6 | 170 | Count_Maintenance6 |  | 10046364
[8 empty] | 10046365 | Count_Maintenance7 | Count_Maintenance7 | 171 | Count_Maintenance7 |  | 10046365
[8 empty] | 10046366 | Count_Maintenance8 | Count_Maintenance8 | 172 | Count_Maintenance8 |  | 10046366
[8 empty] | 161 | Count_OpHour | oph | 173 | Count_OpHour | h | 161
[8 empty] | 16186 | Count_OpHour_Billing | Count_OpHour_Billing | 174 | Count_OpHour_Billing | h | 16186
[8 empty] | 16043 | Count_OpHourGenSet | Count_OpHourGenSet | 175 | Count_OpHourGenSet | h | 16043
[8 empty] | 12581 | Count_OpHourManual | Count_OpHourManual | 176 | Count_OpHourManual | h | 12581
[8 empty] | 179 | Count_Start | Starts | 177 | Count_Start |  | 179
[8 empty] | 210 | CtrMixTemp_W | CtrMixTemp_W | 178 | CtrMixTemp_W | C | 210
[8 empty] | 47 | CtrMixTemp_X | CtrMixTemp_X | 179 | CtrMixTemp_X | C | 47
[8 empty] | 108 | CtrMixTemp_Y | CtrMixTemp_Y | 180 | CtrMixTemp_Y | % | 108
[8 empty] | 223 | CtrModule_Ctr10_W | CtrModule_Ctr10_W | 181 | CtrModule_Ctr10_W |  | 223
[8 empty] | 113 | CtrModule_Ctr10_X | CtrModule_Ctr10_X | 182 | CtrModule_Ctr10_X |  | 113
[8 empty] | 114 | CtrModule_Ctr10_Y | CtrModule_Ctr10_Y | 183 | CtrModule_Ctr10_Y | % | 114
[8 empty] | 224 | CtrModule_Ctr11_W | CtrModule_Ctr11_W | 184 | CtrModule_Ctr11_W |  | 224
[8 empty] | 154 | CtrModule_Ctr11_X | CtrModule_Ctr11_X | 185 | CtrModule_Ctr11_X |  | 154
[8 empty] | 155 | CtrModule_Ctr11_Y | CtrModule_Ctr11_Y | 186 | CtrModule_Ctr11_Y | % | 155
[8 empty] | 177 | CtrModule_Ctr12_W | CtrModule_Ctr12_W | 187 | CtrModule_Ctr12_W |  | 177
[8 empty] | 115 | CtrModule_Ctr12_X | CtrModule_Ctr12_X | 188 | CtrModule_Ctr12_X |  | 115
[8 empty] | 116 | CtrModule_Ctr12_Y | CtrModule_Ctr12_Y | 189 | CtrModule_Ctr12_Y | % | 116
[8 empty] | 188 | CtrModule_Ctr13_W | CtrModule_Ctr13_W | 190 | CtrModule_Ctr13_W |  | 188
[8 empty] | 186 | CtrModule_Ctr13_X | CtrModule_Ctr13_X | 191 | CtrModule_Ctr13_X |  | 186
[8 empty] | 187 | CtrModule_Ctr13_Y | CtrModule_Ctr13_Y | 192 | CtrModule_Ctr13_Y | % | 187
[8 empty] | 19100 | CtrModule_Ctr14_W | CtrModule_Ctr14_W | 193 | CtrModule_Ctr14_W |  | 19100
[8 empty] | 19101 | CtrModule_Ctr14_X | CtrModule_Ctr14_X | 194 | CtrModule_Ctr14_X |  | 19101
[8 empty] | 19102 | CtrModule_Ctr14_Y | CtrModule_Ctr14_Y | 195 | CtrModule_Ctr14_Y |  | 19102
[8 empty] | 19103 | CtrModule_Ctr15_W | CtrModule_Ctr15_W | 196 | CtrModule_Ctr15_W |  | 19103
[8 empty] | 19104 | CtrModule_Ctr15_X | CtrModule_Ctr15_X | 197 | CtrModule_Ctr15_X |  | 19104
[8 empty] | 19105 | CtrModule_Ctr15_Y | CtrModule_Ctr15_Y | 198 | CtrModule_Ctr15_Y |  | 19105
[8 empty] | 19106 | CtrModule_Ctr16_W | CtrModule_Ctr16_W | 199 | CtrModule_Ctr16_W |  | 19106
[8 empty] | 19107 | CtrModule_Ctr16_X | CtrModule_Ctr16_X | 200 | CtrModule_Ctr16_X |  | 19107
[8 empty] | 19108 | CtrModule_Ctr16_Y | CtrModule_Ctr16_Y | 201 | CtrModule_Ctr16_Y |  | 19108
[8 empty] | 222 | CtrModule_Ctr1_W | CtrModule_Ctr1_W | 202 | CtrModule_Ctr1_W |  | 222
[8 empty] | 22 | CtrModule_Ctr1_X | CtrModule_Ctr1_X | 203 | CtrModule_Ctr1_X |  | 22
[8 empty] | 23 | CtrModule_Ctr1_Y | CtrModule_Ctr1_Y | 204 | CtrModule_Ctr1_Y | % | 23
[8 empty] | 201 | CtrModule_Ctr2_W | CtrModule_Ctr2_W | 205 | CtrModule_Ctr2_W |  | 201
[8 empty] | 24 | CtrModule_Ctr2_X | CtrModule_Ctr2_X | 206 | CtrModule_Ctr2_X |  | 24
[8 empty] | 109 | CtrModule_Ctr2_Y | CtrModule_Ctr2_Y | 207 | CtrModule_Ctr2_Y | % | 109
[8 empty] | 215 | CtrModule_Ctr3_W | CtrModule_Ctr3_W | 208 | CtrModule_Ctr3_W |  | 215
[8 empty] | 49 | CtrModule_Ctr3_X | CtrModule_Ctr3_X | 209 | CtrModule_Ctr3_X |  | 49
[8 empty] | 51 | CtrModule_Ctr3_Y | CtrModule_Ctr3_Y | 210 | CtrModule_Ctr3_Y | % | 51
[8 empty] | 229 | CtrModule_Ctr4_W | CtrModule_Ctr4_W | 211 | CtrModule_Ctr4_W |  | 229
[8 empty] | 53 | CtrModule_Ctr4_X | CtrModule_Ctr4_X | 212 | CtrModule_Ctr4_X |  | 53
[8 empty] | 128 | CtrModule_Ctr4_Y | CtrModule_Ctr4_Y | 213 | CtrModule_Ctr4_Y | % | 128
[8 empty] | 230 | CtrModule_Ctr5_W | CtrModule_Ctr5_W | 214 | CtrModule_Ctr5_W |  | 230
[8 empty] | 55 | CtrModule_Ctr5_X | CtrModule_Ctr5_X | 215 | CtrModule_Ctr5_X |  | 55
[8 empty] | 129 | CtrModule_Ctr5_Y | CtrModule_Ctr5_Y | 216 | CtrModule_Ctr5_Y | % | 129
[8 empty] | 231 | CtrModule_Ctr6_W | CtrModule_Ctr6_W | 217 | CtrModule_Ctr6_W |  | 231
[8 empty] | 57 | CtrModule_Ctr6_X | CtrModule_Ctr6_X | 218 | CtrModule_Ctr6_X |  | 57
[8 empty] | 200 | CtrModule_Ctr6_Y | CtrModule_Ctr6_Y | 219 | CtrModule_Ctr6_Y | % | 200
[8 empty] | 232 | CtrModule_Ctr7_W | CtrModule_Ctr7_W | 220 | CtrModule_Ctr7_W |  | 232
[8 empty] | 211 | CtrModule_Ctr7_X | CtrModule_Ctr7_X | 221 | CtrModule_Ctr7_X |  | 211
[8 empty] | 212 | CtrModule_Ctr7_Y | CtrModule_Ctr7_Y | 222 | CtrModule_Ctr7_Y | % | 212
[8 empty] | 198 | CtrModule_Ctr8_W | CtrModule_Ctr8_W | 223 | CtrModule_Ctr8_W |  | 198
[8 empty] | 166 | CtrModule_Ctr8_X | CtrModule_Ctr8_X | 224 | CtrModule_Ctr8_X |  | 166
[8 empty] | 184 | CtrModule_Ctr8_Y | CtrModule_Ctr8_Y | 225 | CtrModule_Ctr8_Y | % | 184
[8 empty] | 10045947 | cust_analoginput_ai001_value | cust_analoginput_ai001_value | 226 | cust_analoginput_ai001_value | float | 10045947
[8 empty] | 10045948 | cust_analoginput_ai002_value | cust_analoginput_ai002_value | 227 | cust_analoginput_ai002_value | float | 10045948
[8 empty] | 10045949 | cust_analoginput_ai003_value | cust_analoginput_ai003_value | 228 | cust_analoginput_ai003_value | float | 10045949
[8 empty] | 10045950 | cust_analoginput_ai004_value | cust_analoginput_ai004_value | 229 | cust_analoginput_ai004_value | float | 10045950
[8 empty] | 10045951 | cust_analoginput_ai005_value | cust_analoginput_ai005_value | 230 | cust_analoginput_ai005_value | float | 10045951
[8 empty] | 10045952 | cust_analoginput_ai006_value | cust_analoginput_ai006_value | 231 | cust_analoginput_ai006_value | float | 10045952
[8 empty] | 10045953 | cust_analoginput_ai007_value | cust_analoginput_ai007_value | 232 | cust_analoginput_ai007_value | float | 10045953
[8 empty] | 10045954 | cust_analoginput_ai008_value | cust_analoginput_ai008_value | 233 | cust_analoginput_ai008_value | float | 10045954
[8 empty] | 10045955 | cust_analoginput_ai009_value | cust_analoginput_ai009_value | 234 | cust_analoginput_ai009_value | float | 10045955
[8 empty] | 10045956 | cust_analoginput_ai010_value | cust_analoginput_ai010_value | 235 | cust_analoginput_ai010_value | float | 10045956
[8 empty] | 10045957 | cust_analoginput_ai011_value | cust_analoginput_ai011_value | 236 | cust_analoginput_ai011_value | float | 10045957
[8 empty] | 10045958 | cust_analoginput_ai012_value | cust_analoginput_ai012_value | 237 | cust_analoginput_ai012_value | float | 10045958
[8 empty] | 10045959 | cust_analoginput_ai013_value | cust_analoginput_ai013_value | 238 | cust_analoginput_ai013_value | float | 10045959
[8 empty] | 10045960 | cust_analoginput_ai014_value | cust_analoginput_ai014_value | 239 | cust_analoginput_ai014_value | float | 10045960
[8 empty] | 10045961 | cust_analoginput_ai015_value | cust_analoginput_ai015_value | 240 | cust_analoginput_ai015_value | float | 10045961
[8 empty] | 10045962 | cust_analoginput_ai016_value | cust_analoginput_ai016_value | 241 | cust_analoginput_ai016_value | float | 10045962
[8 empty] | 10045963 | cust_analoginput_ai017_value | cust_analoginput_ai017_value | 242 | cust_analoginput_ai017_value | float | 10045963
[8 empty] | 10045964 | cust_analoginput_ai018_value | cust_analoginput_ai018_value | 243 | cust_analoginput_ai018_value | float | 10045964
[8 empty] | 10045965 | cust_analoginput_ai019_value | cust_analoginput_ai019_value | 244 | cust_analoginput_ai019_value | float | 10045965
[8 empty] | 10045966 | cust_analoginput_ai020_value | cust_analoginput_ai020_value | 245 | cust_analoginput_ai020_value | float | 10045966
[8 empty] | 10045967 | cust_analoginput_ai021_value | cust_analoginput_ai021_value | 246 | cust_analoginput_ai021_value | float | 10045967
[8 empty] | 10045968 | cust_analoginput_ai022_value | cust_analoginput_ai022_value | 247 | cust_analoginput_ai022_value | float | 10045968
[8 empty] | 10045969 | cust_analoginput_ai023_value | cust_analoginput_ai023_value | 248 | cust_analoginput_ai023_value | float | 10045969
[8 empty] | 10045970 | cust_analoginput_ai024_value | cust_analoginput_ai024_value | 249 | cust_analoginput_ai024_value | float | 10045970
[8 empty] | 10045971 | cust_analoginput_ai025_value | cust_analoginput_ai025_value | 250 | cust_analoginput_ai025_value | float | 10045971
[8 empty] | 10045972 | cust_analoginput_ai026_value | cust_analoginput_ai026_value | 251 | cust_analoginput_ai026_value | float | 10045972
[8 empty] | 10045973 | cust_analoginput_ai027_value | cust_analoginput_ai027_value | 252 | cust_analoginput_ai027_value | float | 10045973
[8 empty] | 10045974 | cust_analoginput_ai028_value | cust_analoginput_ai028_value | 253 | cust_analoginput_ai028_value | float | 10045974
[8 empty] | 10045975 | cust_analoginput_ai029_value | cust_analoginput_ai029_value | 254 | cust_analoginput_ai029_value | float | 10045975
[8 empty] | 10045976 | cust_analoginput_ai030_value | cust_analoginput_ai030_value | 255 | cust_analoginput_ai030_value | float | 10045976
[8 empty] | 10045977 | cust_analoginput_ai031_value | cust_analoginput_ai031_value | 256 | cust_analoginput_ai031_value | float | 10045977
[8 empty] | 10045978 | cust_analoginput_ai032_value | cust_analoginput_ai032_value | 257 | cust_analoginput_ai032_value | float | 10045978
[8 empty] | 10045979 | cust_analoginput_ai033_value | cust_analoginput_ai033_value | 258 | cust_analoginput_ai033_value | float | 10045979
[8 empty] | 10045980 | cust_analoginput_ai034_value | cust_analoginput_ai034_value | 259 | cust_analoginput_ai034_value | float | 10045980
[8 empty] | 10045981 | cust_analoginput_ai035_value | cust_analoginput_ai035_value | 260 | cust_analoginput_ai035_value | float | 10045981
[8 empty] | 10045982 | cust_analoginput_ai036_value | cust_analoginput_ai036_value | 261 | cust_analoginput_ai036_value | float | 10045982
[8 empty] | 10045983 | cust_analoginput_ai037_value | cust_analoginput_ai037_value | 262 | cust_analoginput_ai037_value | float | 10045983
[8 empty] | 10045984 | cust_analoginput_ai038_value | cust_analoginput_ai038_value | 263 | cust_analoginput_ai038_value | float | 10045984
[8 empty] | 10045985 | cust_analoginput_ai039_value | cust_analoginput_ai039_value | 264 | cust_analoginput_ai039_value | float | 10045985
[8 empty] | 10045986 | cust_analoginput_ai040_value | cust_analoginput_ai040_value | 265 | cust_analoginput_ai040_value | float | 10045986
[8 empty] | 10045987 | cust_analoginput_ai041_value | cust_analoginput_ai041_value | 266 | cust_analoginput_ai041_value | float | 10045987
[8 empty] | 10045988 | cust_analoginput_ai042_value | cust_analoginput_ai042_value | 267 | cust_analoginput_ai042_value | float | 10045988
[8 empty] | 10045989 | cust_analoginput_ai043_value | cust_analoginput_ai043_value | 268 | cust_analoginput_ai043_value | float | 10045989
[8 empty] | 10045990 | cust_analoginput_ai044_value | cust_analoginput_ai044_value | 269 | cust_analoginput_ai044_value | float | 10045990
[8 empty] | 10045991 | cust_analoginput_ai045_value | cust_analoginput_ai045_value | 270 | cust_analoginput_ai045_value | float | 10045991
[8 empty] | 10045992 | cust_analoginput_ai046_value | cust_analoginput_ai046_value | 271 | cust_analoginput_ai046_value | float | 10045992
[8 empty] | 10045993 | cust_analoginput_ai047_value | cust_analoginput_ai047_value | 272 | cust_analoginput_ai047_value | float | 10045993
[8 empty] | 10045994 | cust_analoginput_ai048_value | cust_analoginput_ai048_value | 273 | cust_analoginput_ai048_value | float | 10045994
[8 empty] | 10045995 | cust_analoginput_ai049_value | cust_analoginput_ai049_value | 274 | cust_analoginput_ai049_value | float | 10045995
[8 empty] | 10045996 | cust_analoginput_ai050_value | cust_analoginput_ai050_value | 275 | cust_analoginput_ai050_value | float | 10045996
[8 empty] | 10045997 | cust_analoginput_ai051_value | cust_analoginput_ai051_value | 276 | cust_analoginput_ai051_value | float | 10045997
[8 empty] | 10045998 | cust_analoginput_ai052_value | cust_analoginput_ai052_value | 277 | cust_analoginput_ai052_value | float | 10045998
[8 empty] | 10045999 | cust_analoginput_ai053_value | cust_analoginput_ai053_value | 278 | cust_analoginput_ai053_value | float | 10045999
[8 empty] | 10046000 | cust_analoginput_ai054_value | cust_analoginput_ai054_value | 279 | cust_analoginput_ai054_value | float | 10046000
[8 empty] | 10046001 | cust_analoginput_ai055_value | cust_analoginput_ai055_value | 280 | cust_analoginput_ai055_value | float | 10046001
[8 empty] | 10046002 | cust_analoginput_ai056_value | cust_analoginput_ai056_value | 281 | cust_analoginput_ai056_value | float | 10046002
[8 empty] | 10046003 | cust_analoginput_ai057_value | cust_analoginput_ai057_value | 282 | cust_analoginput_ai057_value | float | 10046003
[8 empty] | 10046004 | cust_analoginput_ai058_value | cust_analoginput_ai058_value | 283 | cust_analoginput_ai058_value | float | 10046004
[8 empty] | 10046005 | cust_analoginput_ai059_value | cust_analoginput_ai059_value | 284 | cust_analoginput_ai059_value | float | 10046005
[8 empty] | 10046006 | cust_analoginput_ai060_value | cust_analoginput_ai060_value | 285 | cust_analoginput_ai060_value | float | 10046006
[8 empty] | 10049553 | custom_dpscrcatalyst_22ccfa | custom_dpscrcatalyst_22ccfa | 286 | custom_dpscrcatalyst_22ccfa | mbar | 10049553
[8 empty] | 10049546 | custom_engine_out_nox_mg_16583c | custom_engine_out_nox_mg_16583c | 287 | custom_engine_out_nox_mg_16583c | mg/m3 | 10049546
[8 empty] | 10008984 | CylState_1 | CylState_1 | 288 | CylState_1 |  | 10008984
[8 empty] | 10008986 | CylState_10 | CylState_10 | 289 | CylState_10 |  | 10008986
[8 empty] | 10008988 | CylState_11 | CylState_11 | 290 | CylState_11 |  | 10008988
[8 empty] | 10008989 | CylState_12 | CylState_12 | 291 | CylState_12 |  | 10008989
[8 empty] | 10008990 | CylState_13 | CylState_13 | 292 | CylState_13 |  | 10008990
[8 empty] | 10008993 | CylState_14 | CylState_14 | 293 | CylState_14 |  | 10008993
[8 empty] | 10008991 | CylState_15 | CylState_15 | 294 | CylState_15 |  | 10008991
[8 empty] | 10008992 | CylState_16 | CylState_16 | 295 | CylState_16 |  | 10008992
[8 empty] | 10008994 | CylState_17 | CylState_17 | 296 | CylState_17 |  | 10008994
[8 empty] | 10008995 | CylState_18 | CylState_18 | 297 | CylState_18 |  | 10008995
[8 empty] | 10008997 | CylState_19 | CylState_19 | 298 | CylState_19 |  | 10008997
[8 empty] | 10008999 | CylState_2 | CylState_2 | 299 | CylState_2 |  | 10008999
[8 empty] | 10008996 | CylState_20 | CylState_20 | 300 | CylState_20 |  | 10008996
[8 empty] | 10008998 | CylState_3 | CylState_3 | 301 | CylState_3 |  | 10008998
[8 empty] | 10009000 | CylState_4 | CylState_4 | 302 | CylState_4 |  | 10009000
[8 empty] | 10009001 | CylState_5 | CylState_5 | 303 | CylState_5 |  | 10009001
[8 empty] | 10009002 | CylState_6 | CylState_6 | 304 | CylState_6 |  | 10009002
[8 empty] | 10009004 | CylState_7 | CylState_7 | 305 | CylState_7 |  | 10009004
[8 empty] | 10009003 | CylState_8 | CylState_8 | 306 | CylState_8 |  | 10009003
[8 empty] | 10009005 | CylState_9 | CylState_9 | 307 | CylState_9 |  | 10009005
[8 empty] | 10049422 | ec_lx2_bpoc_0 | ec_lx2_bpoc_0 | 308 | ec_lx2_bpoc_0 | mbar | 10049422
[8 empty] | 10049423 | ec_lx2_bpoc_1 | ec_lx2_bpoc_1 | 309 | ec_lx2_bpoc_1 | mbar | 10049423
[8 empty] | 10049432 | ec_lx2_bpoc_10 | ec_lx2_bpoc_10 | 310 | ec_lx2_bpoc_10 | mbar | 10049432
[8 empty] | 10049424 | ec_lx2_bpoc_2 | ec_lx2_bpoc_2 | 311 | ec_lx2_bpoc_2 | mbar | 10049424
[8 empty] | 10049425 | ec_lx2_bpoc_3 | ec_lx2_bpoc_3 | 312 | ec_lx2_bpoc_3 | mbar | 10049425
[8 empty] | 10049426 | ec_lx2_bpoc_4 | ec_lx2_bpoc_4 | 313 | ec_lx2_bpoc_4 | mbar | 10049426
[8 empty] | 10049427 | ec_lx2_bpoc_5 | ec_lx2_bpoc_5 | 314 | ec_lx2_bpoc_5 | mbar | 10049427
[8 empty] | 10049428 | ec_lx2_bpoc_6 | ec_lx2_bpoc_6 | 315 | ec_lx2_bpoc_6 | mbar | 10049428
[8 empty] | 10049429 | ec_lx2_bpoc_7 | ec_lx2_bpoc_7 | 316 | ec_lx2_bpoc_7 | mbar | 10049429
[8 empty] | 10049430 | ec_lx2_bpoc_8 | ec_lx2_bpoc_8 | 317 | ec_lx2_bpoc_8 | mbar | 10049430
[8 empty] | 10049431 | ec_lx2_bpoc_9 | ec_lx2_bpoc_9 | 318 | ec_lx2_bpoc_9 | mbar | 10049431
[8 empty] | 10049334 | ec_lx2_bpoc_gas_1_0 | ec_lx2_bpoc_gas_1_0 | 319 | ec_lx2_bpoc_gas_1_0 | mbar | 10049334
[8 empty] | 10049378 | ec_lx2_bpoc_gas_1_0_m | ec_lx2_bpoc_gas_1_0_m | 320 | ec_lx2_bpoc_gas_1_0_m |  | 10049378
[8 empty] | 10049335 | ec_lx2_bpoc_gas_1_1 | ec_lx2_bpoc_gas_1_1 | 321 | ec_lx2_bpoc_gas_1_1 | mbar | 10049335
[8 empty] | 10049344 | ec_lx2_bpoc_gas_1_10 | ec_lx2_bpoc_gas_1_10 | 322 | ec_lx2_bpoc_gas_1_10 | mbar | 10049344
[8 empty] | 10049388 | ec_lx2_bpoc_gas_1_10_m | ec_lx2_bpoc_gas_1_10_m | 323 | ec_lx2_bpoc_gas_1_10_m |  | 10049388
[8 empty] | 10049379 | ec_lx2_bpoc_gas_1_1_m | ec_lx2_bpoc_gas_1_1_m | 324 | ec_lx2_bpoc_gas_1_1_m |  | 10049379
[8 empty] | 10049336 | ec_lx2_bpoc_gas_1_2 | ec_lx2_bpoc_gas_1_2 | 325 | ec_lx2_bpoc_gas_1_2 | mbar | 10049336
[8 empty] | 10049380 | ec_lx2_bpoc_gas_1_2_m | ec_lx2_bpoc_gas_1_2_m | 326 | ec_lx2_bpoc_gas_1_2_m |  | 10049380
[8 empty] | 10049337 | ec_lx2_bpoc_gas_1_3 | ec_lx2_bpoc_gas_1_3 | 327 | ec_lx2_bpoc_gas_1_3 | mbar | 10049337
[8 empty] | 10049381 | ec_lx2_bpoc_gas_1_3_m | ec_lx2_bpoc_gas_1_3_m | 328 | ec_lx2_bpoc_gas_1_3_m |  | 10049381
[8 empty] | 10049338 | ec_lx2_bpoc_gas_1_4 | ec_lx2_bpoc_gas_1_4 | 329 | ec_lx2_bpoc_gas_1_4 | mbar | 10049338
[8 empty] | 10049382 | ec_lx2_bpoc_gas_1_4_m | ec_lx2_bpoc_gas_1_4_m | 330 | ec_lx2_bpoc_gas_1_4_m |  | 10049382
[8 empty] | 10049339 | ec_lx2_bpoc_gas_1_5 | ec_lx2_bpoc_gas_1_5 | 331 | ec_lx2_bpoc_gas_1_5 | mbar | 10049339
[8 empty] | 10049383 | ec_lx2_bpoc_gas_1_5_m | ec_lx2_bpoc_gas_1_5_m | 332 | ec_lx2_bpoc_gas_1_5_m |  | 10049383
[8 empty] | 10049340 | ec_lx2_bpoc_gas_1_6 | ec_lx2_bpoc_gas_1_6 | 333 | ec_lx2_bpoc_gas_1_6 | mbar | 10049340
[8 empty] | 10049384 | ec_lx2_bpoc_gas_1_6_m | ec_lx2_bpoc_gas_1_6_m | 334 | ec_lx2_bpoc_gas_1_6_m |  | 10049384
[8 empty] | 10049341 | ec_lx2_bpoc_gas_1_7 | ec_lx2_bpoc_gas_1_7 | 335 | ec_lx2_bpoc_gas_1_7 | mbar | 10049341
[8 empty] | 10049385 | ec_lx2_bpoc_gas_1_7_m | ec_lx2_bpoc_gas_1_7_m | 336 | ec_lx2_bpoc_gas_1_7_m |  | 10049385
[8 empty] | 10049342 | ec_lx2_bpoc_gas_1_8 | ec_lx2_bpoc_gas_1_8 | 337 | ec_lx2_bpoc_gas_1_8 | mbar | 10049342
[8 empty] | 10049386 | ec_lx2_bpoc_gas_1_8_m | ec_lx2_bpoc_gas_1_8_m | 338 | ec_lx2_bpoc_gas_1_8_m |  | 10049386
[8 empty] | 10049343 | ec_lx2_bpoc_gas_1_9 | ec_lx2_bpoc_gas_1_9 | 339 | ec_lx2_bpoc_gas_1_9 | mbar | 10049343
[8 empty] | 10049387 | ec_lx2_bpoc_gas_1_9_m | ec_lx2_bpoc_gas_1_9_m | 340 | ec_lx2_bpoc_gas_1_9_m |  | 10049387
[8 empty] | 10049345 | ec_lx2_bpoc_gas_2_0 | ec_lx2_bpoc_gas_2_0 | 341 | ec_lx2_bpoc_gas_2_0 | mbar | 10049345
[8 empty] | 10049389 | ec_lx2_bpoc_gas_2_0_m | ec_lx2_bpoc_gas_2_0_m | 342 | ec_lx2_bpoc_gas_2_0_m |  | 10049389
[8 empty] | 10049346 | ec_lx2_bpoc_gas_2_1 | ec_lx2_bpoc_gas_2_1 | 343 | ec_lx2_bpoc_gas_2_1 | mbar | 10049346
[8 empty] | 10049355 | ec_lx2_bpoc_gas_2_10 | ec_lx2_bpoc_gas_2_10 | 344 | ec_lx2_bpoc_gas_2_10 | mbar | 10049355
[8 empty] | 10049399 | ec_lx2_bpoc_gas_2_10_m | ec_lx2_bpoc_gas_2_10_m | 345 | ec_lx2_bpoc_gas_2_10_m |  | 10049399
[8 empty] | 10049390 | ec_lx2_bpoc_gas_2_1_m | ec_lx2_bpoc_gas_2_1_m | 346 | ec_lx2_bpoc_gas_2_1_m |  | 10049390
[8 empty] | 10049347 | ec_lx2_bpoc_gas_2_2 | ec_lx2_bpoc_gas_2_2 | 347 | ec_lx2_bpoc_gas_2_2 | mbar | 10049347
[8 empty] | 10049391 | ec_lx2_bpoc_gas_2_2_m | ec_lx2_bpoc_gas_2_2_m | 348 | ec_lx2_bpoc_gas_2_2_m |  | 10049391
[8 empty] | 10049348 | ec_lx2_bpoc_gas_2_3 | ec_lx2_bpoc_gas_2_3 | 349 | ec_lx2_bpoc_gas_2_3 | mbar | 10049348
[8 empty] | 10049392 | ec_lx2_bpoc_gas_2_3_m | ec_lx2_bpoc_gas_2_3_m | 350 | ec_lx2_bpoc_gas_2_3_m |  | 10049392
[8 empty] | 10049349 | ec_lx2_bpoc_gas_2_4 | ec_lx2_bpoc_gas_2_4 | 351 | ec_lx2_bpoc_gas_2_4 | mbar | 10049349
[8 empty] | 10049393 | ec_lx2_bpoc_gas_2_4_m | ec_lx2_bpoc_gas_2_4_m | 352 | ec_lx2_bpoc_gas_2_4_m |  | 10049393
[8 empty] | 10049350 | ec_lx2_bpoc_gas_2_5 | ec_lx2_bpoc_gas_2_5 | 353 | ec_lx2_bpoc_gas_2_5 | mbar | 10049350
[8 empty] | 10049394 | ec_lx2_bpoc_gas_2_5_m | ec_lx2_bpoc_gas_2_5_m | 354 | ec_lx2_bpoc_gas_2_5_m |  | 10049394
[8 empty] | 10049351 | ec_lx2_bpoc_gas_2_6 | ec_lx2_bpoc_gas_2_6 | 355 | ec_lx2_bpoc_gas_2_6 | mbar | 10049351
[8 empty] | 10049395 | ec_lx2_bpoc_gas_2_6_m | ec_lx2_bpoc_gas_2_6_m | 356 | ec_lx2_bpoc_gas_2_6_m |  | 10049395
[8 empty] | 10049352 | ec_lx2_bpoc_gas_2_7 | ec_lx2_bpoc_gas_2_7 | 357 | ec_lx2_bpoc_gas_2_7 | mbar | 10049352
[8 empty] | 10049396 | ec_lx2_bpoc_gas_2_7_m | ec_lx2_bpoc_gas_2_7_m | 358 | ec_lx2_bpoc_gas_2_7_m |  | 10049396
[8 empty] | 10049353 | ec_lx2_bpoc_gas_2_8 | ec_lx2_bpoc_gas_2_8 | 359 | ec_lx2_bpoc_gas_2_8 | mbar | 10049353
[8 empty] | 10049397 | ec_lx2_bpoc_gas_2_8_m | ec_lx2_bpoc_gas_2_8_m | 360 | ec_lx2_bpoc_gas_2_8_m |  | 10049397
[8 empty] | 10049354 | ec_lx2_bpoc_gas_2_9 | ec_lx2_bpoc_gas_2_9 | 361 | ec_lx2_bpoc_gas_2_9 | mbar | 10049354
[8 empty] | 10049398 | ec_lx2_bpoc_gas_2_9_m | ec_lx2_bpoc_gas_2_9_m | 362 | ec_lx2_bpoc_gas_2_9_m |  | 10049398
[8 empty] | 10049356 | ec_lx2_bpoc_gas_3_0 | ec_lx2_bpoc_gas_3_0 | 363 | ec_lx2_bpoc_gas_3_0 | mbar | 10049356
[8 empty] | 10049400 | ec_lx2_bpoc_gas_3_0_m | ec_lx2_bpoc_gas_3_0_m | 364 | ec_lx2_bpoc_gas_3_0_m |  | 10049400
[8 empty] | 10049357 | ec_lx2_bpoc_gas_3_1 | ec_lx2_bpoc_gas_3_1 | 365 | ec_lx2_bpoc_gas_3_1 | mbar | 10049357
[8 empty] | 10049366 | ec_lx2_bpoc_gas_3_10 | ec_lx2_bpoc_gas_3_10 | 366 | ec_lx2_bpoc_gas_3_10 | mbar | 10049366
[8 empty] | 10049410 | ec_lx2_bpoc_gas_3_10_m | ec_lx2_bpoc_gas_3_10_m | 367 | ec_lx2_bpoc_gas_3_10_m |  | 10049410
[8 empty] | 10049401 | ec_lx2_bpoc_gas_3_1_m | ec_lx2_bpoc_gas_3_1_m | 368 | ec_lx2_bpoc_gas_3_1_m |  | 10049401
[8 empty] | 10049358 | ec_lx2_bpoc_gas_3_2 | ec_lx2_bpoc_gas_3_2 | 369 | ec_lx2_bpoc_gas_3_2 | mbar | 10049358
[8 empty] | 10049402 | ec_lx2_bpoc_gas_3_2_m | ec_lx2_bpoc_gas_3_2_m | 370 | ec_lx2_bpoc_gas_3_2_m |  | 10049402
[8 empty] | 10049359 | ec_lx2_bpoc_gas_3_3 | ec_lx2_bpoc_gas_3_3 | 371 | ec_lx2_bpoc_gas_3_3 | mbar | 10049359
[8 empty] | 10049403 | ec_lx2_bpoc_gas_3_3_m | ec_lx2_bpoc_gas_3_3_m | 372 | ec_lx2_bpoc_gas_3_3_m |  | 10049403
[8 empty] | 10049360 | ec_lx2_bpoc_gas_3_4 | ec_lx2_bpoc_gas_3_4 | 373 | ec_lx2_bpoc_gas_3_4 | mbar | 10049360
[8 empty] | 10049404 | ec_lx2_bpoc_gas_3_4_m | ec_lx2_bpoc_gas_3_4_m | 374 | ec_lx2_bpoc_gas_3_4_m |  | 10049404
[8 empty] | 10049361 | ec_lx2_bpoc_gas_3_5 | ec_lx2_bpoc_gas_3_5 | 375 | ec_lx2_bpoc_gas_3_5 | mbar | 10049361
[8 empty] | 10049405 | ec_lx2_bpoc_gas_3_5_m | ec_lx2_bpoc_gas_3_5_m | 376 | ec_lx2_bpoc_gas_3_5_m |  | 10049405
[8 empty] | 10049362 | ec_lx2_bpoc_gas_3_6 | ec_lx2_bpoc_gas_3_6 | 377 | ec_lx2_bpoc_gas_3_6 | mbar | 10049362
[8 empty] | 10049406 | ec_lx2_bpoc_gas_3_6_m | ec_lx2_bpoc_gas_3_6_m | 378 | ec_lx2_bpoc_gas_3_6_m |  | 10049406
[8 empty] | 10049363 | ec_lx2_bpoc_gas_3_7 | ec_lx2_bpoc_gas_3_7 | 379 | ec_lx2_bpoc_gas_3_7 | mbar | 10049363
[8 empty] | 10049407 | ec_lx2_bpoc_gas_3_7_m | ec_lx2_bpoc_gas_3_7_m | 380 | ec_lx2_bpoc_gas_3_7_m |  | 10049407
[8 empty] | 10049364 | ec_lx2_bpoc_gas_3_8 | ec_lx2_bpoc_gas_3_8 | 381 | ec_lx2_bpoc_gas_3_8 | mbar | 10049364
[8 empty] | 10049408 | ec_lx2_bpoc_gas_3_8_m | ec_lx2_bpoc_gas_3_8_m | 382 | ec_lx2_bpoc_gas_3_8_m |  | 10049408
[8 empty] | 10049365 | ec_lx2_bpoc_gas_3_9 | ec_lx2_bpoc_gas_3_9 | 383 | ec_lx2_bpoc_gas_3_9 | mbar | 10049365
[8 empty] | 10049409 | ec_lx2_bpoc_gas_3_9_m | ec_lx2_bpoc_gas_3_9_m | 384 | ec_lx2_bpoc_gas_3_9_m |  | 10049409
[8 empty] | 10049367 | ec_lx2_bpoc_gas_4_0 | ec_lx2_bpoc_gas_4_0 | 385 | ec_lx2_bpoc_gas_4_0 | mbar | 10049367
[8 empty] | 10049411 | ec_lx2_bpoc_gas_4_0_m | ec_lx2_bpoc_gas_4_0_m | 386 | ec_lx2_bpoc_gas_4_0_m |  | 10049411
[8 empty] | 10049368 | ec_lx2_bpoc_gas_4_1 | ec_lx2_bpoc_gas_4_1 | 387 | ec_lx2_bpoc_gas_4_1 | mbar | 10049368
[8 empty] | 10049377 | ec_lx2_bpoc_gas_4_10 | ec_lx2_bpoc_gas_4_10 | 388 | ec_lx2_bpoc_gas_4_10 | mbar | 10049377
[8 empty] | 10049421 | ec_lx2_bpoc_gas_4_10_m | ec_lx2_bpoc_gas_4_10_m | 389 | ec_lx2_bpoc_gas_4_10_m |  | 10049421
[8 empty] | 10049412 | ec_lx2_bpoc_gas_4_1_m | ec_lx2_bpoc_gas_4_1_m | 390 | ec_lx2_bpoc_gas_4_1_m |  | 10049412
[8 empty] | 10049369 | ec_lx2_bpoc_gas_4_2 | ec_lx2_bpoc_gas_4_2 | 391 | ec_lx2_bpoc_gas_4_2 | mbar | 10049369
[8 empty] | 10049413 | ec_lx2_bpoc_gas_4_2_m | ec_lx2_bpoc_gas_4_2_m | 392 | ec_lx2_bpoc_gas_4_2_m |  | 10049413
[8 empty] | 10049370 | ec_lx2_bpoc_gas_4_3 | ec_lx2_bpoc_gas_4_3 | 393 | ec_lx2_bpoc_gas_4_3 | mbar | 10049370
[8 empty] | 10049414 | ec_lx2_bpoc_gas_4_3_m | ec_lx2_bpoc_gas_4_3_m | 394 | ec_lx2_bpoc_gas_4_3_m |  | 10049414
[8 empty] | 10049371 | ec_lx2_bpoc_gas_4_4 | ec_lx2_bpoc_gas_4_4 | 395 | ec_lx2_bpoc_gas_4_4 | mbar | 10049371
[8 empty] | 10049415 | ec_lx2_bpoc_gas_4_4_m | ec_lx2_bpoc_gas_4_4_m | 396 | ec_lx2_bpoc_gas_4_4_m |  | 10049415
[8 empty] | 10049372 | ec_lx2_bpoc_gas_4_5 | ec_lx2_bpoc_gas_4_5 | 397 | ec_lx2_bpoc_gas_4_5 | mbar | 10049372
[8 empty] | 10049416 | ec_lx2_bpoc_gas_4_5_m | ec_lx2_bpoc_gas_4_5_m | 398 | ec_lx2_bpoc_gas_4_5_m |  | 10049416
[8 empty] | 10049373 | ec_lx2_bpoc_gas_4_6 | ec_lx2_bpoc_gas_4_6 | 399 | ec_lx2_bpoc_gas_4_6 | mbar | 10049373
[8 empty] | 10049417 | ec_lx2_bpoc_gas_4_6_m | ec_lx2_bpoc_gas_4_6_m | 400 | ec_lx2_bpoc_gas_4_6_m |  | 10049417
[8 empty] | 10049374 | ec_lx2_bpoc_gas_4_7 | ec_lx2_bpoc_gas_4_7 | 401 | ec_lx2_bpoc_gas_4_7 | mbar | 10049374
[8 empty] | 10049418 | ec_lx2_bpoc_gas_4_7_m | ec_lx2_bpoc_gas_4_7_m | 402 | ec_lx2_bpoc_gas_4_7_m |  | 10049418
[8 empty] | 10049375 | ec_lx2_bpoc_gas_4_8 | ec_lx2_bpoc_gas_4_8 | 403 | ec_lx2_bpoc_gas_4_8 | mbar | 10049375
[8 empty] | 10049419 | ec_lx2_bpoc_gas_4_8_m | ec_lx2_bpoc_gas_4_8_m | 404 | ec_lx2_bpoc_gas_4_8_m |  | 10049419
[8 empty] | 10049376 | ec_lx2_bpoc_gas_4_9 | ec_lx2_bpoc_gas_4_9 | 405 | ec_lx2_bpoc_gas_4_9 | mbar | 10049376
[8 empty] | 10049420 | ec_lx2_bpoc_gas_4_9_m | ec_lx2_bpoc_gas_4_9_m | 406 | ec_lx2_bpoc_gas_4_9_m |  | 10049420
[8 empty] | 1000086 | Efficiency_Estimate_1_Median | Efficiency_Estimate_1_Median | 407 | Efficiency_Estimate_1_Median | % | 1000086
[8 empty] | 1000085 | Efficiency_Estimtate_1 | Efficiency_Estimtate_1 | 408 | Efficiency_Estimtate_1 | % | 1000085
[8 empty] | 10049515 | emission_bamm_nox_noxs_engout_avg | emission_bamm_nox_noxs_engout_avg | 409 | emission_bamm_nox_noxs_engout_avg |  | 10049515
[8 empty] | 10049517 | emission_blx2_active | emission_blx2_active | 410 | emission_blx2_active |  | 10049517
[8 empty] | 10049518 | emission_blx2_ctrl_enable | emission_blx2_ctrl_enable | 411 | emission_blx2_ctrl_enable |  | 10049518
[8 empty] | 10049968 | emission_bnoxs_catout_heater_ok | emission_bnoxs_catout_heater_ok | 412 | emission_bnoxs_catout_heater_ok |  | 10049968
[8 empty] | 10049969 | emission_bnoxs_catout_nox_ok | emission_bnoxs_catout_nox_ok | 413 | emission_bnoxs_catout_nox_ok |  | 10049969
[8 empty] | 10049970 | emission_bnoxs_catout_nox_validity_ok | emission_bnoxs_catout_nox_validity_ok | 414 | emission_bnoxs_catout_nox_validity_ok |  | 10049970
[8 empty] | 10049971 | emission_bnoxs_catout_o2_ok | emission_bnoxs_catout_o2_ok | 415 | emission_bnoxs_catout_o2_ok |  | 10049971
[8 empty] | 10049972 | emission_bnoxs_catout_o2_validity_ok | emission_bnoxs_catout_o2_validity_ok | 416 | emission_bnoxs_catout_o2_validity_ok |  | 10049972
[8 empty] | 10049973 | emission_bnoxs_catout_power_ok | emission_bnoxs_catout_power_ok | 417 | emission_bnoxs_catout_power_ok |  | 10049973
[8 empty] | 10049974 | emission_bnoxs_engout_a_heater_ok | emission_bnoxs_engout_a_heater_ok | 418 | emission_bnoxs_engout_a_heater_ok |  | 10049974
[8 empty] | 10049975 | emission_bnoxs_engout_a_nox_ok | emission_bnoxs_engout_a_nox_ok | 419 | emission_bnoxs_engout_a_nox_ok |  | 10049975
[8 empty] | 10049976 | emission_bnoxs_engout_a_nox_validity_ok | emission_bnoxs_engout_a_nox_validity_ok | 420 | emission_bnoxs_engout_a_nox_validity_ok |  | 10049976
[8 empty] | 10049977 | emission_bnoxs_engout_a_o2_ok | emission_bnoxs_engout_a_o2_ok | 421 | emission_bnoxs_engout_a_o2_ok |  | 10049977
[8 empty] | 10049978 | emission_bnoxs_engout_a_o2_validity_ok | emission_bnoxs_engout_a_o2_validity_ok | 422 | emission_bnoxs_engout_a_o2_validity_ok |  | 10049978
[8 empty] | 10049979 | emission_bnoxs_engout_a_power_ok | emission_bnoxs_engout_a_power_ok | 423 | emission_bnoxs_engout_a_power_ok |  | 10049979
[8 empty] | 10049980 | emission_bnoxs_engout_b_heater_ok | emission_bnoxs_engout_b_heater_ok | 424 | emission_bnoxs_engout_b_heater_ok |  | 10049980
[8 empty] | 10049981 | emission_bnoxs_engout_b_nox_ok | emission_bnoxs_engout_b_nox_ok | 425 | emission_bnoxs_engout_b_nox_ok |  | 10049981
[8 empty] | 10049982 | emission_bnoxs_engout_b_nox_validity_ok | emission_bnoxs_engout_b_nox_validity_ok | 426 | emission_bnoxs_engout_b_nox_validity_ok |  | 10049982
[8 empty] | 10049983 | emission_bnoxs_engout_b_o2_ok | emission_bnoxs_engout_b_o2_ok | 427 | emission_bnoxs_engout_b_o2_ok |  | 10049983
[8 empty] | 10049984 | emission_bnoxs_engout_b_o2_validity_ok | emission_bnoxs_engout_b_o2_validity_ok | 428 | emission_bnoxs_engout_b_o2_validity_ok |  | 10049984
[8 empty] | 10049985 | emission_bnoxs_engout_b_power_ok | emission_bnoxs_engout_b_power_ok | 429 | emission_bnoxs_engout_b_power_ok |  | 10049985
[8 empty] | 10049986 | emission_bnoxs_engout_heater_ok | emission_bnoxs_engout_heater_ok | 430 | emission_bnoxs_engout_heater_ok |  | 10049986
[8 empty] | 10049987 | emission_bnoxs_engout_nox_ok | emission_bnoxs_engout_nox_ok | 431 | emission_bnoxs_engout_nox_ok |  | 10049987
[8 empty] | 10049988 | emission_bnoxs_engout_nox_validity_ok | emission_bnoxs_engout_nox_validity_ok | 432 | emission_bnoxs_engout_nox_validity_ok |  | 10049988
[8 empty] | 10049989 | emission_bnoxs_engout_o2_ok | emission_bnoxs_engout_o2_ok | 433 | emission_bnoxs_engout_o2_ok |  | 10049989
[8 empty] | 10049990 | emission_bnoxs_engout_o2_validity_ok | emission_bnoxs_engout_o2_validity_ok | 434 | emission_bnoxs_engout_o2_validity_ok |  | 10049990
[8 empty] | 10049991 | emission_bnoxs_engout_power_ok | emission_bnoxs_engout_power_ok | 435 | emission_bnoxs_engout_power_ok |  | 10049991
[8 empty] | 10049992 | emission_bscr_emvalve1_cg_dem | emission_bscr_emvalve1_cg_dem | 436 | emission_bscr_emvalve1_cg_dem |  | 10049992
[8 empty] | 10049993 | emission_bscr_emvalve1_sg_dem | emission_bscr_emvalve1_sg_dem | 437 | emission_bscr_emvalve1_sg_dem |  | 10049993
[8 empty] | 10049994 | emission_bscr_extemadjust_run | emission_bscr_extemadjust_run | 438 | emission_bscr_extemadjust_run |  | 10049994
[8 empty] | 10044846 | emission_bscr_injectvalve_urea | emission_bscr_injectvalve_urea | 439 | emission_bscr_injectvalve_urea |  | 10044846
[8 empty] | 10049435 | emission_cnt_noxs_engout_lastdiag | emission_cnt_noxs_engout_lastdiag | 440 | emission_cnt_noxs_engout_lastdiag |  | 10049435
[8 empty] | 10049488 | emission_diff_pres_cat_max | emission_diff_pres_cat_max | 441 | emission_diff_pres_cat_max | mbar | 10049488
[8 empty] | 10049822 | emission_icnt_nox_em_monlim_exc | emission_icnt_nox_em_monlim_exc | 442 | emission_icnt_nox_em_monlim_exc | h | 10049822
[8 empty] | 10049480 | emission_inoxs_catout_ophours | emission_inoxs_catout_ophours | 443 | emission_inoxs_catout_ophours | hours | 10049480
[8 empty] | 10049472 | emission_inoxs_engout_a_ophours | emission_inoxs_engout_a_ophours | 444 | emission_inoxs_engout_a_ophours | hours | 10049472
[8 empty] | 10049476 | emission_inoxs_engout_b_ophours | emission_inoxs_engout_b_ophours | 445 | emission_inoxs_engout_b_ophours | hours | 10049476
[8 empty] | 10049468 | emission_inoxs_engout_ophours | emission_inoxs_engout_ophours | 446 | emission_inoxs_engout_ophours | hours | 10049468
[8 empty] | 10049437 | emission_nox_noxs_engout_durdiag | emission_nox_noxs_engout_durdiag | 447 | emission_nox_noxs_engout_durdiag |  | 10049437
[8 empty] | 10049438 | emission_o2_noxs_engout_durdiag | emission_o2_noxs_engout_durdiag | 448 | emission_o2_noxs_engout_durdiag |  | 10049438
[8 empty] | 10049436 | emission_pc_noxs_engout_diagresult | emission_pc_noxs_engout_diagresult | 449 | emission_pc_noxs_engout_diagresult |  | 10049436
[8 empty] | 10049995 | emission_rco_em_avgshortterm | emission_rco_em_avgshortterm | 450 | emission_rco_em_avgshortterm | mg/Nm3 | 10049995
[8 empty] | 10049996 | emission_rco_em_monlim_hi | emission_rco_em_monlim_hi | 451 | emission_rco_em_monlim_hi | mg/Nm3 | 10049996
[8 empty] | 10044854 | emission_rco_scr_catout_avg | emission_rco_scr_catout_avg | 452 | emission_rco_scr_catout_avg | ppm | 10044854
[8 empty] | 10044857 | emission_rco_scr_cemsextcatout | emission_rco_scr_cemsextcatout | 453 | emission_rco_scr_cemsextcatout | ppm | 10044857
[8 empty] | 10049997 | emission_rco_scr_emline1 | emission_rco_scr_emline1 | 454 | emission_rco_scr_emline1 | ppm | 10049997
[8 empty] | 10050082 | emission_rdpr_scr_cat | emission_rdpr_scr_cat | 455 | emission_rdpr_scr_cat |  | 10050082
[8 empty] | 10044851 | emission_rflow_scr_ureadosingout | emission_rflow_scr_ureadosingout | 456 | emission_rflow_scr_ureadosingout | l/h | 10044851
[8 empty] | 10044845 | emission_rflow_scr_ureadosingunit_ff | emission_rflow_scr_ureadosingunit_ff | 457 | emission_rflow_scr_ureadosingunit_ff | l/h | 10044845
[8 empty] | 10044860 | emission_rhum_catout | emission_rhum_catout | 458 | emission_rhum_catout | % | 10044860
[8 empty] | 10044859 | emission_rno2_scr_cemsextcatout | emission_rno2_scr_cemsextcatout | 459 | emission_rno2_scr_cemsextcatout | ppm | 10044859
[8 empty] | 10049999 | emission_rno2_scr_emline1 | emission_rno2_scr_emline1 | 460 | emission_rno2_scr_emline1 | ppm | 10049999
[8 empty] | 10044856 | emission_rno_scr_cemsextcatout | emission_rno_scr_cemsextcatout | 461 | emission_rno_scr_cemsextcatout | ppm | 10044856
[8 empty] | 10049998 | emission_rno_scr_emline1 | emission_rno_scr_emline1 | 462 | emission_rno_scr_emline1 | ppm | 10049998
[8 empty] | 10049482 | emission_rnox_em_avgdaily | emission_rnox_em_avgdaily | 463 | emission_rnox_em_avgdaily | mg/Nm3 | 10049482
[8 empty] | 10050000 | emission_rnox_em_avgdaily_all | emission_rnox_em_avgdaily_all | 464 | emission_rnox_em_avgdaily_all | mg/Nm3 | 10050000
[8 empty] | 10049481 | emission_rnox_em_avgshortterm | emission_rnox_em_avgshortterm | 465 | emission_rnox_em_avgshortterm | mg/Nm3 | 10049481
[8 empty] | 10049514 | emission_rnox_em_engout_set | emission_rnox_em_engout_set | 466 | emission_rnox_em_engout_set | ppm | 10049514
[8 empty] | 10049820 | emission_rnox_em_monlim_hi | emission_rnox_em_monlim_hi | 467 | emission_rnox_em_monlim_hi | mg/Nm3 | 10049820
[8 empty] | 10049821 | emission_rnox_em_monlim_hitol | emission_rnox_em_monlim_hitol | 468 | emission_rnox_em_monlim_hitol | mg/Nm3 | 10049821
[8 empty] | 10044873 | emission_rnox_noxs_catout | emission_rnox_noxs_catout | 469 | emission_rnox_noxs_catout | ppm | 10044873
[8 empty] | 10049478 | emission_rnox_noxs_catout_durdiag | emission_rnox_noxs_catout_durdiag | 470 | emission_rnox_noxs_catout_durdiag | ppm | 10049478
[8 empty] | 10050001 | emission_rnox_noxs_catout_mg | emission_rnox_noxs_catout_mg | 471 | emission_rnox_noxs_catout_mg | mg/Nm3 | 10050001
[8 empty] | 10044872 | emission_rnox_noxs_engout | emission_rnox_noxs_engout | 472 | emission_rnox_noxs_engout | ppm | 10044872
[8 empty] | 10049483 | emission_rnox_noxs_engout_a | emission_rnox_noxs_engout_a | 473 | emission_rnox_noxs_engout_a | ppm | 10049483
[8 empty] | 10049470 | emission_rnox_noxs_engout_a_durdiag | emission_rnox_noxs_engout_a_durdiag | 474 | emission_rnox_noxs_engout_a_durdiag | ppm | 10049470
[8 empty] | 10050002 | emission_rnox_noxs_engout_a_mg | emission_rnox_noxs_engout_a_mg | 475 | emission_rnox_noxs_engout_a_mg | mg/Nm3 | 10050002
[8 empty] | 10050003 | emission_rnox_noxs_engout_avg | emission_rnox_noxs_engout_avg | 476 | emission_rnox_noxs_engout_avg | ppm | 10050003
[8 empty] | 10049484 | emission_rnox_noxs_engout_b | emission_rnox_noxs_engout_b | 477 | emission_rnox_noxs_engout_b | ppm | 10049484
[8 empty] | 10049474 | emission_rnox_noxs_engout_b_durdiag | emission_rnox_noxs_engout_b_durdiag | 478 | emission_rnox_noxs_engout_b_durdiag | ppm | 10049474
[8 empty] | 10050004 | emission_rnox_noxs_engout_b_mg | emission_rnox_noxs_engout_b_mg | 479 | emission_rnox_noxs_engout_b_mg | mg/Nm3 | 10050004
[8 empty] | 10050005 | emission_rnox_noxs_engout_mg | emission_rnox_noxs_engout_mg | 480 | emission_rnox_noxs_engout_mg | mg/Nm3 | 10050005
[8 empty] | 10049516 | emission_rnox_noxs_engout_mg_avg | emission_rnox_noxs_engout_mg_avg | 481 | emission_rnox_noxs_engout_mg_avg | mg/Nm3 | 10049516
[8 empty] | 10044855 | emission_rnox_scr_catout_avg | emission_rnox_scr_catout_avg | 482 | emission_rnox_scr_catout_avg | ppm | 10044855
[8 empty] | 10044862 | emission_ro2_noxs_catout | emission_ro2_noxs_catout | 483 | emission_ro2_noxs_catout | % | 10044862
[8 empty] | 10049479 | emission_ro2_noxs_catout_durdiag | emission_ro2_noxs_catout_durdiag | 484 | emission_ro2_noxs_catout_durdiag | % | 10049479
[8 empty] | 10050006 | emission_ro2_noxs_catout_filt | emission_ro2_noxs_catout_filt | 485 | emission_ro2_noxs_catout_filt | % | 10050006
[8 empty] | 10044861 | emission_ro2_noxs_engout | emission_ro2_noxs_engout | 486 | emission_ro2_noxs_engout | % | 10044861
[8 empty] | 10049485 | emission_ro2_noxs_engout_a | emission_ro2_noxs_engout_a | 487 | emission_ro2_noxs_engout_a | % | 10049485
[8 empty] | 10049471 | emission_ro2_noxs_engout_a_durdiag | emission_ro2_noxs_engout_a_durdiag | 488 | emission_ro2_noxs_engout_a_durdiag | % | 10049471
[8 empty] | 10050007 | emission_ro2_noxs_engout_a_filt | emission_ro2_noxs_engout_a_filt | 489 | emission_ro2_noxs_engout_a_filt | % | 10050007
[8 empty] | 10050008 | emission_ro2_noxs_engout_avg_filt | emission_ro2_noxs_engout_avg_filt | 490 | emission_ro2_noxs_engout_avg_filt | % | 10050008
[8 empty] | 10049486 | emission_ro2_noxs_engout_b | emission_ro2_noxs_engout_b | 491 | emission_ro2_noxs_engout_b | % | 10049486
[8 empty] | 10049475 | emission_ro2_noxs_engout_b_durdiag | emission_ro2_noxs_engout_b_durdiag | 492 | emission_ro2_noxs_engout_b_durdiag | % | 10049475
[8 empty] | 10050009 | emission_ro2_noxs_engout_b_filt | emission_ro2_noxs_engout_b_filt | 493 | emission_ro2_noxs_engout_b_filt | % | 10050009
[8 empty] | 10050010 | emission_ro2_noxs_engout_filt | emission_ro2_noxs_engout_filt | 494 | emission_ro2_noxs_engout_filt | % | 10050010
[8 empty] | 10044858 | emission_ro2_scr_cemsextcatout | emission_ro2_scr_cemsextcatout | 495 | emission_ro2_scr_cemsextcatout | % | 10044858
[8 empty] | 10049477 | emission_rpc_noxs_catout_diagresult | emission_rpc_noxs_catout_diagresult | 496 | emission_rpc_noxs_catout_diagresult | % | 10049477
[8 empty] | 10049469 | emission_rpc_noxs_engout_a_diagresult | emission_rpc_noxs_engout_a_diagresult | 497 | emission_rpc_noxs_engout_a_diagresult | % | 10049469
[8 empty] | 10049473 | emission_rpc_noxs_engout_b_diagresult | emission_rpc_noxs_engout_b_diagresult | 498 | emission_rpc_noxs_engout_b_diagresult | % | 10049473
[8 empty] | 10044842 | emission_rpr_scr_catin | emission_rpr_scr_catin | 499 | emission_rpr_scr_catin | mbar | 10044842
[8 empty] | 10044844 | emission_rpr_scr_catout | emission_rpr_scr_catout | 500 | emission_rpr_scr_catout | mbar | 10044844
[8 empty] | 10044850 | emission_rpr_scr_comprairsupply | emission_rpr_scr_comprairsupply | 501 | emission_rpr_scr_comprairsupply | bar | 10044850
[8 empty] | 10044843 | emission_rpr_scr_ureadosingin | emission_rpr_scr_ureadosingin | 502 | emission_rpr_scr_ureadosingin | bar | 10044843
[8 empty] | 10044847 | emission_rpr_scr_ureadosingout | emission_rpr_scr_ureadosingout | 503 | emission_rpr_scr_ureadosingout | bar | 10044847
[8 empty] | 10044848 | emission_rt_scr_catavg | emission_rt_scr_catavg | 504 | emission_rt_scr_catavg | °C | 10044848
[8 empty] | 10044852 | emission_rt_scr_catin | emission_rt_scr_catin | 505 | emission_rt_scr_catin | °C | 10044852
[8 empty] | 10044853 | emission_rt_scr_catout | emission_rt_scr_catout | 506 | emission_rt_scr_catout | °C | 10044853
[8 empty] | 10044864 | emission_rvol_scr_ureaconsumption | emission_rvol_scr_ureaconsumption | 507 | emission_rvol_scr_ureaconsumption | m3 | 10044864
[8 empty] | 1040166 | Engine_OpHour_Fixed_Timestamp | Engine_OpHour_Fixed_Timestamp | 508 | Engine_OpHour_Fixed_Timestamp | . | 1040166
[8 empty] | 1040117 | Engine_Slowdown_Time_Detection | Engine_Slowdown_Time_Detection | 509 | Engine_Slowdown_Time_Detection | . | 1040117
[8 empty] | 1040115 | Engine_Slowdown_Time_Monitoring_Sec | Engine_Slowdown_Time_Monitoring_Sec | 510 | Engine_Slowdown_Time_Monitoring_Sec | sec | 1040115
[8 empty] | 1040116 | Engine_Slowdown_Time_Oil_Correction | Engine_Slowdown_Time_Oil_Correction | 511 | Engine_Slowdown_Time_Oil_Correction | . | 1040116
[8 empty] | 10049487 | enginecontroller_blx2_ss | enginecontroller_blx2_ss | 512 | enginecontroller_blx2_ss |  | 10049487
[8 empty] | 10044933 | enginecontroller_rhum_airin_abs | enginecontroller_rhum_airin_abs | 513 | enginecontroller_rhum_airin_abs | g/kg | 10044933
[8 empty] | 10044934 | enginecontroller_rhum_airin_rel | enginecontroller_rhum_airin_rel | 514 | enginecontroller_rhum_airin_rel | % | 10044934
[8 empty] | 10050011 | enginecontroller_rpr_p2s_lx2 | enginecontroller_rpr_p2s_lx2 | 515 | enginecontroller_rpr_p2s_lx2 | mbar | 10050011
[8 empty] | 1019866 | Estimated_Compressor_Bypass_Position | Estimated_Compressor_Bypass_Position | 516 | Estimated_Compressor_Bypass_Position | % | 1019866
[8 empty] | 1019867 | Estimated_IntakeTemperatureRange | Estimated_IntakeTemperatureRange | 517 | Estimated_IntakeTemperatureRange | C | 1019867
[8 empty] | 10050081 | exhaust_bscavvalve | exhaust_bscavvalve | 518 | exhaust_bscavvalve | °C | 10050081
[8 empty] | 10049825 | exhaust_icnt_ophours_oxi | exhaust_icnt_ophours_oxi | 519 | exhaust_icnt_ophours_oxi | h | 10049825
[8 empty] | 19583 | Exhaust_NOx_NOx1 | Exhaust_NOx_NOx1 | 520 | Exhaust_NOx_NOx1 | ppm | 19583
[8 empty] | 19133 | Exhaust_NOx_NOx2 | Exhaust_NOx_NOx2 | 521 | Exhaust_NOx_NOx2 | ppm | 19133
[8 empty] | 19584 | Exhaust_NOx_O2_1 | Exhaust_NOx_O2_1 | 522 | Exhaust_NOx_O2_1 | % | 19584
[8 empty] | 19585 | Exhaust_NOx_O2_2 | Exhaust_NOx_O2_2 | 523 | Exhaust_NOx_O2_2 | % | 19585
[8 empty] | 10049824 | exhaust_rpr_oxicat_diff | exhaust_rpr_oxicat_diff | 524 | exhaust_rpr_oxicat_diff | mbar | 10049824
[8 empty] | 10049823 | exhaust_rpr_oxicat_in | exhaust_rpr_oxicat_in | 525 | exhaust_rpr_oxicat_in | mbar | 10049823
[8 empty] | 10049332 | exhaust_rpr_oxicat_in_fast | exhaust_rpr_oxicat_in_fast | 526 | exhaust_rpr_oxicat_in_fast | bar | 10049332
[8 empty] | 10049333 | exhaust_rpr_oxicat_in_fast_peak | exhaust_rpr_oxicat_in_fast_peak | 527 | exhaust_rpr_oxicat_in_fast_peak | bar | 10049333
[8 empty] | 19079 | Exhaust_TCSpeedA | Exhaust_TCSpeedA | 528 | Exhaust_TCSpeedA | 1000/min | 19079
[8 empty] | 19080 | Exhaust_TCSpeedB | Exhaust_TCSpeedB | 529 | Exhaust_TCSpeedB | 1000/min | 19080
[8 empty] | 19081 | Exhaust_TCSpeedLPA | Exhaust_TCSpeedLPA | 530 | Exhaust_TCSpeedLPA | 1000/min | 19081
[8 empty] | 19082 | Exhaust_TCSpeedLPB | Exhaust_TCSpeedLPB | 531 | Exhaust_TCSpeedLPB | 1000/min | 19082
[8 empty] | 59 | Exhaust_TempBoil | Exhaust_TempBoil | 532 | Exhaust_TempBoil | C | 59
[8 empty] | 61 | Exhaust_TempCat | Exhaust_TempCat | 533 | Exhaust_TempCat | C | 61
[8 empty] | 25 | Exhaust_TempCatIn | Exhaust_TempCatIn | 534 | Exhaust_TempCatIn | C | 25
[8 empty] | 189 | Exhaust_TempCatOut | Exhaust_TempCatOut | 535 | Exhaust_TempCatOut | C | 189
[8 empty] | 26 | Exhaust_TempCyl01 | Exhaust_TempCyl01 | 536 | Exhaust_TempCyl01 | C (high) | 26
[8 empty] | 27 | Exhaust_TempCyl02 | Exhaust_TempCyl02 | 537 | Exhaust_TempCyl02 | C (high) | 27
[8 empty] | 28 | Exhaust_TempCyl03 | Exhaust_TempCyl03 | 538 | Exhaust_TempCyl03 | C (high) | 28
[8 empty] | 29 | Exhaust_TempCyl04 | Exhaust_TempCyl04 | 539 | Exhaust_TempCyl04 | C (high) | 29
[8 empty] | 30 | Exhaust_TempCyl05 | Exhaust_TempCyl05 | 540 | Exhaust_TempCyl05 | C (high) | 30
[8 empty] | 31 | Exhaust_TempCyl06 | Exhaust_TempCyl06 | 541 | Exhaust_TempCyl06 | C (high) | 31
[8 empty] | 32 | Exhaust_TempCyl07 | Exhaust_TempCyl07 | 542 | Exhaust_TempCyl07 | C (high) | 32
[8 empty] | 33 | Exhaust_TempCyl08 | Exhaust_TempCyl08 | 543 | Exhaust_TempCyl08 | C (high) | 33
[8 empty] | 34 | Exhaust_TempCyl09 | Exhaust_TempCyl09 | 544 | Exhaust_TempCyl09 | C (high) | 34
[8 empty] | 35 | Exhaust_TempCyl10 | Exhaust_TempCyl10 | 545 | Exhaust_TempCyl10 | C (high) | 35
[8 empty] | 36 | Exhaust_TempCyl11 | Exhaust_TempCyl11 | 546 | Exhaust_TempCyl11 | C (high) | 36
[8 empty] | 37 | Exhaust_TempCyl12 | Exhaust_TempCyl12 | 547 | Exhaust_TempCyl12 | C (high) | 37
[8 empty] | 38 | Exhaust_TempCyl13 | Exhaust_TempCyl13 | 548 | Exhaust_TempCyl13 | C (high) | 38
[8 empty] | 41 | Exhaust_TempCyl14 | Exhaust_TempCyl14 | 549 | Exhaust_TempCyl14 | C (high) | 41
[8 empty] | 43 | Exhaust_TempCyl15 | Exhaust_TempCyl15 | 550 | Exhaust_TempCyl15 | C (high) | 43
[8 empty] | 44 | Exhaust_TempCyl16 | Exhaust_TempCyl16 | 551 | Exhaust_TempCyl16 | C (high) | 44
[8 empty] | 45 | Exhaust_TempCyl17 | Exhaust_TempCyl17 | 552 | Exhaust_TempCyl17 | C (high) | 45
[8 empty] | 46 | Exhaust_TempCyl18 | Exhaust_TempCyl18 | 553 | Exhaust_TempCyl18 | C (high) | 46
[8 empty] | 48 | Exhaust_TempCyl19 | Exhaust_TempCyl19 | 554 | Exhaust_TempCyl19 | C (high) | 48
[8 empty] | 50 | Exhaust_TempCyl20 | Exhaust_TempCyl20 | 555 | Exhaust_TempCyl20 | C (high) | 50
[8 empty] | 190 | Exhaust_TempCyl21 | Exhaust_TempCyl21 | 556 | Exhaust_TempCyl21 | C (high) | 190
[8 empty] | 193 | Exhaust_TempCyl22 | Exhaust_TempCyl22 | 557 | Exhaust_TempCyl22 | C (high) | 193
[8 empty] | 191 | Exhaust_TempCyl23 | Exhaust_TempCyl23 | 558 | Exhaust_TempCyl23 | C (high) | 191
[8 empty] | 194 | Exhaust_TempCyl24 | Exhaust_TempCyl24 | 559 | Exhaust_TempCyl24 | C (high) | 194
[8 empty] | 52 | Exhaust_TempCylAvg | Exhaust_TempCylAvg | 560 | Exhaust_TempCylAvg | C (high) | 52
[8 empty] | 1000048 | Exhaust_TempCylAvg_ss | Exhaust_TempCylAvg_ss | 561 | Exhaust_TempCylAvg_ss | C | 1000048
[8 empty] | 63 | Exhaust_TempCylMax | Exhaust_TempCylMax | 562 | Exhaust_TempCylMax | C (high) | 63
[8 empty] | 1000050 | Exhaust_TempCylMax_ss | Exhaust_TempCylMax_ss | 563 | Exhaust_TempCylMax_ss | C | 1000050
[8 empty] | 54 | Exhaust_TempCylMin | Exhaust_TempCylMin | 564 | Exhaust_TempCylMin | C (high) | 54
[8 empty] | 1000049 | Exhaust_TempCylMin_ss | Exhaust_TempCylMin_ss | 565 | Exhaust_TempCylMin_ss | C | 1000049
[8 empty] | 214 | Exhaust_TempETCIn | Exhaust_TempETCIn | 566 | Exhaust_TempETCIn | C (high) | 214
[8 empty] | 56 | Exhaust_TempHexIn | Exhaust_TempHexIn | 567 | Exhaust_TempHexIn | C (high) | 56
[8 empty] | 65 | Exhaust_TempHexOut | Exhaust_TempHexOut | 568 | Exhaust_TempHexOut | C (high) | 65
[8 empty] | 19093 | Exhaust_TempLPTCOutletA | Exhaust_TempLPTCOutletA | 569 | Exhaust_TempLPTCOutletA | °C | 19093
[8 empty] | 19094 | Exhaust_TempLPTCOutletB | Exhaust_TempLPTCOutletB | 570 | Exhaust_TempLPTCOutletB | °C | 19094
[8 empty] | 1000051 | Exhaust_TempMaxSpread | Exhaust_TempMaxSpread | 571 | Exhaust_TempMaxSpread | C | 1000051
[8 empty] | 152 | Exhaust_TempThermReact1Avg | Exhaust_TempThermReact1Avg | 572 | Exhaust_TempThermReact1Avg | C (high) | 152
[8 empty] | 153 | Exhaust_TempThermReact2Avg | Exhaust_TempThermReact2Avg | 573 | Exhaust_TempThermReact2Avg | C (high) | 153
[8 empty] | 10044277 | G2_Knck_Abs01 | G2_Knck_Abs01 | 574 | G2_Knck_Abs01 |  | 10044277
[8 empty] | 10044278 | G2_Knck_Abs02 | G2_Knck_Abs02 | 575 | G2_Knck_Abs02 |  | 10044278
[8 empty] | 10044276 | G2_Knck_Abs03 | G2_Knck_Abs03 | 576 | G2_Knck_Abs03 |  | 10044276
[8 empty] | 10044275 | G2_Knck_Abs04 | G2_Knck_Abs04 | 577 | G2_Knck_Abs04 |  | 10044275
[8 empty] | 10044279 | G2_Knck_Abs05 | G2_Knck_Abs05 | 578 | G2_Knck_Abs05 |  | 10044279
[8 empty] | 10044280 | G2_Knck_Abs06 | G2_Knck_Abs06 | 579 | G2_Knck_Abs06 |  | 10044280
[8 empty] | 10044283 | G2_Knck_Abs07 | G2_Knck_Abs07 | 580 | G2_Knck_Abs07 |  | 10044283
[8 empty] | 10044284 | G2_Knck_Abs08 | G2_Knck_Abs08 | 581 | G2_Knck_Abs08 |  | 10044284
[8 empty] | 10044282 | G2_Knck_Abs09 | G2_Knck_Abs09 | 582 | G2_Knck_Abs09 |  | 10044282
[8 empty] | 10044281 | G2_Knck_Abs10 | G2_Knck_Abs10 | 583 | G2_Knck_Abs10 |  | 10044281
[8 empty] | 10044285 | G2_Knck_Abs11 | G2_Knck_Abs11 | 584 | G2_Knck_Abs11 |  | 10044285
[8 empty] | 10044288 | G2_Knck_Abs12 | G2_Knck_Abs12 | 585 | G2_Knck_Abs12 |  | 10044288
[8 empty] | 10044286 | G2_Knck_Abs13 | G2_Knck_Abs13 | 586 | G2_Knck_Abs13 |  | 10044286
[8 empty] | 10044287 | G2_Knck_Abs14 | G2_Knck_Abs14 | 587 | G2_Knck_Abs14 |  | 10044287
[8 empty] | 10044289 | G2_Knck_Abs15 | G2_Knck_Abs15 | 588 | G2_Knck_Abs15 |  | 10044289
[8 empty] | 10044290 | G2_Knck_Abs16 | G2_Knck_Abs16 | 589 | G2_Knck_Abs16 |  | 10044290
[8 empty] | 10044292 | G2_Knck_Abs17 | G2_Knck_Abs17 | 590 | G2_Knck_Abs17 |  | 10044292
[8 empty] | 10044293 | G2_Knck_Abs18 | G2_Knck_Abs18 | 591 | G2_Knck_Abs18 |  | 10044293
[8 empty] | 10044294 | G2_Knck_Abs19 | G2_Knck_Abs19 | 592 | G2_Knck_Abs19 |  | 10044294
[8 empty] | 10044291 | G2_Knck_Abs20 | G2_Knck_Abs20 | 593 | G2_Knck_Abs20 |  | 10044291
[8 empty] | 10044295 | G2_Knck_Rel01 | G2_Knck_Rel01 | 594 | G2_Knck_Rel01 |  | 10044295
[8 empty] | 10044296 | G2_Knck_Rel02 | G2_Knck_Rel02 | 595 | G2_Knck_Rel02 |  | 10044296
[8 empty] | 10044298 | G2_Knck_Rel03 | G2_Knck_Rel03 | 596 | G2_Knck_Rel03 |  | 10044298
[8 empty] | 10044297 | G2_Knck_Rel04 | G2_Knck_Rel04 | 597 | G2_Knck_Rel04 |  | 10044297
[8 empty] | 10044299 | G2_Knck_Rel05 | G2_Knck_Rel05 | 598 | G2_Knck_Rel05 |  | 10044299
[8 empty] | 10044301 | G2_Knck_Rel06 | G2_Knck_Rel06 | 599 | G2_Knck_Rel06 |  | 10044301
[8 empty] | 10044302 | G2_Knck_Rel07 | G2_Knck_Rel07 | 600 | G2_Knck_Rel07 |  | 10044302
[8 empty] | 10044300 | G2_Knck_Rel08 | G2_Knck_Rel08 | 601 | G2_Knck_Rel08 |  | 10044300
[8 empty] | 10044303 | G2_Knck_Rel09 | G2_Knck_Rel09 | 602 | G2_Knck_Rel09 |  | 10044303
[8 empty] | 10044305 | G2_Knck_Rel10 | G2_Knck_Rel10 | 603 | G2_Knck_Rel10 |  | 10044305
[8 empty] | 10044304 | G2_Knck_Rel11 | G2_Knck_Rel11 | 604 | G2_Knck_Rel11 |  | 10044304
[8 empty] | 10044306 | G2_Knck_Rel12 | G2_Knck_Rel12 | 605 | G2_Knck_Rel12 |  | 10044306
[8 empty] | 10044307 | G2_Knck_Rel13 | G2_Knck_Rel13 | 606 | G2_Knck_Rel13 |  | 10044307
[8 empty] | 10044309 | G2_Knck_Rel14 | G2_Knck_Rel14 | 607 | G2_Knck_Rel14 |  | 10044309
[8 empty] | 10044308 | G2_Knck_Rel15 | G2_Knck_Rel15 | 608 | G2_Knck_Rel15 |  | 10044308
[8 empty] | 10044310 | G2_Knck_Rel16 | G2_Knck_Rel16 | 609 | G2_Knck_Rel16 |  | 10044310
[8 empty] | 10044311 | G2_Knck_Rel17 | G2_Knck_Rel17 | 610 | G2_Knck_Rel17 |  | 10044311
[8 empty] | 10044312 | G2_Knck_Rel18 | G2_Knck_Rel18 | 611 | G2_Knck_Rel18 |  | 10044312
[8 empty] | 10044313 | G2_Knck_Rel19 | G2_Knck_Rel19 | 612 | G2_Knck_Rel19 |  | 10044313
[8 empty] | 10044314 | G2_Knck_Rel20 | G2_Knck_Rel20 | 613 | G2_Knck_Rel20 |  | 10044314
[8 empty] | 10049433 | gas_qualmix | gas_qualmix | 614 | gas_qualmix |  | 10049433
[8 empty] | 10049494 | gas_type | gas_type | 615 | gas_type |  | 10049494
[8 empty] | 19134 | Gasmixer_AirThrot | Gasmixer_AirThrot | 616 | Gasmixer_AirThrot | mm | 19134
[8 empty] | 19135 | Gasmixer_AirThrotEnc1 | Gasmixer_AirThrotEnc1 | 617 | Gasmixer_AirThrotEnc1 | % | 19135
[8 empty] | 19136 | Gasmixer_AirThrotEnc2 | Gasmixer_AirThrotEnc2 | 618 | Gasmixer_AirThrotEnc2 | % | 19136
[8 empty] | 87 | Gasmixer_GasMix1Pos | Gasmixer_GasMix1Pos | 619 | Gasmixer_GasMix1Pos | % | 87
[8 empty] | 16545 | Gasmixer_GasMix2Pos | Gasmixer_GasMix2Pos | 620 | Gasmixer_GasMix2Pos | % | 16545
[8 empty] | 19137 | Gasmixer_GasThrot | Gasmixer_GasThrot | 621 | Gasmixer_GasThrot | % | 19137
[8 empty] | 10049875 | gastrain_icnt_gas_normm3 | gastrain_icnt_gas_normm3 | 622 | gastrain_icnt_gas_normm3 |  | 10049875
[8 empty] | 10049876 | gastrain_icnt_gas_opm3 | gastrain_icnt_gas_opm3 | 623 | gastrain_icnt_gas_opm3 |  | 10049876
[8 empty] | 16616 | GasTrain_PressBaro | GasTrain_PressBaro | 624 | GasTrain_PressBaro | mbar | 16616
[8 empty] | 19298 | GasTrain_PressMain | GasTrain_PressMain | 625 | GasTrain_PressMain | mbar | 19298
[8 empty] | 10049874 | gastrain_rpr_gr_avg | gastrain_rpr_gr_avg | 626 | gastrain_rpr_gr_avg |  | 10049874
[8 empty] | 19299 | GasTrain_TempMain | GasTrain_TempMain | 627 | GasTrain_TempMain | °C | 19299
[8 empty] | 20423 | Gen2_ContGen | Gen2_ContGen | 628 | Gen2_ContGen |  | 20423
[8 empty] | 10049872 | generator_boilskid_fan_dem | generator_boilskid_fan_dem | 629 | generator_boilskid_fan_dem |  | 10049872
[8 empty] | 10049866 | generator_rflow_oilskid_de | generator_rflow_oilskid_de | 630 | generator_rflow_oilskid_de |  | 10049866
[8 empty] | 10049867 | generator_rflow_oilskid_nde | generator_rflow_oilskid_nde | 631 | generator_rflow_oilskid_nde |  | 10049867
[8 empty] | 10049873 | generator_rlev_oilskid_tank | generator_rlev_oilskid_tank | 632 | generator_rlev_oilskid_tank |  | 10049873
[8 empty] | 10049868 | generator_rpr_oilskid_hp_de | generator_rpr_oilskid_hp_de | 633 | generator_rpr_oilskid_hp_de |  | 10049868
[8 empty] | 10049869 | generator_rpr_oilskid_hp_nde | generator_rpr_oilskid_hp_nde | 634 | generator_rpr_oilskid_hp_nde |  | 10049869
[8 empty] | 10049871 | generator_rt_oilskid_tank | generator_rt_oilskid_tank | 635 | generator_rt_oilskid_tank |  | 10049871
[8 empty] | 58 | Generator_TempBear1 | Generator_TempBear1 | 636 | Generator_TempBear1 | C | 58
[8 empty] | 60 | Generator_TempBear2 | Generator_TempBear2 | 637 | Generator_TempBear2 | C | 60
[8 empty] | 19138 | Generator_TempInlet | Generator_TempInlet | 638 | Generator_TempInlet | °C | 19138
[8 empty] | 19300 | Generator_TempOutlet | Generator_TempOutlet | 639 | Generator_TempOutlet | °C | 19300
[8 empty] | 62 | Generator_TempWind1 | Generator_TempWind1 | 640 | Generator_TempWind1 | C | 62
[8 empty] | 64 | Generator_TempWind2 | Generator_TempWind2 | 641 | Generator_TempWind2 | C | 64
[8 empty] | 66 | Generator_TempWind3 | Generator_TempWind3 | 642 | Generator_TempWind3 | C | 66
[8 empty] | 67 | Generator_VoltExit | Generator_VoltExit | 643 | Generator_VoltExit | V | 67
[8 empty] | 1001003 | Geno_BearingTempMeasured_DriveEnd | Geno_BearingTempMeasured_DriveEnd | 644 | Geno_BearingTempMeasured_DriveEnd | C | 1001003
[8 empty] | 1001002 | Geno_BearingTempMeasured_NonDriveEnd | Geno_BearingTempMeasured_NonDriveEnd | 645 | Geno_BearingTempMeasured_NonDriveEnd | C | 1001002
[8 empty] | 1001001 | Geno_BearingTempPrediction_DriveEnd | Geno_BearingTempPrediction_DriveEnd | 646 | Geno_BearingTempPrediction_DriveEnd | C | 1001001
[8 empty] | 1001000 | Geno_BearingTempPrediction_NonDriveEnd | Geno_BearingTempPrediction_NonDriveEnd | 647 | Geno_BearingTempPrediction_NonDriveEnd | C | 1001000
[8 empty] | 1040230 | Genset_Oph_Recalculation_Start_Point | Genset_Oph_Recalculation_Start_Point | 648 | Genset_Oph_Recalculation_Start_Point | . | 1040230
[8 empty] | 1040167 | GenSet_OpHour_Fixed_Timestamp | GenSet_OpHour_Fixed_Timestamp | 649 | GenSet_OpHour_Fixed_Timestamp | . | 1040167
[8 empty] | 1040176 | GenSet_OpHours_Backup | GenSet_OpHours_Backup | 650 | GenSet_OpHours_Backup | oph | 1040176
[8 empty] | 10049526 | halio_power_apparent_s | halio_power_apparent_s | 651 | halio_power_apparent_s | kVA | 10049526
[8 empty] | 10049525 | halio_power_fact_cos_phi | halio_power_fact_cos_phi | 652 | halio_power_fact_cos_phi |  | 10049525
[8 empty] | 10047723 | halio_rf_mmd | halio_rf_mmd | 653 | halio_rf_mmd | Hz | 10047723
[8 empty] | 10049434 | halio_rf_mmd_2 | halio_rf_mmd_2 | 654 | halio_rf_mmd_2 | Hz | 10049434
[8 empty] | 10047710 | halio_ru_bus_l1_2 | halio_ru_bus_l1_2 | 655 | halio_ru_bus_l1_2 | V | 10047710
[8 empty] | 10047713 | halio_ru_bus_l1n | halio_ru_bus_l1n | 656 | halio_ru_bus_l1n | V | 10047713
[8 empty] | 10047711 | halio_ru_bus_l2_3 | halio_ru_bus_l2_3 | 657 | halio_ru_bus_l2_3 | V | 10047711
[8 empty] | 10047714 | halio_ru_bus_l2n | halio_ru_bus_l2n | 658 | halio_ru_bus_l2n | V | 10047714
[8 empty] | 10047712 | halio_ru_bus_l3_1 | halio_ru_bus_l3_1 | 659 | halio_ru_bus_l3_1 | V | 10047712
[8 empty] | 10047715 | halio_ru_bus_l3n | halio_ru_bus_l3n | 660 | halio_ru_bus_l3n | V | 10047715
[8 empty] | 10047716 | halio_ru_l1_2 | halio_ru_l1_2 | 661 | halio_ru_l1_2 | V | 10047716
[8 empty] | 10047719 | halio_ru_l1n | halio_ru_l1n | 662 | halio_ru_l1n | V | 10047719
[8 empty] | 10047717 | halio_ru_l2_3 | halio_ru_l2_3 | 663 | halio_ru_l2_3 | V | 10047717
[8 empty] | 10047720 | halio_ru_l2n | halio_ru_l2n | 664 | halio_ru_l2n | V | 10047720
[8 empty] | 10047718 | halio_ru_l3_1 | halio_ru_l3_1 | 665 | halio_ru_l3_1 | V | 10047718
[8 empty] | 10047721 | halio_ru_l3n | halio_ru_l3n | 666 | halio_ru_l3n | V | 10047721
[8 empty] | 10049870 | heatingcooling_rt_ecwbeng | heatingcooling_rt_ecwbeng | 667 | heatingcooling_rt_ecwbeng |  | 10049870
[8 empty] | 225 | Hyd_OilCount_Trend_ActiveEnergy | Hyd_OilCount_Trend_ActiveEnergy | 668 | Hyd_OilCount_Trend_ActiveEnergy |  | 225
[8 empty] | 226 | Hyd_OilCount_Trend_AvgPower | Hyd_OilCount_Trend_AvgPower | 669 | Hyd_OilCount_Trend_AvgPower | kW | 226
[8 empty] | 237 | Hyd_OilCount_Trend_DeltaOpH | Hyd_OilCount_Trend_DeltaOpH | 670 | Hyd_OilCount_Trend_DeltaOpH |  | 237
[8 empty] | 227 | Hyd_OilCount_Trend_OilConsumption | Hyd_OilCount_Trend_OilConsumption | 671 | Hyd_OilCount_Trend_OilConsumption | g/kWh | 227
[8 empty] | 228 | Hyd_OilCount_Trend_OilVolume | Hyd_OilCount_Trend_OilVolume | 672 | Hyd_OilCount_Trend_OilVolume | ml | 228
[8 empty] | 69 | Hyd_PressCoolWat | Hyd_PressCoolWat | 673 | Hyd_PressCoolWat | bar | 69
[8 empty] | 217 | Hyd_PressCrankCase | Hyd_PressCrankCase | 674 | Hyd_PressCrankCase | mbar | 217
[8 empty] | 68 | Hyd_PressOil | Hyd_PressOil | 675 | Hyd_PressOil | bar | 68
[8 empty] | 16546 | Hyd_PressOilDif | Hyd_PressOilDif | 676 | Hyd_PressOilDif | bar | 16546
[8 empty] | 19301 | Hyd_PressOilDif1 | Hyd_PressOilDif1 | 677 | Hyd_PressOilDif1 | bar | 19301
[8 empty] | 19302 | Hyd_PressTCOilFiltIn | Hyd_PressTCOilFiltIn | 678 | Hyd_PressTCOilFiltIn | bar | 19302
[8 empty] | 70 | Hyd_TempCoolWat | Hyd_TempCoolWat | 679 | Hyd_TempCoolWat | C | 70
[8 empty] | 71 | Hyd_TempOil | Hyd_TempOil | 680 | Hyd_TempOil | C | 71
[8 empty] | 19303 | Hyd_TempOilPumpOut | Hyd_TempOilPumpOut | 681 | Hyd_TempOilPumpOut | °C | 19303
[8 empty] | 72 | Hyd_TempWatRet | Hyd_TempWatRet | 682 | Hyd_TempWatRet | C | 72
[8 empty] | 156 | Hyd_TempWatRetCoolOut | Hyd_TempWatRetCoolOut | 683 | Hyd_TempWatRetCoolOut | C | 156
[8 empty] | 185 | Hyd_TempWatRetPreEng | Hyd_TempWatRetPreEng | 684 | Hyd_TempWatRetPreEng | C | 185
[8 empty] | 10008987 | iDays_SinceStart | iDays_SinceStart | 685 | iDays_SinceStart |  | 10008987
[8 empty] | 20628 | Ignition_IC_HW_Vers | Ignition_IC_HW_Vers | 686 | Ignition_IC_HW_Vers |  | 20628
[8 empty] | 20641 | Ignition_IC_SW_Vers | Ignition_IC_SW_Vers | 687 | Ignition_IC_SW_Vers |  | 20641
[8 empty] | 126 | Ignition_ITPAvg | Ignition_ITPAvg | 688 | Ignition_ITPAvg | °KW | 126
[8 empty] | 16591 | Ignition_ITPCyl01 | Ignition_ITPCyl01 | 689 | Ignition_ITPCyl01 | °KW | 16591
[8 empty] | 16592 | Ignition_ITPCyl02 | Ignition_ITPCyl02 | 690 | Ignition_ITPCyl02 | °KW | 16592
[8 empty] | 16593 | Ignition_ITPCyl03 | Ignition_ITPCyl03 | 691 | Ignition_ITPCyl03 | °KW | 16593
[8 empty] | 16594 | Ignition_ITPCyl04 | Ignition_ITPCyl04 | 692 | Ignition_ITPCyl04 | °KW | 16594
[8 empty] | 16595 | Ignition_ITPCyl05 | Ignition_ITPCyl05 | 693 | Ignition_ITPCyl05 | °KW | 16595
[8 empty] | 16596 | Ignition_ITPCyl06 | Ignition_ITPCyl06 | 694 | Ignition_ITPCyl06 | °KW | 16596
[8 empty] | 16597 | Ignition_ITPCyl07 | Ignition_ITPCyl07 | 695 | Ignition_ITPCyl07 | °KW | 16597
[8 empty] | 16598 | Ignition_ITPCyl08 | Ignition_ITPCyl08 | 696 | Ignition_ITPCyl08 | °KW | 16598
[8 empty] | 16599 | Ignition_ITPCyl09 | Ignition_ITPCyl09 | 697 | Ignition_ITPCyl09 | °KW | 16599
[8 empty] | 16600 | Ignition_ITPCyl10 | Ignition_ITPCyl10 | 698 | Ignition_ITPCyl10 | °KW | 16600
[8 empty] | 16601 | Ignition_ITPCyl11 | Ignition_ITPCyl11 | 699 | Ignition_ITPCyl11 | °KW | 16601
[8 empty] | 16602 | Ignition_ITPCyl12 | Ignition_ITPCyl12 | 700 | Ignition_ITPCyl12 | °KW | 16602
[8 empty] | 16603 | Ignition_ITPCyl13 | Ignition_ITPCyl13 | 701 | Ignition_ITPCyl13 | °KW | 16603
[8 empty] | 16604 | Ignition_ITPCyl14 | Ignition_ITPCyl14 | 702 | Ignition_ITPCyl14 | °KW | 16604
[8 empty] | 16605 | Ignition_ITPCyl15 | Ignition_ITPCyl15 | 703 | Ignition_ITPCyl15 | °KW | 16605
[8 empty] | 16606 | Ignition_ITPCyl16 | Ignition_ITPCyl16 | 704 | Ignition_ITPCyl16 | °KW | 16606
[8 empty] | 16607 | Ignition_ITPCyl17 | Ignition_ITPCyl17 | 705 | Ignition_ITPCyl17 | °KW | 16607
[8 empty] | 16608 | Ignition_ITPCyl18 | Ignition_ITPCyl18 | 706 | Ignition_ITPCyl18 | °KW | 16608
[8 empty] | 16609 | Ignition_ITPCyl19 | Ignition_ITPCyl19 | 707 | Ignition_ITPCyl19 | °KW | 16609
[8 empty] | 16610 | Ignition_ITPCyl20 | Ignition_ITPCyl20 | 708 | Ignition_ITPCyl20 | °KW | 16610
[8 empty] | 16611 | Ignition_ITPCyl21 | Ignition_ITPCyl21 | 709 | Ignition_ITPCyl21 | °KW | 16611
[8 empty] | 16612 | Ignition_ITPCyl22 | Ignition_ITPCyl22 | 710 | Ignition_ITPCyl22 | °KW | 16612
[8 empty] | 16613 | Ignition_ITPCyl23 | Ignition_ITPCyl23 | 711 | Ignition_ITPCyl23 | °KW | 16613
[8 empty] | 16614 | Ignition_ITPCyl24 | Ignition_ITPCyl24 | 712 | Ignition_ITPCyl24 | °KW | 16614
[8 empty] | 117 | Ignition_SAFI_ElectTemp1 | Ignition_SAFI_ElectTemp1 | 713 | Ignition_SAFI_ElectTemp1 | C | 117
[8 empty] | 176 | Ignition_SAFI_ElectTemp10 | Ignition_SAFI_ElectTemp10 | 714 | Ignition_SAFI_ElectTemp10 | C | 176
[8 empty] | 192 | Ignition_SAFI_ElectTemp11 | Ignition_SAFI_ElectTemp11 | 715 | Ignition_SAFI_ElectTemp11 | C | 192
[8 empty] | 195 | Ignition_SAFI_ElectTemp12 | Ignition_SAFI_ElectTemp12 | 716 | Ignition_SAFI_ElectTemp12 | C | 195
[8 empty] | 162 | Ignition_SAFI_ElectTemp2 | Ignition_SAFI_ElectTemp2 | 717 | Ignition_SAFI_ElectTemp2 | C | 162
[8 empty] | 163 | Ignition_SAFI_ElectTemp3 | Ignition_SAFI_ElectTemp3 | 718 | Ignition_SAFI_ElectTemp3 | C | 163
[8 empty] | 164 | Ignition_SAFI_ElectTemp4 | Ignition_SAFI_ElectTemp4 | 719 | Ignition_SAFI_ElectTemp4 | C | 164
[8 empty] | 165 | Ignition_SAFI_ElectTemp5 | Ignition_SAFI_ElectTemp5 | 720 | Ignition_SAFI_ElectTemp5 | C | 165
[8 empty] | 119 | Ignition_SAFI_ElectTemp6 | Ignition_SAFI_ElectTemp6 | 721 | Ignition_SAFI_ElectTemp6 | C | 119
[8 empty] | 173 | Ignition_SAFI_ElectTemp7 | Ignition_SAFI_ElectTemp7 | 722 | Ignition_SAFI_ElectTemp7 | C | 173
[8 empty] | 167 | Ignition_SAFI_ElectTemp8 | Ignition_SAFI_ElectTemp8 | 723 | Ignition_SAFI_ElectTemp8 | C | 167
[8 empty] | 174 | Ignition_SAFI_ElectTemp9 | Ignition_SAFI_ElectTemp9 | 724 | Ignition_SAFI_ElectTemp9 | C | 174
[8 empty] | 20220 | Ignition_SAFI_FilterVers1 | Ignition_SAFI_FilterVers1 | 725 | Ignition_SAFI_FilterVers1 |  | 20220
[8 empty] | 20265 | Ignition_SAFI_FilterVers10 | Ignition_SAFI_FilterVers10 | 726 | Ignition_SAFI_FilterVers10 |  | 20265
[8 empty] | 20266 | Ignition_SAFI_FilterVers11 | Ignition_SAFI_FilterVers11 | 727 | Ignition_SAFI_FilterVers11 |  | 20266
[8 empty] | 20267 | Ignition_SAFI_FilterVers12 | Ignition_SAFI_FilterVers12 | 728 | Ignition_SAFI_FilterVers12 |  | 20267
[8 empty] | 20221 | Ignition_SAFI_FilterVers2 | Ignition_SAFI_FilterVers2 | 729 | Ignition_SAFI_FilterVers2 |  | 20221
[8 empty] | 20232 | Ignition_SAFI_FilterVers3 | Ignition_SAFI_FilterVers3 | 730 | Ignition_SAFI_FilterVers3 |  | 20232
[8 empty] | 20222 | Ignition_SAFI_FilterVers4 | Ignition_SAFI_FilterVers4 | 731 | Ignition_SAFI_FilterVers4 |  | 20222
[8 empty] | 20223 | Ignition_SAFI_FilterVers5 | Ignition_SAFI_FilterVers5 | 732 | Ignition_SAFI_FilterVers5 |  | 20223
[8 empty] | 20224 | Ignition_SAFI_FilterVers6 | Ignition_SAFI_FilterVers6 | 733 | Ignition_SAFI_FilterVers6 |  | 20224
[8 empty] | 20225 | Ignition_SAFI_FilterVers7 | Ignition_SAFI_FilterVers7 | 734 | Ignition_SAFI_FilterVers7 |  | 20225
[8 empty] | 20239 | Ignition_SAFI_FilterVers8 | Ignition_SAFI_FilterVers8 | 735 | Ignition_SAFI_FilterVers8 |  | 20239
[8 empty] | 20264 | Ignition_SAFI_FilterVers9 | Ignition_SAFI_FilterVers9 | 736 | Ignition_SAFI_FilterVers9 |  | 20264
[8 empty] | 20184 | Ignition_SAFI_HW_Vers1 | Ignition_SAFI_HW_Vers1 | 737 | Ignition_SAFI_HW_Vers1 |  | 20184
[8 empty] | 20245 | Ignition_SAFI_HW_Vers10 | Ignition_SAFI_HW_Vers10 | 738 | Ignition_SAFI_HW_Vers10 |  | 20245
[8 empty] | 20246 | Ignition_SAFI_HW_Vers11 | Ignition_SAFI_HW_Vers11 | 739 | Ignition_SAFI_HW_Vers11 |  | 20246
[8 empty] | 20247 | Ignition_SAFI_HW_Vers12 | Ignition_SAFI_HW_Vers12 | 740 | Ignition_SAFI_HW_Vers12 |  | 20247
[8 empty] | 20185 | Ignition_SAFI_HW_Vers2 | Ignition_SAFI_HW_Vers2 | 741 | Ignition_SAFI_HW_Vers2 |  | 20185
[8 empty] | 20226 | Ignition_SAFI_HW_Vers3 | Ignition_SAFI_HW_Vers3 | 742 | Ignition_SAFI_HW_Vers3 |  | 20226
[8 empty] | 20186 | Ignition_SAFI_HW_Vers4 | Ignition_SAFI_HW_Vers4 | 743 | Ignition_SAFI_HW_Vers4 |  | 20186
[8 empty] | 20187 | Ignition_SAFI_HW_Vers5 | Ignition_SAFI_HW_Vers5 | 744 | Ignition_SAFI_HW_Vers5 |  | 20187
[8 empty] | 20188 | Ignition_SAFI_HW_Vers6 | Ignition_SAFI_HW_Vers6 | 745 | Ignition_SAFI_HW_Vers6 |  | 20188
[8 empty] | 20189 | Ignition_SAFI_HW_Vers7 | Ignition_SAFI_HW_Vers7 | 746 | Ignition_SAFI_HW_Vers7 |  | 20189
[8 empty] | 20233 | Ignition_SAFI_HW_Vers8 | Ignition_SAFI_HW_Vers8 | 747 | Ignition_SAFI_HW_Vers8 |  | 20233
[8 empty] | 20244 | Ignition_SAFI_HW_Vers9 | Ignition_SAFI_HW_Vers9 | 748 | Ignition_SAFI_HW_Vers9 |  | 20244
[8 empty] | 20630 | Ignition_SAFI_HWOpt_Vers1 | Ignition_SAFI_HWOpt_Vers1 | 749 | Ignition_SAFI_HWOpt_Vers1 |  | 20630
[8 empty] | 20639 | Ignition_SAFI_HWOpt_Vers10 | Ignition_SAFI_HWOpt_Vers10 | 750 | Ignition_SAFI_HWOpt_Vers10 |  | 20639
[8 empty] | 20642 | Ignition_SAFI_HWOpt_Vers11 | Ignition_SAFI_HWOpt_Vers11 | 751 | Ignition_SAFI_HWOpt_Vers11 |  | 20642
[8 empty] | 20640 | Ignition_SAFI_HWOpt_Vers12 | Ignition_SAFI_HWOpt_Vers12 | 752 | Ignition_SAFI_HWOpt_Vers12 |  | 20640
[8 empty] | 20631 | Ignition_SAFI_HWOpt_Vers2 | Ignition_SAFI_HWOpt_Vers2 | 753 | Ignition_SAFI_HWOpt_Vers2 |  | 20631
[8 empty] | 20632 | Ignition_SAFI_HWOpt_Vers3 | Ignition_SAFI_HWOpt_Vers3 | 754 | Ignition_SAFI_HWOpt_Vers3 |  | 20632
[8 empty] | 20633 | Ignition_SAFI_HWOpt_Vers4 | Ignition_SAFI_HWOpt_Vers4 | 755 | Ignition_SAFI_HWOpt_Vers4 |  | 20633
[8 empty] | 20634 | Ignition_SAFI_HWOpt_Vers5 | Ignition_SAFI_HWOpt_Vers5 | 756 | Ignition_SAFI_HWOpt_Vers5 |  | 20634
[8 empty] | 20635 | Ignition_SAFI_HWOpt_Vers6 | Ignition_SAFI_HWOpt_Vers6 | 757 | Ignition_SAFI_HWOpt_Vers6 |  | 20635
[8 empty] | 20636 | Ignition_SAFI_HWOpt_Vers7 | Ignition_SAFI_HWOpt_Vers7 | 758 | Ignition_SAFI_HWOpt_Vers7 |  | 20636
[8 empty] | 20637 | Ignition_SAFI_HWOpt_Vers8 | Ignition_SAFI_HWOpt_Vers8 | 759 | Ignition_SAFI_HWOpt_Vers8 |  | 20637
[8 empty] | 20638 | Ignition_SAFI_HWOpt_Vers9 | Ignition_SAFI_HWOpt_Vers9 | 760 | Ignition_SAFI_HWOpt_Vers9 |  | 20638
[8 empty] | 20196 | Ignition_SAFI_OpHours1 | Ignition_SAFI_OpHours1 | 761 | Ignition_SAFI_OpHours1 |  | 20196
[8 empty] | 20253 | Ignition_SAFI_OpHours10 | Ignition_SAFI_OpHours10 | 762 | Ignition_SAFI_OpHours10 |  | 20253
[8 empty] | 20254 | Ignition_SAFI_OpHours11 | Ignition_SAFI_OpHours11 | 763 | Ignition_SAFI_OpHours11 |  | 20254
[8 empty] | 20255 | Ignition_SAFI_OpHours12 | Ignition_SAFI_OpHours12 | 764 | Ignition_SAFI_OpHours12 |  | 20255
[8 empty] | 20197 | Ignition_SAFI_OpHours2 | Ignition_SAFI_OpHours2 | 765 | Ignition_SAFI_OpHours2 |  | 20197
[8 empty] | 20228 | Ignition_SAFI_OpHours3 | Ignition_SAFI_OpHours3 | 766 | Ignition_SAFI_OpHours3 |  | 20228
[8 empty] | 20198 | Ignition_SAFI_OpHours4 | Ignition_SAFI_OpHours4 | 767 | Ignition_SAFI_OpHours4 |  | 20198
[8 empty] | 20199 | Ignition_SAFI_OpHours5 | Ignition_SAFI_OpHours5 | 768 | Ignition_SAFI_OpHours5 |  | 20199
[8 empty] | 20200 | Ignition_SAFI_OpHours6 | Ignition_SAFI_OpHours6 | 769 | Ignition_SAFI_OpHours6 |  | 20200
[8 empty] | 20201 | Ignition_SAFI_OpHours7 | Ignition_SAFI_OpHours7 | 770 | Ignition_SAFI_OpHours7 |  | 20201
[8 empty] | 20235 | Ignition_SAFI_OpHours8 | Ignition_SAFI_OpHours8 | 771 | Ignition_SAFI_OpHours8 |  | 20235
[8 empty] | 20252 | Ignition_SAFI_OpHours9 | Ignition_SAFI_OpHours9 | 772 | Ignition_SAFI_OpHours9 |  | 20252
[8 empty] | 20208 | Ignition_SAFI_ProdDate1 | Ignition_SAFI_ProdDate1 | 773 | Ignition_SAFI_ProdDate1 |  | 20208
[8 empty] | 20269 | Ignition_SAFI_ProdDate10 | Ignition_SAFI_ProdDate10 | 774 | Ignition_SAFI_ProdDate10 |  | 20269
[8 empty] | 10049853 | Ignition_SAFI_ProdDate10_day | Ignition_SAFI_ProdDate10_day | 775 | Ignition_SAFI_ProdDate10_day |  | 10049853
[8 empty] | 10049841 | Ignition_SAFI_ProdDate10_mon | Ignition_SAFI_ProdDate10_mon | 776 | Ignition_SAFI_ProdDate10_mon |  | 10049841
[8 empty] | 20270 | Ignition_SAFI_ProdDate11 | Ignition_SAFI_ProdDate11 | 777 | Ignition_SAFI_ProdDate11 |  | 20270
[8 empty] | 10049854 | Ignition_SAFI_ProdDate11_day | Ignition_SAFI_ProdDate11_day | 778 | Ignition_SAFI_ProdDate11_day |  | 10049854
[8 empty] | 10049842 | Ignition_SAFI_ProdDate11_mon | Ignition_SAFI_ProdDate11_mon | 779 | Ignition_SAFI_ProdDate11_mon |  | 10049842
[8 empty] | 20271 | Ignition_SAFI_ProdDate12 | Ignition_SAFI_ProdDate12 | 780 | Ignition_SAFI_ProdDate12 |  | 20271
[8 empty] | 10049855 | Ignition_SAFI_ProdDate12_day | Ignition_SAFI_ProdDate12_day | 781 | Ignition_SAFI_ProdDate12_day |  | 10049855
[8 empty] | 10049843 | Ignition_SAFI_ProdDate12_mon | Ignition_SAFI_ProdDate12_mon | 782 | Ignition_SAFI_ProdDate12_mon |  | 10049843
[8 empty] | 10049844 | Ignition_SAFI_ProdDate1_day | Ignition_SAFI_ProdDate1_day | 783 | Ignition_SAFI_ProdDate1_day |  | 10049844
[8 empty] | 10049832 | Ignition_SAFI_ProdDate1_mon | Ignition_SAFI_ProdDate1_mon | 784 | Ignition_SAFI_ProdDate1_mon |  | 10049832
[8 empty] | 20209 | Ignition_SAFI_ProdDate2 | Ignition_SAFI_ProdDate2 | 785 | Ignition_SAFI_ProdDate2 |  | 20209
[8 empty] | 10049845 | Ignition_SAFI_ProdDate2_day | Ignition_SAFI_ProdDate2_day | 786 | Ignition_SAFI_ProdDate2_day |  | 10049845
[8 empty] | 10049833 | Ignition_SAFI_ProdDate2_mon | Ignition_SAFI_ProdDate2_mon | 787 | Ignition_SAFI_ProdDate2_mon |  | 10049833
[8 empty] | 20230 | Ignition_SAFI_ProdDate3 | Ignition_SAFI_ProdDate3 | 788 | Ignition_SAFI_ProdDate3 |  | 20230
[8 empty] | 10049846 | Ignition_SAFI_ProdDate3_day | Ignition_SAFI_ProdDate3_day | 789 | Ignition_SAFI_ProdDate3_day |  | 10049846
[8 empty] | 10049834 | Ignition_SAFI_ProdDate3_mon | Ignition_SAFI_ProdDate3_mon | 790 | Ignition_SAFI_ProdDate3_mon |  | 10049834
[8 empty] | 20210 | Ignition_SAFI_ProdDate4 | Ignition_SAFI_ProdDate4 | 791 | Ignition_SAFI_ProdDate4 |  | 20210
[8 empty] | 10049847 | Ignition_SAFI_ProdDate4_day | Ignition_SAFI_ProdDate4_day | 792 | Ignition_SAFI_ProdDate4_day |  | 10049847
[8 empty] | 10049835 | Ignition_SAFI_ProdDate4_mon | Ignition_SAFI_ProdDate4_mon | 793 | Ignition_SAFI_ProdDate4_mon |  | 10049835
[8 empty] | 20211 | Ignition_SAFI_ProdDate5 | Ignition_SAFI_ProdDate5 | 794 | Ignition_SAFI_ProdDate5 |  | 20211
[8 empty] | 10049848 | Ignition_SAFI_ProdDate5_day | Ignition_SAFI_ProdDate5_day | 795 | Ignition_SAFI_ProdDate5_day |  | 10049848
[8 empty] | 10049836 | Ignition_SAFI_ProdDate5_mon | Ignition_SAFI_ProdDate5_mon | 796 | Ignition_SAFI_ProdDate5_mon |  | 10049836
[8 empty] | 20212 | Ignition_SAFI_ProdDate6 | Ignition_SAFI_ProdDate6 | 797 | Ignition_SAFI_ProdDate6 |  | 20212
[8 empty] | 10049849 | Ignition_SAFI_ProdDate6_day | Ignition_SAFI_ProdDate6_day | 798 | Ignition_SAFI_ProdDate6_day |  | 10049849
[8 empty] | 10049837 | Ignition_SAFI_ProdDate6_mon | Ignition_SAFI_ProdDate6_mon | 799 | Ignition_SAFI_ProdDate6_mon |  | 10049837
[8 empty] | 20213 | Ignition_SAFI_ProdDate7 | Ignition_SAFI_ProdDate7 | 800 | Ignition_SAFI_ProdDate7 |  | 20213
[8 empty] | 10049850 | Ignition_SAFI_ProdDate7_day | Ignition_SAFI_ProdDate7_day | 801 | Ignition_SAFI_ProdDate7_day |  | 10049850
[8 empty] | 10049838 | Ignition_SAFI_ProdDate7_mon | Ignition_SAFI_ProdDate7_mon | 802 | Ignition_SAFI_ProdDate7_mon |  | 10049838
[8 empty] | 20237 | Ignition_SAFI_ProdDate8 | Ignition_SAFI_ProdDate8 | 803 | Ignition_SAFI_ProdDate8 |  | 20237
[8 empty] | 10049851 | Ignition_SAFI_ProdDate8_day | Ignition_SAFI_ProdDate8_day | 804 | Ignition_SAFI_ProdDate8_day |  | 10049851
[8 empty] | 10049839 | Ignition_SAFI_ProdDate8_mon | Ignition_SAFI_ProdDate8_mon | 805 | Ignition_SAFI_ProdDate8_mon |  | 10049839
[8 empty] | 20268 | Ignition_SAFI_ProdDate9 | Ignition_SAFI_ProdDate9 | 806 | Ignition_SAFI_ProdDate9 |  | 20268
[8 empty] | 10049852 | Ignition_SAFI_ProdDate9_day | Ignition_SAFI_ProdDate9_day | 807 | Ignition_SAFI_ProdDate9_day |  | 10049852
[8 empty] | 10049840 | Ignition_SAFI_ProdDate9_mon | Ignition_SAFI_ProdDate9_mon | 808 | Ignition_SAFI_ProdDate9_mon |  | 10049840
[8 empty] | 20202 | Ignition_SAFI_SerialNr1 | Ignition_SAFI_SerialNr1 | 809 | Ignition_SAFI_SerialNr1 |  | 20202
[8 empty] | 20257 | Ignition_SAFI_SerialNr10 | Ignition_SAFI_SerialNr10 | 810 | Ignition_SAFI_SerialNr10 |  | 20257
[8 empty] | 20258 | Ignition_SAFI_SerialNr11 | Ignition_SAFI_SerialNr11 | 811 | Ignition_SAFI_SerialNr11 |  | 20258
[8 empty] | 20259 | Ignition_SAFI_SerialNr12 | Ignition_SAFI_SerialNr12 | 812 | Ignition_SAFI_SerialNr12 |  | 20259
[8 empty] | 20203 | Ignition_SAFI_SerialNr2 | Ignition_SAFI_SerialNr2 | 813 | Ignition_SAFI_SerialNr2 |  | 20203
[8 empty] | 20229 | Ignition_SAFI_SerialNr3 | Ignition_SAFI_SerialNr3 | 814 | Ignition_SAFI_SerialNr3 |  | 20229
[8 empty] | 20204 | Ignition_SAFI_SerialNr4 | Ignition_SAFI_SerialNr4 | 815 | Ignition_SAFI_SerialNr4 |  | 20204
[8 empty] | 20205 | Ignition_SAFI_SerialNr5 | Ignition_SAFI_SerialNr5 | 816 | Ignition_SAFI_SerialNr5 |  | 20205
[8 empty] | 20206 | Ignition_SAFI_SerialNr6 | Ignition_SAFI_SerialNr6 | 817 | Ignition_SAFI_SerialNr6 |  | 20206
[8 empty] | 20207 | Ignition_SAFI_SerialNr7 | Ignition_SAFI_SerialNr7 | 818 | Ignition_SAFI_SerialNr7 |  | 20207
[8 empty] | 20236 | Ignition_SAFI_SerialNr8 | Ignition_SAFI_SerialNr8 | 819 | Ignition_SAFI_SerialNr8 |  | 20236
[8 empty] | 20256 | Ignition_SAFI_SerialNr9 | Ignition_SAFI_SerialNr9 | 820 | Ignition_SAFI_SerialNr9 |  | 20256
[8 empty] | 20190 | Ignition_SAFI_SW_Vers1 | Ignition_SAFI_SW_Vers1 | 821 | Ignition_SAFI_SW_Vers1 |  | 20190
[8 empty] | 20249 | Ignition_SAFI_SW_Vers10 | Ignition_SAFI_SW_Vers10 | 822 | Ignition_SAFI_SW_Vers10 |  | 20249
[8 empty] | 20250 | Ignition_SAFI_SW_Vers11 | Ignition_SAFI_SW_Vers11 | 823 | Ignition_SAFI_SW_Vers11 |  | 20250
[8 empty] | 20251 | Ignition_SAFI_SW_Vers12 | Ignition_SAFI_SW_Vers12 | 824 | Ignition_SAFI_SW_Vers12 |  | 20251
[8 empty] | 20191 | Ignition_SAFI_SW_Vers2 | Ignition_SAFI_SW_Vers2 | 825 | Ignition_SAFI_SW_Vers2 |  | 20191
[8 empty] | 20227 | Ignition_SAFI_SW_Vers3 | Ignition_SAFI_SW_Vers3 | 826 | Ignition_SAFI_SW_Vers3 |  | 20227
[8 empty] | 20192 | Ignition_SAFI_SW_Vers4 | Ignition_SAFI_SW_Vers4 | 827 | Ignition_SAFI_SW_Vers4 |  | 20192
[8 empty] | 20193 | Ignition_SAFI_SW_Vers5 | Ignition_SAFI_SW_Vers5 | 828 | Ignition_SAFI_SW_Vers5 |  | 20193
[8 empty] | 20194 | Ignition_SAFI_SW_Vers6 | Ignition_SAFI_SW_Vers6 | 829 | Ignition_SAFI_SW_Vers6 |  | 20194
[8 empty] | 20195 | Ignition_SAFI_SW_Vers7 | Ignition_SAFI_SW_Vers7 | 830 | Ignition_SAFI_SW_Vers7 |  | 20195
[8 empty] | 20234 | Ignition_SAFI_SW_Vers8 | Ignition_SAFI_SW_Vers8 | 831 | Ignition_SAFI_SW_Vers8 |  | 20234
[8 empty] | 20248 | Ignition_SAFI_SW_Vers9 | Ignition_SAFI_SW_Vers9 | 832 | Ignition_SAFI_SW_Vers9 |  | 20248
[8 empty] | 20214 | Ignition_SAFI_TeethError1 | Ignition_SAFI_TeethError1 | 833 | Ignition_SAFI_TeethError1 |  | 20214
[8 empty] | 20261 | Ignition_SAFI_TeethError10 | Ignition_SAFI_TeethError10 | 834 | Ignition_SAFI_TeethError10 |  | 20261
[8 empty] | 20262 | Ignition_SAFI_TeethError11 | Ignition_SAFI_TeethError11 | 835 | Ignition_SAFI_TeethError11 |  | 20262
[8 empty] | 20263 | Ignition_SAFI_TeethError12 | Ignition_SAFI_TeethError12 | 836 | Ignition_SAFI_TeethError12 |  | 20263
[8 empty] | 20215 | Ignition_SAFI_TeethError2 | Ignition_SAFI_TeethError2 | 837 | Ignition_SAFI_TeethError2 |  | 20215
[8 empty] | 20231 | Ignition_SAFI_TeethError3 | Ignition_SAFI_TeethError3 | 838 | Ignition_SAFI_TeethError3 |  | 20231
[8 empty] | 20216 | Ignition_SAFI_TeethError4 | Ignition_SAFI_TeethError4 | 839 | Ignition_SAFI_TeethError4 |  | 20216
[8 empty] | 20217 | Ignition_SAFI_TeethError5 | Ignition_SAFI_TeethError5 | 840 | Ignition_SAFI_TeethError5 |  | 20217
[8 empty] | 20218 | Ignition_SAFI_TeethError6 | Ignition_SAFI_TeethError6 | 841 | Ignition_SAFI_TeethError6 |  | 20218
[8 empty] | 20219 | Ignition_SAFI_TeethError7 | Ignition_SAFI_TeethError7 | 842 | Ignition_SAFI_TeethError7 |  | 20219
[8 empty] | 20238 | Ignition_SAFI_TeethError8 | Ignition_SAFI_TeethError8 | 843 | Ignition_SAFI_TeethError8 |  | 20238
[8 empty] | 20260 | Ignition_SAFI_TeethError9 | Ignition_SAFI_TeethError9 | 844 | Ignition_SAFI_TeethError9 |  | 20260
[8 empty] | 10009031 | iSA_PICurGrad01 | iSA_PICurGrad01 | 845 | iSA_PICurGrad01 |  | 10009031
[8 empty] | 10009032 | iSA_PICurGrad02 | iSA_PICurGrad02 | 846 | iSA_PICurGrad02 |  | 10009032
[8 empty] | 10009034 | iSA_PICurGrad03 | iSA_PICurGrad03 | 847 | iSA_PICurGrad03 |  | 10009034
[8 empty] | 10009033 | iSA_PICurGrad04 | iSA_PICurGrad04 | 848 | iSA_PICurGrad04 |  | 10009033
[8 empty] | 10009035 | iSA_PICurGrad05 | iSA_PICurGrad05 | 849 | iSA_PICurGrad05 |  | 10009035
[8 empty] | 10009036 | iSA_PICurGrad06 | iSA_PICurGrad06 | 850 | iSA_PICurGrad06 |  | 10009036
[8 empty] | 10009038 | iSA_PICurGrad07 | iSA_PICurGrad07 | 851 | iSA_PICurGrad07 |  | 10009038
[8 empty] | 10009037 | iSA_PICurGrad08 | iSA_PICurGrad08 | 852 | iSA_PICurGrad08 |  | 10009037
[8 empty] | 10009039 | iSA_PICurGrad09 | iSA_PICurGrad09 | 853 | iSA_PICurGrad09 |  | 10009039
[8 empty] | 10009040 | iSA_PICurGrad10 | iSA_PICurGrad10 | 854 | iSA_PICurGrad10 |  | 10009040
[8 empty] | 10009041 | iSA_PICurGrad11 | iSA_PICurGrad11 | 855 | iSA_PICurGrad11 |  | 10009041
[8 empty] | 10009042 | iSA_PICurGrad12 | iSA_PICurGrad12 | 856 | iSA_PICurGrad12 |  | 10009042
[8 empty] | 10009043 | iSA_PICurGrad13 | iSA_PICurGrad13 | 857 | iSA_PICurGrad13 |  | 10009043
[8 empty] | 10009044 | iSA_PICurGrad14 | iSA_PICurGrad14 | 858 | iSA_PICurGrad14 |  | 10009044
[8 empty] | 10009046 | iSA_PICurGrad15 | iSA_PICurGrad15 | 859 | iSA_PICurGrad15 |  | 10009046
[8 empty] | 10008972 | iSA_PICurGrad16 | iSA_PICurGrad16 | 860 | iSA_PICurGrad16 |  | 10008972
[8 empty] | 10008971 | iSA_PICurGrad17 | iSA_PICurGrad17 | 861 | iSA_PICurGrad17 |  | 10008971
[8 empty] | 10008973 | iSA_PICurGrad18 | iSA_PICurGrad18 | 862 | iSA_PICurGrad18 |  | 10008973
[8 empty] | 10008978 | iSA_PICurGrad19 | iSA_PICurGrad19 | 863 | iSA_PICurGrad19 |  | 10008978
[8 empty] | 10008975 | iSA_PICurGrad20 | iSA_PICurGrad20 | 864 | iSA_PICurGrad20 |  | 10008975
[8 empty] | 1040164 | Issue_Eng_OpHour | Issue_Eng_OpHour | 865 | Issue_Eng_OpHour | . | 1040164
[8 empty] | 1040165 | Issue_GenSet_OpHour | Issue_GenSet_OpHour | 866 | Issue_GenSet_OpHour | . | 1040165
[8 empty] | 10008738 | item_count | item_count | 867 | item_count |  | 10008738
[8 empty] | 130 | Knock_KLS90_CurrSensor1 | Knock_KLS90_CurrSensor1 | 868 | Knock_KLS90_CurrSensor1 | mA | 130
[8 empty] | 131 | Knock_KLS90_CurrSensor2 | Knock_KLS90_CurrSensor2 | 869 | Knock_KLS90_CurrSensor2 | mA | 131
[8 empty] | 133 | Knock_KLS98_IntKnock_Cyl01 | Knock_KLS98_IntKnock_Cyl01 | 870 | Knock_KLS98_IntKnock_Cyl01 | % | 133
[8 empty] | 151 | Knock_KLS98_IntKnock_Cyl02 | Knock_KLS98_IntKnock_Cyl02 | 871 | Knock_KLS98_IntKnock_Cyl02 | % | 151
[8 empty] | 135 | Knock_KLS98_IntKnock_Cyl03 | Knock_KLS98_IntKnock_Cyl03 | 872 | Knock_KLS98_IntKnock_Cyl03 | % | 135
[8 empty] | 145 | Knock_KLS98_IntKnock_Cyl04 | Knock_KLS98_IntKnock_Cyl04 | 873 | Knock_KLS98_IntKnock_Cyl04 | % | 145
[8 empty] | 146 | Knock_KLS98_IntKnock_Cyl05 | Knock_KLS98_IntKnock_Cyl05 | 874 | Knock_KLS98_IntKnock_Cyl05 | % | 146
[8 empty] | 168 | Knock_KLS98_IntKnock_Cyl06 | Knock_KLS98_IntKnock_Cyl06 | 875 | Knock_KLS98_IntKnock_Cyl06 | % | 168
[8 empty] | 138 | Knock_KLS98_IntKnock_Cyl07 | Knock_KLS98_IntKnock_Cyl07 | 876 | Knock_KLS98_IntKnock_Cyl07 | % | 138
[8 empty] | 142 | Knock_KLS98_IntKnock_Cyl08 | Knock_KLS98_IntKnock_Cyl08 | 877 | Knock_KLS98_IntKnock_Cyl08 | % | 142
[8 empty] | 141 | Knock_KLS98_IntKnock_Cyl09 | Knock_KLS98_IntKnock_Cyl09 | 878 | Knock_KLS98_IntKnock_Cyl09 | % | 141
[8 empty] | 139 | Knock_KLS98_IntKnock_Cyl10 | Knock_KLS98_IntKnock_Cyl10 | 879 | Knock_KLS98_IntKnock_Cyl10 | % | 139
[8 empty] | 140 | Knock_KLS98_IntKnock_Cyl11 | Knock_KLS98_IntKnock_Cyl11 | 880 | Knock_KLS98_IntKnock_Cyl11 | % | 140
[8 empty] | 137 | Knock_KLS98_IntKnock_Cyl12 | Knock_KLS98_IntKnock_Cyl12 | 881 | Knock_KLS98_IntKnock_Cyl12 | % | 137
[8 empty] | 169 | Knock_KLS98_IntKnock_Cyl13 | Knock_KLS98_IntKnock_Cyl13 | 882 | Knock_KLS98_IntKnock_Cyl13 | % | 169
[8 empty] | 136 | Knock_KLS98_IntKnock_Cyl14 | Knock_KLS98_IntKnock_Cyl14 | 883 | Knock_KLS98_IntKnock_Cyl14 | % | 136
[8 empty] | 170 | Knock_KLS98_IntKnock_Cyl15 | Knock_KLS98_IntKnock_Cyl15 | 884 | Knock_KLS98_IntKnock_Cyl15 | % | 170
[8 empty] | 134 | Knock_KLS98_IntKnock_Cyl16 | Knock_KLS98_IntKnock_Cyl16 | 885 | Knock_KLS98_IntKnock_Cyl16 | % | 134
[8 empty] | 171 | Knock_KLS98_IntKnock_Cyl17 | Knock_KLS98_IntKnock_Cyl17 | 886 | Knock_KLS98_IntKnock_Cyl17 | % | 171
[8 empty] | 147 | Knock_KLS98_IntKnock_Cyl18 | Knock_KLS98_IntKnock_Cyl18 | 887 | Knock_KLS98_IntKnock_Cyl18 | % | 147
[8 empty] | 172 | Knock_KLS98_IntKnock_Cyl19 | Knock_KLS98_IntKnock_Cyl19 | 888 | Knock_KLS98_IntKnock_Cyl19 | % | 172
[8 empty] | 148 | Knock_KLS98_IntKnock_Cyl20 | Knock_KLS98_IntKnock_Cyl20 | 889 | Knock_KLS98_IntKnock_Cyl20 | % | 148
[8 empty] | 207 | Knock_KLS98_IntKnock_Cyl21 | Knock_KLS98_IntKnock_Cyl21 | 890 | Knock_KLS98_IntKnock_Cyl21 | % | 207
[8 empty] | 209 | Knock_KLS98_IntKnock_Cyl22 | Knock_KLS98_IntKnock_Cyl22 | 891 | Knock_KLS98_IntKnock_Cyl22 | % | 209
[8 empty] | 208 | Knock_KLS98_IntKnock_Cyl23 | Knock_KLS98_IntKnock_Cyl23 | 892 | Knock_KLS98_IntKnock_Cyl23 | % | 208
[8 empty] | 218 | Knock_KLS98_IntKnock_Cyl24 | Knock_KLS98_IntKnock_Cyl24 | 893 | Knock_KLS98_IntKnock_Cyl24 | % | 218
[8 empty] | 16547 | Knock_KLS98_Knock_Cyl01 | Safi W1 Z01 | 894 | Knock_KLS98_Knock_Cyl01 | mV | 16547
[8 empty] | 16548 | Knock_KLS98_Knock_Cyl02 | Safi W1 Z02 | 895 | Knock_KLS98_Knock_Cyl02 | mV | 16548
[8 empty] | 16549 | Knock_KLS98_Knock_Cyl03 | Safi W1 Z03 | 896 | Knock_KLS98_Knock_Cyl03 | mV | 16549
[8 empty] | 16550 | Knock_KLS98_Knock_Cyl04 | Safi W1 Z04 | 897 | Knock_KLS98_Knock_Cyl04 | mV | 16550
[8 empty] | 16551 | Knock_KLS98_Knock_Cyl05 | Safi W1 Z05 | 898 | Knock_KLS98_Knock_Cyl05 | mV | 16551
[8 empty] | 16552 | Knock_KLS98_Knock_Cyl06 | Safi W1 Z06 | 899 | Knock_KLS98_Knock_Cyl06 | mV | 16552
[8 empty] | 16553 | Knock_KLS98_Knock_Cyl07 | Safi W1 Z07 | 900 | Knock_KLS98_Knock_Cyl07 | mV | 16553
[8 empty] | 16554 | Knock_KLS98_Knock_Cyl08 | Safi W1 Z08 | 901 | Knock_KLS98_Knock_Cyl08 | mV | 16554
[8 empty] | 16555 | Knock_KLS98_Knock_Cyl09 | Safi W1 Z09 | 902 | Knock_KLS98_Knock_Cyl09 | mV | 16555
[8 empty] | 16556 | Knock_KLS98_Knock_Cyl10 | Safi W1 Z10 | 903 | Knock_KLS98_Knock_Cyl10 | mV | 16556
[8 empty] | 16557 | Knock_KLS98_Knock_Cyl11 | Safi W1 Z11 | 904 | Knock_KLS98_Knock_Cyl11 | mV | 16557
[8 empty] | 16558 | Knock_KLS98_Knock_Cyl12 | Safi W1 Z12 | 905 | Knock_KLS98_Knock_Cyl12 | mV | 16558
[8 empty] | 16559 | Knock_KLS98_Knock_Cyl13 | Safi W1 Z13 | 906 | Knock_KLS98_Knock_Cyl13 | mV | 16559
[8 empty] | 16560 | Knock_KLS98_Knock_Cyl14 | Safi W1 Z14 | 907 | Knock_KLS98_Knock_Cyl14 | mV | 16560
[8 empty] | 16561 | Knock_KLS98_Knock_Cyl15 | Safi W1 Z15 | 908 | Knock_KLS98_Knock_Cyl15 | mV | 16561
[8 empty] | 16562 | Knock_KLS98_Knock_Cyl16 | Safi W1 Z16 | 909 | Knock_KLS98_Knock_Cyl16 | mV | 16562
[8 empty] | 16563 | Knock_KLS98_Knock_Cyl17 | Safi W1 Z17 | 910 | Knock_KLS98_Knock_Cyl17 | mV | 16563
[8 empty] | 16564 | Knock_KLS98_Knock_Cyl18 | Safi W1 Z18 | 911 | Knock_KLS98_Knock_Cyl18 | mV | 16564
[8 empty] | 16565 | Knock_KLS98_Knock_Cyl19 | Safi W1 Z19 | 912 | Knock_KLS98_Knock_Cyl19 | mV | 16565
[8 empty] | 16566 | Knock_KLS98_Knock_Cyl20 | Safi W1 Z20 | 913 | Knock_KLS98_Knock_Cyl20 | mV | 16566
[8 empty] | 16567 | Knock_KLS98_Knock_Cyl21 | Safi W1 Z21 | 914 | Knock_KLS98_Knock_Cyl21 | mV | 16567
[8 empty] | 16568 | Knock_KLS98_Knock_Cyl22 | Safi W1 Z22 | 915 | Knock_KLS98_Knock_Cyl22 | mV | 16568
[8 empty] | 16569 | Knock_KLS98_Knock_Cyl23 | Safi W1 Z23 | 916 | Knock_KLS98_Knock_Cyl23 | mV | 16569
[8 empty] | 16570 | Knock_KLS98_Knock_Cyl24 | Safi W1 Z24 | 917 | Knock_KLS98_Knock_Cyl24 | mV | 16570
[8 empty] | 20629 | Knock_KLS98_SW_Vers | Knock_KLS98_SW_Vers | 918 | Knock_KLS98_SW_Vers |  | 20629
[8 empty] | 19139 | Knock_PBC_KnockPress_Avg | Knock_PBC_KnockPress_Avg | 919 | Knock_PBC_KnockPress_Avg | mbar | 19139
[8 empty] | 19140 | Knock_PBC_KnockPress_Cyl01 | Knock_PBC_KnockPress_Cyl01 | 920 | Knock_PBC_KnockPress_Cyl01 | mbar | 19140
[8 empty] | 19141 | Knock_PBC_KnockPress_Cyl02 | Knock_PBC_KnockPress_Cyl02 | 921 | Knock_PBC_KnockPress_Cyl02 | mbar | 19141
[8 empty] | 19142 | Knock_PBC_KnockPress_Cyl03 | Knock_PBC_KnockPress_Cyl03 | 922 | Knock_PBC_KnockPress_Cyl03 | mbar | 19142
[8 empty] | 19143 | Knock_PBC_KnockPress_Cyl04 | Knock_PBC_KnockPress_Cyl04 | 923 | Knock_PBC_KnockPress_Cyl04 | mbar | 19143
[8 empty] | 19144 | Knock_PBC_KnockPress_Cyl05 | Knock_PBC_KnockPress_Cyl05 | 924 | Knock_PBC_KnockPress_Cyl05 | mbar | 19144
[8 empty] | 19145 | Knock_PBC_KnockPress_Cyl06 | Knock_PBC_KnockPress_Cyl06 | 925 | Knock_PBC_KnockPress_Cyl06 | mbar | 19145
[8 empty] | 19146 | Knock_PBC_KnockPress_Cyl07 | Knock_PBC_KnockPress_Cyl07 | 926 | Knock_PBC_KnockPress_Cyl07 | mbar | 19146
[8 empty] | 19147 | Knock_PBC_KnockPress_Cyl08 | Knock_PBC_KnockPress_Cyl08 | 927 | Knock_PBC_KnockPress_Cyl08 | mbar | 19147
[8 empty] | 19148 | Knock_PBC_KnockPress_Cyl09 | Knock_PBC_KnockPress_Cyl09 | 928 | Knock_PBC_KnockPress_Cyl09 |  | 19148
[8 empty] | 19149 | Knock_PBC_KnockPress_Cyl10 | Knock_PBC_KnockPress_Cyl10 | 929 | Knock_PBC_KnockPress_Cyl10 | mbar | 19149
[8 empty] | 19150 | Knock_PBC_KnockPress_Cyl11 | Knock_PBC_KnockPress_Cyl11 | 930 | Knock_PBC_KnockPress_Cyl11 | mbar | 19150
[8 empty] | 19151 | Knock_PBC_KnockPress_Cyl12 | Knock_PBC_KnockPress_Cyl12 | 931 | Knock_PBC_KnockPress_Cyl12 | mbar | 19151
[8 empty] | 19152 | Knock_PBC_KnockPress_Cyl13 | Knock_PBC_KnockPress_Cyl13 | 932 | Knock_PBC_KnockPress_Cyl13 | mbar | 19152
[8 empty] | 19153 | Knock_PBC_KnockPress_Cyl14 | Knock_PBC_KnockPress_Cyl14 | 933 | Knock_PBC_KnockPress_Cyl14 | mbar | 19153
[8 empty] | 19154 | Knock_PBC_KnockPress_Cyl15 | Knock_PBC_KnockPress_Cyl15 | 934 | Knock_PBC_KnockPress_Cyl15 | mbar | 19154
[8 empty] | 19155 | Knock_PBC_KnockPress_Cyl16 | Knock_PBC_KnockPress_Cyl16 | 935 | Knock_PBC_KnockPress_Cyl16 | mbar | 19155
[8 empty] | 19156 | Knock_PBC_KnockPress_Cyl17 | Knock_PBC_KnockPress_Cyl17 | 936 | Knock_PBC_KnockPress_Cyl17 | mbar | 19156
[8 empty] | 19157 | Knock_PBC_KnockPress_Cyl18 | Knock_PBC_KnockPress_Cyl18 | 937 | Knock_PBC_KnockPress_Cyl18 | mbar | 19157
[8 empty] | 19158 | Knock_PBC_KnockPress_Cyl19 | Knock_PBC_KnockPress_Cyl19 | 938 | Knock_PBC_KnockPress_Cyl19 | mbar | 19158
[8 empty] | 19159 | Knock_PBC_KnockPress_Cyl20 | Knock_PBC_KnockPress_Cyl20 | 939 | Knock_PBC_KnockPress_Cyl20 | mbar | 19159
[8 empty] | 19160 | Knock_PBC_KnockPress_Cyl21 | Knock_PBC_KnockPress_Cyl21 | 940 | Knock_PBC_KnockPress_Cyl21 | mbar | 19160
[8 empty] | 19161 | Knock_PBC_KnockPress_Cyl22 | Knock_PBC_KnockPress_Cyl22 | 941 | Knock_PBC_KnockPress_Cyl22 | mbar | 19161
[8 empty] | 19162 | Knock_PBC_KnockPress_Cyl23 | Knock_PBC_KnockPress_Cyl23 | 942 | Knock_PBC_KnockPress_Cyl23 | mbar | 19162
[8 empty] | 19163 | Knock_PBC_KnockPress_Cyl24 | Knock_PBC_KnockPress_Cyl24 | 943 | Knock_PBC_KnockPress_Cyl24 | mbar | 19163
[8 empty] | 19164 | Knock_PBC_KnockPress_Max | Knock_PBC_KnockPress_Max | 944 | Knock_PBC_KnockPress_Max | mbar | 19164
[8 empty] | 19165 | Knock_PBC_KnockPress_Min | Knock_PBC_KnockPress_Min | 945 | Knock_PBC_KnockPress_Min | mbar | 19165
[8 empty] | 19166 | Knock_PBC_PMax_Avg | Knock_PBC_PMax_Avg | 946 | Knock_PBC_PMax_Avg | bar | 19166
[8 empty] | 19167 | Knock_PBC_PMax_Cyl01 | Knock_PBC_PMax_Cyl01 | 947 | Knock_PBC_PMax_Cyl01 | bar | 19167
[8 empty] | 19168 | Knock_PBC_PMax_Cyl02 | Knock_PBC_PMax_Cyl02 | 948 | Knock_PBC_PMax_Cyl02 | bar | 19168
[8 empty] | 19169 | Knock_PBC_PMax_Cyl03 | Knock_PBC_PMax_Cyl03 | 949 | Knock_PBC_PMax_Cyl03 | bar | 19169
[8 empty] | 19170 | Knock_PBC_PMax_Cyl04 | Knock_PBC_PMax_Cyl04 | 950 | Knock_PBC_PMax_Cyl04 | bar | 19170
[8 empty] | 19171 | Knock_PBC_PMax_Cyl05 | Knock_PBC_PMax_Cyl05 | 951 | Knock_PBC_PMax_Cyl05 | bar | 19171
[8 empty] | 19172 | Knock_PBC_PMax_Cyl06 | Knock_PBC_PMax_Cyl06 | 952 | Knock_PBC_PMax_Cyl06 | bar | 19172
[8 empty] | 19173 | Knock_PBC_PMax_Cyl07 | Knock_PBC_PMax_Cyl07 | 953 | Knock_PBC_PMax_Cyl07 | bar | 19173
[8 empty] | 19174 | Knock_PBC_PMax_Cyl08 | Knock_PBC_PMax_Cyl08 | 954 | Knock_PBC_PMax_Cyl08 | bar | 19174
[8 empty] | 19175 | Knock_PBC_PMax_Cyl09 | Knock_PBC_PMax_Cyl09 | 955 | Knock_PBC_PMax_Cyl09 | bar | 19175
[8 empty] | 19176 | Knock_PBC_PMax_Cyl10 | Knock_PBC_PMax_Cyl10 | 956 | Knock_PBC_PMax_Cyl10 | bar | 19176
[8 empty] | 19177 | Knock_PBC_PMax_Cyl11 | Knock_PBC_PMax_Cyl11 | 957 | Knock_PBC_PMax_Cyl11 | bar | 19177
[8 empty] | 19178 | Knock_PBC_PMax_Cyl12 | Knock_PBC_PMax_Cyl12 | 958 | Knock_PBC_PMax_Cyl12 | bar | 19178
[8 empty] | 19179 | Knock_PBC_PMax_Cyl13 | Knock_PBC_PMax_Cyl13 | 959 | Knock_PBC_PMax_Cyl13 | bar | 19179
[8 empty] | 19180 | Knock_PBC_PMax_Cyl14 | Knock_PBC_PMax_Cyl14 | 960 | Knock_PBC_PMax_Cyl14 | bar | 19180
[8 empty] | 19181 | Knock_PBC_PMax_Cyl15 | Knock_PBC_PMax_Cyl15 | 961 | Knock_PBC_PMax_Cyl15 | bar | 19181
[8 empty] | 19182 | Knock_PBC_PMax_Cyl16 | Knock_PBC_PMax_Cyl16 | 962 | Knock_PBC_PMax_Cyl16 | bar | 19182
[8 empty] | 19183 | Knock_PBC_PMax_Cyl17 | Knock_PBC_PMax_Cyl17 | 963 | Knock_PBC_PMax_Cyl17 | bar | 19183
[8 empty] | 19184 | Knock_PBC_PMax_Cyl18 | Knock_PBC_PMax_Cyl18 | 964 | Knock_PBC_PMax_Cyl18 | bar | 19184
[8 empty] | 19185 | Knock_PBC_PMax_Cyl19 | Knock_PBC_PMax_Cyl19 | 965 | Knock_PBC_PMax_Cyl19 | bar | 19185
[8 empty] | 19186 | Knock_PBC_PMax_Cyl20 | Knock_PBC_PMax_Cyl20 | 966 | Knock_PBC_PMax_Cyl20 | bar | 19186
[8 empty] | 19187 | Knock_PBC_PMax_Cyl21 | Knock_PBC_PMax_Cyl21 | 967 | Knock_PBC_PMax_Cyl21 | bar | 19187
[8 empty] | 19188 | Knock_PBC_PMax_Cyl22 | Knock_PBC_PMax_Cyl22 | 968 | Knock_PBC_PMax_Cyl22 | bar | 19188
[8 empty] | 19189 | Knock_PBC_PMax_Cyl23 | Knock_PBC_PMax_Cyl23 | 969 | Knock_PBC_PMax_Cyl23 | bar | 19189
[8 empty] | 19190 | Knock_PBC_PMax_Cyl24 | Knock_PBC_PMax_Cyl24 | 970 | Knock_PBC_PMax_Cyl24 | bar | 19190
[8 empty] | 19191 | Knock_PBC_PMax_Max | Knock_PBC_PMax_Max | 971 | Knock_PBC_PMax_Max | bar | 19191
[8 empty] | 19192 | Knock_PBC_PMax_Min | Knock_PBC_PMax_Min | 972 | Knock_PBC_PMax_Min | bar | 19192
[8 empty] | 10008716 | Knock_Valve_Noise_Cyl01 | Safi W2 Z01 | 973 | Knock_Valve_Noise_Cyl01 | mV | 10008716
[8 empty] | 10008714 | Knock_Valve_Noise_Cyl02 | Safi W2 Z02 | 974 | Knock_Valve_Noise_Cyl02 | mV | 10008714
[8 empty] | 10008717 | Knock_Valve_Noise_Cyl03 | Safi W2 Z03 | 975 | Knock_Valve_Noise_Cyl03 | mV | 10008717
[8 empty] | 10008719 | Knock_Valve_Noise_Cyl04 | Safi W2 Z04 | 976 | Knock_Valve_Noise_Cyl04 | mV | 10008719
[8 empty] | 10008715 | Knock_Valve_Noise_Cyl05 | Safi W2 Z05 | 977 | Knock_Valve_Noise_Cyl05 | mV | 10008715
[8 empty] | 10008718 | Knock_Valve_Noise_Cyl06 | Safi W2 Z06 | 978 | Knock_Valve_Noise_Cyl06 | mV | 10008718
[8 empty] | 10008720 | Knock_Valve_Noise_Cyl07 | Safi W2 Z07 | 979 | Knock_Valve_Noise_Cyl07 | mV | 10008720
[8 empty] | 10008721 | Knock_Valve_Noise_Cyl08 | Safi W2 Z08 | 980 | Knock_Valve_Noise_Cyl08 | mV | 10008721
[8 empty] | 10008722 | Knock_Valve_Noise_Cyl09 | Safi W2 Z09 | 981 | Knock_Valve_Noise_Cyl09 | mV | 10008722
[8 empty] | 10008723 | Knock_Valve_Noise_Cyl10 | Safi W2 Z10 | 982 | Knock_Valve_Noise_Cyl10 | mV | 10008723
[8 empty] | 10008724 | Knock_Valve_Noise_Cyl11 | Safi W2 Z11 | 983 | Knock_Valve_Noise_Cyl11 | mV | 10008724
[8 empty] | 10008728 | Knock_Valve_Noise_Cyl12 | Safi W2 Z12 | 984 | Knock_Valve_Noise_Cyl12 | mV | 10008728
[8 empty] | 10008726 | Knock_Valve_Noise_Cyl13 | Safi W2 Z13 | 985 | Knock_Valve_Noise_Cyl13 | mV | 10008726
[8 empty] | 10008729 | Knock_Valve_Noise_Cyl14 | Safi W2 Z14 | 986 | Knock_Valve_Noise_Cyl14 | mV | 10008729
[8 empty] | 10008727 | Knock_Valve_Noise_Cyl15 | Safi W2 Z15 | 987 | Knock_Valve_Noise_Cyl15 | mV | 10008727
[8 empty] | 10008730 | Knock_Valve_Noise_Cyl16 | Safi W2 Z16 | 988 | Knock_Valve_Noise_Cyl16 | mV | 10008730
[8 empty] | 10008725 | Knock_Valve_Noise_Cyl17 | Safi W2 Z17 | 989 | Knock_Valve_Noise_Cyl17 | mV | 10008725
[8 empty] | 10008732 | Knock_Valve_Noise_Cyl18 | Safi W2 Z18 | 990 | Knock_Valve_Noise_Cyl18 | mV | 10008732
[8 empty] | 10008733 | Knock_Valve_Noise_Cyl19 | Safi W2 Z19 | 991 | Knock_Valve_Noise_Cyl19 | mV | 10008733
[8 empty] | 10008734 | Knock_Valve_Noise_Cyl20 | Safi W2 Z20 | 992 | Knock_Valve_Noise_Cyl20 | mV | 10008734
[8 empty] | 10008731 | Knock_Valve_Noise_Cyl21 | Safi W2 Z21 | 993 | Knock_Valve_Noise_Cyl21 | mV | 10008731
[8 empty] | 10008736 | Knock_Valve_Noise_Cyl22 | Safi W2 Z22 | 994 | Knock_Valve_Noise_Cyl22 | mV | 10008736
[8 empty] | 10008735 | Knock_Valve_Noise_Cyl23 | Safi W2 Z23 | 995 | Knock_Valve_Noise_Cyl23 | mV | 10008735
[8 empty] | 10008737 | Knock_Valve_Noise_Cyl24 | Safi W2 Z24 | 996 | Knock_Valve_Noise_Cyl24 | mV | 10008737
[8 empty] | 16571 | Leanox_P2Error | Leanox_P2Error | 997 | Leanox_P2Error | mbar | 16571
[8 empty] | 20330 | Leanox_P2Set | Leanox_P2Set | 998 | Leanox_P2Set | mbar | 20330
[8 empty] | 19193 | Leanox_RatioMix | Leanox_RatioMix | 999 | Leanox_RatioMix | % | 19193
[8 empty] | 10044874 | LVRT_Events | LVRT_Events | 1000 | LVRT_Events |  | 10044874
[8 empty] | 10049466 | manualdata_valverecession_EngineOpH | manualdata_valverecession_EngineOpH | 1001 | manualdata_valverecession_EngineOpH | hours | 10049466
[8 empty] | 10049527 | manualdata_valverecession_EngineStarts | manualdata_valverecession_EngineStarts | 1002 | manualdata_valverecession_EngineStarts | Starts | 10049527
[8 empty] | 10044516 | manualdata_valverecession_lev_cyl01 | manualdata_valverecession_lev_cyl01 | 1003 | manualdata_valverecession_lev_cyl01 | mm | 10044516
[8 empty] | 10044517 | manualdata_valverecession_lev_cyl02 | manualdata_valverecession_lev_cyl02 | 1004 | manualdata_valverecession_lev_cyl02 | mm | 10044517
[8 empty] | 10044518 | manualdata_valverecession_lev_cyl03 | manualdata_valverecession_lev_cyl03 | 1005 | manualdata_valverecession_lev_cyl03 | mm | 10044518
[8 empty] | 10044519 | manualdata_valverecession_lev_cyl04 | manualdata_valverecession_lev_cyl04 | 1006 | manualdata_valverecession_lev_cyl04 | mm | 10044519
[8 empty] | 10044520 | manualdata_valverecession_lev_cyl05 | manualdata_valverecession_lev_cyl05 | 1007 | manualdata_valverecession_lev_cyl05 | mm | 10044520
[8 empty] | 10044521 | manualdata_valverecession_lev_cyl06 | manualdata_valverecession_lev_cyl06 | 1008 | manualdata_valverecession_lev_cyl06 | mm | 10044521
[8 empty] | 10044522 | manualdata_valverecession_lev_cyl07 | manualdata_valverecession_lev_cyl07 | 1009 | manualdata_valverecession_lev_cyl07 | mm | 10044522
[8 empty] | 10044523 | manualdata_valverecession_lev_cyl08 | manualdata_valverecession_lev_cyl08 | 1010 | manualdata_valverecession_lev_cyl08 | mm | 10044523
[8 empty] | 10044524 | manualdata_valverecession_lev_cyl09 | manualdata_valverecession_lev_cyl09 | 1011 | manualdata_valverecession_lev_cyl09 | mm | 10044524
[8 empty] | 10044525 | manualdata_valverecession_lev_cyl10 | manualdata_valverecession_lev_cyl10 | 1012 | manualdata_valverecession_lev_cyl10 | mm | 10044525
[8 empty] | 10044526 | manualdata_valverecession_lev_cyl11 | manualdata_valverecession_lev_cyl11 | 1013 | manualdata_valverecession_lev_cyl11 | mm | 10044526
[8 empty] | 10044527 | manualdata_valverecession_lev_cyl12 | manualdata_valverecession_lev_cyl12 | 1014 | manualdata_valverecession_lev_cyl12 | mm | 10044527
[8 empty] | 10044528 | manualdata_valverecession_lev_cyl13 | manualdata_valverecession_lev_cyl13 | 1015 | manualdata_valverecession_lev_cyl13 | mm | 10044528
[8 empty] | 10044529 | manualdata_valverecession_lev_cyl14 | manualdata_valverecession_lev_cyl14 | 1016 | manualdata_valverecession_lev_cyl14 | mm | 10044529
[8 empty] | 10044530 | manualdata_valverecession_lev_cyl15 | manualdata_valverecession_lev_cyl15 | 1017 | manualdata_valverecession_lev_cyl15 | mm | 10044530
[8 empty] | 10044531 | manualdata_valverecession_lev_cyl16 | manualdata_valverecession_lev_cyl16 | 1018 | manualdata_valverecession_lev_cyl16 | mm | 10044531
[8 empty] | 10044532 | manualdata_valverecession_lev_cyl17 | manualdata_valverecession_lev_cyl17 | 1019 | manualdata_valverecession_lev_cyl17 | mm | 10044532
[8 empty] | 10044533 | manualdata_valverecession_lev_cyl18 | manualdata_valverecession_lev_cyl18 | 1020 | manualdata_valverecession_lev_cyl18 | mm | 10044533
[8 empty] | 10044534 | manualdata_valverecession_lev_cyl19 | manualdata_valverecession_lev_cyl19 | 1021 | manualdata_valverecession_lev_cyl19 | mm | 10044534
[8 empty] | 10044535 | manualdata_valverecession_lev_cyl20 | manualdata_valverecession_lev_cyl20 | 1022 | manualdata_valverecession_lev_cyl20 | mm | 10044535
[8 empty] | 10044536 | manualdata_valverecession_lev_cyl21 | manualdata_valverecession_lev_cyl21 | 1023 | manualdata_valverecession_lev_cyl21 | mm | 10044536
[8 empty] | 10044537 | manualdata_valverecession_lev_cyl22 | manualdata_valverecession_lev_cyl22 | 1024 | manualdata_valverecession_lev_cyl22 | mm | 10044537
[8 empty] | 10044538 | manualdata_valverecession_lev_cyl23 | manualdata_valverecession_lev_cyl23 | 1025 | manualdata_valverecession_lev_cyl23 | mm | 10044538
[8 empty] | 10044539 | manualdata_valverecession_lev_cyl24 | manualdata_valverecession_lev_cyl24 | 1026 | manualdata_valverecession_lev_cyl24 | mm | 10044539
[8 empty] | 10044464 | manualdata_valverecession_liv_cyl01 | manualdata_valverecession_liv_cyl01 | 1027 | manualdata_valverecession_liv_cyl01 | mm | 10044464
[8 empty] | 10044468 | manualdata_valverecession_liv_cyl02 | manualdata_valverecession_liv_cyl02 | 1028 | manualdata_valverecession_liv_cyl02 | mm | 10044468
[8 empty] | 10044471 | manualdata_valverecession_liv_cyl03 | manualdata_valverecession_liv_cyl03 | 1029 | manualdata_valverecession_liv_cyl03 | mm | 10044471
[8 empty] | 10044472 | manualdata_valverecession_liv_cyl04 | manualdata_valverecession_liv_cyl04 | 1030 | manualdata_valverecession_liv_cyl04 | mm | 10044472
[8 empty] | 10044473 | manualdata_valverecession_liv_cyl05 | manualdata_valverecession_liv_cyl05 | 1031 | manualdata_valverecession_liv_cyl05 | mm | 10044473
[8 empty] | 10044474 | manualdata_valverecession_liv_cyl06 | manualdata_valverecession_liv_cyl06 | 1032 | manualdata_valverecession_liv_cyl06 | mm | 10044474
[8 empty] | 10044475 | manualdata_valverecession_liv_cyl07 | manualdata_valverecession_liv_cyl07 | 1033 | manualdata_valverecession_liv_cyl07 | mm | 10044475
[8 empty] | 10044476 | manualdata_valverecession_liv_cyl08 | manualdata_valverecession_liv_cyl08 | 1034 | manualdata_valverecession_liv_cyl08 | mm | 10044476
[8 empty] | 10044477 | manualdata_valverecession_liv_cyl09 | manualdata_valverecession_liv_cyl09 | 1035 | manualdata_valverecession_liv_cyl09 | mm | 10044477
[8 empty] | 10044478 | manualdata_valverecession_liv_cyl10 | manualdata_valverecession_liv_cyl10 | 1036 | manualdata_valverecession_liv_cyl10 | mm | 10044478
[8 empty] | 10044479 | manualdata_valverecession_liv_cyl11 | manualdata_valverecession_liv_cyl11 | 1037 | manualdata_valverecession_liv_cyl11 | mm | 10044479
[8 empty] | 10044480 | manualdata_valverecession_liv_cyl12 | manualdata_valverecession_liv_cyl12 | 1038 | manualdata_valverecession_liv_cyl12 | mm | 10044480
[8 empty] | 10044481 | manualdata_valverecession_liv_cyl13 | manualdata_valverecession_liv_cyl13 | 1039 | manualdata_valverecession_liv_cyl13 | mm | 10044481
[8 empty] | 10044482 | manualdata_valverecession_liv_cyl14 | manualdata_valverecession_liv_cyl14 | 1040 | manualdata_valverecession_liv_cyl14 | mm | 10044482
[8 empty] | 10044483 | manualdata_valverecession_liv_cyl15 | manualdata_valverecession_liv_cyl15 | 1041 | manualdata_valverecession_liv_cyl15 | mm | 10044483
[8 empty] | 10044484 | manualdata_valverecession_liv_cyl16 | manualdata_valverecession_liv_cyl16 | 1042 | manualdata_valverecession_liv_cyl16 | mm | 10044484
[8 empty] | 10044485 | manualdata_valverecession_liv_cyl17 | manualdata_valverecession_liv_cyl17 | 1043 | manualdata_valverecession_liv_cyl17 | mm | 10044485
[8 empty] | 10044486 | manualdata_valverecession_liv_cyl18 | manualdata_valverecession_liv_cyl18 | 1044 | manualdata_valverecession_liv_cyl18 | mm | 10044486
[8 empty] | 10044487 | manualdata_valverecession_liv_cyl19 | manualdata_valverecession_liv_cyl19 | 1045 | manualdata_valverecession_liv_cyl19 | mm | 10044487
[8 empty] | 10044488 | manualdata_valverecession_liv_cyl20 | manualdata_valverecession_liv_cyl20 | 1046 | manualdata_valverecession_liv_cyl20 | mm | 10044488
[8 empty] | 10044489 | manualdata_valverecession_liv_cyl21 | manualdata_valverecession_liv_cyl21 | 1047 | manualdata_valverecession_liv_cyl21 | mm | 10044489
[8 empty] | 10044490 | manualdata_valverecession_liv_cyl22 | manualdata_valverecession_liv_cyl22 | 1048 | manualdata_valverecession_liv_cyl22 | mm | 10044490
[8 empty] | 10044491 | manualdata_valverecession_liv_cyl23 | manualdata_valverecession_liv_cyl23 | 1049 | manualdata_valverecession_liv_cyl23 | mm | 10044491
[8 empty] | 10044515 | manualdata_valverecession_liv_cyl24 | manualdata_valverecession_liv_cyl24 | 1050 | manualdata_valverecession_liv_cyl24 | mm | 10044515
[8 empty] | 10044564 | manualdata_valverecession_rev_cyl01 | manualdata_valverecession_rev_cyl01 | 1051 | manualdata_valverecession_rev_cyl01 | mm | 10044564
[8 empty] | 10044565 | manualdata_valverecession_rev_cyl02 | manualdata_valverecession_rev_cyl02 | 1052 | manualdata_valverecession_rev_cyl02 | mm | 10044565
[8 empty] | 10044566 | manualdata_valverecession_rev_cyl03 | manualdata_valverecession_rev_cyl03 | 1053 | manualdata_valverecession_rev_cyl03 | mm | 10044566
[8 empty] | 10044567 | manualdata_valverecession_rev_cyl04 | manualdata_valverecession_rev_cyl04 | 1054 | manualdata_valverecession_rev_cyl04 | mm | 10044567
[8 empty] | 10044568 | manualdata_valverecession_rev_cyl05 | manualdata_valverecession_rev_cyl05 | 1055 | manualdata_valverecession_rev_cyl05 | mm | 10044568
[8 empty] | 10044569 | manualdata_valverecession_rev_cyl06 | manualdata_valverecession_rev_cyl06 | 1056 | manualdata_valverecession_rev_cyl06 | mm | 10044569
[8 empty] | 10044570 | manualdata_valverecession_rev_cyl07 | manualdata_valverecession_rev_cyl07 | 1057 | manualdata_valverecession_rev_cyl07 | mm | 10044570
[8 empty] | 10044571 | manualdata_valverecession_rev_cyl08 | manualdata_valverecession_rev_cyl08 | 1058 | manualdata_valverecession_rev_cyl08 | mm | 10044571
[8 empty] | 10044572 | manualdata_valverecession_rev_cyl09 | manualdata_valverecession_rev_cyl09 | 1059 | manualdata_valverecession_rev_cyl09 | mm | 10044572
[8 empty] | 10044573 | manualdata_valverecession_rev_cyl10 | manualdata_valverecession_rev_cyl10 | 1060 | manualdata_valverecession_rev_cyl10 | mm | 10044573
[8 empty] | 10044574 | manualdata_valverecession_rev_cyl11 | manualdata_valverecession_rev_cyl11 | 1061 | manualdata_valverecession_rev_cyl11 | mm | 10044574
[8 empty] | 10044575 | manualdata_valverecession_rev_cyl12 | manualdata_valverecession_rev_cyl12 | 1062 | manualdata_valverecession_rev_cyl12 | mm | 10044575
[8 empty] | 10044576 | manualdata_valverecession_rev_cyl13 | manualdata_valverecession_rev_cyl13 | 1063 | manualdata_valverecession_rev_cyl13 | mm | 10044576
[8 empty] | 10044577 | manualdata_valverecession_rev_cyl14 | manualdata_valverecession_rev_cyl14 | 1064 | manualdata_valverecession_rev_cyl14 | mm | 10044577
[8 empty] | 10044578 | manualdata_valverecession_rev_cyl15 | manualdata_valverecession_rev_cyl15 | 1065 | manualdata_valverecession_rev_cyl15 | mm | 10044578
[8 empty] | 10044579 | manualdata_valverecession_rev_cyl16 | manualdata_valverecession_rev_cyl16 | 1066 | manualdata_valverecession_rev_cyl16 | mm | 10044579
[8 empty] | 10044580 | manualdata_valverecession_rev_cyl17 | manualdata_valverecession_rev_cyl17 | 1067 | manualdata_valverecession_rev_cyl17 | mm | 10044580
[8 empty] | 10044581 | manualdata_valverecession_rev_cyl18 | manualdata_valverecession_rev_cyl18 | 1068 | manualdata_valverecession_rev_cyl18 | mm | 10044581
[8 empty] | 10044582 | manualdata_valverecession_rev_cyl19 | manualdata_valverecession_rev_cyl19 | 1069 | manualdata_valverecession_rev_cyl19 | mm | 10044582
[8 empty] | 10044583 | manualdata_valverecession_rev_cyl20 | manualdata_valverecession_rev_cyl20 | 1070 | manualdata_valverecession_rev_cyl20 | mm | 10044583
[8 empty] | 10044584 | manualdata_valverecession_rev_cyl21 | manualdata_valverecession_rev_cyl21 | 1071 | manualdata_valverecession_rev_cyl21 | mm | 10044584
[8 empty] | 10044585 | manualdata_valverecession_rev_cyl22 | manualdata_valverecession_rev_cyl22 | 1072 | manualdata_valverecession_rev_cyl22 | mm | 10044585
[8 empty] | 10044586 | manualdata_valverecession_rev_cyl23 | manualdata_valverecession_rev_cyl23 | 1073 | manualdata_valverecession_rev_cyl23 | mm | 10044586
[8 empty] | 10044587 | manualdata_valverecession_rev_cyl24 | manualdata_valverecession_rev_cyl24 | 1074 | manualdata_valverecession_rev_cyl24 | mm | 10044587
[8 empty] | 10044540 | manualdata_valverecession_riv_cyl01 | manualdata_valverecession_riv_cyl01 | 1075 | manualdata_valverecession_riv_cyl01 | mm | 10044540
[8 empty] | 10044541 | manualdata_valverecession_riv_cyl02 | manualdata_valverecession_riv_cyl02 | 1076 | manualdata_valverecession_riv_cyl02 | mm | 10044541
[8 empty] | 10044542 | manualdata_valverecession_riv_cyl03 | manualdata_valverecession_riv_cyl03 | 1077 | manualdata_valverecession_riv_cyl03 | mm | 10044542
[8 empty] | 10044543 | manualdata_valverecession_riv_cyl04 | manualdata_valverecession_riv_cyl04 | 1078 | manualdata_valverecession_riv_cyl04 | mm | 10044543
[8 empty] | 10044544 | manualdata_valverecession_riv_cyl05 | manualdata_valverecession_riv_cyl05 | 1079 | manualdata_valverecession_riv_cyl05 | mm | 10044544
[8 empty] | 10044545 | manualdata_valverecession_riv_cyl06 | manualdata_valverecession_riv_cyl06 | 1080 | manualdata_valverecession_riv_cyl06 | mm | 10044545
[8 empty] | 10044546 | manualdata_valverecession_riv_cyl07 | manualdata_valverecession_riv_cyl07 | 1081 | manualdata_valverecession_riv_cyl07 | mm | 10044546
[8 empty] | 10044547 | manualdata_valverecession_riv_cyl08 | manualdata_valverecession_riv_cyl08 | 1082 | manualdata_valverecession_riv_cyl08 | mm | 10044547
[8 empty] | 10044548 | manualdata_valverecession_riv_cyl09 | manualdata_valverecession_riv_cyl09 | 1083 | manualdata_valverecession_riv_cyl09 | mm | 10044548
[8 empty] | 10044549 | manualdata_valverecession_riv_cyl10 | manualdata_valverecession_riv_cyl10 | 1084 | manualdata_valverecession_riv_cyl10 | mm | 10044549
[8 empty] | 10044550 | manualdata_valverecession_riv_cyl11 | manualdata_valverecession_riv_cyl11 | 1085 | manualdata_valverecession_riv_cyl11 | mm | 10044550
[8 empty] | 10044551 | manualdata_valverecession_riv_cyl12 | manualdata_valverecession_riv_cyl12 | 1086 | manualdata_valverecession_riv_cyl12 | mm | 10044551
[8 empty] | 10044552 | manualdata_valverecession_riv_cyl13 | manualdata_valverecession_riv_cyl13 | 1087 | manualdata_valverecession_riv_cyl13 | mm | 10044552
[8 empty] | 10044553 | manualdata_valverecession_riv_cyl14 | manualdata_valverecession_riv_cyl14 | 1088 | manualdata_valverecession_riv_cyl14 | mm | 10044553
[8 empty] | 10044554 | manualdata_valverecession_riv_cyl15 | manualdata_valverecession_riv_cyl15 | 1089 | manualdata_valverecession_riv_cyl15 | mm | 10044554
[8 empty] | 10044555 | manualdata_valverecession_riv_cyl16 | manualdata_valverecession_riv_cyl16 | 1090 | manualdata_valverecession_riv_cyl16 | mm | 10044555
[8 empty] | 10044556 | manualdata_valverecession_riv_cyl17 | manualdata_valverecession_riv_cyl17 | 1091 | manualdata_valverecession_riv_cyl17 | mm | 10044556
[8 empty] | 10044557 | manualdata_valverecession_riv_cyl18 | manualdata_valverecession_riv_cyl18 | 1092 | manualdata_valverecession_riv_cyl18 | mm | 10044557
[8 empty] | 10044558 | manualdata_valverecession_riv_cyl19 | manualdata_valverecession_riv_cyl19 | 1093 | manualdata_valverecession_riv_cyl19 | mm | 10044558
[8 empty] | 10044559 | manualdata_valverecession_riv_cyl20 | manualdata_valverecession_riv_cyl20 | 1094 | manualdata_valverecession_riv_cyl20 | mm | 10044559
[8 empty] | 10044560 | manualdata_valverecession_riv_cyl21 | manualdata_valverecession_riv_cyl21 | 1095 | manualdata_valverecession_riv_cyl21 | mm | 10044560
[8 empty] | 10044561 | manualdata_valverecession_riv_cyl22 | manualdata_valverecession_riv_cyl22 | 1096 | manualdata_valverecession_riv_cyl22 | mm | 10044561
[8 empty] | 10044562 | manualdata_valverecession_riv_cyl23 | manualdata_valverecession_riv_cyl23 | 1097 | manualdata_valverecession_riv_cyl23 | mm | 10044562
[8 empty] | 10044563 | manualdata_valverecession_riv_cyl24 | manualdata_valverecession_riv_cyl24 | 1098 | manualdata_valverecession_riv_cyl24 | mm | 10044563
[8 empty] | 110 | MMD_CountEnergAct | MMD_CountEnergAct | 1099 | MMD_CountEnergAct | MWh | 110
[8 empty] | 10049829 | MMD_CountEnergActReturn | MMD_CountEnergActReturn | 1100 | MMD_CountEnergActReturn |  | 10049829
[8 empty] | 122 | MMD_CountEnergReact | MMD_CountEnergReact | 1101 | MMD_CountEnergReact | Mvarh | 122
[8 empty] | 10049830 | MMD_CountEnergReactReturn | MMD_CountEnergReactReturn | 1102 | MMD_CountEnergReactReturn |  | 10049830
[8 empty] | 74 | MMD_CurrAvg | MMD_CurrAvg | 1103 | MMD_CurrAvg | A | 74
[8 empty] | 20624 | MMD_HW_Vers1 | MMD_HW_Vers1 | 1104 | MMD_HW_Vers1 |  | 20624
[8 empty] | 20626 | MMD_HW_Vers2 | MMD_HW_Vers2 | 1105 | MMD_HW_Vers2 |  | 20626
[8 empty] | 76 | MMD_PowerReact | MMD_PowerReact | 1106 | MMD_PowerReact | kvar | 76
[8 empty] | 20625 | MMD_SW_Vers1 | MMD_SW_Vers1 | 1107 | MMD_SW_Vers1 |  | 20625
[8 empty] | 20627 | MMD_SW_Vers2 | MMD_SW_Vers2 | 1108 | MMD_SW_Vers2 |  | 20627
[8 empty] | 73 | MMD_VoltAvg | MMD_VoltAvg | 1109 | MMD_VoltAvg | V | 73
[8 empty] | 20644 | Module_Vers_AmmBase | Module_Vers_AmmBase | 1110 | Module_Vers_AmmBase |  | 20644
[8 empty] | 20645 | Module_Vers_AuxiliariesGeneral | Module_Vers_AuxiliariesGeneral | 1111 | Module_Vers_AuxiliariesGeneral |  | 20645
[8 empty] | 20656 | Module_Vers_CBM | Module_Vers_CBM | 1112 | Module_Vers_CBM |  | 20656
[8 empty] | 20646 | Module_Vers_ChargingUnit | Module_Vers_ChargingUnit | 1113 | Module_Vers_ChargingUnit |  | 20646
[8 empty] | 20647 | Module_Vers_Coupling | Module_Vers_Coupling | 1114 | Module_Vers_Coupling |  | 20647
[8 empty] | 20648 | Module_Vers_Customized | Module_Vers_Customized | 1115 | Module_Vers_Customized |  | 20648
[8 empty] | 20649 | Module_Vers_Emission | Module_Vers_Emission | 1116 | Module_Vers_Emission |  | 20649
[8 empty] | 20657 | Module_Vers_EngineController | Module_Vers_EngineController | 1117 | Module_Vers_EngineController |  | 20657
[8 empty] | 20658 | Module_Vers_EngineGeneral | Module_Vers_EngineGeneral | 1118 | Module_Vers_EngineGeneral |  | 20658
[8 empty] | 20650 | Module_Vers_Exhaust | Module_Vers_Exhaust | 1119 | Module_Vers_Exhaust |  | 20650
[8 empty] | 20659 | Module_Vers_GasMeteringUnit | Module_Vers_GasMeteringUnit | 1120 | Module_Vers_GasMeteringUnit |  | 20659
[8 empty] | 20660 | Module_Vers_Gasmixer | Module_Vers_Gasmixer | 1121 | Module_Vers_Gasmixer |  | 20660
[8 empty] | 20661 | Module_Vers_Gastrain | Module_Vers_Gastrain | 1122 | Module_Vers_Gastrain |  | 20661
[8 empty] | 20651 | Module_Vers_Generator | Module_Vers_Generator | 1123 | Module_Vers_Generator |  | 20651
[8 empty] | 20652 | Module_Vers_Grid | Module_Vers_Grid | 1124 | Module_Vers_Grid |  | 20652
[8 empty] | 20653 | Module_Vers_HalIO | Module_Vers_HalIO | 1125 | Module_Vers_HalIO |  | 20653
[8 empty] | 20654 | Module_Vers_HeatingCooling | Module_Vers_HeatingCooling | 1126 | Module_Vers_HeatingCooling |  | 20654
[8 empty] | 20662 | Module_Vers_IC | Module_Vers_IC | 1127 | Module_Vers_IC |  | 20662
[8 empty] | 20663 | Module_Vers_Ignition | Module_Vers_Ignition | 1128 | Module_Vers_Ignition |  | 20663
[8 empty] | 20664 | Module_Vers_KLS98 | Module_Vers_KLS98 | 1129 | Module_Vers_KLS98 |  | 20664
[8 empty] | 20665 | Module_Vers_Knocking | Module_Vers_Knocking | 1130 | Module_Vers_Knocking |  | 20665
[8 empty] | 20666 | Module_Vers_MONIC | Module_Vers_MONIC | 1131 | Module_Vers_MONIC |  | 20666
[8 empty] | 20673 | Module_Vers_NotConnected | Module_Vers_NotConnected | 1132 | Module_Vers_NotConnected |  | 20673
[8 empty] | 20655 | Module_Vers_Opstate | Module_Vers_Opstate | 1133 | Module_Vers_Opstate |  | 20655
[8 empty] | 20667 | Module_Vers_ParaBase | Module_Vers_ParaBase | 1134 | Module_Vers_ParaBase |  | 20667
[8 empty] | 20668 | Module_Vers_SAFI | Module_Vers_SAFI | 1135 | Module_Vers_SAFI |  | 20668
[8 empty] | 20669 | Module_Vers_Synchronization | Module_Vers_Synchronization | 1136 | Module_Vers_Synchronization |  | 20669
[8 empty] | 20670 | Module_Vers_ThermalReactor | Module_Vers_ThermalReactor | 1137 | Module_Vers_ThermalReactor |  | 20670
[8 empty] | 20671 | Module_Vers_Ventilation | Module_Vers_Ventilation | 1138 | Module_Vers_Ventilation |  | 20671
[8 empty] | 20672 | Module_Vers_Visu | Module_Vers_Visu | 1139 | Module_Vers_Visu |  | 20672
[8 empty] | 19964 | ModuleNumber | ModuleNumber | 1140 | ModuleNumber |  | 19964
[8 empty] | 78 | Monic_VoltAvg | Monic_VoltAvg | 1141 | Monic_VoltAvg | kV | 78
[8 empty] | 80 | Monic_VoltCyl01 | Monic_VoltCyl01 | 1142 | Monic_VoltCyl01 | kV | 80
[8 empty] | 82 | Monic_VoltCyl02 | Monic_VoltCyl02 | 1143 | Monic_VoltCyl02 | kV | 82
[8 empty] | 83 | Monic_VoltCyl03 | Monic_VoltCyl03 | 1144 | Monic_VoltCyl03 | kV | 83
[8 empty] | 84 | Monic_VoltCyl04 | Monic_VoltCyl04 | 1145 | Monic_VoltCyl04 | kV | 84
[8 empty] | 85 | Monic_VoltCyl05 | Monic_VoltCyl05 | 1146 | Monic_VoltCyl05 | kV | 85
[8 empty] | 86 | Monic_VoltCyl06 | Monic_VoltCyl06 | 1147 | Monic_VoltCyl06 | kV | 86
[8 empty] | 88 | Monic_VoltCyl07 | Monic_VoltCyl07 | 1148 | Monic_VoltCyl07 | kV | 88
[8 empty] | 90 | Monic_VoltCyl08 | Monic_VoltCyl08 | 1149 | Monic_VoltCyl08 | kV | 90
[8 empty] | 92 | Monic_VoltCyl09 | Monic_VoltCyl09 | 1150 | Monic_VoltCyl09 | kV | 92
[8 empty] | 93 | Monic_VoltCyl10 | Monic_VoltCyl10 | 1151 | Monic_VoltCyl10 | kV | 93
[8 empty] | 94 | Monic_VoltCyl11 | Monic_VoltCyl11 | 1152 | Monic_VoltCyl11 | kV | 94
[8 empty] | 95 | Monic_VoltCyl12 | Monic_VoltCyl12 | 1153 | Monic_VoltCyl12 | kV | 95
[8 empty] | 96 | Monic_VoltCyl13 | Monic_VoltCyl13 | 1154 | Monic_VoltCyl13 | kV | 96
[8 empty] | 97 | Monic_VoltCyl14 | Monic_VoltCyl14 | 1155 | Monic_VoltCyl14 | kV | 97
[8 empty] | 98 | Monic_VoltCyl15 | Monic_VoltCyl15 | 1156 | Monic_VoltCyl15 | kV | 98
[8 empty] | 99 | Monic_VoltCyl16 | Monic_VoltCyl16 | 1157 | Monic_VoltCyl16 | kV | 99
[8 empty] | 118 | Monic_VoltCyl17 | Monic_VoltCyl17 | 1158 | Monic_VoltCyl17 | kV | 118
[8 empty] | 120 | Monic_VoltCyl18 | Monic_VoltCyl18 | 1159 | Monic_VoltCyl18 | kV | 120
[8 empty] | 121 | Monic_VoltCyl19 | Monic_VoltCyl19 | 1160 | Monic_VoltCyl19 | kV | 121
[8 empty] | 123 | Monic_VoltCyl20 | Monic_VoltCyl20 | 1161 | Monic_VoltCyl20 | kV | 123
[8 empty] | 203 | Monic_VoltCyl21 | Monic_VoltCyl21 | 1162 | Monic_VoltCyl21 | kV | 203
[8 empty] | 204 | Monic_VoltCyl22 | Monic_VoltCyl22 | 1163 | Monic_VoltCyl22 | kV | 204
[8 empty] | 205 | Monic_VoltCyl23 | Monic_VoltCyl23 | 1164 | Monic_VoltCyl23 | kV | 205
[8 empty] | 206 | Monic_VoltCyl24 | Monic_VoltCyl24 | 1165 | Monic_VoltCyl24 | kV | 206
[8 empty] | 100 | Monic_VoltMax | Monic_VoltMax | 1166 | Monic_VoltMax | kV | 100
[8 empty] | 101 | Monic_VoltMin | Monic_VoltMin | 1167 | Monic_VoltMin | kV | 101
[8 empty] | 1000079 | OFRUL_RUL | OFRUL_RUL | 1168 | OFRUL_RUL | oph | 1000079
[8 empty] | 27825 | oil_amb_temp | oil_amb_temp | 1169 | oil_amb_temp | °C | 27825
[8 empty] | 27844 | oil_cal_zero | oil_cal_zero | 1170 | oil_cal_zero |  | 27844
[8 empty] | 27826 | oil_condition | oil_condition | 1171 | oil_condition | % | 27826
[8 empty] | 27853 | oil_fe_bin_cnt_1 | oil_fe_bin_cnt_1 | 1172 | oil_fe_bin_cnt_1 |  | 27853
[8 empty] | 27854 | oil_fe_bin_cnt_2 | oil_fe_bin_cnt_2 | 1173 | oil_fe_bin_cnt_2 |  | 27854
[8 empty] | 27855 | oil_fe_bin_cnt_3 | oil_fe_bin_cnt_3 | 1174 | oil_fe_bin_cnt_3 |  | 27855
[8 empty] | 27856 | oil_fe_bin_cnt_4 | oil_fe_bin_cnt_4 | 1175 | oil_fe_bin_cnt_4 |  | 27856
[8 empty] | 27857 | oil_fe_bin_cnt_5 | oil_fe_bin_cnt_5 | 1176 | oil_fe_bin_cnt_5 |  | 27857
[8 empty] | 27858 | oil_fe_bin_cnt_6 | oil_fe_bin_cnt_6 | 1177 | oil_fe_bin_cnt_6 |  | 27858
[8 empty] | 27859 | oil_fe_bin_cnt_7 | oil_fe_bin_cnt_7 | 1178 | oil_fe_bin_cnt_7 |  | 27859
[8 empty] | 27867 | oil_fe_bin_size_1 | oil_fe_bin_size_1 | 1179 | oil_fe_bin_size_1 |  | 27867
[8 empty] | 27868 | oil_fe_bin_size_2 | oil_fe_bin_size_2 | 1180 | oil_fe_bin_size_2 |  | 27868
[8 empty] | 27869 | oil_fe_bin_size_3 | oil_fe_bin_size_3 | 1181 | oil_fe_bin_size_3 |  | 27869
[8 empty] | 27870 | oil_fe_bin_size_4 | oil_fe_bin_size_4 | 1182 | oil_fe_bin_size_4 |  | 27870
[8 empty] | 27871 | oil_fe_bin_size_5 | oil_fe_bin_size_5 | 1183 | oil_fe_bin_size_5 |  | 27871
[8 empty] | 27872 | oil_fe_bin_size_6 | oil_fe_bin_size_6 | 1184 | oil_fe_bin_size_6 |  | 27872
[8 empty] | 27873 | oil_fe_bin_size_7 | oil_fe_bin_size_7 | 1185 | oil_fe_bin_size_7 |  | 27873
[8 empty] | 27852 | oil_fe_mass | oil_fe_mass | 1186 | oil_fe_mass |  | 27852
[8 empty] | 27851 | oil_gastops_status | oil_gastops_status | 1187 | oil_gastops_status |  | 27851
[8 empty] | 27848 | oil_hw_version | oil_hw_version | 1188 | oil_hw_version |  | 27848
[8 empty] | 27827 | oil_max_amb_temp | oil_max_amb_temp | 1189 | oil_max_amb_temp | °C | 27827
[8 empty] | 27860 | oil_nfe_bin_cnt_1 | oil_nfe_bin_cnt_1 | 1190 | oil_nfe_bin_cnt_1 |  | 27860
[8 empty] | 27861 | oil_nfe_bin_cnt_2 | oil_nfe_bin_cnt_2 | 1191 | oil_nfe_bin_cnt_2 |  | 27861
[8 empty] | 27862 | oil_nfe_bin_cnt_3 | oil_nfe_bin_cnt_3 | 1192 | oil_nfe_bin_cnt_3 |  | 27862
[8 empty] | 27863 | oil_nfe_bin_cnt_4 | oil_nfe_bin_cnt_4 | 1193 | oil_nfe_bin_cnt_4 |  | 27863
[8 empty] | 27864 | oil_nfe_bin_cnt_5 | oil_nfe_bin_cnt_5 | 1194 | oil_nfe_bin_cnt_5 |  | 27864
[8 empty] | 27865 | oil_nfe_bin_cnt_6 | oil_nfe_bin_cnt_6 | 1195 | oil_nfe_bin_cnt_6 |  | 27865
[8 empty] | 27866 | oil_nfe_bin_cnt_7 | oil_nfe_bin_cnt_7 | 1196 | oil_nfe_bin_cnt_7 |  | 27866
[8 empty] | 27845 | oil_node_address | oil_node_address | 1197 | oil_node_address |  | 27845
[8 empty] | 27824 | oil_oil_temp | oil_oil_temp | 1198 | oil_oil_temp | °C | 27824
[8 empty] | 1000087 | Oil_Remaining_Useful_Life | Oil_Remaining_Useful_Life | 1199 | Oil_Remaining_Useful_Life | oph | 1000087
[8 empty] | 1000021 | Oil_Sample_Aluminium | Oil_Sample_Aluminium | 1200 | Oil_Sample_Aluminium | mg/kg | 1000021
[8 empty] | 1000038 | Oil_Sample_Antimony | Oil_Sample_Antimony | 1201 | Oil_Sample_Antimony | mg/kg | 1000038
[8 empty] | 1040153 | Oil_Sample_Appearance | Oil_Sample_Appearance | 1202 | Oil_Sample_Appearance |  | 1040153
[8 empty] | 1000019 | Oil_Sample_Barium | Oil_Sample_Barium | 1203 | Oil_Sample_Barium | mg/kg | 1000019
[8 empty] | 1000008 | Oil_Sample_Booked_In_Date | Oil_Sample_Booked_In_Date | 1204 | Oil_Sample_Booked_In_Date |  | 1000008
[8 empty] | 1000029 | Oil_Sample_Boron | Oil_Sample_Boron | 1205 | Oil_Sample_Boron | mg/kg | 1000029
[8 empty] | 1000037 | Oil_Sample_Cadmium | Oil_Sample_Cadmium | 1206 | Oil_Sample_Cadmium | mg/kg | 1000037
[8 empty] | 1000018 | Oil_Sample_Calcium | Oil_Sample_Calcium | 1207 | Oil_Sample_Calcium | mg/kg | 1000018
[8 empty] | 1000023 | Oil_Sample_Chromium | Oil_Sample_Chromium | 1208 | Oil_Sample_Chromium | mg/kg | 1000023
[8 empty] | 1040154 | Oil_Sample_Colour | Oil_Sample_Colour | 1209 | Oil_Sample_Colour |  | 1040154
[8 empty] | 1040155 | Oil_Sample_Conductivity | Oil_Sample_Conductivity | 1210 | Oil_Sample_Conductivity |  | 1040155
[8 empty] | 1000024 | Oil_Sample_Copper | Oil_Sample_Copper | 1211 | Oil_Sample_Copper | mg/kg | 1000024
[8 empty] | 1000005 | Oil_Sample_Date_Taken | Oil_Sample_Date_Taken | 1212 | Oil_Sample_Date_Taken |  | 1000005
[8 empty] | 1000046 | Oil_Sample_Density15 | Oil_Sample_Density15 | 1213 | Oil_Sample_Density15 |  | 1000046
[8 empty] | 1000042 | Oil_Sample_Glycol | Oil_Sample_Glycol | 1214 | Oil_Sample_Glycol | % | 1000042
[8 empty] | 1000000 | Oil_Sample_Id | Oil_Sample_Id | 1215 | Oil_Sample_Id |  | 1000000
[8 empty] | 1000013 | Oil_Sample_Insolubles | Oil_Sample_Insolubles | 1216 | Oil_Sample_Insolubles | % | 1000013
[8 empty] | 1000045 | Oil_Sample_IPH | Oil_Sample_IPH | 1217 | Oil_Sample_IPH |  | 1000045
[8 empty] | 1000022 | Oil_Sample_Iron | Oil_Sample_Iron | 1218 | Oil_Sample_Iron | mg/kg | 1000022
[8 empty] | 1000009 | Oil_Sample_Lab_Memo | Oil_Sample_Lab_Memo | 1219 | Oil_Sample_Lab_Memo |  | 1000009
[8 empty] | 1000025 | Oil_Sample_Lead | Oil_Sample_Lead | 1220 | Oil_Sample_Lead | mg/kg | 1000025
[8 empty] | 1000020 | Oil_Sample_Magnesium | Oil_Sample_Magnesium | 1221 | Oil_Sample_Magnesium | mg/kg | 1000020
[8 empty] | 1000035 | Oil_Sample_Manganese | Oil_Sample_Manganese | 1222 | Oil_Sample_Manganese | mg/kg | 1000035
[8 empty] | 1000031 | Oil_Sample_Molybdenum | Oil_Sample_Molybdenum | 1223 | Oil_Sample_Molybdenum | mg/kg | 1000031
[8 empty] | 1000032 | Oil_Sample_Nickel | Oil_Sample_Nickel | 1224 | Oil_Sample_Nickel | mg/kg | 1000032
[8 empty] | 1000041 | Oil_Sample_Nitration | Oil_Sample_Nitration | 1225 | Oil_Sample_Nitration | ABS/cm | 1000041
[8 empty] | 1000003 | Oil_Sample_Oil_Added | Oil_Sample_Oil_Added | 1226 | Oil_Sample_Oil_Added |  | 1000003
[8 empty] | 1000047 | Oil_Sample_Oil_Condition | Oil_Sample_Oil_Condition | 1227 | Oil_Sample_Oil_Condition |  | 1000047
[8 empty] | 1000002 | Oil_Sample_Oil_Hours | Oil_Sample_Oil_Hours | 1228 | Oil_Sample_Oil_Hours | oil hours | 1000002
[8 empty] | 1000040 | Oil_Sample_Oxidation | Oil_Sample_Oxidation | 1229 | Oil_Sample_Oxidation | ABS/cm | 1000040
[8 empty] | 1000016 | Oil_Sample_Phosphorus | Oil_Sample_Phosphorus | 1230 | Oil_Sample_Phosphorus | mg/kg | 1000016
[8 empty] | 1000036 | Oil_Sample_Potassium | Oil_Sample_Potassium | 1231 | Oil_Sample_Potassium | mg/kg | 1000036
[8 empty] | 1000007 | Oil_Sample_Receipt_Date | Oil_Sample_Receipt_Date | 1232 | Oil_Sample_Receipt_Date |  | 1000007
[8 empty] | 1000027 | Oil_Sample_Silicon | Oil_Sample_Silicon | 1233 | Oil_Sample_Silicon | mg/kg | 1000027
[8 empty] | 1000033 | Oil_Sample_Silver | Oil_Sample_Silver | 1234 | Oil_Sample_Silver | mg/kg | 1000033
[8 empty] | 1000028 | Oil_Sample_Sodium | Oil_Sample_Sodium | 1235 | Oil_Sample_Sodium | mg/kg | 1000028
[8 empty] | 1000014 | Oil_Sample_TAN | Oil_Sample_TAN | 1236 | Oil_Sample_TAN | mg KOH/g | 1000014
[8 empty] | 1000015 | Oil_Sample_TBN | Oil_Sample_TBN | 1237 | Oil_Sample_TBN | mg KOH/g | 1000015
[8 empty] | 1000006 | Oil_Sample_Ticket_Number | Oil_Sample_Ticket_Number | 1238 | Oil_Sample_Ticket_Number |  | 1000006
[8 empty] | 1000026 | Oil_Sample_Tin | Oil_Sample_Tin | 1239 | Oil_Sample_Tin | mg/kg | 1000026
[8 empty] | 1000034 | Oil_Sample_Titanium | Oil_Sample_Titanium | 1240 | Oil_Sample_Titanium | mg/kg | 1000034
[8 empty] | 1000001 | Oil_Sample_Unit_Hours | Oil_Sample_Unit_Hours | 1241 | Oil_Sample_Unit_Hours | oph | 1000001
[8 empty] | 1000030 | Oil_Sample_Vanadium | Oil_Sample_Vanadium | 1242 | Oil_Sample_Vanadium | mg/kg | 1000030
[8 empty] | 1000011 | Oil_Sample_Viscosity100 | Oil_Sample_Viscosity100 | 1243 | Oil_Sample_Viscosity100 | mmÂ²/sec | 1000011
[8 empty] | 1000010 | Oil_Sample_Viscosity40 | Oil_Sample_Viscosity40 | 1244 | Oil_Sample_Viscosity40 | mmÂ²/sec | 1000010
[8 empty] | 1000012 | Oil_Sample_Water | Oil_Sample_Water | 1245 | Oil_Sample_Water | % | 1000012
[8 empty] | 1000017 | Oil_Sample_Zinc | Oil_Sample_Zinc | 1246 | Oil_Sample_Zinc | mg/kg | 1000017
[8 empty] | 27847 | oil_serial_number | oil_serial_number | 1247 | oil_serial_number |  | 27847
[8 empty] | 27850 | oil_serial_number_hi | oil_serial_number_hi | 1248 | oil_serial_number_hi |  | 27850
[8 empty] | 27846 | oil_serial_type | oil_serial_type | 1249 | oil_serial_type |  | 27846
[8 empty] | 27849 | oil_sw_version | oil_sw_version | 1250 | oil_sw_version |  | 27849
[8 empty] | 1258 | OperationalCondition | Status | 1251 | OperationalCondition |  | 1258
[8 empty] | 10044821 | OperationalConditionNumeric | OperationalConditionNumeric | 1252 | OperationalConditionNumeric |  | 10044821
[8 empty] | 667 | OperationalState | OperationalState | 1253 | OperationalState |  | 667
[8 empty] | 1040157 | OpH_Jumps | OpH_Jumps | 1254 | OpH_Jumps | count | 1040157
[8 empty] | 1040158 | OpH_Spikes | OpH_Spikes | 1255 | OpH_Spikes | count | 1040158
[8 empty] | 1040168 | OpHours_BackUp_Counter | OpHours_BackUp_Counter | 1256 | OpHours_BackUp_Counter | h | 1040168
[8 empty] | 1016494 | OPHSR_calc_OphToStart | OPHSR_calc_OphToStart | 1257 | OPHSR_calc_OphToStart | Oph/Starts | 1016494
[8 empty] | 10050012 | opstate_iidx_omss | opstate_iidx_omss | 1258 | opstate_iidx_omss |  | 10050012
[8 empty] | 10050013 | opstate_iidx_rss | opstate_iidx_rss | 1259 | opstate_iidx_rss |  | 10050013
[8 empty] | 10045525 | out_ha_rf_mmd_busbar_1 | out_ha_rf_mmd_busbar_1 | 1260 | out_ha_rf_mmd_busbar_1 |  | 10045525
[8 empty] | 10045521 | out_ha_rf_mmd_synch1_1 | out_ha_rf_mmd_synch1_1 | 1261 | out_ha_rf_mmd_synch1_1 |  | 10045521
[8 empty] | 10045522 | out_ha_rf_mmd_synch1_2 | out_ha_rf_mmd_synch1_2 | 1262 | out_ha_rf_mmd_synch1_2 |  | 10045522
[8 empty] | 10045523 | out_ha_rf_mmd_synch2_1 | out_ha_rf_mmd_synch2_1 | 1263 | out_ha_rf_mmd_synch2_1 |  | 10045523
[8 empty] | 10045524 | out_ha_rf_mmd_synch2_2 | out_ha_rf_mmd_synch2_2 | 1264 | out_ha_rf_mmd_synch2_2 |  | 10045524
[8 empty] | 10049312 | p_reddelta_ch4_norm | p_reddelta_ch4_norm | 1265 | p_reddelta_ch4_norm | % | 10049312
[8 empty] | 10049297 | p_reddelta_ch_t1hp_norm | p_reddelta_ch_t1hp_norm | 1266 | p_reddelta_ch_t1hp_norm | % | 10049297
[8 empty] | 10049308 | p_reddelta_cospctr_f_norm | p_reddelta_cospctr_f_norm | 1267 | p_reddelta_cospctr_f_norm | % | 10049308
[8 empty] | 10049302 | p_reddelta_cospctr_t_norm | p_reddelta_cospctr_t_norm | 1268 | p_reddelta_cospctr_t_norm | % | 10049302
[8 empty] | 10049309 | p_reddelta_cospctr_u_norm | p_reddelta_cospctr_u_norm | 1269 | p_reddelta_cospctr_u_norm | % | 10049309
[8 empty] | 10049323 | p_reddelta_cv_norm | p_reddelta_cv_norm | 1270 | p_reddelta_cv_norm | % | 10049323
[8 empty] | 10049300 | p_reddelta_egt_norm | p_reddelta_egt_norm | 1271 | p_reddelta_egt_norm | % | 10049300
[8 empty] | 10049324 | p_reddelta_eta_gen_norm | p_reddelta_eta_gen_norm | 1272 | p_reddelta_eta_gen_norm | % | 10049324
[8 empty] | 10049310 | p_reddelta_evu_norm | p_reddelta_evu_norm | 1273 | p_reddelta_evu_norm | % | 10049310
[8 empty] | 10049313 | p_reddelta_gaspr_norm | p_reddelta_gaspr_norm | 1274 | p_reddelta_gaspr_norm | % | 10049313
[8 empty] | 10049303 | p_reddelta_hictr_norm | p_reddelta_hictr_norm | 1275 | p_reddelta_hictr_norm | % | 10049303
[8 empty] | 10049317 | p_reddelta_hum_norm | p_reddelta_hum_norm | 1276 | p_reddelta_hum_norm | % | 10049317
[8 empty] | 10049318 | p_reddelta_knck_opti_norm | p_reddelta_knck_opti_norm | 1277 | p_reddelta_knck_opti_norm | % | 10049318
[8 empty] | 10049304 | p_reddelta_leanox_norm | p_reddelta_leanox_norm | 1278 | p_reddelta_leanox_norm | % | 10049304
[8 empty] | 10049306 | p_reddelta_pbc_norm | p_reddelta_pbc_norm | 1279 | p_reddelta_pbc_norm | % | 10049306
[8 empty] | 10049299 | p_reddelta_pr_cc_norm | p_reddelta_pr_cc_norm | 1280 | p_reddelta_pr_cc_norm | % | 10049299
[8 empty] | 10049301 | p_reddelta_pr_gr_norm | p_reddelta_pr_gr_norm | 1281 | p_reddelta_pr_gr_norm | % | 10049301
[8 empty] | 10049307 | p_reddelta_pr_pcgt_norm | p_reddelta_pr_pcgt_norm | 1282 | p_reddelta_pr_pcgt_norm | % | 10049307
[8 empty] | 10049314 | p_reddelta_suctpr_norm | p_reddelta_suctpr_norm | 1283 | p_reddelta_suctpr_norm | % | 10049314
[8 empty] | 10049298 | p_reddelta_t_ecw_norm | p_reddelta_t_ecw_norm | 1284 | p_reddelta_t_ecw_norm | % | 10049298
[8 empty] | 10049322 | p_reddelta_t_genairin_norm | p_reddelta_t_genairin_norm | 1285 | p_reddelta_t_genairin_norm | % | 10049322
[8 empty] | 10049321 | p_reddelta_t_genswitchcab_norm | p_reddelta_t_genswitchcab_norm | 1286 | p_reddelta_t_genswitchcab_norm | % | 10049321
[8 empty] | 10049316 | p_reddelta_t_hwr_norm | p_reddelta_t_hwr_norm | 1287 | p_reddelta_t_hwr_norm | % | 10049316
[8 empty] | 10049311 | p_reddelta_t_inairer_norm | p_reddelta_t_inairer_norm | 1288 | p_reddelta_t_inairer_norm | % | 10049311
[8 empty] | 10049305 | p_reddelta_t_oil_norm | p_reddelta_t_oil_norm | 1289 | p_reddelta_t_oil_norm | % | 10049305
[8 empty] | 10049320 | p_reddelta_t_transformer_norm | p_reddelta_t_transformer_norm | 1290 | p_reddelta_t_transformer_norm | % | 10049320
[8 empty] | 10049315 | p_reddelta_tc_norm | p_reddelta_tc_norm | 1291 | p_reddelta_tc_norm | % | 10049315
[8 empty] | 10049325 | p_unred | p_unred | 1292 | p_unred | kW | 10049325
[8 empty] | 16619 | Para_Aux_AirStart_HysMaxInlet | Para_Aux_AirStart_HysMaxInlet | 1293 | Para_Aux_AirStart_HysMaxInlet |  | 16619
[8 empty] | 16620 | Para_Aux_AirStart_HysMin1 | Para_Aux_AirStart_HysMin1 | 1294 | Para_Aux_AirStart_HysMin1 |  | 16620
[8 empty] | 16621 | Para_Aux_AirStart_HysMinInlet | Para_Aux_AirStart_HysMinInlet | 1295 | Para_Aux_AirStart_HysMinInlet | bar | 16621
[8 empty] | 16622 | Para_Aux_AirStart_LimitMaxInlet | Para_Aux_AirStart_LimitMaxInlet | 1296 | Para_Aux_AirStart_LimitMaxInlet | bar | 16622
[8 empty] | 16623 | Para_Aux_AirStart_LimitMin1 | Para_Aux_AirStart_LimitMin1 | 1297 | Para_Aux_AirStart_LimitMin1 | bar | 16623
[8 empty] | 16624 | Para_Aux_AirStart_LimitMinInlet | Para_Aux_AirStart_LimitMinInlet | 1298 | Para_Aux_AirStart_LimitMinInlet | bar | 16624
[8 empty] | 10001481 | Para_Aux_AirStart_N_AirStarter_Exist | Para_Aux_AirStart_N_AirStarter_Exist | 1299 | Para_Aux_AirStart_N_AirStarter_Exist |  | 10001481
[8 empty] | 10001509 | Para_Aux_AirStart_Pr_AirStarter_Supply_Exist | Para_Aux_AirStart_Pr_AirStarter_Supply_Exist | 1300 | Para_Aux_AirStart_Pr_AirStarter_Supply_Exist |  | 10001509
[8 empty] | 10000238 | Para_Aux_AirStart_Pr_AirStarter_Supply_HiHi | Para_Aux_AirStart_Pr_AirStarter_Supply_HiHi | 1301 | Para_Aux_AirStart_Pr_AirStarter_Supply_HiHi |  | 10000238
[8 empty] | 10000160 | Para_Aux_AirStart_Pr_AirStarter_Supply_LoLo | Para_Aux_AirStart_Pr_AirStarter_Supply_LoLo | 1302 | Para_Aux_AirStart_Pr_AirStarter_Supply_LoLo |  | 10000160
[8 empty] | 10001477 | Para_Aux_AirStart_Pr_AirStarter_SupplyScalMax | Para_Aux_AirStart_Pr_AirStarter_SupplyScalMax | 1303 | Para_Aux_AirStart_Pr_AirStarter_SupplyScalMax |  | 10001477
[8 empty] | 10001513 | Para_Aux_AirStart_Pr_AirStarter_SupplyScalMin | Para_Aux_AirStart_Pr_AirStarter_SupplyScalMin | 1304 | Para_Aux_AirStart_Pr_AirStarter_SupplyScalMin |  | 10001513
[8 empty] | 10001506 | Para_Aux_AirStart_Pr_AirStarter_Tank_Exist | Para_Aux_AirStart_Pr_AirStarter_Tank_Exist | 1305 | Para_Aux_AirStart_Pr_AirStarter_Tank_Exist |  | 10001506
[8 empty] | 10000159 | Para_Aux_AirStart_Pr_AirStarter_Tank_Lo | Para_Aux_AirStart_Pr_AirStarter_Tank_Lo | 1306 | Para_Aux_AirStart_Pr_AirStarter_Tank_Lo |  | 10000159
[8 empty] | 10001508 | Para_Aux_AirStart_Pr_AirStarter_TankScalMax | Para_Aux_AirStart_Pr_AirStarter_TankScalMax | 1307 | Para_Aux_AirStart_Pr_AirStarter_TankScalMax |  | 10001508
[8 empty] | 10001510 | Para_Aux_AirStart_Pr_AirStarter_TankScalMin | Para_Aux_AirStart_Pr_AirStarter_TankScalMin | 1308 | Para_Aux_AirStart_Pr_AirStarter_TankScalMin |  | 10001510
[8 empty] | 16625 | Para_Aux_AirStart_StartTime | Para_Aux_AirStart_StartTime | 1309 | Para_Aux_AirStart_StartTime | s | 16625
[8 empty] | 10000161 | Para_Aux_AirStart_tiAirStarter_OnTime | Para_Aux_AirStart_tiAirStarter_OnTime | 1310 | Para_Aux_AirStart_tiAirStarter_OnTime |  | 10000161
[8 empty] | 10000120 | Para_Aux_AuxChC_Visible | Para_Aux_AuxChC_Visible | 1311 | Para_Aux_AuxChC_Visible |  | 10000120
[8 empty] | 10000138 | Para_Aux_BarometricPress_Pr_Baro_Exist | Para_Aux_BarometricPress_Pr_Baro_Exist | 1312 | Para_Aux_BarometricPress_Pr_Baro_Exist |  | 10000138
[8 empty] | 10000137 | Para_Aux_BarometricPress_Pr_Baro_site | Para_Aux_BarometricPress_Pr_Baro_site | 1313 | Para_Aux_BarometricPress_Pr_Baro_site |  | 10000137
[8 empty] | 10000136 | Para_Aux_BarometricPress_Pr_Baro_siteDevMax | Para_Aux_BarometricPress_Pr_Baro_siteDevMax | 1314 | Para_Aux_BarometricPress_Pr_Baro_siteDevMax |  | 10000136
[8 empty] | 10008438 | Para_Aux_BHV_Active | Para_Aux_BHV_Active | 1315 | Para_Aux_BHV_Active |  | 10008438
[8 empty] | 10008951 | Para_Aux_BoP_BOP_ChCoolCirc_Act | Para_Aux_BoP_BOP_ChCoolCirc_Act | 1316 | Para_Aux_BoP_BOP_ChCoolCirc_Act |  | 10008951
[8 empty] | 10008949 | Para_Aux_BoP_BOP_EmCoolCirc_Act | Para_Aux_BoP_BOP_EmCoolCirc_Act | 1317 | Para_Aux_BoP_BOP_EmCoolCirc_Act |  | 10008949
[8 empty] | 10008953 | Para_Aux_BoP_BOP_ERVent_Act | Para_Aux_BoP_BOP_ERVent_Act | 1318 | Para_Aux_BoP_BOP_ERVent_Act |  | 10008953
[8 empty] | 10008954 | Para_Aux_BoP_BOP_ExhGasSys_Act | Para_Aux_BoP_BOP_ExhGasSys_Act | 1319 | Para_Aux_BoP_BOP_ExhGasSys_Act |  | 10008954
[8 empty] | 10008950 | Para_Aux_BoP_BOP_HeatCirc_Act | Para_Aux_BoP_BOP_HeatCirc_Act | 1320 | Para_Aux_BoP_BOP_HeatCirc_Act |  | 10008950
[8 empty] | 10008952 | Para_Aux_BoP_BOP_MainGasPrep_Act | Para_Aux_BoP_BOP_MainGasPrep_Act | 1321 | Para_Aux_BoP_BOP_MainGasPrep_Act |  | 10008952
[8 empty] | 10008369 | Para_Aux_CDP_Active | Para_Aux_CDP_Active | 1322 | Para_Aux_CDP_Active |  | 10008369
[8 empty] | 10000171 | Para_Aux_ChargeCooler_ChC_CtrNum | Para_Aux_ChargeCooler_ChC_CtrNum | 1323 | Para_Aux_ChargeCooler_ChC_CtrNum |  | 10000171
[8 empty] | 10008380 | Para_Aux_ChargeCooler_CHC_Heating_active | Para_Aux_ChargeCooler_CHC_Heating_active | 1324 | Para_Aux_ChargeCooler_CHC_Heating_active |  | 10008380
[8 empty] | 10000176 | Para_Aux_ChargeCooler_ChC_NumDemAux | Para_Aux_ChargeCooler_ChC_NumDemAux | 1325 | Para_Aux_ChargeCooler_ChC_NumDemAux |  | 10000176
[8 empty] | 10000170 | Para_Aux_ChargeCooler_ChC_NumStages | Para_Aux_ChargeCooler_ChC_NumStages | 1326 | Para_Aux_ChargeCooler_ChC_NumStages |  | 10000170
[8 empty] | 10000174 | Para_Aux_ChargeCooler_ChC_OpMode | Para_Aux_ChargeCooler_ChC_OpMode | 1327 | Para_Aux_ChargeCooler_ChC_OpMode |  | 10000174
[8 empty] | 10000179 | Para_Aux_ChargeCooler_ChC_ValPosHyHi_On | Para_Aux_ChargeCooler_ChC_ValPosHyHi_On | 1328 | Para_Aux_ChargeCooler_ChC_ValPosHyHi_On |  | 10000179
[8 empty] | 10000177 | Para_Aux_ChargeCooler_ChC_ValPosLimHi_On | Para_Aux_ChargeCooler_ChC_ValPosLimHi_On | 1329 | Para_Aux_ChargeCooler_ChC_ValPosLimHi_On |  | 10000177
[8 empty] | 10000183 | Para_Aux_ChargeCooler_ChC_ValPosLimStageDown | Para_Aux_ChargeCooler_ChC_ValPosLimStageDown | 1330 | Para_Aux_ChargeCooler_ChC_ValPosLimStageDown |  | 10000183
[8 empty] | 10000180 | Para_Aux_ChargeCooler_ChC_ValPosLimStageUp | Para_Aux_ChargeCooler_ChC_ValPosLimStageUp | 1331 | Para_Aux_ChargeCooler_ChC_ValPosLimStageUp |  | 10000180
[8 empty] | 10000181 | Para_Aux_ChargeCooler_tiChC_DelayOff | Para_Aux_ChargeCooler_tiChC_DelayOff | 1332 | Para_Aux_ChargeCooler_tiChC_DelayOff |  | 10000181
[8 empty] | 10000187 | Para_Aux_ChargeCooler_tiChC_DelayStageDown | Para_Aux_ChargeCooler_tiChC_DelayStageDown | 1333 | Para_Aux_ChargeCooler_tiChC_DelayStageDown |  | 10000187
[8 empty] | 10000182 | Para_Aux_ChargeCooler_tiChC_DelayStageUp | Para_Aux_ChargeCooler_tiChC_DelayStageUp | 1334 | Para_Aux_ChargeCooler_tiChC_DelayStageUp |  | 10000182
[8 empty] | 16626 | Para_Aux_DumpRad_DelaySwitchOffCooler | Para_Aux_DumpRad_DelaySwitchOffCooler | 1335 | Para_Aux_DumpRad_DelaySwitchOffCooler | s | 16626
[8 empty] | 16627 | Para_Aux_DumpRad_DelaySwitchOffRadStep | Para_Aux_DumpRad_DelaySwitchOffRadStep | 1336 | Para_Aux_DumpRad_DelaySwitchOffRadStep | s | 16627
[8 empty] | 16628 | Para_Aux_DumpRad_DelaySwitchOnRadStep | Para_Aux_DumpRad_DelaySwitchOnRadStep | 1337 | Para_Aux_DumpRad_DelaySwitchOnRadStep | s | 16628
[8 empty] | 10000173 | Para_Aux_DumpRad_EC_St1onlyP | Para_Aux_DumpRad_EC_St1onlyP | 1338 | Para_Aux_DumpRad_EC_St1onlyP |  | 10000173
[8 empty] | 16629 | Para_Aux_DumpRad_HysSwitchOnCooler | Para_Aux_DumpRad_HysSwitchOnCooler | 1339 | Para_Aux_DumpRad_HysSwitchOnCooler | % | 16629
[8 empty] | 16630 | Para_Aux_DumpRad_LimitSwitchOffRadStepPos | Para_Aux_DumpRad_LimitSwitchOffRadStepPos | 1340 | Para_Aux_DumpRad_LimitSwitchOffRadStepPos | % | 16630
[8 empty] | 16631 | Para_Aux_DumpRad_LimitSwitchOnCooler | Para_Aux_DumpRad_LimitSwitchOnCooler | 1341 | Para_Aux_DumpRad_LimitSwitchOnCooler | % | 16631
[8 empty] | 16632 | Para_Aux_DumpRad_LimitSwitchOnRadStepPos | Para_Aux_DumpRad_LimitSwitchOnRadStepPos | 1342 | Para_Aux_DumpRad_LimitSwitchOnRadStepPos | % | 16632
[8 empty] | 16633 | Para_Aux_DumpRad_NumbAll | Para_Aux_DumpRad_NumbAll | 1343 | Para_Aux_DumpRad_NumbAll |  | 16633
[8 empty] | 16634 | Para_Aux_DumpRad_NumbAux | Para_Aux_DumpRad_NumbAux | 1344 | Para_Aux_DumpRad_NumbAux |  | 16634
[8 empty] | 16635 | Para_Aux_DumpRad_SelectCtr | Para_Aux_DumpRad_SelectCtr | 1345 | Para_Aux_DumpRad_SelectCtr |  | 16635
[8 empty] | 16636 | Para_Aux_DumpRad_Type | Para_Aux_DumpRad_Type | 1346 | Para_Aux_DumpRad_Type |  | 16636
[8 empty] | 10008832 | Para_Aux_FireProtFlap1_InlAir_visible | Para_Aux_FireProtFlap1_InlAir_visible | 1347 | Para_Aux_FireProtFlap1_InlAir_visible |  | 10008832
[8 empty] | 10008873 | Para_Aux_FireProtFlap1_OutlAir_visible | Para_Aux_FireProtFlap1_OutlAir_visible | 1348 | Para_Aux_FireProtFlap1_OutlAir_visible |  | 10008873
[8 empty] | 10008875 | Para_Aux_FireProtFlap2_InlAir_visible | Para_Aux_FireProtFlap2_InlAir_visible | 1349 | Para_Aux_FireProtFlap2_InlAir_visible |  | 10008875
[8 empty] | 10008876 | Para_Aux_FireProtFlap2_OutlAir_visible | Para_Aux_FireProtFlap2_OutlAir_visible | 1350 | Para_Aux_FireProtFlap2_OutlAir_visible |  | 10008876
[8 empty] | 10008437 | Para_Aux_FreshOilPump_tiFreshOilPump_RTC_Time | Para_Aux_FreshOilPump_tiFreshOilPump_RTC_Time | 1351 | Para_Aux_FreshOilPump_tiFreshOilPump_RTC_Time |  | 10008437
[8 empty] | 16637 | Para_Aux_GasRail_ActBlowOffDiffPressMax | Para_Aux_GasRail_ActBlowOffDiffPressMax | 1352 | Para_Aux_GasRail_ActBlowOffDiffPressMax |  | 16637
[8 empty] | 16638 | Para_Aux_GasRail_AirPressCorr | Para_Aux_GasRail_AirPressCorr | 1353 | Para_Aux_GasRail_AirPressCorr | mbar | 16638
[8 empty] | 16639 | Para_Aux_GasRail_BlowOffValveOnTimeMax | Para_Aux_GasRail_BlowOffValveOnTimeMax | 1354 | Para_Aux_GasRail_BlowOffValveOnTimeMax | s | 16639
[8 empty] | 16640 | Para_Aux_GasRail_BlowOffValveOnTimeMin | Para_Aux_GasRail_BlowOffValveOnTimeMin | 1355 | Para_Aux_GasRail_BlowOffValveOnTimeMin | s | 16640
[8 empty] | 16641 | Para_Aux_GasRail_ChargePress1 | Para_Aux_GasRail_ChargePress1 | 1356 | Para_Aux_GasRail_ChargePress1 | mbar | 16641
[8 empty] | 16642 | Para_Aux_GasRail_ChargePress2 | Para_Aux_GasRail_ChargePress2 | 1357 | Para_Aux_GasRail_ChargePress2 | mbar | 16642
[8 empty] | 16643 | Para_Aux_GasRail_DiffPress1 | Para_Aux_GasRail_DiffPress1 | 1358 | Para_Aux_GasRail_DiffPress1 | mbar | 16643
[8 empty] | 16644 | Para_Aux_GasRail_DiffPress2 | Para_Aux_GasRail_DiffPress2 | 1359 | Para_Aux_GasRail_DiffPress2 | mbar | 16644
[8 empty] | 16645 | Para_Aux_GasRail_HysBlowOffDiffMax | Para_Aux_GasRail_HysBlowOffDiffMax | 1360 | Para_Aux_GasRail_HysBlowOffDiffMax | mbar | 16645
[8 empty] | 16646 | Para_Aux_GasRail_LimitBlowOffDiffMax | Para_Aux_GasRail_LimitBlowOffDiffMax | 1361 | Para_Aux_GasRail_LimitBlowOffDiffMax | mbar | 16646
[8 empty] | 16647 | Para_Aux_GasRail_LimitPressHigh | Para_Aux_GasRail_LimitPressHigh | 1362 | Para_Aux_GasRail_LimitPressHigh | mbar | 16647
[8 empty] | 16648 | Para_Aux_GasRail_LimitPressLow | Para_Aux_GasRail_LimitPressLow | 1363 | Para_Aux_GasRail_LimitPressLow | mbar | 16648
[8 empty] | 16649 | Para_Aux_GasRail_PressCtrAdjBoost | Para_Aux_GasRail_PressCtrAdjBoost | 1364 | Para_Aux_GasRail_PressCtrAdjBoost |  | 16649
[8 empty] | 16650 | Para_Aux_GasRail_RampSetPressChange | Para_Aux_GasRail_RampSetPressChange | 1365 | Para_Aux_GasRail_RampSetPressChange | mbar/s | 16650
[8 empty] | 16651 | Para_Aux_GasRail_SetPressFix | Para_Aux_GasRail_SetPressFix | 1366 | Para_Aux_GasRail_SetPressFix | mbar | 16651
[8 empty] | 16652 | Para_Aux_GasRail_SetPressFixTime | Para_Aux_GasRail_SetPressFixTime | 1367 | Para_Aux_GasRail_SetPressFixTime | s | 16652
[8 empty] | 16653 | Para_Aux_GasRail_SetPressRangeBegin | Para_Aux_GasRail_SetPressRangeBegin | 1368 | Para_Aux_GasRail_SetPressRangeBegin | mbar | 16653
[8 empty] | 16654 | Para_Aux_GasRail_SetPressRangeEnd | Para_Aux_GasRail_SetPressRangeEnd | 1369 | Para_Aux_GasRail_SetPressRangeEnd | mbar | 16654
[8 empty] | 16655 | Para_Aux_GasRail_SpeedLimitValveClose | Para_Aux_GasRail_SpeedLimitValveClose | 1370 | Para_Aux_GasRail_SpeedLimitValveClose | 1/min | 16655
[8 empty] | 16656 | Para_Aux_GasTrain1_ActMeasure | Para_Aux_GasTrain1_ActMeasure | 1371 | Para_Aux_GasTrain1_ActMeasure |  | 16656
[8 empty] | 16657 | Para_Aux_GasTrain1_HysMax1 | Para_Aux_GasTrain1_HysMax1 | 1372 | Para_Aux_GasTrain1_HysMax1 |  | 16657
[8 empty] | 16658 | Para_Aux_GasTrain1_HysMax2 | Para_Aux_GasTrain1_HysMax2 | 1373 | Para_Aux_GasTrain1_HysMax2 | bar | 16658
[8 empty] | 16659 | Para_Aux_GasTrain1_HysMin1 | Para_Aux_GasTrain1_HysMin1 | 1374 | Para_Aux_GasTrain1_HysMin1 | bar | 16659
[8 empty] | 16660 | Para_Aux_GasTrain1_HysMin2 | Para_Aux_GasTrain1_HysMin2 | 1375 | Para_Aux_GasTrain1_HysMin2 | bar | 16660
[8 empty] | 16661 | Para_Aux_GasTrain1_LimitMax1 | Para_Aux_GasTrain1_LimitMax1 | 1376 | Para_Aux_GasTrain1_LimitMax1 | bar | 16661
[8 empty] | 16662 | Para_Aux_GasTrain1_LimitMax2 | Para_Aux_GasTrain1_LimitMax2 | 1377 | Para_Aux_GasTrain1_LimitMax2 | bar | 16662
[8 empty] | 16663 | Para_Aux_GasTrain1_LimitMin1 | Para_Aux_GasTrain1_LimitMin1 | 1378 | Para_Aux_GasTrain1_LimitMin1 |  | 16663
[8 empty] | 16664 | Para_Aux_GasTrain1_LimitMin2 | Para_Aux_GasTrain1_LimitMin2 | 1379 | Para_Aux_GasTrain1_LimitMin2 | bar | 16664
[8 empty] | 16665 | Para_Aux_GasTrain1_Range20mA | Para_Aux_GasTrain1_Range20mA | 1380 | Para_Aux_GasTrain1_Range20mA |  | 16665
[8 empty] | 16666 | Para_Aux_GasTrain1_Range4mA | Para_Aux_GasTrain1_Range4mA | 1381 | Para_Aux_GasTrain1_Range4mA | bar | 16666
[8 empty] | 10008370 | Para_Aux_HWF_Active | Para_Aux_HWF_Active | 1382 | Para_Aux_HWF_Active |  | 10008370
[8 empty] | 16667 | Para_Aux_IntakeAir_HysOpenInLouv | Para_Aux_IntakeAir_HysOpenInLouv | 1383 | Para_Aux_IntakeAir_HysOpenInLouv | °C | 16667
[8 empty] | 16668 | Para_Aux_IntakeAir_HysStartInVent | Para_Aux_IntakeAir_HysStartInVent | 1384 | Para_Aux_IntakeAir_HysStartInVent | °C | 16668
[8 empty] | 16669 | Para_Aux_IntakeAir_LimitOpenInLouv | Para_Aux_IntakeAir_LimitOpenInLouv | 1385 | Para_Aux_IntakeAir_LimitOpenInLouv | °C | 16669
[8 empty] | 16670 | Para_Aux_IntakeAir_LimitStartInVent | Para_Aux_IntakeAir_LimitStartInVent | 1386 | Para_Aux_IntakeAir_LimitStartInVent | °C | 16670
[8 empty] | 16671 | Para_Aux_IntakeAir_TempIntakeAirWarn | Para_Aux_IntakeAir_TempIntakeAirWarn | 1387 | Para_Aux_IntakeAir_TempIntakeAirWarn | °C | 16671
[8 empty] | 16672 | Para_Aux_IntakeAirPress_ActMeasure | Para_Aux_IntakeAirPress_ActMeasure | 1388 | Para_Aux_IntakeAirPress_ActMeasure |  | 16672
[8 empty] | 16673 | Para_Aux_IntakeAirPress_HysMax1 | Para_Aux_IntakeAirPress_HysMax1 | 1389 | Para_Aux_IntakeAirPress_HysMax1 | mbar | 16673
[8 empty] | 16674 | Para_Aux_IntakeAirPress_HysMin1 | Para_Aux_IntakeAirPress_HysMin1 | 1390 | Para_Aux_IntakeAirPress_HysMin1 | mbar | 16674
[8 empty] | 16675 | Para_Aux_IntakeAirPress_LimitMax1 | Para_Aux_IntakeAirPress_LimitMax1 | 1391 | Para_Aux_IntakeAirPress_LimitMax1 | mbar | 16675
[8 empty] | 16676 | Para_Aux_IntakeAirPress_LimitMin1 | Para_Aux_IntakeAirPress_LimitMin1 | 1392 | Para_Aux_IntakeAirPress_LimitMin1 | mbar | 16676
[8 empty] | 16677 | Para_Aux_IntakeAirPress_Range20mA | Para_Aux_IntakeAirPress_Range20mA | 1393 | Para_Aux_IntakeAirPress_Range20mA |  | 16677
[8 empty] | 16678 | Para_Aux_IntakeAirPress_Range4mA | Para_Aux_IntakeAirPress_Range4mA | 1394 | Para_Aux_IntakeAirPress_Range4mA |  | 16678
[8 empty] | 10008222 | Para_Aux_ManOpMode_ManAuxCtr_Active | Para_Aux_ManOpMode_ManAuxCtr_Active | 1395 | Para_Aux_ManOpMode_ManAuxCtr_Active |  | 10008222
[8 empty] | 10008221 | Para_Aux_ManOpMode_tiManAuxCtr_Max | Para_Aux_ManOpMode_tiManAuxCtr_Max | 1396 | Para_Aux_ManOpMode_tiManAuxCtr_Max |  | 10008221
[8 empty] | 10008806 | Para_Aux_OutAirER_Fan_FU | Para_Aux_OutAirER_Fan_FU | 1397 | Para_Aux_OutAirER_Fan_FU |  | 10008806
[8 empty] | 16679 | Para_Aux_OutDoor_Hys1 | Para_Aux_OutDoor_Hys1 | 1398 | Para_Aux_OutDoor_Hys1 | °C | 16679
[8 empty] | 16680 | Para_Aux_OutDoor_Hys2 | Para_Aux_OutDoor_Hys2 | 1399 | Para_Aux_OutDoor_Hys2 | °C | 16680
[8 empty] | 16681 | Para_Aux_OutDoor_Hys3 | Para_Aux_OutDoor_Hys3 | 1400 | Para_Aux_OutDoor_Hys3 | °C | 16681
[8 empty] | 16682 | Para_Aux_OutDoor_Hys4 | Para_Aux_OutDoor_Hys4 | 1401 | Para_Aux_OutDoor_Hys4 | °C | 16682
[8 empty] | 16683 | Para_Aux_OutDoor_Limit1 | Para_Aux_OutDoor_Limit1 | 1402 | Para_Aux_OutDoor_Limit1 | °C | 16683
[8 empty] | 16684 | Para_Aux_OutDoor_Limit2 | Para_Aux_OutDoor_Limit2 | 1403 | Para_Aux_OutDoor_Limit2 | °C | 16684
[8 empty] | 16685 | Para_Aux_OutDoor_Limit3 | Para_Aux_OutDoor_Limit3 | 1404 | Para_Aux_OutDoor_Limit3 | °C | 16685
[8 empty] | 16686 | Para_Aux_OutDoor_Limit4 | Para_Aux_OutDoor_Limit4 | 1405 | Para_Aux_OutDoor_Limit4 | °C | 16686
[8 empty] | 16687 | Para_Aux_PreChambDifPress_ActMeasure | Para_Aux_PreChambDifPress_ActMeasure | 1406 | Para_Aux_PreChambDifPress_ActMeasure |  | 16687
[8 empty] | 16688 | Para_Aux_PreChambDifPress_HysMax | Para_Aux_PreChambDifPress_HysMax | 1407 | Para_Aux_PreChambDifPress_HysMax | mbar | 16688
[8 empty] | 16689 | Para_Aux_PreChambDifPress_HysMin | Para_Aux_PreChambDifPress_HysMin | 1408 | Para_Aux_PreChambDifPress_HysMin | mbar | 16689
[8 empty] | 16690 | Para_Aux_PreChambDifPress_LimitMax | Para_Aux_PreChambDifPress_LimitMax | 1409 | Para_Aux_PreChambDifPress_LimitMax | mbar | 16690
[8 empty] | 16691 | Para_Aux_PreChambDifPress_LimitMaxP1 | Para_Aux_PreChambDifPress_LimitMaxP1 | 1410 | Para_Aux_PreChambDifPress_LimitMaxP1 | mbar | 16691
[8 empty] | 16692 | Para_Aux_PreChambDifPress_LimitMaxP2 | Para_Aux_PreChambDifPress_LimitMaxP2 | 1411 | Para_Aux_PreChambDifPress_LimitMaxP2 | mbar | 16692
[8 empty] | 16693 | Para_Aux_PreChambDifPress_LimitMin | Para_Aux_PreChambDifPress_LimitMin | 1412 | Para_Aux_PreChambDifPress_LimitMin | mbar | 16693
[8 empty] | 16694 | Para_Aux_PreChambDifPress_LimitMinP1 | Para_Aux_PreChambDifPress_LimitMinP1 | 1413 | Para_Aux_PreChambDifPress_LimitMinP1 | mbar | 16694
[8 empty] | 16695 | Para_Aux_PreChambDifPress_LimitMinP2 | Para_Aux_PreChambDifPress_LimitMinP2 | 1414 | Para_Aux_PreChambDifPress_LimitMinP2 | mbar | 16695
[8 empty] | 16696 | Para_Aux_PreChambDifPress_Range20mA | Para_Aux_PreChambDifPress_Range20mA | 1415 | Para_Aux_PreChambDifPress_Range20mA | bar | 16696
[8 empty] | 16697 | Para_Aux_PreChambDifPress_Range4mA | Para_Aux_PreChambDifPress_Range4mA | 1416 | Para_Aux_PreChambDifPress_Range4mA | bar | 16697
[8 empty] | 16698 | Para_Aux_PreChambDifPress_SwitchPointHysMax | Para_Aux_PreChambDifPress_SwitchPointHysMax | 1417 | Para_Aux_PreChambDifPress_SwitchPointHysMax | mbar | 16698
[8 empty] | 16699 | Para_Aux_PreChambDifPress_SwitchPointLimitMax | Para_Aux_PreChambDifPress_SwitchPointLimitMax | 1418 | Para_Aux_PreChambDifPress_SwitchPointLimitMax | mbar | 16699
[8 empty] | 16700 | Para_Aux_PreChambGasComp_CompOff | Para_Aux_PreChambGasComp_CompOff | 1419 | Para_Aux_PreChambGasComp_CompOff | bar | 16700
[8 empty] | 16701 | Para_Aux_PreChambGasComp_CompOn | Para_Aux_PreChambGasComp_CompOn | 1420 | Para_Aux_PreChambGasComp_CompOn | bar | 16701
[8 empty] | 16702 | Para_Aux_PreChambGasComp_Max | Para_Aux_PreChambGasComp_Max | 1421 | Para_Aux_PreChambGasComp_Max | bar | 16702
[8 empty] | 16703 | Para_Aux_PreChambGasComp_MaxHys | Para_Aux_PreChambGasComp_MaxHys | 1422 | Para_Aux_PreChambGasComp_MaxHys | bar | 16703
[8 empty] | 16704 | Para_Aux_PreChambGasComp_Min | Para_Aux_PreChambGasComp_Min | 1423 | Para_Aux_PreChambGasComp_Min | bar | 16704
[8 empty] | 16705 | Para_Aux_PreChambGasComp_MinHys | Para_Aux_PreChambGasComp_MinHys | 1424 | Para_Aux_PreChambGasComp_MinHys | bar | 16705
[8 empty] | 10000114 | Para_Aux_PreChambGasComp_Pr_PCGComp_Active | Para_Aux_PreChambGasComp_Pr_PCGComp_Active | 1425 | Para_Aux_PreChambGasComp_Pr_PCGComp_Active |  | 10000114
[8 empty] | 16706 | Para_Aux_PreChambGasTrain_ActMeasure | Para_Aux_PreChambGasTrain_ActMeasure | 1426 | Para_Aux_PreChambGasTrain_ActMeasure |  | 16706
[8 empty] | 16707 | Para_Aux_PreChambGasTrain_ActMeasureTemp | Para_Aux_PreChambGasTrain_ActMeasureTemp | 1427 | Para_Aux_PreChambGasTrain_ActMeasureTemp |  | 16707
[8 empty] | 16708 | Para_Aux_PreChambGasTrain_BoostPress1 | Para_Aux_PreChambGasTrain_BoostPress1 | 1428 | Para_Aux_PreChambGasTrain_BoostPress1 | mbar | 16708
[8 empty] | 16709 | Para_Aux_PreChambGasTrain_BoostPress2 | Para_Aux_PreChambGasTrain_BoostPress2 | 1429 | Para_Aux_PreChambGasTrain_BoostPress2 | mbar | 16709
[8 empty] | 16710 | Para_Aux_PreChambGasTrain_DiffPress1 | Para_Aux_PreChambGasTrain_DiffPress1 | 1430 | Para_Aux_PreChambGasTrain_DiffPress1 | mbar | 16710
[8 empty] | 16711 | Para_Aux_PreChambGasTrain_DiffPress2 | Para_Aux_PreChambGasTrain_DiffPress2 | 1431 | Para_Aux_PreChambGasTrain_DiffPress2 | mbar | 16711
[8 empty] | 16712 | Para_Aux_PreChambGasTrain_HysMax1 | Para_Aux_PreChambGasTrain_HysMax1 | 1432 | Para_Aux_PreChambGasTrain_HysMax1 | bar | 16712
[8 empty] | 16713 | Para_Aux_PreChambGasTrain_HysMax2 | Para_Aux_PreChambGasTrain_HysMax2 | 1433 | Para_Aux_PreChambGasTrain_HysMax2 | bar | 16713
[8 empty] | 16714 | Para_Aux_PreChambGasTrain_HysMin | Para_Aux_PreChambGasTrain_HysMin | 1434 | Para_Aux_PreChambGasTrain_HysMin | bar | 16714
[8 empty] | 16715 | Para_Aux_PreChambGasTrain_HysMin2 | Para_Aux_PreChambGasTrain_HysMin2 | 1435 | Para_Aux_PreChambGasTrain_HysMin2 | bar | 16715
[8 empty] | 16716 | Para_Aux_PreChambGasTrain_LimitMax1 | Para_Aux_PreChambGasTrain_LimitMax1 | 1436 | Para_Aux_PreChambGasTrain_LimitMax1 | bar | 16716
[8 empty] | 16717 | Para_Aux_PreChambGasTrain_LimitMax2 | Para_Aux_PreChambGasTrain_LimitMax2 | 1437 | Para_Aux_PreChambGasTrain_LimitMax2 | bar | 16717
[8 empty] | 16718 | Para_Aux_PreChambGasTrain_LimitMin | Para_Aux_PreChambGasTrain_LimitMin | 1438 | Para_Aux_PreChambGasTrain_LimitMin |  | 16718
[8 empty] | 16719 | Para_Aux_PreChambGasTrain_LimitMin2 | Para_Aux_PreChambGasTrain_LimitMin2 | 1439 | Para_Aux_PreChambGasTrain_LimitMin2 | bar | 16719
[8 empty] | 16720 | Para_Aux_PreChambGasTrain_RampSetPressChange | Para_Aux_PreChambGasTrain_RampSetPressChange | 1440 | Para_Aux_PreChambGasTrain_RampSetPressChange | mbar/s | 16720
[8 empty] | 16721 | Para_Aux_PreChambGasTrain_Range20mA | Para_Aux_PreChambGasTrain_Range20mA | 1441 | Para_Aux_PreChambGasTrain_Range20mA |  | 16721
[8 empty] | 16722 | Para_Aux_PreChambGasTrain_Range4mA | Para_Aux_PreChambGasTrain_Range4mA | 1442 | Para_Aux_PreChambGasTrain_Range4mA | bar | 16722
[8 empty] | 16723 | Para_Aux_PreChambGasTrain_RangeBeginSetPress | Para_Aux_PreChambGasTrain_RangeBeginSetPress | 1443 | Para_Aux_PreChambGasTrain_RangeBeginSetPress | mbar | 16723
[8 empty] | 16724 | Para_Aux_PreChambGasTrain_RangeEndSetPress | Para_Aux_PreChambGasTrain_RangeEndSetPress | 1444 | Para_Aux_PreChambGasTrain_RangeEndSetPress | mbar | 16724
[8 empty] | 16725 | Para_Aux_PreChambGasTrain_SigAdjustBoost | Para_Aux_PreChambGasTrain_SigAdjustBoost | 1445 | Para_Aux_PreChambGasTrain_SigAdjustBoost |  | 16725
[8 empty] | 20121 | Para_Aux_RoomVent_Act_ERV_AirFlowMon | Para_Aux_RoomVent_Act_ERV_AirFlowMon | 1446 | Para_Aux_RoomVent_Act_ERV_AirFlowMon |  | 20121
[8 empty] | 16726 | Para_Aux_RoomVent_ActPurgecycle | Para_Aux_RoomVent_ActPurgecycle | 1447 | Para_Aux_RoomVent_ActPurgecycle |  | 16726
[8 empty] | 16727 | Para_Aux_RoomVent_HysMaxRoomTemp | Para_Aux_RoomVent_HysMaxRoomTemp | 1448 | Para_Aux_RoomVent_HysMaxRoomTemp | °C | 16727
[8 empty] | 16728 | Para_Aux_RoomVent_HysRoomTemp | Para_Aux_RoomVent_HysRoomTemp | 1449 | Para_Aux_RoomVent_HysRoomTemp | °C | 16728
[8 empty] | 16729 | Para_Aux_RoomVent_HysRTStartVent | Para_Aux_RoomVent_HysRTStartVent | 1450 | Para_Aux_RoomVent_HysRTStartVent | °C | 16729
[8 empty] | 16730 | Para_Aux_RoomVent_HysRTStartVentStandby | Para_Aux_RoomVent_HysRTStartVentStandby | 1451 | Para_Aux_RoomVent_HysRTStartVentStandby | °C | 16730
[8 empty] | 16731 | Para_Aux_RoomVent_HysRTVentStep2 | Para_Aux_RoomVent_HysRTVentStep2 | 1452 | Para_Aux_RoomVent_HysRTVentStep2 | °C | 16731
[8 empty] | 16732 | Para_Aux_RoomVent_LimitRoomTemp | Para_Aux_RoomVent_LimitRoomTemp | 1453 | Para_Aux_RoomVent_LimitRoomTemp | °C | 16732
[8 empty] | 16733 | Para_Aux_RoomVent_LimitRTStartVent | Para_Aux_RoomVent_LimitRTStartVent | 1454 | Para_Aux_RoomVent_LimitRTStartVent | °C | 16733
[8 empty] | 16734 | Para_Aux_RoomVent_LimitRTStartVentStandby | Para_Aux_RoomVent_LimitRTStartVentStandby | 1455 | Para_Aux_RoomVent_LimitRTStartVentStandby | °C | 16734
[8 empty] | 16735 | Para_Aux_RoomVent_LimitRTVentStep2 | Para_Aux_RoomVent_LimitRTVentStep2 | 1456 | Para_Aux_RoomVent_LimitRTVentStep2 | °C | 16735
[8 empty] | 16736 | Para_Aux_RoomVent_MaxRoomTemp | Para_Aux_RoomVent_MaxRoomTemp | 1457 | Para_Aux_RoomVent_MaxRoomTemp | °C | 16736
[8 empty] | 16737 | Para_Aux_RoomVent_PurgeTimeMax | Para_Aux_RoomVent_PurgeTimeMax | 1458 | Para_Aux_RoomVent_PurgeTimeMax |  | 16737
[8 empty] | 16738 | Para_Aux_RoomVent_SetpointRTCtr | Para_Aux_RoomVent_SetpointRTCtr | 1459 | Para_Aux_RoomVent_SetpointRTCtr | °C | 16738
[8 empty] | 16739 | Para_Aux_RoomVent_SetpointRTCtrStandby | Para_Aux_RoomVent_SetpointRTCtrStandby | 1460 | Para_Aux_RoomVent_SetpointRTCtrStandby | °C | 16739
[8 empty] | 10008331 | Para_Aux_Ventilation_CircLouvre_Pos_CircLou1_Active | Para_Aux_Ventilation_CircLouvre_Pos_CircLou1_Active | 1461 | Para_Aux_Ventilation_CircLouvre_Pos_CircLou1_Active |  | 10008331
[8 empty] | 10008255 | Para_Aux_Ventilation_CircLouvre_Pos_CircLou1_ScalMax | Para_Aux_Ventilation_CircLouvre_Pos_CircLou1_ScalMax | 1462 | Para_Aux_Ventilation_CircLouvre_Pos_CircLou1_ScalMax |  | 10008255
[8 empty] | 10008334 | Para_Aux_Ventilation_CircLouvre_Pos_CircLou1_ScalMin | Para_Aux_Ventilation_CircLouvre_Pos_CircLou1_ScalMin | 1463 | Para_Aux_Ventilation_CircLouvre_Pos_CircLou1_ScalMin |  | 10008334
[8 empty] | 10008335 | Para_Aux_Ventilation_CircLouvre_Pos_CircLou2_Active | Para_Aux_Ventilation_CircLouvre_Pos_CircLou2_Active | 1464 | Para_Aux_Ventilation_CircLouvre_Pos_CircLou2_Active |  | 10008335
[8 empty] | 10008338 | Para_Aux_Ventilation_CircLouvre_Pos_CircLou2_ScalMax | Para_Aux_Ventilation_CircLouvre_Pos_CircLou2_ScalMax | 1465 | Para_Aux_Ventilation_CircLouvre_Pos_CircLou2_ScalMax |  | 10008338
[8 empty] | 10008336 | Para_Aux_Ventilation_CircLouvre_Pos_CircLou2_ScalMin | Para_Aux_Ventilation_CircLouvre_Pos_CircLou2_ScalMin | 1466 | Para_Aux_Ventilation_CircLouvre_Pos_CircLou2_ScalMin |  | 10008336
[8 empty] | 10008284 | Para_Aux_Ventilation_CircLouvre_T_InAirER_Rel_CircOp | Para_Aux_Ventilation_CircLouvre_T_InAirER_Rel_CircOp | 1467 | Para_Aux_Ventilation_CircLouvre_T_InAirER_Rel_CircOp |  | 10008284
[8 empty] | 10008337 | Para_Aux_Ventilation_CircLouvre_T_InAirER_Rel_CircOp_Hy | Para_Aux_Ventilation_CircLouvre_T_InAirER_Rel_CircOp_Hy | 1468 | Para_Aux_Ventilation_CircLouvre_T_InAirER_Rel_CircOp_Hy |  | 10008337
[8 empty] | 10008968 | Para_Aux_Ventilation_Ctr_RDP_OutlVE_Dep_EngP | Para_Aux_Ventilation_Ctr_RDP_OutlVE_Dep_EngP | 1469 | Para_Aux_Ventilation_Ctr_RDP_OutlVE_Dep_EngP |  | 10008968
[8 empty] | 10008966 | Para_Aux_Ventilation_Ctr_RDP_OutlVE_Dep_InlVent | Para_Aux_Ventilation_Ctr_RDP_OutlVE_Dep_InlVent | 1470 | Para_Aux_Ventilation_Ctr_RDP_OutlVE_Dep_InlVent |  | 10008966
[8 empty] | 10000154 | Para_Aux_Ventilation_ER_VentColdCountryMode | Para_Aux_Ventilation_ER_VentColdCountryMode | 1471 | Para_Aux_Ventilation_ER_VentColdCountryMode |  | 10000154
[8 empty] | 10008280 | Para_Aux_Ventilation_InletLouvre_InlVent_Ctr_InlLou_Active | Para_Aux_Ventilation_InletLouvre_InlVent_Ctr_InlLou_Active | 1472 | Para_Aux_Ventilation_InletLouvre_InlVent_Ctr_InlLou_Active |  | 10008280
[8 empty] | 10008274 | Para_Aux_Ventilation_InletLouvre_Pos_InlLou1_Active | Para_Aux_Ventilation_InletLouvre_Pos_InlLou1_Active | 1473 | Para_Aux_Ventilation_InletLouvre_Pos_InlLou1_Active |  | 10008274
[8 empty] | 10008276 | Para_Aux_Ventilation_InletLouvre_Pos_InlLou1_ScalMax | Para_Aux_Ventilation_InletLouvre_Pos_InlLou1_ScalMax | 1474 | Para_Aux_Ventilation_InletLouvre_Pos_InlLou1_ScalMax |  | 10008276
[8 empty] | 10008275 | Para_Aux_Ventilation_InletLouvre_Pos_InlLou1_ScalMin | Para_Aux_Ventilation_InletLouvre_Pos_InlLou1_ScalMin | 1475 | Para_Aux_Ventilation_InletLouvre_Pos_InlLou1_ScalMin |  | 10008275
[8 empty] | 10008277 | Para_Aux_Ventilation_InletLouvre_Pos_InlLou2_Active | Para_Aux_Ventilation_InletLouvre_Pos_InlLou2_Active | 1476 | Para_Aux_Ventilation_InletLouvre_Pos_InlLou2_Active |  | 10008277
[8 empty] | 10008278 | Para_Aux_Ventilation_InletLouvre_Pos_InlLou2_ScalMax | Para_Aux_Ventilation_InletLouvre_Pos_InlLou2_ScalMax | 1477 | Para_Aux_Ventilation_InletLouvre_Pos_InlLou2_ScalMax |  | 10008278
[8 empty] | 10008279 | Para_Aux_Ventilation_InletLouvre_Pos_InlLou2_ScalMin | Para_Aux_Ventilation_InletLouvre_Pos_InlLou2_ScalMin | 1478 | Para_Aux_Ventilation_InletLouvre_Pos_InlLou2_ScalMin |  | 10008279
[8 empty] | 10008944 | Para_Aux_Ventilation_InletLouvre_PosLim_InlLou_Rel_ERV | Para_Aux_Ventilation_InletLouvre_PosLim_InlLou_Rel_ERV | 1479 | Para_Aux_Ventilation_InletLouvre_PosLim_InlLou_Rel_ERV |  | 10008944
[8 empty] | 10008945 | Para_Aux_Ventilation_InletLouvre_PosLim_InlLou_Rel_ERV_Hy | Para_Aux_Ventilation_InletLouvre_PosLim_InlLou_Rel_ERV_Hy | 1480 | Para_Aux_Ventilation_InletLouvre_PosLim_InlLou_Rel_ERV_Hy |  | 10008945
[8 empty] | 10008282 | Para_Aux_Ventilation_InletLouvre_PosLim_InlLou_Rel_FC_ER | Para_Aux_Ventilation_InletLouvre_PosLim_InlLou_Rel_FC_ER | 1481 | Para_Aux_Ventilation_InletLouvre_PosLim_InlLou_Rel_FC_ER |  | 10008282
[8 empty] | 10008281 | Para_Aux_Ventilation_InletLouvre_PosLim_InlLou_Rel_FC_ER_Hy | Para_Aux_Ventilation_InletLouvre_PosLim_InlLou_Rel_FC_ER_Hy | 1482 | Para_Aux_Ventilation_InletLouvre_PosLim_InlLou_Rel_FC_ER_Hy |  | 10008281
[8 empty] | 10008940 | Para_Aux_Ventilation_InletLouvre_TypeCtr_InlLou_ERV | Para_Aux_Ventilation_InletLouvre_TypeCtr_InlLou_ERV | 1483 | Para_Aux_Ventilation_InletLouvre_TypeCtr_InlLou_ERV |  | 10008940
[8 empty] | 10008942 | Para_Aux_Ventilation_InletLouvre_TypeFeedback_InlLou_ERV | Para_Aux_Ventilation_InletLouvre_TypeFeedback_InlLou_ERV | 1484 | Para_Aux_Ventilation_InletLouvre_TypeFeedback_InlLou_ERV |  | 10008942
[8 empty] | 10000162 | Para_Aux_Ventilation_Louvers | Para_Aux_Ventilation_Louvers | 1485 | Para_Aux_Ventilation_Louvers |  | 10000162
[8 empty] | 10008252 | Para_Aux_Ventilation_OutletLouvre_OutlVent_Ctr_OutlLou_Active | Para_Aux_Ventilation_OutletLouvre_OutlVent_Ctr_OutlLou_Active | 1486 | Para_Aux_Ventilation_OutletLouvre_OutlVent_Ctr_OutlLou_Active |  | 10008252
[8 empty] | 10008240 | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou1_Active | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou1_Active | 1487 | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou1_Active |  | 10008240
[8 empty] | 10008242 | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou1_ScalMax | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou1_ScalMax | 1488 | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou1_ScalMax |  | 10008242
[8 empty] | 10008243 | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou1_ScalMin | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou1_ScalMin | 1489 | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou1_ScalMin |  | 10008243
[8 empty] | 10008246 | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou2_Active | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou2_Active | 1490 | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou2_Active |  | 10008246
[8 empty] | 10008244 | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou2_ScalMax | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou2_ScalMax | 1491 | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou2_ScalMax |  | 10008244
[8 empty] | 10008245 | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou2_ScalMin | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou2_ScalMin | 1492 | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou2_ScalMin |  | 10008245
[8 empty] | 10008946 | Para_Aux_Ventilation_OutletLouvre_PosLim_OutlLou_Rel_ERV | Para_Aux_Ventilation_OutletLouvre_PosLim_OutlLou_Rel_ERV | 1493 | Para_Aux_Ventilation_OutletLouvre_PosLim_OutlLou_Rel_ERV |  | 10008946
[8 empty] | 10008947 | Para_Aux_Ventilation_OutletLouvre_PosLim_OutlLou_Rel_ERV_Hy | Para_Aux_Ventilation_OutletLouvre_PosLim_OutlLou_Rel_ERV_Hy | 1494 | Para_Aux_Ventilation_OutletLouvre_PosLim_OutlLou_Rel_ERV_Hy |  | 10008947
[8 empty] | 10008251 | Para_Aux_Ventilation_OutletLouvre_PosLim_OutlLou_Rel_FC_ER | Para_Aux_Ventilation_OutletLouvre_PosLim_OutlLou_Rel_FC_ER | 1495 | Para_Aux_Ventilation_OutletLouvre_PosLim_OutlLou_Rel_FC_ER |  | 10008251
[8 empty] | 10008254 | Para_Aux_Ventilation_OutletLouvre_PosLim_OutlLou_Rel_FC_ER_Hy | Para_Aux_Ventilation_OutletLouvre_PosLim_OutlLou_Rel_FC_ER_Hy | 1496 | Para_Aux_Ventilation_OutletLouvre_PosLim_OutlLou_Rel_FC_ER_Hy |  | 10008254
[8 empty] | 10008941 | Para_Aux_Ventilation_OutletLouvre_TypeCtr_OutlLou_ERV | Para_Aux_Ventilation_OutletLouvre_TypeCtr_OutlLou_ERV | 1497 | Para_Aux_Ventilation_OutletLouvre_TypeCtr_OutlLou_ERV |  | 10008941
[8 empty] | 10008943 | Para_Aux_Ventilation_OutletLouvre_TypeFeedback_OutlLou_ERV | Para_Aux_Ventilation_OutletLouvre_TypeFeedback_OutlLou_ERV | 1498 | Para_Aux_Ventilation_OutletLouvre_TypeFeedback_OutlLou_ERV |  | 10008943
[8 empty] | 10008247 | Para_Aux_Ventilation_PrDiff_ER_Active | Para_Aux_Ventilation_PrDiff_ER_Active | 1499 | Para_Aux_Ventilation_PrDiff_ER_Active |  | 10008247
[8 empty] | 10008256 | Para_Aux_Ventilation_PrDiff_ER_Lim_High | Para_Aux_Ventilation_PrDiff_ER_Lim_High | 1500 | Para_Aux_Ventilation_PrDiff_ER_Lim_High |  | 10008256
[8 empty] | 10008348 | Para_Aux_Ventilation_PrDiff_ER_Lim_High_Hy | Para_Aux_Ventilation_PrDiff_ER_Lim_High_Hy | 1501 | Para_Aux_Ventilation_PrDiff_ER_Lim_High_Hy |  | 10008348
[8 empty] | 10008349 | Para_Aux_Ventilation_PrDiff_ER_Lim_Low | Para_Aux_Ventilation_PrDiff_ER_Lim_Low | 1502 | Para_Aux_Ventilation_PrDiff_ER_Lim_Low |  | 10008349
[8 empty] | 10008350 | Para_Aux_Ventilation_PrDiff_ER_Lim_Low_Hy | Para_Aux_Ventilation_PrDiff_ER_Lim_Low_Hy | 1503 | Para_Aux_Ventilation_PrDiff_ER_Lim_Low_Hy |  | 10008350
[8 empty] | 10008250 | Para_Aux_Ventilation_PrDiff_ER_ScalMax | Para_Aux_Ventilation_PrDiff_ER_ScalMax | 1504 | Para_Aux_Ventilation_PrDiff_ER_ScalMax |  | 10008250
[8 empty] | 10008248 | Para_Aux_Ventilation_PrDiff_ER_ScalMin | Para_Aux_Ventilation_PrDiff_ER_ScalMin | 1505 | Para_Aux_Ventilation_PrDiff_ER_ScalMin |  | 10008248
[8 empty] | 10000166 | Para_Aux_Ventilation_Purgecycle_Active | Para_Aux_Ventilation_Purgecycle_Active | 1506 | Para_Aux_Ventilation_Purgecycle_Active |  | 10000166
[8 empty] | 10008956 | Para_Aux_Ventilation_Scal_CtrInlVentER_Set_Max | Para_Aux_Ventilation_Scal_CtrInlVentER_Set_Max | 1507 | Para_Aux_Ventilation_Scal_CtrInlVentER_Set_Max |  | 10008956
[8 empty] | 10008955 | Para_Aux_Ventilation_Scal_CtrInlVentER_Set_Min | Para_Aux_Ventilation_Scal_CtrInlVentER_Set_Min | 1508 | Para_Aux_Ventilation_Scal_CtrInlVentER_Set_Min |  | 10008955
[8 empty] | 10008958 | Para_Aux_Ventilation_Scal_OffSetMax_CtrOutlVent | Para_Aux_Ventilation_Scal_OffSetMax_CtrOutlVent | 1509 | Para_Aux_Ventilation_Scal_OffSetMax_CtrOutlVent |  | 10008958
[8 empty] | 10008962 | Para_Aux_Ventilation_Scal_OffSetMax_Pel | Para_Aux_Ventilation_Scal_OffSetMax_Pel | 1510 | Para_Aux_Ventilation_Scal_OffSetMax_Pel |  | 10008962
[8 empty] | 10008957 | Para_Aux_Ventilation_Scal_OffSetMin_CtrOutlVent | Para_Aux_Ventilation_Scal_OffSetMin_CtrOutlVent | 1511 | Para_Aux_Ventilation_Scal_OffSetMin_CtrOutlVent |  | 10008957
[8 empty] | 10008959 | Para_Aux_Ventilation_Scal_OffSetMin_Pel | Para_Aux_Ventilation_Scal_OffSetMin_Pel | 1512 | Para_Aux_Ventilation_Scal_OffSetMin_Pel |  | 10008959
[8 empty] | 10008961 | Para_Aux_Ventilation_Scal_PmaxEl | Para_Aux_Ventilation_Scal_PmaxEl | 1513 | Para_Aux_Ventilation_Scal_PmaxEl |  | 10008961
[8 empty] | 10008960 | Para_Aux_Ventilation_Scal_PminEl | Para_Aux_Ventilation_Scal_PminEl | 1514 | Para_Aux_Ventilation_Scal_PminEl |  | 10008960
[8 empty] | 10008862 | Para_Aux_Ventilation_Vent_SpeedDif | Para_Aux_Ventilation_Vent_SpeedDif | 1515 | Para_Aux_Ventilation_Vent_SpeedDif |  | 10008862
[8 empty] | 10000131 | Para_Aux_Ventilation_VISA | Para_Aux_Ventilation_VISA | 1516 | Para_Aux_Ventilation_VISA |  | 10000131
[8 empty] | 10049966 | Para_base_tvisversion_xx | Para_base_tvisversion_xx | 1517 | Para_base_tvisversion_xx |  | 10049966
[8 empty] | 10049967 | Para_base_tvisversion_xxbase_tvisversion_yy | Para_base_tvisversion_xxbase_tvisversion_yy | 1518 | Para_base_tvisversion_xxbase_tvisversion_yy |  | 10049967
[8 empty] | 19095 | Para_Bearing_ConrodAlarm | Para_Bearing_ConrodAlarm | 1519 | Para_Bearing_ConrodAlarm | °C | 19095
[8 empty] | 16740 | Para_Bearing_MainLimit | Para_Bearing_MainLimit | 1520 | Para_Bearing_MainLimit |  | 16740
[8 empty] | 16741 | Para_CtrModule_Ctr1_ActStep_NEx | Para_CtrModule_Ctr1_ActStep_NEx | 1521 | Para_CtrModule_Ctr1_ActStep_NEx |  | 16741
[8 empty] | 16742 | Para_CtrModule_Ctr1_CycleTime | Para_CtrModule_Ctr1_CycleTime | 1522 | Para_CtrModule_Ctr1_CycleTime | ms | 16742
[8 empty] | 16743 | Para_CtrModule_Ctr1_DComp | Para_CtrModule_Ctr1_DComp | 1523 | Para_CtrModule_Ctr1_DComp |  | 16743
[8 empty] | 16744 | Para_CtrModule_Ctr1_DCompTune | Para_CtrModule_Ctr1_DCompTune | 1524 | Para_CtrModule_Ctr1_DCompTune |  | 16744
[8 empty] | 16745 | Para_CtrModule_Ctr1_DCompWMax | Para_CtrModule_Ctr1_DCompWMax | 1525 | Para_CtrModule_Ctr1_DCompWMax |  | 16745
[8 empty] | 16746 | Para_CtrModule_Ctr1_DCompWMin | Para_CtrModule_Ctr1_DCompWMin | 1526 | Para_CtrModule_Ctr1_DCompWMin |  | 16746
[8 empty] | 16747 | Para_CtrModule_Ctr1_DeadBand | Para_CtrModule_Ctr1_DeadBand | 1527 | Para_CtrModule_Ctr1_DeadBand | x | 16747
[8 empty] | 16748 | Para_CtrModule_Ctr1_Format | Para_CtrModule_Ctr1_Format | 1528 | Para_CtrModule_Ctr1_Format |  | 16748
[8 empty] | 16749 | Para_CtrModule_Ctr1_IComp | Para_CtrModule_Ctr1_IComp | 1529 | Para_CtrModule_Ctr1_IComp |  | 16749
[8 empty] | 16750 | Para_CtrModule_Ctr1_ICompTune | Para_CtrModule_Ctr1_ICompTune | 1530 | Para_CtrModule_Ctr1_ICompTune |  | 16750
[8 empty] | 16751 | Para_CtrModule_Ctr1_ICompWMax | Para_CtrModule_Ctr1_ICompWMax | 1531 | Para_CtrModule_Ctr1_ICompWMax |  | 16751
[8 empty] | 16752 | Para_CtrModule_Ctr1_ICompWMin | Para_CtrModule_Ctr1_ICompWMin | 1532 | Para_CtrModule_Ctr1_ICompWMin |  | 16752
[8 empty] | 16753 | Para_CtrModule_Ctr1_InvertCtrTune | Para_CtrModule_Ctr1_InvertCtrTune | 1533 | Para_CtrModule_Ctr1_InvertCtrTune |  | 16753
[8 empty] | 16754 | Para_CtrModule_Ctr1_Name | Para_CtrModule_Ctr1_Name | 1534 | Para_CtrModule_Ctr1_Name |  | 16754
[8 empty] | 16755 | Para_CtrModule_Ctr1_NameF | Para_CtrModule_Ctr1_NameF | 1535 | Para_CtrModule_Ctr1_NameF |  | 16755
[8 empty] | 16756 | Para_CtrModule_Ctr1_OptWorkPoint | Para_CtrModule_Ctr1_OptWorkPoint | 1536 | Para_CtrModule_Ctr1_OptWorkPoint |  | 16756
[8 empty] | 16757 | Para_CtrModule_Ctr1_PComp | Para_CtrModule_Ctr1_PComp | 1537 | Para_CtrModule_Ctr1_PComp |  | 16757
[8 empty] | 16758 | Para_CtrModule_Ctr1_PCompTune | Para_CtrModule_Ctr1_PCompTune | 1538 | Para_CtrModule_Ctr1_PCompTune |  | 16758
[8 empty] | 16759 | Para_CtrModule_Ctr1_PCompWMax | Para_CtrModule_Ctr1_PCompWMax | 1539 | Para_CtrModule_Ctr1_PCompWMax |  | 16759
[8 empty] | 16760 | Para_CtrModule_Ctr1_PCompWMin | Para_CtrModule_Ctr1_PCompWMin | 1540 | Para_CtrModule_Ctr1_PCompWMin |  | 16760
[8 empty] | 16761 | Para_CtrModule_Ctr1_RangeBegin | Para_CtrModule_Ctr1_RangeBegin | 1541 | Para_CtrModule_Ctr1_RangeBegin | x | 16761
[8 empty] | 16762 | Para_CtrModule_Ctr1_RangeEnd | Para_CtrModule_Ctr1_RangeEnd | 1542 | Para_CtrModule_Ctr1_RangeEnd | x | 16762
[8 empty] | 16763 | Para_CtrModule_Ctr1_Unit | Para_CtrModule_Ctr1_Unit | 1543 | Para_CtrModule_Ctr1_Unit |  | 16763
[8 empty] | 16764 | Para_CtrModule_Ctr1_UserLevelIntExt | Para_CtrModule_Ctr1_UserLevelIntExt | 1544 | Para_CtrModule_Ctr1_UserLevelIntExt |  | 16764
[8 empty] | 16765 | Para_CtrModule_Ctr1_UserLevelManAut | Para_CtrModule_Ctr1_UserLevelManAut | 1545 | Para_CtrModule_Ctr1_UserLevelManAut |  | 16765
[8 empty] | 16766 | Para_CtrModule_Ctr1_UserLevelSet | Para_CtrModule_Ctr1_UserLevelSet | 1546 | Para_CtrModule_Ctr1_UserLevelSet |  | 16766
[8 empty] | 16767 | Para_CtrModule_Ctr1_UserLevelTune | Para_CtrModule_Ctr1_UserLevelTune | 1547 | Para_CtrModule_Ctr1_UserLevelTune |  | 16767
[8 empty] | 16768 | Para_CtrModule_Ctr1_WMax | Para_CtrModule_Ctr1_WMax | 1548 | Para_CtrModule_Ctr1_WMax | x | 16768
[8 empty] | 16769 | Para_CtrModule_Ctr1_WMin | Para_CtrModule_Ctr1_WMin | 1549 | Para_CtrModule_Ctr1_WMin | x | 16769
[8 empty] | 16770 | Para_CtrModule_Ctr1_WRampNeg | Para_CtrModule_Ctr1_WRampNeg | 1550 | Para_CtrModule_Ctr1_WRampNeg | x/s | 16770
[8 empty] | 16771 | Para_CtrModule_Ctr1_WRampPos | Para_CtrModule_Ctr1_WRampPos | 1551 | Para_CtrModule_Ctr1_WRampPos | x/s | 16771
[8 empty] | 16772 | Para_CtrModule_Ctr1_WStart | Para_CtrModule_Ctr1_WStart | 1552 | Para_CtrModule_Ctr1_WStart | x | 16772
[8 empty] | 16773 | Para_CtrModule_Ctr1_YBlock | Para_CtrModule_Ctr1_YBlock | 1553 | Para_CtrModule_Ctr1_YBlock | % | 16773
[8 empty] | 16774 | Para_CtrModule_Ctr1_YHl | Para_CtrModule_Ctr1_YHl | 1554 | Para_CtrModule_Ctr1_YHl | % | 16774
[8 empty] | 16775 | Para_CtrModule_Ctr1_YMax | Para_CtrModule_Ctr1_YMax | 1555 | Para_CtrModule_Ctr1_YMax | % | 16775
[8 empty] | 16776 | Para_CtrModule_Ctr1_YMin | Para_CtrModule_Ctr1_YMin | 1556 | Para_CtrModule_Ctr1_YMin | % | 16776
[8 empty] | 16777 | Para_CtrModule_Ctr1_YRampNeg | Para_CtrModule_Ctr1_YRampNeg | 1557 | Para_CtrModule_Ctr1_YRampNeg | %/TA | 16777
[8 empty] | 16778 | Para_CtrModule_Ctr1_YRampPos | Para_CtrModule_Ctr1_YRampPos | 1558 | Para_CtrModule_Ctr1_YRampPos | %/TA | 16778
[8 empty] | 16779 | Para_CtrModule_Ctr1_YRampTune | Para_CtrModule_Ctr1_YRampTune | 1559 | Para_CtrModule_Ctr1_YRampTune | %/TA | 16779
[8 empty] | 16780 | Para_CtrModule_Ctr2_ActStep_NEx | Para_CtrModule_Ctr2_ActStep_NEx | 1560 | Para_CtrModule_Ctr2_ActStep_NEx |  | 16780
[8 empty] | 16781 | Para_CtrModule_Ctr2_CycleTime | Para_CtrModule_Ctr2_CycleTime | 1561 | Para_CtrModule_Ctr2_CycleTime | ms | 16781
[8 empty] | 16782 | Para_CtrModule_Ctr2_DComp | Para_CtrModule_Ctr2_DComp | 1562 | Para_CtrModule_Ctr2_DComp |  | 16782
[8 empty] | 16783 | Para_CtrModule_Ctr2_DCompTune | Para_CtrModule_Ctr2_DCompTune | 1563 | Para_CtrModule_Ctr2_DCompTune |  | 16783
[8 empty] | 16784 | Para_CtrModule_Ctr2_DCompWMax | Para_CtrModule_Ctr2_DCompWMax | 1564 | Para_CtrModule_Ctr2_DCompWMax |  | 16784
[8 empty] | 16785 | Para_CtrModule_Ctr2_DCompWMin | Para_CtrModule_Ctr2_DCompWMin | 1565 | Para_CtrModule_Ctr2_DCompWMin |  | 16785
[8 empty] | 16786 | Para_CtrModule_Ctr2_DeadBand | Para_CtrModule_Ctr2_DeadBand | 1566 | Para_CtrModule_Ctr2_DeadBand | x | 16786
[8 empty] | 16787 | Para_CtrModule_Ctr2_Format | Para_CtrModule_Ctr2_Format | 1567 | Para_CtrModule_Ctr2_Format |  | 16787
[8 empty] | 16788 | Para_CtrModule_Ctr2_IComp | Para_CtrModule_Ctr2_IComp | 1568 | Para_CtrModule_Ctr2_IComp |  | 16788
[8 empty] | 16789 | Para_CtrModule_Ctr2_ICompTune | Para_CtrModule_Ctr2_ICompTune | 1569 | Para_CtrModule_Ctr2_ICompTune |  | 16789
[8 empty] | 16790 | Para_CtrModule_Ctr2_ICompWMax | Para_CtrModule_Ctr2_ICompWMax | 1570 | Para_CtrModule_Ctr2_ICompWMax |  | 16790
[8 empty] | 16791 | Para_CtrModule_Ctr2_ICompWMin | Para_CtrModule_Ctr2_ICompWMin | 1571 | Para_CtrModule_Ctr2_ICompWMin |  | 16791
[8 empty] | 16792 | Para_CtrModule_Ctr2_InvertCtrTune | Para_CtrModule_Ctr2_InvertCtrTune | 1572 | Para_CtrModule_Ctr2_InvertCtrTune |  | 16792
[8 empty] | 16793 | Para_CtrModule_Ctr2_Name | Para_CtrModule_Ctr2_Name | 1573 | Para_CtrModule_Ctr2_Name |  | 16793
[8 empty] | 16794 | Para_CtrModule_Ctr2_NameF | Para_CtrModule_Ctr2_NameF | 1574 | Para_CtrModule_Ctr2_NameF |  | 16794
[8 empty] | 16795 | Para_CtrModule_Ctr2_OptWorkPoint | Para_CtrModule_Ctr2_OptWorkPoint | 1575 | Para_CtrModule_Ctr2_OptWorkPoint |  | 16795
[8 empty] | 16796 | Para_CtrModule_Ctr2_PComp | Para_CtrModule_Ctr2_PComp | 1576 | Para_CtrModule_Ctr2_PComp |  | 16796
[8 empty] | 16797 | Para_CtrModule_Ctr2_PCompTune | Para_CtrModule_Ctr2_PCompTune | 1577 | Para_CtrModule_Ctr2_PCompTune |  | 16797
[8 empty] | 16798 | Para_CtrModule_Ctr2_PCompWMax | Para_CtrModule_Ctr2_PCompWMax | 1578 | Para_CtrModule_Ctr2_PCompWMax |  | 16798
[8 empty] | 16799 | Para_CtrModule_Ctr2_PCompWMin | Para_CtrModule_Ctr2_PCompWMin | 1579 | Para_CtrModule_Ctr2_PCompWMin |  | 16799
[8 empty] | 16800 | Para_CtrModule_Ctr2_RangeBegin | Para_CtrModule_Ctr2_RangeBegin | 1580 | Para_CtrModule_Ctr2_RangeBegin | x | 16800
[8 empty] | 16801 | Para_CtrModule_Ctr2_RangeEnd | Para_CtrModule_Ctr2_RangeEnd | 1581 | Para_CtrModule_Ctr2_RangeEnd | x | 16801
[8 empty] | 16802 | Para_CtrModule_Ctr2_Unit | Para_CtrModule_Ctr2_Unit | 1582 | Para_CtrModule_Ctr2_Unit |  | 16802
[8 empty] | 16803 | Para_CtrModule_Ctr2_UserLevelIntExt | Para_CtrModule_Ctr2_UserLevelIntExt | 1583 | Para_CtrModule_Ctr2_UserLevelIntExt |  | 16803
[8 empty] | 16804 | Para_CtrModule_Ctr2_UserLevelManAut | Para_CtrModule_Ctr2_UserLevelManAut | 1584 | Para_CtrModule_Ctr2_UserLevelManAut |  | 16804
[8 empty] | 16805 | Para_CtrModule_Ctr2_UserLevelSet | Para_CtrModule_Ctr2_UserLevelSet | 1585 | Para_CtrModule_Ctr2_UserLevelSet |  | 16805
[8 empty] | 16806 | Para_CtrModule_Ctr2_UserLevelTune | Para_CtrModule_Ctr2_UserLevelTune | 1586 | Para_CtrModule_Ctr2_UserLevelTune |  | 16806
[8 empty] | 16807 | Para_CtrModule_Ctr2_WMax | Para_CtrModule_Ctr2_WMax | 1587 | Para_CtrModule_Ctr2_WMax | x | 16807
[8 empty] | 16808 | Para_CtrModule_Ctr2_WMin | Para_CtrModule_Ctr2_WMin | 1588 | Para_CtrModule_Ctr2_WMin | x | 16808
[8 empty] | 16809 | Para_CtrModule_Ctr2_WRampNeg | Para_CtrModule_Ctr2_WRampNeg | 1589 | Para_CtrModule_Ctr2_WRampNeg | x/s | 16809
[8 empty] | 16810 | Para_CtrModule_Ctr2_WRampPos | Para_CtrModule_Ctr2_WRampPos | 1590 | Para_CtrModule_Ctr2_WRampPos | x/s | 16810
[8 empty] | 16811 | Para_CtrModule_Ctr2_WStart | Para_CtrModule_Ctr2_WStart | 1591 | Para_CtrModule_Ctr2_WStart | x | 16811
[8 empty] | 16812 | Para_CtrModule_Ctr2_YBlock | Para_CtrModule_Ctr2_YBlock | 1592 | Para_CtrModule_Ctr2_YBlock | % | 16812
[8 empty] | 16813 | Para_CtrModule_Ctr2_YHl | Para_CtrModule_Ctr2_YHl | 1593 | Para_CtrModule_Ctr2_YHl | % | 16813
[8 empty] | 16814 | Para_CtrModule_Ctr2_YMax | Para_CtrModule_Ctr2_YMax | 1594 | Para_CtrModule_Ctr2_YMax | % | 16814
[8 empty] | 16815 | Para_CtrModule_Ctr2_YMin | Para_CtrModule_Ctr2_YMin | 1595 | Para_CtrModule_Ctr2_YMin | % | 16815
[8 empty] | 16816 | Para_CtrModule_Ctr2_YRampNeg | Para_CtrModule_Ctr2_YRampNeg | 1596 | Para_CtrModule_Ctr2_YRampNeg | %/TA | 16816
[8 empty] | 16817 | Para_CtrModule_Ctr2_YRampPos | Para_CtrModule_Ctr2_YRampPos | 1597 | Para_CtrModule_Ctr2_YRampPos | %/TA | 16817
[8 empty] | 16818 | Para_CtrModule_Ctr2_YRampTune | Para_CtrModule_Ctr2_YRampTune | 1598 | Para_CtrModule_Ctr2_YRampTune | %/TA | 16818
[8 empty] | 16819 | Para_CtrModule_Ctr3_ActStep_NEx | Para_CtrModule_Ctr3_ActStep_NEx | 1599 | Para_CtrModule_Ctr3_ActStep_NEx |  | 16819
[8 empty] | 16820 | Para_CtrModule_Ctr3_CycleTime | Para_CtrModule_Ctr3_CycleTime | 1600 | Para_CtrModule_Ctr3_CycleTime |  | 16820
[8 empty] | 16821 | Para_CtrModule_Ctr3_DComp | Para_CtrModule_Ctr3_DComp | 1601 | Para_CtrModule_Ctr3_DComp |  | 16821
[8 empty] | 16822 | Para_CtrModule_Ctr3_DCompTune | Para_CtrModule_Ctr3_DCompTune | 1602 | Para_CtrModule_Ctr3_DCompTune |  | 16822
[8 empty] | 16823 | Para_CtrModule_Ctr3_DCompWMax | Para_CtrModule_Ctr3_DCompWMax | 1603 | Para_CtrModule_Ctr3_DCompWMax |  | 16823
[8 empty] | 16824 | Para_CtrModule_Ctr3_DCompWMin | Para_CtrModule_Ctr3_DCompWMin | 1604 | Para_CtrModule_Ctr3_DCompWMin |  | 16824
[8 empty] | 16825 | Para_CtrModule_Ctr3_DeadBand | Para_CtrModule_Ctr3_DeadBand | 1605 | Para_CtrModule_Ctr3_DeadBand |  | 16825
[8 empty] | 16826 | Para_CtrModule_Ctr3_Format | Para_CtrModule_Ctr3_Format | 1606 | Para_CtrModule_Ctr3_Format |  | 16826
[8 empty] | 16827 | Para_CtrModule_Ctr3_IComp | Para_CtrModule_Ctr3_IComp | 1607 | Para_CtrModule_Ctr3_IComp |  | 16827
[8 empty] | 16828 | Para_CtrModule_Ctr3_ICompTune | Para_CtrModule_Ctr3_ICompTune | 1608 | Para_CtrModule_Ctr3_ICompTune |  | 16828
[8 empty] | 16829 | Para_CtrModule_Ctr3_ICompWMax | Para_CtrModule_Ctr3_ICompWMax | 1609 | Para_CtrModule_Ctr3_ICompWMax |  | 16829
[8 empty] | 16830 | Para_CtrModule_Ctr3_ICompWMin | Para_CtrModule_Ctr3_ICompWMin | 1610 | Para_CtrModule_Ctr3_ICompWMin |  | 16830
[8 empty] | 16831 | Para_CtrModule_Ctr3_InvertCtrTune | Para_CtrModule_Ctr3_InvertCtrTune | 1611 | Para_CtrModule_Ctr3_InvertCtrTune |  | 16831
[8 empty] | 16832 | Para_CtrModule_Ctr3_Name | Para_CtrModule_Ctr3_Name | 1612 | Para_CtrModule_Ctr3_Name |  | 16832
[8 empty] | 16833 | Para_CtrModule_Ctr3_NameF | Para_CtrModule_Ctr3_NameF | 1613 | Para_CtrModule_Ctr3_NameF |  | 16833
[8 empty] | 16834 | Para_CtrModule_Ctr3_OptWorkPoint | Para_CtrModule_Ctr3_OptWorkPoint | 1614 | Para_CtrModule_Ctr3_OptWorkPoint |  | 16834
[8 empty] | 16835 | Para_CtrModule_Ctr3_PComp | Para_CtrModule_Ctr3_PComp | 1615 | Para_CtrModule_Ctr3_PComp |  | 16835
[8 empty] | 16836 | Para_CtrModule_Ctr3_PCompTune | Para_CtrModule_Ctr3_PCompTune | 1616 | Para_CtrModule_Ctr3_PCompTune |  | 16836
[8 empty] | 16837 | Para_CtrModule_Ctr3_PCompWMax | Para_CtrModule_Ctr3_PCompWMax | 1617 | Para_CtrModule_Ctr3_PCompWMax |  | 16837
[8 empty] | 16838 | Para_CtrModule_Ctr3_PCompWMin | Para_CtrModule_Ctr3_PCompWMin | 1618 | Para_CtrModule_Ctr3_PCompWMin |  | 16838
[8 empty] | 16839 | Para_CtrModule_Ctr3_RangeBegin | Para_CtrModule_Ctr3_RangeBegin | 1619 | Para_CtrModule_Ctr3_RangeBegin |  | 16839
[8 empty] | 16840 | Para_CtrModule_Ctr3_RangeEnd | Para_CtrModule_Ctr3_RangeEnd | 1620 | Para_CtrModule_Ctr3_RangeEnd |  | 16840
[8 empty] | 16841 | Para_CtrModule_Ctr3_Unit | Para_CtrModule_Ctr3_Unit | 1621 | Para_CtrModule_Ctr3_Unit |  | 16841
[8 empty] | 16842 | Para_CtrModule_Ctr3_UserLevelIntExt | Para_CtrModule_Ctr3_UserLevelIntExt | 1622 | Para_CtrModule_Ctr3_UserLevelIntExt |  | 16842
[8 empty] | 16843 | Para_CtrModule_Ctr3_UserLevelManAut | Para_CtrModule_Ctr3_UserLevelManAut | 1623 | Para_CtrModule_Ctr3_UserLevelManAut |  | 16843
[8 empty] | 16844 | Para_CtrModule_Ctr3_UserLevelSet | Para_CtrModule_Ctr3_UserLevelSet | 1624 | Para_CtrModule_Ctr3_UserLevelSet |  | 16844
[8 empty] | 16845 | Para_CtrModule_Ctr3_UserLevelTune | Para_CtrModule_Ctr3_UserLevelTune | 1625 | Para_CtrModule_Ctr3_UserLevelTune |  | 16845
[8 empty] | 16846 | Para_CtrModule_Ctr3_WMax | Para_CtrModule_Ctr3_WMax | 1626 | Para_CtrModule_Ctr3_WMax |  | 16846
[8 empty] | 16847 | Para_CtrModule_Ctr3_WMin | Para_CtrModule_Ctr3_WMin | 1627 | Para_CtrModule_Ctr3_WMin |  | 16847
[8 empty] | 16848 | Para_CtrModule_Ctr3_WRampNeg | Para_CtrModule_Ctr3_WRampNeg | 1628 | Para_CtrModule_Ctr3_WRampNeg |  | 16848
[8 empty] | 16849 | Para_CtrModule_Ctr3_WRampPos | Para_CtrModule_Ctr3_WRampPos | 1629 | Para_CtrModule_Ctr3_WRampPos |  | 16849
[8 empty] | 16850 | Para_CtrModule_Ctr3_WStart | Para_CtrModule_Ctr3_WStart | 1630 | Para_CtrModule_Ctr3_WStart |  | 16850
[8 empty] | 16851 | Para_CtrModule_Ctr3_YBlock | Para_CtrModule_Ctr3_YBlock | 1631 | Para_CtrModule_Ctr3_YBlock |  | 16851
[8 empty] | 16852 | Para_CtrModule_Ctr3_YHl | Para_CtrModule_Ctr3_YHl | 1632 | Para_CtrModule_Ctr3_YHl | % | 16852
[8 empty] | 16853 | Para_CtrModule_Ctr3_YMax | Para_CtrModule_Ctr3_YMax | 1633 | Para_CtrModule_Ctr3_YMax |  | 16853
[8 empty] | 16854 | Para_CtrModule_Ctr3_YMin | Para_CtrModule_Ctr3_YMin | 1634 | Para_CtrModule_Ctr3_YMin |  | 16854
[8 empty] | 16855 | Para_CtrModule_Ctr3_YRampNeg | Para_CtrModule_Ctr3_YRampNeg | 1635 | Para_CtrModule_Ctr3_YRampNeg |  | 16855
[8 empty] | 16856 | Para_CtrModule_Ctr3_YRampPos | Para_CtrModule_Ctr3_YRampPos | 1636 | Para_CtrModule_Ctr3_YRampPos |  | 16856
[8 empty] | 16857 | Para_CtrModule_Ctr3_YRampTune | Para_CtrModule_Ctr3_YRampTune | 1637 | Para_CtrModule_Ctr3_YRampTune | %/TA | 16857
[8 empty] | 16858 | Para_CtrModule_Ctr4_ActStep_NEx | Para_CtrModule_Ctr4_ActStep_NEx | 1638 | Para_CtrModule_Ctr4_ActStep_NEx |  | 16858
[8 empty] | 16859 | Para_CtrModule_Ctr4_CycleTime | Para_CtrModule_Ctr4_CycleTime | 1639 | Para_CtrModule_Ctr4_CycleTime |  | 16859
[8 empty] | 16860 | Para_CtrModule_Ctr4_DComp | Para_CtrModule_Ctr4_DComp | 1640 | Para_CtrModule_Ctr4_DComp |  | 16860
[8 empty] | 16861 | Para_CtrModule_Ctr4_DCompTune | Para_CtrModule_Ctr4_DCompTune | 1641 | Para_CtrModule_Ctr4_DCompTune |  | 16861
[8 empty] | 16862 | Para_CtrModule_Ctr4_DCompWMax | Para_CtrModule_Ctr4_DCompWMax | 1642 | Para_CtrModule_Ctr4_DCompWMax |  | 16862
[8 empty] | 16863 | Para_CtrModule_Ctr4_DCompWMin | Para_CtrModule_Ctr4_DCompWMin | 1643 | Para_CtrModule_Ctr4_DCompWMin |  | 16863
[8 empty] | 16864 | Para_CtrModule_Ctr4_DeadBand | Para_CtrModule_Ctr4_DeadBand | 1644 | Para_CtrModule_Ctr4_DeadBand |  | 16864
[8 empty] | 16865 | Para_CtrModule_Ctr4_Format | Para_CtrModule_Ctr4_Format | 1645 | Para_CtrModule_Ctr4_Format |  | 16865
[8 empty] | 16866 | Para_CtrModule_Ctr4_IComp | Para_CtrModule_Ctr4_IComp | 1646 | Para_CtrModule_Ctr4_IComp |  | 16866
[8 empty] | 16867 | Para_CtrModule_Ctr4_ICompTune | Para_CtrModule_Ctr4_ICompTune | 1647 | Para_CtrModule_Ctr4_ICompTune |  | 16867
[8 empty] | 16868 | Para_CtrModule_Ctr4_ICompWMax | Para_CtrModule_Ctr4_ICompWMax | 1648 | Para_CtrModule_Ctr4_ICompWMax |  | 16868
[8 empty] | 16869 | Para_CtrModule_Ctr4_ICompWMin | Para_CtrModule_Ctr4_ICompWMin | 1649 | Para_CtrModule_Ctr4_ICompWMin |  | 16869
[8 empty] | 16870 | Para_CtrModule_Ctr4_InvertCtrTune | Para_CtrModule_Ctr4_InvertCtrTune | 1650 | Para_CtrModule_Ctr4_InvertCtrTune |  | 16870
[8 empty] | 16871 | Para_CtrModule_Ctr4_Name | Para_CtrModule_Ctr4_Name | 1651 | Para_CtrModule_Ctr4_Name |  | 16871
[8 empty] | 16872 | Para_CtrModule_Ctr4_NameF | Para_CtrModule_Ctr4_NameF | 1652 | Para_CtrModule_Ctr4_NameF |  | 16872
[8 empty] | 16873 | Para_CtrModule_Ctr4_OptWorkPoint | Para_CtrModule_Ctr4_OptWorkPoint | 1653 | Para_CtrModule_Ctr4_OptWorkPoint |  | 16873
[8 empty] | 16874 | Para_CtrModule_Ctr4_PComp | Para_CtrModule_Ctr4_PComp | 1654 | Para_CtrModule_Ctr4_PComp |  | 16874
[8 empty] | 16875 | Para_CtrModule_Ctr4_PCompTune | Para_CtrModule_Ctr4_PCompTune | 1655 | Para_CtrModule_Ctr4_PCompTune |  | 16875
[8 empty] | 16876 | Para_CtrModule_Ctr4_PCompWMax | Para_CtrModule_Ctr4_PCompWMax | 1656 | Para_CtrModule_Ctr4_PCompWMax |  | 16876
[8 empty] | 16877 | Para_CtrModule_Ctr4_PCompWMin | Para_CtrModule_Ctr4_PCompWMin | 1657 | Para_CtrModule_Ctr4_PCompWMin |  | 16877
[8 empty] | 16878 | Para_CtrModule_Ctr4_RangeBegin | Para_CtrModule_Ctr4_RangeBegin | 1658 | Para_CtrModule_Ctr4_RangeBegin |  | 16878
[8 empty] | 16879 | Para_CtrModule_Ctr4_RangeEnd | Para_CtrModule_Ctr4_RangeEnd | 1659 | Para_CtrModule_Ctr4_RangeEnd |  | 16879
[8 empty] | 16880 | Para_CtrModule_Ctr4_Unit | Para_CtrModule_Ctr4_Unit | 1660 | Para_CtrModule_Ctr4_Unit |  | 16880
[8 empty] | 16881 | Para_CtrModule_Ctr4_UserLevelIntExt | Para_CtrModule_Ctr4_UserLevelIntExt | 1661 | Para_CtrModule_Ctr4_UserLevelIntExt |  | 16881
[8 empty] | 16882 | Para_CtrModule_Ctr4_UserLevelManAut | Para_CtrModule_Ctr4_UserLevelManAut | 1662 | Para_CtrModule_Ctr4_UserLevelManAut |  | 16882
[8 empty] | 16883 | Para_CtrModule_Ctr4_UserLevelSet | Para_CtrModule_Ctr4_UserLevelSet | 1663 | Para_CtrModule_Ctr4_UserLevelSet |  | 16883
[8 empty] | 16884 | Para_CtrModule_Ctr4_UserLevelTune | Para_CtrModule_Ctr4_UserLevelTune | 1664 | Para_CtrModule_Ctr4_UserLevelTune |  | 16884
[8 empty] | 16885 | Para_CtrModule_Ctr4_WMax | Para_CtrModule_Ctr4_WMax | 1665 | Para_CtrModule_Ctr4_WMax |  | 16885
[8 empty] | 16886 | Para_CtrModule_Ctr4_WMin | Para_CtrModule_Ctr4_WMin | 1666 | Para_CtrModule_Ctr4_WMin |  | 16886
[8 empty] | 16887 | Para_CtrModule_Ctr4_WRampNeg | Para_CtrModule_Ctr4_WRampNeg | 1667 | Para_CtrModule_Ctr4_WRampNeg |  | 16887
[8 empty] | 16888 | Para_CtrModule_Ctr4_WRampPos | Para_CtrModule_Ctr4_WRampPos | 1668 | Para_CtrModule_Ctr4_WRampPos |  | 16888
[8 empty] | 16889 | Para_CtrModule_Ctr4_WStart | Para_CtrModule_Ctr4_WStart | 1669 | Para_CtrModule_Ctr4_WStart |  | 16889
[8 empty] | 16890 | Para_CtrModule_Ctr4_YBlock | Para_CtrModule_Ctr4_YBlock | 1670 | Para_CtrModule_Ctr4_YBlock |  | 16890
[8 empty] | 16891 | Para_CtrModule_Ctr4_YHl | Para_CtrModule_Ctr4_YHl | 1671 | Para_CtrModule_Ctr4_YHl | % | 16891
[8 empty] | 16892 | Para_CtrModule_Ctr4_YMax | Para_CtrModule_Ctr4_YMax | 1672 | Para_CtrModule_Ctr4_YMax |  | 16892
[8 empty] | 16893 | Para_CtrModule_Ctr4_YMin | Para_CtrModule_Ctr4_YMin | 1673 | Para_CtrModule_Ctr4_YMin |  | 16893
[8 empty] | 16894 | Para_CtrModule_Ctr4_YRampNeg | Para_CtrModule_Ctr4_YRampNeg | 1674 | Para_CtrModule_Ctr4_YRampNeg |  | 16894
[8 empty] | 16895 | Para_CtrModule_Ctr4_YRampPos | Para_CtrModule_Ctr4_YRampPos | 1675 | Para_CtrModule_Ctr4_YRampPos |  | 16895
[8 empty] | 16896 | Para_CtrModule_Ctr4_YRampTune | Para_CtrModule_Ctr4_YRampTune | 1676 | Para_CtrModule_Ctr4_YRampTune | %/TA | 16896
[8 empty] | 16897 | Para_CtrModule_Ctr5_CycleTime | Para_CtrModule_Ctr5_CycleTime | 1677 | Para_CtrModule_Ctr5_CycleTime |  | 16897
[8 empty] | 16898 | Para_CtrModule_Ctr5_DComp | Para_CtrModule_Ctr5_DComp | 1678 | Para_CtrModule_Ctr5_DComp |  | 16898
[8 empty] | 16899 | Para_CtrModule_Ctr5_DCompTune | Para_CtrModule_Ctr5_DCompTune | 1679 | Para_CtrModule_Ctr5_DCompTune |  | 16899
[8 empty] | 16900 | Para_CtrModule_Ctr5_DCompWMax | Para_CtrModule_Ctr5_DCompWMax | 1680 | Para_CtrModule_Ctr5_DCompWMax |  | 16900
[8 empty] | 16901 | Para_CtrModule_Ctr5_DCompWMin | Para_CtrModule_Ctr5_DCompWMin | 1681 | Para_CtrModule_Ctr5_DCompWMin |  | 16901
[8 empty] | 16902 | Para_CtrModule_Ctr5_DeadBand | Para_CtrModule_Ctr5_DeadBand | 1682 | Para_CtrModule_Ctr5_DeadBand |  | 16902
[8 empty] | 16903 | Para_CtrModule_Ctr5_Format | Para_CtrModule_Ctr5_Format | 1683 | Para_CtrModule_Ctr5_Format |  | 16903
[8 empty] | 16904 | Para_CtrModule_Ctr5_IComp | Para_CtrModule_Ctr5_IComp | 1684 | Para_CtrModule_Ctr5_IComp |  | 16904
[8 empty] | 16905 | Para_CtrModule_Ctr5_ICompTune | Para_CtrModule_Ctr5_ICompTune | 1685 | Para_CtrModule_Ctr5_ICompTune |  | 16905
[8 empty] | 16906 | Para_CtrModule_Ctr5_ICompWMax | Para_CtrModule_Ctr5_ICompWMax | 1686 | Para_CtrModule_Ctr5_ICompWMax |  | 16906
[8 empty] | 16907 | Para_CtrModule_Ctr5_ICompWMin | Para_CtrModule_Ctr5_ICompWMin | 1687 | Para_CtrModule_Ctr5_ICompWMin |  | 16907
[8 empty] | 16908 | Para_CtrModule_Ctr5_InvertCtrTune | Para_CtrModule_Ctr5_InvertCtrTune | 1688 | Para_CtrModule_Ctr5_InvertCtrTune |  | 16908
[8 empty] | 16909 | Para_CtrModule_Ctr5_Name | Para_CtrModule_Ctr5_Name | 1689 | Para_CtrModule_Ctr5_Name |  | 16909
[8 empty] | 16910 | Para_CtrModule_Ctr5_NameF | Para_CtrModule_Ctr5_NameF | 1690 | Para_CtrModule_Ctr5_NameF |  | 16910
[8 empty] | 16911 | Para_CtrModule_Ctr5_OptWorkPoint | Para_CtrModule_Ctr5_OptWorkPoint | 1691 | Para_CtrModule_Ctr5_OptWorkPoint |  | 16911
[8 empty] | 16912 | Para_CtrModule_Ctr5_PComp | Para_CtrModule_Ctr5_PComp | 1692 | Para_CtrModule_Ctr5_PComp |  | 16912
[8 empty] | 16913 | Para_CtrModule_Ctr5_PCompTune | Para_CtrModule_Ctr5_PCompTune | 1693 | Para_CtrModule_Ctr5_PCompTune |  | 16913
[8 empty] | 16914 | Para_CtrModule_Ctr5_PCompWMax | Para_CtrModule_Ctr5_PCompWMax | 1694 | Para_CtrModule_Ctr5_PCompWMax |  | 16914
[8 empty] | 16915 | Para_CtrModule_Ctr5_PCompWMin | Para_CtrModule_Ctr5_PCompWMin | 1695 | Para_CtrModule_Ctr5_PCompWMin |  | 16915
[8 empty] | 16916 | Para_CtrModule_Ctr5_RangeBegin | Para_CtrModule_Ctr5_RangeBegin | 1696 | Para_CtrModule_Ctr5_RangeBegin | x | 16916
[8 empty] | 16917 | Para_CtrModule_Ctr5_RangeEnd | Para_CtrModule_Ctr5_RangeEnd | 1697 | Para_CtrModule_Ctr5_RangeEnd | x | 16917
[8 empty] | 16918 | Para_CtrModule_Ctr5_Unit | Para_CtrModule_Ctr5_Unit | 1698 | Para_CtrModule_Ctr5_Unit |  | 16918
[8 empty] | 16919 | Para_CtrModule_Ctr5_UserLevelIntExt | Para_CtrModule_Ctr5_UserLevelIntExt | 1699 | Para_CtrModule_Ctr5_UserLevelIntExt |  | 16919
[8 empty] | 16920 | Para_CtrModule_Ctr5_UserLevelManAut | Para_CtrModule_Ctr5_UserLevelManAut | 1700 | Para_CtrModule_Ctr5_UserLevelManAut |  | 16920
[8 empty] | 16921 | Para_CtrModule_Ctr5_UserLevelSet | Para_CtrModule_Ctr5_UserLevelSet | 1701 | Para_CtrModule_Ctr5_UserLevelSet |  | 16921
[8 empty] | 16922 | Para_CtrModule_Ctr5_UserLevelTune | Para_CtrModule_Ctr5_UserLevelTune | 1702 | Para_CtrModule_Ctr5_UserLevelTune |  | 16922
[8 empty] | 16923 | Para_CtrModule_Ctr5_WMax | Para_CtrModule_Ctr5_WMax | 1703 | Para_CtrModule_Ctr5_WMax |  | 16923
[8 empty] | 16924 | Para_CtrModule_Ctr5_WMin | Para_CtrModule_Ctr5_WMin | 1704 | Para_CtrModule_Ctr5_WMin |  | 16924
[8 empty] | 16925 | Para_CtrModule_Ctr5_WRampNeg | Para_CtrModule_Ctr5_WRampNeg | 1705 | Para_CtrModule_Ctr5_WRampNeg |  | 16925
[8 empty] | 16926 | Para_CtrModule_Ctr5_WRampPos | Para_CtrModule_Ctr5_WRampPos | 1706 | Para_CtrModule_Ctr5_WRampPos |  | 16926
[8 empty] | 16927 | Para_CtrModule_Ctr5_WStart | Para_CtrModule_Ctr5_WStart | 1707 | Para_CtrModule_Ctr5_WStart |  | 16927
[8 empty] | 16928 | Para_CtrModule_Ctr5_YBlock | Para_CtrModule_Ctr5_YBlock | 1708 | Para_CtrModule_Ctr5_YBlock |  | 16928
[8 empty] | 16929 | Para_CtrModule_Ctr5_YHl | Para_CtrModule_Ctr5_YHl | 1709 | Para_CtrModule_Ctr5_YHl | % | 16929
[8 empty] | 16930 | Para_CtrModule_Ctr5_YMax | Para_CtrModule_Ctr5_YMax | 1710 | Para_CtrModule_Ctr5_YMax |  | 16930
[8 empty] | 16931 | Para_CtrModule_Ctr5_YMin | Para_CtrModule_Ctr5_YMin | 1711 | Para_CtrModule_Ctr5_YMin |  | 16931
[8 empty] | 16932 | Para_CtrModule_Ctr5_YRampNeg | Para_CtrModule_Ctr5_YRampNeg | 1712 | Para_CtrModule_Ctr5_YRampNeg |  | 16932
[8 empty] | 16933 | Para_CtrModule_Ctr5_YRampPos | Para_CtrModule_Ctr5_YRampPos | 1713 | Para_CtrModule_Ctr5_YRampPos |  | 16933
[8 empty] | 16934 | Para_CtrModule_Ctr5_YRampTune | Para_CtrModule_Ctr5_YRampTune | 1714 | Para_CtrModule_Ctr5_YRampTune | %/TA | 16934
[8 empty] | 16935 | Para_CtrModule_Ctr6_CycleTime | Para_CtrModule_Ctr6_CycleTime | 1715 | Para_CtrModule_Ctr6_CycleTime | ms | 16935
[8 empty] | 16936 | Para_CtrModule_Ctr6_DComp | Para_CtrModule_Ctr6_DComp | 1716 | Para_CtrModule_Ctr6_DComp |  | 16936
[8 empty] | 16937 | Para_CtrModule_Ctr6_DCompTune | Para_CtrModule_Ctr6_DCompTune | 1717 | Para_CtrModule_Ctr6_DCompTune |  | 16937
[8 empty] | 16938 | Para_CtrModule_Ctr6_DCompWMax | Para_CtrModule_Ctr6_DCompWMax | 1718 | Para_CtrModule_Ctr6_DCompWMax |  | 16938
[8 empty] | 16939 | Para_CtrModule_Ctr6_DCompWMin | Para_CtrModule_Ctr6_DCompWMin | 1719 | Para_CtrModule_Ctr6_DCompWMin |  | 16939
[8 empty] | 16940 | Para_CtrModule_Ctr6_DeadBand | Para_CtrModule_Ctr6_DeadBand | 1720 | Para_CtrModule_Ctr6_DeadBand | x | 16940
[8 empty] | 16941 | Para_CtrModule_Ctr6_Format | Para_CtrModule_Ctr6_Format | 1721 | Para_CtrModule_Ctr6_Format |  | 16941
[8 empty] | 16942 | Para_CtrModule_Ctr6_IComp | Para_CtrModule_Ctr6_IComp | 1722 | Para_CtrModule_Ctr6_IComp |  | 16942
[8 empty] | 16943 | Para_CtrModule_Ctr6_ICompTune | Para_CtrModule_Ctr6_ICompTune | 1723 | Para_CtrModule_Ctr6_ICompTune |  | 16943
[8 empty] | 16944 | Para_CtrModule_Ctr6_ICompWMax | Para_CtrModule_Ctr6_ICompWMax | 1724 | Para_CtrModule_Ctr6_ICompWMax |  | 16944
[8 empty] | 16945 | Para_CtrModule_Ctr6_ICompWMin | Para_CtrModule_Ctr6_ICompWMin | 1725 | Para_CtrModule_Ctr6_ICompWMin |  | 16945
[8 empty] | 16946 | Para_CtrModule_Ctr6_InvertCtrTune | Para_CtrModule_Ctr6_InvertCtrTune | 1726 | Para_CtrModule_Ctr6_InvertCtrTune |  | 16946
[8 empty] | 16947 | Para_CtrModule_Ctr6_Name | Para_CtrModule_Ctr6_Name | 1727 | Para_CtrModule_Ctr6_Name |  | 16947
[8 empty] | 16948 | Para_CtrModule_Ctr6_NameF | Para_CtrModule_Ctr6_NameF | 1728 | Para_CtrModule_Ctr6_NameF |  | 16948
[8 empty] | 16949 | Para_CtrModule_Ctr6_OptWorkPoint | Para_CtrModule_Ctr6_OptWorkPoint | 1729 | Para_CtrModule_Ctr6_OptWorkPoint |  | 16949
[8 empty] | 16950 | Para_CtrModule_Ctr6_PComp | Para_CtrModule_Ctr6_PComp | 1730 | Para_CtrModule_Ctr6_PComp |  | 16950
[8 empty] | 16951 | Para_CtrModule_Ctr6_PCompTune | Para_CtrModule_Ctr6_PCompTune | 1731 | Para_CtrModule_Ctr6_PCompTune |  | 16951
[8 empty] | 16952 | Para_CtrModule_Ctr6_PCompWMax | Para_CtrModule_Ctr6_PCompWMax | 1732 | Para_CtrModule_Ctr6_PCompWMax |  | 16952
[8 empty] | 16953 | Para_CtrModule_Ctr6_PCompWMin | Para_CtrModule_Ctr6_PCompWMin | 1733 | Para_CtrModule_Ctr6_PCompWMin |  | 16953
[8 empty] | 16954 | Para_CtrModule_Ctr6_RangeBegin | Para_CtrModule_Ctr6_RangeBegin | 1734 | Para_CtrModule_Ctr6_RangeBegin | x | 16954
[8 empty] | 16955 | Para_CtrModule_Ctr6_RangeEnd | Para_CtrModule_Ctr6_RangeEnd | 1735 | Para_CtrModule_Ctr6_RangeEnd | x | 16955
[8 empty] | 16956 | Para_CtrModule_Ctr6_Unit | Para_CtrModule_Ctr6_Unit | 1736 | Para_CtrModule_Ctr6_Unit |  | 16956
[8 empty] | 16957 | Para_CtrModule_Ctr6_UserLevelIntExt | Para_CtrModule_Ctr6_UserLevelIntExt | 1737 | Para_CtrModule_Ctr6_UserLevelIntExt |  | 16957
[8 empty] | 16958 | Para_CtrModule_Ctr6_UserLevelManAut | Para_CtrModule_Ctr6_UserLevelManAut | 1738 | Para_CtrModule_Ctr6_UserLevelManAut |  | 16958
[8 empty] | 16959 | Para_CtrModule_Ctr6_UserLevelSet | Para_CtrModule_Ctr6_UserLevelSet | 1739 | Para_CtrModule_Ctr6_UserLevelSet |  | 16959
[8 empty] | 16960 | Para_CtrModule_Ctr6_UserLevelTune | Para_CtrModule_Ctr6_UserLevelTune | 1740 | Para_CtrModule_Ctr6_UserLevelTune |  | 16960
[8 empty] | 16961 | Para_CtrModule_Ctr6_WMax | Para_CtrModule_Ctr6_WMax | 1741 | Para_CtrModule_Ctr6_WMax | x | 16961
[8 empty] | 16962 | Para_CtrModule_Ctr6_WMin | Para_CtrModule_Ctr6_WMin | 1742 | Para_CtrModule_Ctr6_WMin | x | 16962
[8 empty] | 16963 | Para_CtrModule_Ctr6_WRampNeg | Para_CtrModule_Ctr6_WRampNeg | 1743 | Para_CtrModule_Ctr6_WRampNeg | x/s | 16963
[8 empty] | 16964 | Para_CtrModule_Ctr6_WRampPos | Para_CtrModule_Ctr6_WRampPos | 1744 | Para_CtrModule_Ctr6_WRampPos | x/s | 16964
[8 empty] | 16965 | Para_CtrModule_Ctr6_WStart | Para_CtrModule_Ctr6_WStart | 1745 | Para_CtrModule_Ctr6_WStart | x | 16965
[8 empty] | 16966 | Para_CtrModule_Ctr6_YBlock | Para_CtrModule_Ctr6_YBlock | 1746 | Para_CtrModule_Ctr6_YBlock | % | 16966
[8 empty] | 16967 | Para_CtrModule_Ctr6_YHl | Para_CtrModule_Ctr6_YHl | 1747 | Para_CtrModule_Ctr6_YHl | % | 16967
[8 empty] | 16968 | Para_CtrModule_Ctr6_YMax | Para_CtrModule_Ctr6_YMax | 1748 | Para_CtrModule_Ctr6_YMax | % | 16968
[8 empty] | 16969 | Para_CtrModule_Ctr6_YMin | Para_CtrModule_Ctr6_YMin | 1749 | Para_CtrModule_Ctr6_YMin | % | 16969
[8 empty] | 16970 | Para_CtrModule_Ctr6_YRampNeg | Para_CtrModule_Ctr6_YRampNeg | 1750 | Para_CtrModule_Ctr6_YRampNeg | %/TA | 16970
[8 empty] | 16971 | Para_CtrModule_Ctr6_YRampPos | Para_CtrModule_Ctr6_YRampPos | 1751 | Para_CtrModule_Ctr6_YRampPos | %/TA | 16971
[8 empty] | 16972 | Para_CtrModule_Ctr6_YRampTune | Para_CtrModule_Ctr6_YRampTune | 1752 | Para_CtrModule_Ctr6_YRampTune | %/TA | 16972
[8 empty] | 16973 | Para_CtrModule_Ctr7_CycleTime | Para_CtrModule_Ctr7_CycleTime | 1753 | Para_CtrModule_Ctr7_CycleTime | ms | 16973
[8 empty] | 16974 | Para_CtrModule_Ctr7_DComp | Para_CtrModule_Ctr7_DComp | 1754 | Para_CtrModule_Ctr7_DComp |  | 16974
[8 empty] | 16975 | Para_CtrModule_Ctr7_DCompTune | Para_CtrModule_Ctr7_DCompTune | 1755 | Para_CtrModule_Ctr7_DCompTune |  | 16975
[8 empty] | 16976 | Para_CtrModule_Ctr7_DCompWMax | Para_CtrModule_Ctr7_DCompWMax | 1756 | Para_CtrModule_Ctr7_DCompWMax |  | 16976
[8 empty] | 16977 | Para_CtrModule_Ctr7_DCompWMin | Para_CtrModule_Ctr7_DCompWMin | 1757 | Para_CtrModule_Ctr7_DCompWMin |  | 16977
[8 empty] | 16978 | Para_CtrModule_Ctr7_DeadBand | Para_CtrModule_Ctr7_DeadBand | 1758 | Para_CtrModule_Ctr7_DeadBand | x | 16978
[8 empty] | 16979 | Para_CtrModule_Ctr7_Format | Para_CtrModule_Ctr7_Format | 1759 | Para_CtrModule_Ctr7_Format |  | 16979
[8 empty] | 16980 | Para_CtrModule_Ctr7_IComp | Para_CtrModule_Ctr7_IComp | 1760 | Para_CtrModule_Ctr7_IComp |  | 16980
[8 empty] | 16981 | Para_CtrModule_Ctr7_ICompTune | Para_CtrModule_Ctr7_ICompTune | 1761 | Para_CtrModule_Ctr7_ICompTune |  | 16981
[8 empty] | 16982 | Para_CtrModule_Ctr7_ICompWMax | Para_CtrModule_Ctr7_ICompWMax | 1762 | Para_CtrModule_Ctr7_ICompWMax |  | 16982
[8 empty] | 16983 | Para_CtrModule_Ctr7_ICompWMin | Para_CtrModule_Ctr7_ICompWMin | 1763 | Para_CtrModule_Ctr7_ICompWMin |  | 16983
[8 empty] | 16984 | Para_CtrModule_Ctr7_InvertCtrTune | Para_CtrModule_Ctr7_InvertCtrTune | 1764 | Para_CtrModule_Ctr7_InvertCtrTune |  | 16984
[8 empty] | 16985 | Para_CtrModule_Ctr7_Name | Para_CtrModule_Ctr7_Name | 1765 | Para_CtrModule_Ctr7_Name |  | 16985
[8 empty] | 16986 | Para_CtrModule_Ctr7_NameF | Para_CtrModule_Ctr7_NameF | 1766 | Para_CtrModule_Ctr7_NameF |  | 16986
[8 empty] | 16987 | Para_CtrModule_Ctr7_OptWorkPoint | Para_CtrModule_Ctr7_OptWorkPoint | 1767 | Para_CtrModule_Ctr7_OptWorkPoint |  | 16987
[8 empty] | 16988 | Para_CtrModule_Ctr7_PComp | Para_CtrModule_Ctr7_PComp | 1768 | Para_CtrModule_Ctr7_PComp |  | 16988
[8 empty] | 16989 | Para_CtrModule_Ctr7_PCompTune | Para_CtrModule_Ctr7_PCompTune | 1769 | Para_CtrModule_Ctr7_PCompTune |  | 16989
[8 empty] | 16990 | Para_CtrModule_Ctr7_PCompWMax | Para_CtrModule_Ctr7_PCompWMax | 1770 | Para_CtrModule_Ctr7_PCompWMax |  | 16990
[8 empty] | 16991 | Para_CtrModule_Ctr7_PCompWMin | Para_CtrModule_Ctr7_PCompWMin | 1771 | Para_CtrModule_Ctr7_PCompWMin |  | 16991
[8 empty] | 16992 | Para_CtrModule_Ctr7_RangeBegin | Para_CtrModule_Ctr7_RangeBegin | 1772 | Para_CtrModule_Ctr7_RangeBegin | x | 16992
[8 empty] | 16993 | Para_CtrModule_Ctr7_RangeEnd | Para_CtrModule_Ctr7_RangeEnd | 1773 | Para_CtrModule_Ctr7_RangeEnd | x | 16993
[8 empty] | 16994 | Para_CtrModule_Ctr7_Unit | Para_CtrModule_Ctr7_Unit | 1774 | Para_CtrModule_Ctr7_Unit |  | 16994
[8 empty] | 16995 | Para_CtrModule_Ctr7_UserLevelIntExt | Para_CtrModule_Ctr7_UserLevelIntExt | 1775 | Para_CtrModule_Ctr7_UserLevelIntExt |  | 16995
[8 empty] | 16996 | Para_CtrModule_Ctr7_UserLevelManAut | Para_CtrModule_Ctr7_UserLevelManAut | 1776 | Para_CtrModule_Ctr7_UserLevelManAut |  | 16996
[8 empty] | 16997 | Para_CtrModule_Ctr7_UserLevelSet | Para_CtrModule_Ctr7_UserLevelSet | 1777 | Para_CtrModule_Ctr7_UserLevelSet |  | 16997
[8 empty] | 16998 | Para_CtrModule_Ctr7_UserLevelTune | Para_CtrModule_Ctr7_UserLevelTune | 1778 | Para_CtrModule_Ctr7_UserLevelTune |  | 16998
[8 empty] | 16999 | Para_CtrModule_Ctr7_WMax | Para_CtrModule_Ctr7_WMax | 1779 | Para_CtrModule_Ctr7_WMax | x | 16999
[8 empty] | 17000 | Para_CtrModule_Ctr7_WMin | Para_CtrModule_Ctr7_WMin | 1780 | Para_CtrModule_Ctr7_WMin | x | 17000
[8 empty] | 17001 | Para_CtrModule_Ctr7_WRampNeg | Para_CtrModule_Ctr7_WRampNeg | 1781 | Para_CtrModule_Ctr7_WRampNeg | x/s | 17001
[8 empty] | 17002 | Para_CtrModule_Ctr7_WRampPos | Para_CtrModule_Ctr7_WRampPos | 1782 | Para_CtrModule_Ctr7_WRampPos | x/s | 17002
[8 empty] | 17003 | Para_CtrModule_Ctr7_WStart | Para_CtrModule_Ctr7_WStart | 1783 | Para_CtrModule_Ctr7_WStart | x | 17003
[8 empty] | 17004 | Para_CtrModule_Ctr7_YBlock | Para_CtrModule_Ctr7_YBlock | 1784 | Para_CtrModule_Ctr7_YBlock | % | 17004
[8 empty] | 17005 | Para_CtrModule_Ctr7_YHl | Para_CtrModule_Ctr7_YHl | 1785 | Para_CtrModule_Ctr7_YHl | % | 17005
[8 empty] | 17006 | Para_CtrModule_Ctr7_YMax | Para_CtrModule_Ctr7_YMax | 1786 | Para_CtrModule_Ctr7_YMax | % | 17006
[8 empty] | 17007 | Para_CtrModule_Ctr7_YMin | Para_CtrModule_Ctr7_YMin | 1787 | Para_CtrModule_Ctr7_YMin | % | 17007
[8 empty] | 17008 | Para_CtrModule_Ctr7_YRampNeg | Para_CtrModule_Ctr7_YRampNeg | 1788 | Para_CtrModule_Ctr7_YRampNeg | %/TA | 17008
[8 empty] | 17009 | Para_CtrModule_Ctr7_YRampPos | Para_CtrModule_Ctr7_YRampPos | 1789 | Para_CtrModule_Ctr7_YRampPos | %/TA | 17009
[8 empty] | 17010 | Para_CtrModule_Ctr7_YRampTune | Para_CtrModule_Ctr7_YRampTune | 1790 | Para_CtrModule_Ctr7_YRampTune | %/TA | 17010
[8 empty] | 17011 | Para_CtrModule_Ctr8_CycleTime | Para_CtrModule_Ctr8_CycleTime | 1791 | Para_CtrModule_Ctr8_CycleTime | ms | 17011
[8 empty] | 17012 | Para_CtrModule_Ctr8_DComp | Para_CtrModule_Ctr8_DComp | 1792 | Para_CtrModule_Ctr8_DComp |  | 17012
[8 empty] | 17013 | Para_CtrModule_Ctr8_DCompTune | Para_CtrModule_Ctr8_DCompTune | 1793 | Para_CtrModule_Ctr8_DCompTune |  | 17013
[8 empty] | 17014 | Para_CtrModule_Ctr8_DCompWMax | Para_CtrModule_Ctr8_DCompWMax | 1794 | Para_CtrModule_Ctr8_DCompWMax |  | 17014
[8 empty] | 17015 | Para_CtrModule_Ctr8_DCompWMin | Para_CtrModule_Ctr8_DCompWMin | 1795 | Para_CtrModule_Ctr8_DCompWMin |  | 17015
[8 empty] | 17016 | Para_CtrModule_Ctr8_DeadBand | Para_CtrModule_Ctr8_DeadBand | 1796 | Para_CtrModule_Ctr8_DeadBand | x | 17016
[8 empty] | 17017 | Para_CtrModule_Ctr8_Format | Para_CtrModule_Ctr8_Format | 1797 | Para_CtrModule_Ctr8_Format |  | 17017
[8 empty] | 17018 | Para_CtrModule_Ctr8_IComp | Para_CtrModule_Ctr8_IComp | 1798 | Para_CtrModule_Ctr8_IComp |  | 17018
[8 empty] | 17019 | Para_CtrModule_Ctr8_ICompTune | Para_CtrModule_Ctr8_ICompTune | 1799 | Para_CtrModule_Ctr8_ICompTune |  | 17019
[8 empty] | 17020 | Para_CtrModule_Ctr8_ICompWMax | Para_CtrModule_Ctr8_ICompWMax | 1800 | Para_CtrModule_Ctr8_ICompWMax |  | 17020
[8 empty] | 17021 | Para_CtrModule_Ctr8_ICompWMin | Para_CtrModule_Ctr8_ICompWMin | 1801 | Para_CtrModule_Ctr8_ICompWMin |  | 17021
[8 empty] | 17022 | Para_CtrModule_Ctr8_InvertCtrTune | Para_CtrModule_Ctr8_InvertCtrTune | 1802 | Para_CtrModule_Ctr8_InvertCtrTune |  | 17022
[8 empty] | 17023 | Para_CtrModule_Ctr8_Name | Para_CtrModule_Ctr8_Name | 1803 | Para_CtrModule_Ctr8_Name |  | 17023
[8 empty] | 17024 | Para_CtrModule_Ctr8_NameF | Para_CtrModule_Ctr8_NameF | 1804 | Para_CtrModule_Ctr8_NameF |  | 17024
[8 empty] | 17025 | Para_CtrModule_Ctr8_OptWorkPoint | Para_CtrModule_Ctr8_OptWorkPoint | 1805 | Para_CtrModule_Ctr8_OptWorkPoint |  | 17025
[8 empty] | 17026 | Para_CtrModule_Ctr8_PComp | Para_CtrModule_Ctr8_PComp | 1806 | Para_CtrModule_Ctr8_PComp |  | 17026
[8 empty] | 17027 | Para_CtrModule_Ctr8_PCompTune | Para_CtrModule_Ctr8_PCompTune | 1807 | Para_CtrModule_Ctr8_PCompTune |  | 17027
[8 empty] | 17028 | Para_CtrModule_Ctr8_PCompWMax | Para_CtrModule_Ctr8_PCompWMax | 1808 | Para_CtrModule_Ctr8_PCompWMax |  | 17028
[8 empty] | 17029 | Para_CtrModule_Ctr8_PCompWMin | Para_CtrModule_Ctr8_PCompWMin | 1809 | Para_CtrModule_Ctr8_PCompWMin |  | 17029
[8 empty] | 17030 | Para_CtrModule_Ctr8_RangeBegin | Para_CtrModule_Ctr8_RangeBegin | 1810 | Para_CtrModule_Ctr8_RangeBegin | x | 17030
[8 empty] | 17031 | Para_CtrModule_Ctr8_RangeEnd | Para_CtrModule_Ctr8_RangeEnd | 1811 | Para_CtrModule_Ctr8_RangeEnd | x | 17031
[8 empty] | 17032 | Para_CtrModule_Ctr8_Unit | Para_CtrModule_Ctr8_Unit | 1812 | Para_CtrModule_Ctr8_Unit |  | 17032
[8 empty] | 17033 | Para_CtrModule_Ctr8_UserLevelIntExt | Para_CtrModule_Ctr8_UserLevelIntExt | 1813 | Para_CtrModule_Ctr8_UserLevelIntExt |  | 17033
[8 empty] | 17034 | Para_CtrModule_Ctr8_UserLevelManAut | Para_CtrModule_Ctr8_UserLevelManAut | 1814 | Para_CtrModule_Ctr8_UserLevelManAut |  | 17034
[8 empty] | 17035 | Para_CtrModule_Ctr8_UserLevelSet | Para_CtrModule_Ctr8_UserLevelSet | 1815 | Para_CtrModule_Ctr8_UserLevelSet |  | 17035
[8 empty] | 17036 | Para_CtrModule_Ctr8_UserLevelTune | Para_CtrModule_Ctr8_UserLevelTune | 1816 | Para_CtrModule_Ctr8_UserLevelTune |  | 17036
[8 empty] | 17037 | Para_CtrModule_Ctr8_WMax | Para_CtrModule_Ctr8_WMax | 1817 | Para_CtrModule_Ctr8_WMax | x | 17037
[8 empty] | 17038 | Para_CtrModule_Ctr8_WMin | Para_CtrModule_Ctr8_WMin | 1818 | Para_CtrModule_Ctr8_WMin | x | 17038
[8 empty] | 17039 | Para_CtrModule_Ctr8_WRampNeg | Para_CtrModule_Ctr8_WRampNeg | 1819 | Para_CtrModule_Ctr8_WRampNeg | x/s | 17039
[8 empty] | 17040 | Para_CtrModule_Ctr8_WRampPos | Para_CtrModule_Ctr8_WRampPos | 1820 | Para_CtrModule_Ctr8_WRampPos | x/s | 17040
[8 empty] | 17041 | Para_CtrModule_Ctr8_WStart | Para_CtrModule_Ctr8_WStart | 1821 | Para_CtrModule_Ctr8_WStart | x | 17041
[8 empty] | 17042 | Para_CtrModule_Ctr8_YBlock | Para_CtrModule_Ctr8_YBlock | 1822 | Para_CtrModule_Ctr8_YBlock | % | 17042
[8 empty] | 17043 | Para_CtrModule_Ctr8_YHl | Para_CtrModule_Ctr8_YHl | 1823 | Para_CtrModule_Ctr8_YHl | % | 17043
[8 empty] | 17044 | Para_CtrModule_Ctr8_YMax | Para_CtrModule_Ctr8_YMax | 1824 | Para_CtrModule_Ctr8_YMax | % | 17044
[8 empty] | 17045 | Para_CtrModule_Ctr8_YMin | Para_CtrModule_Ctr8_YMin | 1825 | Para_CtrModule_Ctr8_YMin | % | 17045
[8 empty] | 17046 | Para_CtrModule_Ctr8_YRampNeg | Para_CtrModule_Ctr8_YRampNeg | 1826 | Para_CtrModule_Ctr8_YRampNeg | %/TA | 17046
[8 empty] | 17047 | Para_CtrModule_Ctr8_YRampPos | Para_CtrModule_Ctr8_YRampPos | 1827 | Para_CtrModule_Ctr8_YRampPos | %/TA | 17047
[8 empty] | 17048 | Para_CtrModule_Ctr8_YRampTune | Para_CtrModule_Ctr8_YRampTune | 1828 | Para_CtrModule_Ctr8_YRampTune | %/TA | 17048
[8 empty] | 17049 | Para_CtrModule_CtrX10_CycleTime | Para_CtrModule_CtrX10_CycleTime | 1829 | Para_CtrModule_CtrX10_CycleTime | ms | 17049
[8 empty] | 17050 | Para_CtrModule_CtrX10_DComp | Para_CtrModule_CtrX10_DComp | 1830 | Para_CtrModule_CtrX10_DComp | TV/TA | 17050
[8 empty] | 17051 | Para_CtrModule_CtrX10_DCompTune | Para_CtrModule_CtrX10_DCompTune | 1831 | Para_CtrModule_CtrX10_DCompTune |  | 17051
[8 empty] | 17052 | Para_CtrModule_CtrX10_DeadBand | Para_CtrModule_CtrX10_DeadBand | 1832 | Para_CtrModule_CtrX10_DeadBand | °C | 17052
[8 empty] | 17053 | Para_CtrModule_CtrX10_IComp | Para_CtrModule_CtrX10_IComp | 1833 | Para_CtrModule_CtrX10_IComp | TA/TN | 17053
[8 empty] | 17054 | Para_CtrModule_CtrX10_ICompTune | Para_CtrModule_CtrX10_ICompTune | 1834 | Para_CtrModule_CtrX10_ICompTune |  | 17054
[8 empty] | 17055 | Para_CtrModule_CtrX10_InvertCtrTune | Para_CtrModule_CtrX10_InvertCtrTune | 1835 | Para_CtrModule_CtrX10_InvertCtrTune |  | 17055
[8 empty] | 17056 | Para_CtrModule_CtrX10_PComp | Para_CtrModule_CtrX10_PComp | 1836 | Para_CtrModule_CtrX10_PComp |  | 17056
[8 empty] | 17057 | Para_CtrModule_CtrX10_PCompTune | Para_CtrModule_CtrX10_PCompTune | 1837 | Para_CtrModule_CtrX10_PCompTune |  | 17057
[8 empty] | 17058 | Para_CtrModule_CtrX10_RangeBegin | Para_CtrModule_CtrX10_RangeBegin | 1838 | Para_CtrModule_CtrX10_RangeBegin | °C | 17058
[8 empty] | 17059 | Para_CtrModule_CtrX10_RangeEnd | Para_CtrModule_CtrX10_RangeEnd | 1839 | Para_CtrModule_CtrX10_RangeEnd | °C | 17059
[8 empty] | 17060 | Para_CtrModule_CtrX10_UserLevelIntExt | Para_CtrModule_CtrX10_UserLevelIntExt | 1840 | Para_CtrModule_CtrX10_UserLevelIntExt |  | 17060
[8 empty] | 17061 | Para_CtrModule_CtrX10_UserLevelManAut | Para_CtrModule_CtrX10_UserLevelManAut | 1841 | Para_CtrModule_CtrX10_UserLevelManAut |  | 17061
[8 empty] | 17062 | Para_CtrModule_CtrX10_UserLevelSet | Para_CtrModule_CtrX10_UserLevelSet | 1842 | Para_CtrModule_CtrX10_UserLevelSet |  | 17062
[8 empty] | 17063 | Para_CtrModule_CtrX10_UserLevelTune | Para_CtrModule_CtrX10_UserLevelTune | 1843 | Para_CtrModule_CtrX10_UserLevelTune |  | 17063
[8 empty] | 17064 | Para_CtrModule_CtrX10_WMax | Para_CtrModule_CtrX10_WMax | 1844 | Para_CtrModule_CtrX10_WMax | °C | 17064
[8 empty] | 17065 | Para_CtrModule_CtrX10_WMin | Para_CtrModule_CtrX10_WMin | 1845 | Para_CtrModule_CtrX10_WMin | °C | 17065
[8 empty] | 17066 | Para_CtrModule_CtrX10_WRampNeg | Para_CtrModule_CtrX10_WRampNeg | 1846 | Para_CtrModule_CtrX10_WRampNeg | °C/s | 17066
[8 empty] | 17067 | Para_CtrModule_CtrX10_WRampPos | Para_CtrModule_CtrX10_WRampPos | 1847 | Para_CtrModule_CtrX10_WRampPos | °C/s | 17067
[8 empty] | 17068 | Para_CtrModule_CtrX10_WStart | Para_CtrModule_CtrX10_WStart | 1848 | Para_CtrModule_CtrX10_WStart | °C | 17068
[8 empty] | 17069 | Para_CtrModule_CtrX10_YBlock | Para_CtrModule_CtrX10_YBlock | 1849 | Para_CtrModule_CtrX10_YBlock | % | 17069
[8 empty] | 17070 | Para_CtrModule_CtrX10_YHl | Para_CtrModule_CtrX10_YHl | 1850 | Para_CtrModule_CtrX10_YHl |  | 17070
[8 empty] | 17071 | Para_CtrModule_CtrX10_YMax | Para_CtrModule_CtrX10_YMax | 1851 | Para_CtrModule_CtrX10_YMax | % | 17071
[8 empty] | 17072 | Para_CtrModule_CtrX10_YMin | Para_CtrModule_CtrX10_YMin | 1852 | Para_CtrModule_CtrX10_YMin | % | 17072
[8 empty] | 17073 | Para_CtrModule_CtrX10_YRampNeg | Para_CtrModule_CtrX10_YRampNeg | 1853 | Para_CtrModule_CtrX10_YRampNeg | %/TA | 17073
[8 empty] | 17074 | Para_CtrModule_CtrX10_YRampPos | Para_CtrModule_CtrX10_YRampPos | 1854 | Para_CtrModule_CtrX10_YRampPos | %/TA | 17074
[8 empty] | 17075 | Para_CtrModule_CtrX10_YRampTune | Para_CtrModule_CtrX10_YRampTune | 1855 | Para_CtrModule_CtrX10_YRampTune | %/TA | 17075
[8 empty] | 17076 | Para_CtrModule_CtrX11_CycleTime | Para_CtrModule_CtrX11_CycleTime | 1856 | Para_CtrModule_CtrX11_CycleTime | ms | 17076
[8 empty] | 17077 | Para_CtrModule_CtrX11_DComp | Para_CtrModule_CtrX11_DComp | 1857 | Para_CtrModule_CtrX11_DComp | TV/TA | 17077
[8 empty] | 17078 | Para_CtrModule_CtrX11_DCompTune | Para_CtrModule_CtrX11_DCompTune | 1858 | Para_CtrModule_CtrX11_DCompTune |  | 17078
[8 empty] | 17079 | Para_CtrModule_CtrX11_DeadBand | Para_CtrModule_CtrX11_DeadBand | 1859 | Para_CtrModule_CtrX11_DeadBand | °C | 17079
[8 empty] | 17080 | Para_CtrModule_CtrX11_IComp | Para_CtrModule_CtrX11_IComp | 1860 | Para_CtrModule_CtrX11_IComp | TA/TN | 17080
[8 empty] | 17081 | Para_CtrModule_CtrX11_ICompTune | Para_CtrModule_CtrX11_ICompTune | 1861 | Para_CtrModule_CtrX11_ICompTune |  | 17081
[8 empty] | 17082 | Para_CtrModule_CtrX11_InvertCtrTune | Para_CtrModule_CtrX11_InvertCtrTune | 1862 | Para_CtrModule_CtrX11_InvertCtrTune |  | 17082
[8 empty] | 17083 | Para_CtrModule_CtrX11_PComp | Para_CtrModule_CtrX11_PComp | 1863 | Para_CtrModule_CtrX11_PComp |  | 17083
[8 empty] | 17084 | Para_CtrModule_CtrX11_PCompTune | Para_CtrModule_CtrX11_PCompTune | 1864 | Para_CtrModule_CtrX11_PCompTune |  | 17084
[8 empty] | 17085 | Para_CtrModule_CtrX11_RangeBegin | Para_CtrModule_CtrX11_RangeBegin | 1865 | Para_CtrModule_CtrX11_RangeBegin | °C | 17085
[8 empty] | 17086 | Para_CtrModule_CtrX11_RangeEnd | Para_CtrModule_CtrX11_RangeEnd | 1866 | Para_CtrModule_CtrX11_RangeEnd | °C | 17086
[8 empty] | 17087 | Para_CtrModule_CtrX11_UserLevelIntExt | Para_CtrModule_CtrX11_UserLevelIntExt | 1867 | Para_CtrModule_CtrX11_UserLevelIntExt |  | 17087
[8 empty] | 17088 | Para_CtrModule_CtrX11_UserLevelManAut | Para_CtrModule_CtrX11_UserLevelManAut | 1868 | Para_CtrModule_CtrX11_UserLevelManAut |  | 17088
[8 empty] | 17089 | Para_CtrModule_CtrX11_UserLevelSet | Para_CtrModule_CtrX11_UserLevelSet | 1869 | Para_CtrModule_CtrX11_UserLevelSet |  | 17089
[8 empty] | 17090 | Para_CtrModule_CtrX11_UserLevelTune | Para_CtrModule_CtrX11_UserLevelTune | 1870 | Para_CtrModule_CtrX11_UserLevelTune |  | 17090
[8 empty] | 17091 | Para_CtrModule_CtrX11_WMax | Para_CtrModule_CtrX11_WMax | 1871 | Para_CtrModule_CtrX11_WMax | °C | 17091
[8 empty] | 17092 | Para_CtrModule_CtrX11_WMin | Para_CtrModule_CtrX11_WMin | 1872 | Para_CtrModule_CtrX11_WMin | °C | 17092
[8 empty] | 17093 | Para_CtrModule_CtrX11_WRampNeg | Para_CtrModule_CtrX11_WRampNeg | 1873 | Para_CtrModule_CtrX11_WRampNeg | °C/s | 17093
[8 empty] | 17094 | Para_CtrModule_CtrX11_WRampPos | Para_CtrModule_CtrX11_WRampPos | 1874 | Para_CtrModule_CtrX11_WRampPos | °C/s | 17094
[8 empty] | 17095 | Para_CtrModule_CtrX11_WStart | Para_CtrModule_CtrX11_WStart | 1875 | Para_CtrModule_CtrX11_WStart | °C | 17095
[8 empty] | 17096 | Para_CtrModule_CtrX11_YBlock | Para_CtrModule_CtrX11_YBlock | 1876 | Para_CtrModule_CtrX11_YBlock | % | 17096
[8 empty] | 17097 | Para_CtrModule_CtrX11_YHl | Para_CtrModule_CtrX11_YHl | 1877 | Para_CtrModule_CtrX11_YHl |  | 17097
[8 empty] | 17098 | Para_CtrModule_CtrX11_YMax | Para_CtrModule_CtrX11_YMax | 1878 | Para_CtrModule_CtrX11_YMax | % | 17098
[8 empty] | 17099 | Para_CtrModule_CtrX11_YMin | Para_CtrModule_CtrX11_YMin | 1879 | Para_CtrModule_CtrX11_YMin | % | 17099
[8 empty] | 17100 | Para_CtrModule_CtrX11_YRampNeg | Para_CtrModule_CtrX11_YRampNeg | 1880 | Para_CtrModule_CtrX11_YRampNeg | %/TA | 17100
[8 empty] | 17101 | Para_CtrModule_CtrX11_YRampPos | Para_CtrModule_CtrX11_YRampPos | 1881 | Para_CtrModule_CtrX11_YRampPos | %/TA | 17101
[8 empty] | 17102 | Para_CtrModule_CtrX11_YRampTune | Para_CtrModule_CtrX11_YRampTune | 1882 | Para_CtrModule_CtrX11_YRampTune | %/TA | 17102
[8 empty] | 17103 | Para_CtrModule_CtrX12_CycleTime | Para_CtrModule_CtrX12_CycleTime | 1883 | Para_CtrModule_CtrX12_CycleTime | ms | 17103
[8 empty] | 17104 | Para_CtrModule_CtrX12_DComp | Para_CtrModule_CtrX12_DComp | 1884 | Para_CtrModule_CtrX12_DComp | TV/TA | 17104
[8 empty] | 17105 | Para_CtrModule_CtrX12_DCompTune | Para_CtrModule_CtrX12_DCompTune | 1885 | Para_CtrModule_CtrX12_DCompTune |  | 17105
[8 empty] | 17106 | Para_CtrModule_CtrX12_DeadBand | Para_CtrModule_CtrX12_DeadBand | 1886 | Para_CtrModule_CtrX12_DeadBand |  | 17106
[8 empty] | 17107 | Para_CtrModule_CtrX12_IComp | Para_CtrModule_CtrX12_IComp | 1887 | Para_CtrModule_CtrX12_IComp | TA/TN | 17107
[8 empty] | 17108 | Para_CtrModule_CtrX12_ICompTune | Para_CtrModule_CtrX12_ICompTune | 1888 | Para_CtrModule_CtrX12_ICompTune |  | 17108
[8 empty] | 17109 | Para_CtrModule_CtrX12_InvertCtrTune | Para_CtrModule_CtrX12_InvertCtrTune | 1889 | Para_CtrModule_CtrX12_InvertCtrTune |  | 17109
[8 empty] | 17110 | Para_CtrModule_CtrX12_PComp | Para_CtrModule_CtrX12_PComp | 1890 | Para_CtrModule_CtrX12_PComp |  | 17110
[8 empty] | 17111 | Para_CtrModule_CtrX12_PCompTune | Para_CtrModule_CtrX12_PCompTune | 1891 | Para_CtrModule_CtrX12_PCompTune |  | 17111
[8 empty] | 17112 | Para_CtrModule_CtrX12_RangeBegin | Para_CtrModule_CtrX12_RangeBegin | 1892 | Para_CtrModule_CtrX12_RangeBegin |  | 17112
[8 empty] | 17113 | Para_CtrModule_CtrX12_RangeEnd | Para_CtrModule_CtrX12_RangeEnd | 1893 | Para_CtrModule_CtrX12_RangeEnd |  | 17113
[8 empty] | 17114 | Para_CtrModule_CtrX12_UserLevelIntExt | Para_CtrModule_CtrX12_UserLevelIntExt | 1894 | Para_CtrModule_CtrX12_UserLevelIntExt |  | 17114
[8 empty] | 17115 | Para_CtrModule_CtrX12_UserLevelManAut | Para_CtrModule_CtrX12_UserLevelManAut | 1895 | Para_CtrModule_CtrX12_UserLevelManAut |  | 17115
[8 empty] | 17116 | Para_CtrModule_CtrX12_UserLevelSet | Para_CtrModule_CtrX12_UserLevelSet | 1896 | Para_CtrModule_CtrX12_UserLevelSet |  | 17116
[8 empty] | 17117 | Para_CtrModule_CtrX12_UserLevelTune | Para_CtrModule_CtrX12_UserLevelTune | 1897 | Para_CtrModule_CtrX12_UserLevelTune |  | 17117
[8 empty] | 17118 | Para_CtrModule_CtrX12_WMax | Para_CtrModule_CtrX12_WMax | 1898 | Para_CtrModule_CtrX12_WMax |  | 17118
[8 empty] | 17119 | Para_CtrModule_CtrX12_WMin | Para_CtrModule_CtrX12_WMin | 1899 | Para_CtrModule_CtrX12_WMin |  | 17119
[8 empty] | 17120 | Para_CtrModule_CtrX12_WRampNeg | Para_CtrModule_CtrX12_WRampNeg | 1900 | Para_CtrModule_CtrX12_WRampNeg | °C/s | 17120
[8 empty] | 17121 | Para_CtrModule_CtrX12_WRampPos | Para_CtrModule_CtrX12_WRampPos | 1901 | Para_CtrModule_CtrX12_WRampPos | °C/s | 17121
[8 empty] | 17122 | Para_CtrModule_CtrX12_WStart | Para_CtrModule_CtrX12_WStart | 1902 | Para_CtrModule_CtrX12_WStart |  | 17122
[8 empty] | 17123 | Para_CtrModule_CtrX12_YBlock | Para_CtrModule_CtrX12_YBlock | 1903 | Para_CtrModule_CtrX12_YBlock |  | 17123
[8 empty] | 17124 | Para_CtrModule_CtrX12_YHl | Para_CtrModule_CtrX12_YHl | 1904 | Para_CtrModule_CtrX12_YHl |  | 17124
[8 empty] | 17125 | Para_CtrModule_CtrX12_YMax | Para_CtrModule_CtrX12_YMax | 1905 | Para_CtrModule_CtrX12_YMax | % | 17125
[8 empty] | 17126 | Para_CtrModule_CtrX12_YMin | Para_CtrModule_CtrX12_YMin | 1906 | Para_CtrModule_CtrX12_YMin | % | 17126
[8 empty] | 17127 | Para_CtrModule_CtrX12_YRampNeg | Para_CtrModule_CtrX12_YRampNeg | 1907 | Para_CtrModule_CtrX12_YRampNeg | %/TA | 17127
[8 empty] | 17128 | Para_CtrModule_CtrX12_YRampPos | Para_CtrModule_CtrX12_YRampPos | 1908 | Para_CtrModule_CtrX12_YRampPos | %/TA | 17128
[8 empty] | 17129 | Para_CtrModule_CtrX12_YRampTune | Para_CtrModule_CtrX12_YRampTune | 1909 | Para_CtrModule_CtrX12_YRampTune | %/TA | 17129
[8 empty] | 17130 | Para_CtrModule_CtrX13_CycleTime | Para_CtrModule_CtrX13_CycleTime | 1910 | Para_CtrModule_CtrX13_CycleTime | ms | 17130
[8 empty] | 17131 | Para_CtrModule_CtrX13_DCompTune | Para_CtrModule_CtrX13_DCompTune | 1911 | Para_CtrModule_CtrX13_DCompTune |  | 17131
[8 empty] | 17132 | Para_CtrModule_CtrX13_DeadBand | Para_CtrModule_CtrX13_DeadBand | 1912 | Para_CtrModule_CtrX13_DeadBand |  | 17132
[8 empty] | 17133 | Para_CtrModule_CtrX13_ICompTune | Para_CtrModule_CtrX13_ICompTune | 1913 | Para_CtrModule_CtrX13_ICompTune |  | 17133
[8 empty] | 17134 | Para_CtrModule_CtrX13_InvertCtrTune | Para_CtrModule_CtrX13_InvertCtrTune | 1914 | Para_CtrModule_CtrX13_InvertCtrTune |  | 17134
[8 empty] | 17135 | Para_CtrModule_CtrX13_PCompTune | Para_CtrModule_CtrX13_PCompTune | 1915 | Para_CtrModule_CtrX13_PCompTune |  | 17135
[8 empty] | 17136 | Para_CtrModule_CtrX13_RangeBegin | Para_CtrModule_CtrX13_RangeBegin | 1916 | Para_CtrModule_CtrX13_RangeBegin |  | 17136
[8 empty] | 17137 | Para_CtrModule_CtrX13_RangeEnd | Para_CtrModule_CtrX13_RangeEnd | 1917 | Para_CtrModule_CtrX13_RangeEnd |  | 17137
[8 empty] | 17138 | Para_CtrModule_CtrX13_UserLevelIntExt | Para_CtrModule_CtrX13_UserLevelIntExt | 1918 | Para_CtrModule_CtrX13_UserLevelIntExt |  | 17138
[8 empty] | 17139 | Para_CtrModule_CtrX13_UserLevelManAut | Para_CtrModule_CtrX13_UserLevelManAut | 1919 | Para_CtrModule_CtrX13_UserLevelManAut |  | 17139
[8 empty] | 17140 | Para_CtrModule_CtrX13_UserLevelSet | Para_CtrModule_CtrX13_UserLevelSet | 1920 | Para_CtrModule_CtrX13_UserLevelSet |  | 17140
[8 empty] | 17141 | Para_CtrModule_CtrX13_UserLevelTune | Para_CtrModule_CtrX13_UserLevelTune | 1921 | Para_CtrModule_CtrX13_UserLevelTune |  | 17141
[8 empty] | 17142 | Para_CtrModule_CtrX13_WMax | Para_CtrModule_CtrX13_WMax | 1922 | Para_CtrModule_CtrX13_WMax |  | 17142
[8 empty] | 17143 | Para_CtrModule_CtrX13_WMin | Para_CtrModule_CtrX13_WMin | 1923 | Para_CtrModule_CtrX13_WMin |  | 17143
[8 empty] | 17144 | Para_CtrModule_CtrX13_WRampNeg | Para_CtrModule_CtrX13_WRampNeg | 1924 | Para_CtrModule_CtrX13_WRampNeg | /s | 17144
[8 empty] | 17145 | Para_CtrModule_CtrX13_WRampPos | Para_CtrModule_CtrX13_WRampPos | 1925 | Para_CtrModule_CtrX13_WRampPos | /s | 17145
[8 empty] | 17146 | Para_CtrModule_CtrX13_WStart | Para_CtrModule_CtrX13_WStart | 1926 | Para_CtrModule_CtrX13_WStart |  | 17146
[8 empty] | 17147 | Para_CtrModule_CtrX13_YBlock | Para_CtrModule_CtrX13_YBlock | 1927 | Para_CtrModule_CtrX13_YBlock | % | 17147
[8 empty] | 17148 | Para_CtrModule_CtrX13_YHl | Para_CtrModule_CtrX13_YHl | 1928 | Para_CtrModule_CtrX13_YHl | % | 17148
[8 empty] | 17149 | Para_CtrModule_CtrX13_YMax | Para_CtrModule_CtrX13_YMax | 1929 | Para_CtrModule_CtrX13_YMax | % | 17149
[8 empty] | 17150 | Para_CtrModule_CtrX13_YMin | Para_CtrModule_CtrX13_YMin | 1930 | Para_CtrModule_CtrX13_YMin | % | 17150
[8 empty] | 17151 | Para_CtrModule_CtrX13_YRampTune | Para_CtrModule_CtrX13_YRampTune | 1931 | Para_CtrModule_CtrX13_YRampTune | %/TA | 17151
[8 empty] | 17152 | Para_CtrModule_CtrX14_CycleTime | Para_CtrModule_CtrX14_CycleTime | 1932 | Para_CtrModule_CtrX14_CycleTime | ms | 17152
[8 empty] | 17153 | Para_CtrModule_CtrX14_DCompTune | Para_CtrModule_CtrX14_DCompTune | 1933 | Para_CtrModule_CtrX14_DCompTune |  | 17153
[8 empty] | 17154 | Para_CtrModule_CtrX14_DeadBand | Para_CtrModule_CtrX14_DeadBand | 1934 | Para_CtrModule_CtrX14_DeadBand | °C | 17154
[8 empty] | 17155 | Para_CtrModule_CtrX14_ICompTune | Para_CtrModule_CtrX14_ICompTune | 1935 | Para_CtrModule_CtrX14_ICompTune |  | 17155
[8 empty] | 17156 | Para_CtrModule_CtrX14_InvertCtrTune | Para_CtrModule_CtrX14_InvertCtrTune | 1936 | Para_CtrModule_CtrX14_InvertCtrTune |  | 17156
[8 empty] | 17157 | Para_CtrModule_CtrX14_PCompTune | Para_CtrModule_CtrX14_PCompTune | 1937 | Para_CtrModule_CtrX14_PCompTune |  | 17157
[8 empty] | 17158 | Para_CtrModule_CtrX14_RangeBegin | Para_CtrModule_CtrX14_RangeBegin | 1938 | Para_CtrModule_CtrX14_RangeBegin | °C | 17158
[8 empty] | 17159 | Para_CtrModule_CtrX14_RangeEnd | Para_CtrModule_CtrX14_RangeEnd | 1939 | Para_CtrModule_CtrX14_RangeEnd | °C | 17159
[8 empty] | 17160 | Para_CtrModule_CtrX14_UserLevelIntExt | Para_CtrModule_CtrX14_UserLevelIntExt | 1940 | Para_CtrModule_CtrX14_UserLevelIntExt |  | 17160
[8 empty] | 17161 | Para_CtrModule_CtrX14_UserLevelManAut | Para_CtrModule_CtrX14_UserLevelManAut | 1941 | Para_CtrModule_CtrX14_UserLevelManAut |  | 17161
[8 empty] | 17162 | Para_CtrModule_CtrX14_UserLevelSet | Para_CtrModule_CtrX14_UserLevelSet | 1942 | Para_CtrModule_CtrX14_UserLevelSet |  | 17162
[8 empty] | 17163 | Para_CtrModule_CtrX14_UserLevelTune | Para_CtrModule_CtrX14_UserLevelTune | 1943 | Para_CtrModule_CtrX14_UserLevelTune |  | 17163
[8 empty] | 17164 | Para_CtrModule_CtrX14_WMax | Para_CtrModule_CtrX14_WMax | 1944 | Para_CtrModule_CtrX14_WMax | °C | 17164
[8 empty] | 17165 | Para_CtrModule_CtrX14_WMin | Para_CtrModule_CtrX14_WMin | 1945 | Para_CtrModule_CtrX14_WMin | °C | 17165
[8 empty] | 17166 | Para_CtrModule_CtrX14_WRampNeg | Para_CtrModule_CtrX14_WRampNeg | 1946 | Para_CtrModule_CtrX14_WRampNeg | °C/s | 17166
[8 empty] | 17167 | Para_CtrModule_CtrX14_WRampPos | Para_CtrModule_CtrX14_WRampPos | 1947 | Para_CtrModule_CtrX14_WRampPos | °C/s | 17167
[8 empty] | 17168 | Para_CtrModule_CtrX14_WStart | Para_CtrModule_CtrX14_WStart | 1948 | Para_CtrModule_CtrX14_WStart | °C | 17168
[8 empty] | 17169 | Para_CtrModule_CtrX14_YBlock | Para_CtrModule_CtrX14_YBlock | 1949 | Para_CtrModule_CtrX14_YBlock | % | 17169
[8 empty] | 17170 | Para_CtrModule_CtrX14_YHl | Para_CtrModule_CtrX14_YHl | 1950 | Para_CtrModule_CtrX14_YHl | % | 17170
[8 empty] | 17171 | Para_CtrModule_CtrX14_YMax | Para_CtrModule_CtrX14_YMax | 1951 | Para_CtrModule_CtrX14_YMax | % | 17171
[8 empty] | 17172 | Para_CtrModule_CtrX14_YMin | Para_CtrModule_CtrX14_YMin | 1952 | Para_CtrModule_CtrX14_YMin | % | 17172
[8 empty] | 17173 | Para_CtrModule_CtrX14_YRampTune | Para_CtrModule_CtrX14_YRampTune | 1953 | Para_CtrModule_CtrX14_YRampTune | %/TA | 17173
[8 empty] | 17174 | Para_CtrModule_CtrX15_CycleTime | Para_CtrModule_CtrX15_CycleTime | 1954 | Para_CtrModule_CtrX15_CycleTime | ms | 17174
[8 empty] | 17175 | Para_CtrModule_CtrX15_DCompTune | Para_CtrModule_CtrX15_DCompTune | 1955 | Para_CtrModule_CtrX15_DCompTune |  | 17175
[8 empty] | 17176 | Para_CtrModule_CtrX15_DeadBand | Para_CtrModule_CtrX15_DeadBand | 1956 | Para_CtrModule_CtrX15_DeadBand | °C | 17176
[8 empty] | 17177 | Para_CtrModule_CtrX15_ICompTune | Para_CtrModule_CtrX15_ICompTune | 1957 | Para_CtrModule_CtrX15_ICompTune |  | 17177
[8 empty] | 17178 | Para_CtrModule_CtrX15_InvertCtrTune | Para_CtrModule_CtrX15_InvertCtrTune | 1958 | Para_CtrModule_CtrX15_InvertCtrTune |  | 17178
[8 empty] | 17179 | Para_CtrModule_CtrX15_PCompTune | Para_CtrModule_CtrX15_PCompTune | 1959 | Para_CtrModule_CtrX15_PCompTune |  | 17179
[8 empty] | 17180 | Para_CtrModule_CtrX15_RangeBegin | Para_CtrModule_CtrX15_RangeBegin | 1960 | Para_CtrModule_CtrX15_RangeBegin | °C | 17180
[8 empty] | 17181 | Para_CtrModule_CtrX15_RangeEnd | Para_CtrModule_CtrX15_RangeEnd | 1961 | Para_CtrModule_CtrX15_RangeEnd | °C | 17181
[8 empty] | 17182 | Para_CtrModule_CtrX15_UserLevelIntExt | Para_CtrModule_CtrX15_UserLevelIntExt | 1962 | Para_CtrModule_CtrX15_UserLevelIntExt |  | 17182
[8 empty] | 17183 | Para_CtrModule_CtrX15_UserLevelManAut | Para_CtrModule_CtrX15_UserLevelManAut | 1963 | Para_CtrModule_CtrX15_UserLevelManAut |  | 17183
[8 empty] | 17184 | Para_CtrModule_CtrX15_UserLevelSet | Para_CtrModule_CtrX15_UserLevelSet | 1964 | Para_CtrModule_CtrX15_UserLevelSet |  | 17184
[8 empty] | 17185 | Para_CtrModule_CtrX15_UserLevelTune | Para_CtrModule_CtrX15_UserLevelTune | 1965 | Para_CtrModule_CtrX15_UserLevelTune |  | 17185
[8 empty] | 17186 | Para_CtrModule_CtrX15_WMax | Para_CtrModule_CtrX15_WMax | 1966 | Para_CtrModule_CtrX15_WMax | °C | 17186
[8 empty] | 17187 | Para_CtrModule_CtrX15_WMin | Para_CtrModule_CtrX15_WMin | 1967 | Para_CtrModule_CtrX15_WMin | °C | 17187
[8 empty] | 17188 | Para_CtrModule_CtrX15_WRampNeg | Para_CtrModule_CtrX15_WRampNeg | 1968 | Para_CtrModule_CtrX15_WRampNeg | °C/s | 17188
[8 empty] | 17189 | Para_CtrModule_CtrX15_WRampPos | Para_CtrModule_CtrX15_WRampPos | 1969 | Para_CtrModule_CtrX15_WRampPos | °C/s | 17189
[8 empty] | 17190 | Para_CtrModule_CtrX15_WStart | Para_CtrModule_CtrX15_WStart | 1970 | Para_CtrModule_CtrX15_WStart | °C | 17190
[8 empty] | 17191 | Para_CtrModule_CtrX15_YBlock | Para_CtrModule_CtrX15_YBlock | 1971 | Para_CtrModule_CtrX15_YBlock | % | 17191
[8 empty] | 17192 | Para_CtrModule_CtrX15_YHl | Para_CtrModule_CtrX15_YHl | 1972 | Para_CtrModule_CtrX15_YHl | % | 17192
[8 empty] | 17193 | Para_CtrModule_CtrX15_YMax | Para_CtrModule_CtrX15_YMax | 1973 | Para_CtrModule_CtrX15_YMax | % | 17193
[8 empty] | 17194 | Para_CtrModule_CtrX15_YMin | Para_CtrModule_CtrX15_YMin | 1974 | Para_CtrModule_CtrX15_YMin | % | 17194
[8 empty] | 17195 | Para_CtrModule_CtrX15_YRampTune | Para_CtrModule_CtrX15_YRampTune | 1975 | Para_CtrModule_CtrX15_YRampTune | %/TA | 17195
[8 empty] | 17196 | Para_CtrModule_CtrX16_CycleTime | Para_CtrModule_CtrX16_CycleTime | 1976 | Para_CtrModule_CtrX16_CycleTime | ms | 17196
[8 empty] | 17197 | Para_CtrModule_CtrX16_DCompTune | Para_CtrModule_CtrX16_DCompTune | 1977 | Para_CtrModule_CtrX16_DCompTune |  | 17197
[8 empty] | 17198 | Para_CtrModule_CtrX16_DeadBand | Para_CtrModule_CtrX16_DeadBand | 1978 | Para_CtrModule_CtrX16_DeadBand | mbar | 17198
[8 empty] | 17199 | Para_CtrModule_CtrX16_ICompTune | Para_CtrModule_CtrX16_ICompTune | 1979 | Para_CtrModule_CtrX16_ICompTune |  | 17199
[8 empty] | 17200 | Para_CtrModule_CtrX16_InvertCtrTune | Para_CtrModule_CtrX16_InvertCtrTune | 1980 | Para_CtrModule_CtrX16_InvertCtrTune |  | 17200
[8 empty] | 17201 | Para_CtrModule_CtrX16_PCompTune | Para_CtrModule_CtrX16_PCompTune | 1981 | Para_CtrModule_CtrX16_PCompTune |  | 17201
[8 empty] | 17202 | Para_CtrModule_CtrX16_RangeBegin | Para_CtrModule_CtrX16_RangeBegin | 1982 | Para_CtrModule_CtrX16_RangeBegin | mbar | 17202
[8 empty] | 17203 | Para_CtrModule_CtrX16_RangeEnd | Para_CtrModule_CtrX16_RangeEnd | 1983 | Para_CtrModule_CtrX16_RangeEnd | mbar | 17203
[8 empty] | 17204 | Para_CtrModule_CtrX16_UserLevelIntExt | Para_CtrModule_CtrX16_UserLevelIntExt | 1984 | Para_CtrModule_CtrX16_UserLevelIntExt |  | 17204
[8 empty] | 17205 | Para_CtrModule_CtrX16_UserLevelManAut | Para_CtrModule_CtrX16_UserLevelManAut | 1985 | Para_CtrModule_CtrX16_UserLevelManAut |  | 17205
[8 empty] | 17206 | Para_CtrModule_CtrX16_UserLevelSet | Para_CtrModule_CtrX16_UserLevelSet | 1986 | Para_CtrModule_CtrX16_UserLevelSet |  | 17206
[8 empty] | 17207 | Para_CtrModule_CtrX16_UserLevelTune | Para_CtrModule_CtrX16_UserLevelTune | 1987 | Para_CtrModule_CtrX16_UserLevelTune |  | 17207
[8 empty] | 17208 | Para_CtrModule_CtrX16_WMax | Para_CtrModule_CtrX16_WMax | 1988 | Para_CtrModule_CtrX16_WMax | mbar | 17208
[8 empty] | 17209 | Para_CtrModule_CtrX16_WMin | Para_CtrModule_CtrX16_WMin | 1989 | Para_CtrModule_CtrX16_WMin | mbar | 17209
[8 empty] | 17210 | Para_CtrModule_CtrX16_WRampNeg | Para_CtrModule_CtrX16_WRampNeg | 1990 | Para_CtrModule_CtrX16_WRampNeg | mbar/s | 17210
[8 empty] | 17211 | Para_CtrModule_CtrX16_WRampPos | Para_CtrModule_CtrX16_WRampPos | 1991 | Para_CtrModule_CtrX16_WRampPos | mbar/s | 17211
[8 empty] | 17212 | Para_CtrModule_CtrX16_WStart | Para_CtrModule_CtrX16_WStart | 1992 | Para_CtrModule_CtrX16_WStart | mbar | 17212
[8 empty] | 17213 | Para_CtrModule_CtrX16_YBlock | Para_CtrModule_CtrX16_YBlock | 1993 | Para_CtrModule_CtrX16_YBlock | % | 17213
[8 empty] | 17214 | Para_CtrModule_CtrX16_YHl | Para_CtrModule_CtrX16_YHl | 1994 | Para_CtrModule_CtrX16_YHl | % | 17214
[8 empty] | 17215 | Para_CtrModule_CtrX16_YMax | Para_CtrModule_CtrX16_YMax | 1995 | Para_CtrModule_CtrX16_YMax | % | 17215
[8 empty] | 17216 | Para_CtrModule_CtrX16_YMin | Para_CtrModule_CtrX16_YMin | 1996 | Para_CtrModule_CtrX16_YMin | % | 17216
[8 empty] | 17217 | Para_CtrModule_CtrX16_YRampTune | Para_CtrModule_CtrX16_YRampTune | 1997 | Para_CtrModule_CtrX16_YRampTune | %/TA | 17217
[8 empty] | 10000709 | Para_Custom_AnalogIn_10_CustAnaIn_MinMaxActive10 | Para_Custom_AnalogIn_10_CustAnaIn_MinMaxActive10 | 1998 | Para_Custom_AnalogIn_10_CustAnaIn_MinMaxActive10 |  | 10000709
[8 empty] | 10008505 | Para_Custom_AnalogIn_10_CustAnaIn_Typ10 | Para_Custom_AnalogIn_10_CustAnaIn_Typ10 | 1999 | Para_Custom_AnalogIn_10_CustAnaIn_Typ10 |  | 10008505
[8 empty] | 10000829 | Para_Custom_AnalogIn_10_Hystereses | Para_Custom_AnalogIn_10_Hystereses | 2000 | Para_Custom_AnalogIn_10_Hystereses |  | 10000829
[8 empty] | 10000862 | Para_Custom_AnalogIn_10_LimitHi | Para_Custom_AnalogIn_10_LimitHi | 2001 | Para_Custom_AnalogIn_10_LimitHi |  | 10000862
[8 empty] | 10002804 | Para_Custom_AnalogIn_10_LimitHiHi | Para_Custom_AnalogIn_10_LimitHiHi | 2002 | Para_Custom_AnalogIn_10_LimitHiHi |  | 10002804
[8 empty] | 10000888 | Para_Custom_AnalogIn_10_LimitLo | Para_Custom_AnalogIn_10_LimitLo | 2003 | Para_Custom_AnalogIn_10_LimitLo |  | 10000888
[8 empty] | 10002824 | Para_Custom_AnalogIn_10_LimitLoLo | Para_Custom_AnalogIn_10_LimitLoLo | 2004 | Para_Custom_AnalogIn_10_LimitLoLo |  | 10002824
[8 empty] | 10000710 | Para_Custom_AnalogIn_11_CustAnaIn_MinMaxActive11 | Para_Custom_AnalogIn_11_CustAnaIn_MinMaxActive11 | 2005 | Para_Custom_AnalogIn_11_CustAnaIn_MinMaxActive11 |  | 10000710
[8 empty] | 10008503 | Para_Custom_AnalogIn_11_CustAnaIn_Typ11 | Para_Custom_AnalogIn_11_CustAnaIn_Typ11 | 2006 | Para_Custom_AnalogIn_11_CustAnaIn_Typ11 |  | 10008503
[8 empty] | 10000831 | Para_Custom_AnalogIn_11_Hystereses | Para_Custom_AnalogIn_11_Hystereses | 2007 | Para_Custom_AnalogIn_11_Hystereses |  | 10000831
[8 empty] | 10000860 | Para_Custom_AnalogIn_11_LimitHi | Para_Custom_AnalogIn_11_LimitHi | 2008 | Para_Custom_AnalogIn_11_LimitHi |  | 10000860
[8 empty] | 10002815 | Para_Custom_AnalogIn_11_LimitHiHi | Para_Custom_AnalogIn_11_LimitHiHi | 2009 | Para_Custom_AnalogIn_11_LimitHiHi |  | 10002815
[8 empty] | 10000892 | Para_Custom_AnalogIn_11_LimitLo | Para_Custom_AnalogIn_11_LimitLo | 2010 | Para_Custom_AnalogIn_11_LimitLo |  | 10000892
[8 empty] | 10002813 | Para_Custom_AnalogIn_11_LimitLoLo | Para_Custom_AnalogIn_11_LimitLoLo | 2011 | Para_Custom_AnalogIn_11_LimitLoLo |  | 10002813
[8 empty] | 10000712 | Para_Custom_AnalogIn_12_CustAnaIn_MinMaxActive12 | Para_Custom_AnalogIn_12_CustAnaIn_MinMaxActive12 | 2012 | Para_Custom_AnalogIn_12_CustAnaIn_MinMaxActive12 |  | 10000712
[8 empty] | 10008504 | Para_Custom_AnalogIn_12_CustAnaIn_Typ12 | Para_Custom_AnalogIn_12_CustAnaIn_Typ12 | 2013 | Para_Custom_AnalogIn_12_CustAnaIn_Typ12 |  | 10008504
[8 empty] | 10000832 | Para_Custom_AnalogIn_12_Hystereses | Para_Custom_AnalogIn_12_Hystereses | 2014 | Para_Custom_AnalogIn_12_Hystereses |  | 10000832
[8 empty] | 10000861 | Para_Custom_AnalogIn_12_LimitHi | Para_Custom_AnalogIn_12_LimitHi | 2015 | Para_Custom_AnalogIn_12_LimitHi |  | 10000861
[8 empty] | 10002823 | Para_Custom_AnalogIn_12_LimitHiHi | Para_Custom_AnalogIn_12_LimitHiHi | 2016 | Para_Custom_AnalogIn_12_LimitHiHi |  | 10002823
[8 empty] | 10000893 | Para_Custom_AnalogIn_12_LimitLo | Para_Custom_AnalogIn_12_LimitLo | 2017 | Para_Custom_AnalogIn_12_LimitLo |  | 10000893
[8 empty] | 10002822 | Para_Custom_AnalogIn_12_LimitLoLo | Para_Custom_AnalogIn_12_LimitLoLo | 2018 | Para_Custom_AnalogIn_12_LimitLoLo |  | 10002822
[8 empty] | 10000713 | Para_Custom_AnalogIn_13_CustAnaIn_MinMaxActive13 | Para_Custom_AnalogIn_13_CustAnaIn_MinMaxActive13 | 2019 | Para_Custom_AnalogIn_13_CustAnaIn_MinMaxActive13 |  | 10000713
[8 empty] | 10008508 | Para_Custom_AnalogIn_13_CustAnaIn_Typ13 | Para_Custom_AnalogIn_13_CustAnaIn_Typ13 | 2020 | Para_Custom_AnalogIn_13_CustAnaIn_Typ13 |  | 10008508
[8 empty] | 10000834 | Para_Custom_AnalogIn_13_Hystereses | Para_Custom_AnalogIn_13_Hystereses | 2021 | Para_Custom_AnalogIn_13_Hystereses |  | 10000834
[8 empty] | 10000863 | Para_Custom_AnalogIn_13_LimitHi | Para_Custom_AnalogIn_13_LimitHi | 2022 | Para_Custom_AnalogIn_13_LimitHi |  | 10000863
[8 empty] | 10002819 | Para_Custom_AnalogIn_13_LimitHiHi | Para_Custom_AnalogIn_13_LimitHiHi | 2023 | Para_Custom_AnalogIn_13_LimitHiHi |  | 10002819
[8 empty] | 10000891 | Para_Custom_AnalogIn_13_LimitLo | Para_Custom_AnalogIn_13_LimitLo | 2024 | Para_Custom_AnalogIn_13_LimitLo |  | 10000891
[8 empty] | 10002828 | Para_Custom_AnalogIn_13_LimitLoLo | Para_Custom_AnalogIn_13_LimitLoLo | 2025 | Para_Custom_AnalogIn_13_LimitLoLo |  | 10002828
[8 empty] | 10000711 | Para_Custom_AnalogIn_14_CustAnaIn_MinMaxActive14 | Para_Custom_AnalogIn_14_CustAnaIn_MinMaxActive14 | 2026 | Para_Custom_AnalogIn_14_CustAnaIn_MinMaxActive14 |  | 10000711
[8 empty] | 10008587 | Para_Custom_AnalogIn_14_CustAnaIn_Typ14 | Para_Custom_AnalogIn_14_CustAnaIn_Typ14 | 2027 | Para_Custom_AnalogIn_14_CustAnaIn_Typ14 |  | 10008587
[8 empty] | 10000837 | Para_Custom_AnalogIn_14_Hystereses | Para_Custom_AnalogIn_14_Hystereses | 2028 | Para_Custom_AnalogIn_14_Hystereses |  | 10000837
[8 empty] | 10000864 | Para_Custom_AnalogIn_14_LimitHi | Para_Custom_AnalogIn_14_LimitHi | 2029 | Para_Custom_AnalogIn_14_LimitHi |  | 10000864
[8 empty] | 10002827 | Para_Custom_AnalogIn_14_LimitHiHi | Para_Custom_AnalogIn_14_LimitHiHi | 2030 | Para_Custom_AnalogIn_14_LimitHiHi |  | 10002827
[8 empty] | 10000894 | Para_Custom_AnalogIn_14_LimitLo | Para_Custom_AnalogIn_14_LimitLo | 2031 | Para_Custom_AnalogIn_14_LimitLo |  | 10000894
[8 empty] | 10002837 | Para_Custom_AnalogIn_14_LimitLoLo | Para_Custom_AnalogIn_14_LimitLoLo | 2032 | Para_Custom_AnalogIn_14_LimitLoLo |  | 10002837
[8 empty] | 10000714 | Para_Custom_AnalogIn_15_CustAnaIn_MinMaxActive15 | Para_Custom_AnalogIn_15_CustAnaIn_MinMaxActive15 | 2033 | Para_Custom_AnalogIn_15_CustAnaIn_MinMaxActive15 |  | 10000714
[8 empty] | 10008592 | Para_Custom_AnalogIn_15_CustAnaIn_Typ15 | Para_Custom_AnalogIn_15_CustAnaIn_Typ15 | 2034 | Para_Custom_AnalogIn_15_CustAnaIn_Typ15 |  | 10008592
[8 empty] | 10000833 | Para_Custom_AnalogIn_15_Hystereses | Para_Custom_AnalogIn_15_Hystereses | 2035 | Para_Custom_AnalogIn_15_Hystereses |  | 10000833
[8 empty] | 10000865 | Para_Custom_AnalogIn_15_LimitHi | Para_Custom_AnalogIn_15_LimitHi | 2036 | Para_Custom_AnalogIn_15_LimitHi |  | 10000865
[8 empty] | 10002835 | Para_Custom_AnalogIn_15_LimitHiHi | Para_Custom_AnalogIn_15_LimitHiHi | 2037 | Para_Custom_AnalogIn_15_LimitHiHi |  | 10002835
[8 empty] | 10000896 | Para_Custom_AnalogIn_15_LimitLo | Para_Custom_AnalogIn_15_LimitLo | 2038 | Para_Custom_AnalogIn_15_LimitLo |  | 10000896
[8 empty] | 10002832 | Para_Custom_AnalogIn_15_LimitLoLo | Para_Custom_AnalogIn_15_LimitLoLo | 2039 | Para_Custom_AnalogIn_15_LimitLoLo |  | 10002832
[8 empty] | 10000718 | Para_Custom_AnalogIn_16_CustAnaIn_MinMaxActive16 | Para_Custom_AnalogIn_16_CustAnaIn_MinMaxActive16 | 2040 | Para_Custom_AnalogIn_16_CustAnaIn_MinMaxActive16 |  | 10000718
[8 empty] | 10008591 | Para_Custom_AnalogIn_16_CustAnaIn_Typ16 | Para_Custom_AnalogIn_16_CustAnaIn_Typ16 | 2041 | Para_Custom_AnalogIn_16_CustAnaIn_Typ16 |  | 10008591
[8 empty] | 10000836 | Para_Custom_AnalogIn_16_Hystereses | Para_Custom_AnalogIn_16_Hystereses | 2042 | Para_Custom_AnalogIn_16_Hystereses |  | 10000836
[8 empty] | 10000866 | Para_Custom_AnalogIn_16_LimitHi | Para_Custom_AnalogIn_16_LimitHi | 2043 | Para_Custom_AnalogIn_16_LimitHi |  | 10000866
[8 empty] | 10002836 | Para_Custom_AnalogIn_16_LimitHiHi | Para_Custom_AnalogIn_16_LimitHiHi | 2044 | Para_Custom_AnalogIn_16_LimitHiHi |  | 10002836
[8 empty] | 10000898 | Para_Custom_AnalogIn_16_LimitLo | Para_Custom_AnalogIn_16_LimitLo | 2045 | Para_Custom_AnalogIn_16_LimitLo |  | 10000898
[8 empty] | 10002838 | Para_Custom_AnalogIn_16_LimitLoLo | Para_Custom_AnalogIn_16_LimitLoLo | 2046 | Para_Custom_AnalogIn_16_LimitLoLo |  | 10002838
[8 empty] | 10000149 | Para_Custom_AnalogIn_17_CustAnaIn_Active17 | Para_Custom_AnalogIn_17_CustAnaIn_Active17 | 2047 | Para_Custom_AnalogIn_17_CustAnaIn_Active17 |  | 10000149
[8 empty] | 10000717 | Para_Custom_AnalogIn_17_CustAnaIn_MinMaxActive17 | Para_Custom_AnalogIn_17_CustAnaIn_MinMaxActive17 | 2048 | Para_Custom_AnalogIn_17_CustAnaIn_MinMaxActive17 |  | 10000717
[8 empty] | 10001166 | Para_Custom_AnalogIn_17_CustAnaIn_Set4mA17 | Para_Custom_AnalogIn_17_CustAnaIn_Set4mA17 | 2049 | Para_Custom_AnalogIn_17_CustAnaIn_Set4mA17 |  | 10001166
[8 empty] | 10008594 | Para_Custom_AnalogIn_17_CustAnaIn_Typ17 | Para_Custom_AnalogIn_17_CustAnaIn_Typ17 | 2050 | Para_Custom_AnalogIn_17_CustAnaIn_Typ17 |  | 10008594
[8 empty] | 10000835 | Para_Custom_AnalogIn_17_Hystereses | Para_Custom_AnalogIn_17_Hystereses | 2051 | Para_Custom_AnalogIn_17_Hystereses |  | 10000835
[8 empty] | 10000868 | Para_Custom_AnalogIn_17_LimitHi | Para_Custom_AnalogIn_17_LimitHi | 2052 | Para_Custom_AnalogIn_17_LimitHi |  | 10000868
[8 empty] | 10002848 | Para_Custom_AnalogIn_17_LimitHiHi | Para_Custom_AnalogIn_17_LimitHiHi | 2053 | Para_Custom_AnalogIn_17_LimitHiHi |  | 10002848
[8 empty] | 10000897 | Para_Custom_AnalogIn_17_LimitLo | Para_Custom_AnalogIn_17_LimitLo | 2054 | Para_Custom_AnalogIn_17_LimitLo |  | 10000897
[8 empty] | 10002842 | Para_Custom_AnalogIn_17_LimitLoLo | Para_Custom_AnalogIn_17_LimitLoLo | 2055 | Para_Custom_AnalogIn_17_LimitLoLo |  | 10002842
[8 empty] | 10000920 | Para_Custom_AnalogIn_17_ScaleMax | Para_Custom_AnalogIn_17_ScaleMax | 2056 | Para_Custom_AnalogIn_17_ScaleMax |  | 10000920
[8 empty] | 10000934 | Para_Custom_AnalogIn_17_ScaleMin | Para_Custom_AnalogIn_17_ScaleMin | 2057 | Para_Custom_AnalogIn_17_ScaleMin |  | 10000934
[8 empty] | 10000150 | Para_Custom_AnalogIn_18_CustAnaIn_Active18 | Para_Custom_AnalogIn_18_CustAnaIn_Active18 | 2058 | Para_Custom_AnalogIn_18_CustAnaIn_Active18 |  | 10000150
[8 empty] | 10000716 | Para_Custom_AnalogIn_18_CustAnaIn_MinMaxActive18 | Para_Custom_AnalogIn_18_CustAnaIn_MinMaxActive18 | 2059 | Para_Custom_AnalogIn_18_CustAnaIn_MinMaxActive18 |  | 10000716
[8 empty] | 10001161 | Para_Custom_AnalogIn_18_CustAnaIn_Set4mA18 | Para_Custom_AnalogIn_18_CustAnaIn_Set4mA18 | 2060 | Para_Custom_AnalogIn_18_CustAnaIn_Set4mA18 |  | 10001161
[8 empty] | 10008593 | Para_Custom_AnalogIn_18_CustAnaIn_Typ18 | Para_Custom_AnalogIn_18_CustAnaIn_Typ18 | 2061 | Para_Custom_AnalogIn_18_CustAnaIn_Typ18 |  | 10008593
[8 empty] | 10000838 | Para_Custom_AnalogIn_18_Hystereses | Para_Custom_AnalogIn_18_Hystereses | 2062 | Para_Custom_AnalogIn_18_Hystereses |  | 10000838
[8 empty] | 10000867 | Para_Custom_AnalogIn_18_LimitHi | Para_Custom_AnalogIn_18_LimitHi | 2063 | Para_Custom_AnalogIn_18_LimitHi |  | 10000867
[8 empty] | 10002845 | Para_Custom_AnalogIn_18_LimitHiHi | Para_Custom_AnalogIn_18_LimitHiHi | 2064 | Para_Custom_AnalogIn_18_LimitHiHi |  | 10002845
[8 empty] | 10000895 | Para_Custom_AnalogIn_18_LimitLo | Para_Custom_AnalogIn_18_LimitLo | 2065 | Para_Custom_AnalogIn_18_LimitLo |  | 10000895
[8 empty] | 10002846 | Para_Custom_AnalogIn_18_LimitLoLo | Para_Custom_AnalogIn_18_LimitLoLo | 2066 | Para_Custom_AnalogIn_18_LimitLoLo |  | 10002846
[8 empty] | 10000919 | Para_Custom_AnalogIn_18_ScaleMax | Para_Custom_AnalogIn_18_ScaleMax | 2067 | Para_Custom_AnalogIn_18_ScaleMax |  | 10000919
[8 empty] | 10000932 | Para_Custom_AnalogIn_18_ScaleMin | Para_Custom_AnalogIn_18_ScaleMin | 2068 | Para_Custom_AnalogIn_18_ScaleMin |  | 10000932
[8 empty] | 10000153 | Para_Custom_AnalogIn_19_CustAnaIn_Active19 | Para_Custom_AnalogIn_19_CustAnaIn_Active19 | 2069 | Para_Custom_AnalogIn_19_CustAnaIn_Active19 |  | 10000153
[8 empty] | 10000719 | Para_Custom_AnalogIn_19_CustAnaIn_MinMaxActive19 | Para_Custom_AnalogIn_19_CustAnaIn_MinMaxActive19 | 2070 | Para_Custom_AnalogIn_19_CustAnaIn_MinMaxActive19 |  | 10000719
[8 empty] | 10001162 | Para_Custom_AnalogIn_19_CustAnaIn_Set4mA19 | Para_Custom_AnalogIn_19_CustAnaIn_Set4mA19 | 2071 | Para_Custom_AnalogIn_19_CustAnaIn_Set4mA19 |  | 10001162
[8 empty] | 10008596 | Para_Custom_AnalogIn_19_CustAnaIn_Typ19 | Para_Custom_AnalogIn_19_CustAnaIn_Typ19 | 2072 | Para_Custom_AnalogIn_19_CustAnaIn_Typ19 |  | 10008596
[8 empty] | 10000840 | Para_Custom_AnalogIn_19_Hystereses | Para_Custom_AnalogIn_19_Hystereses | 2073 | Para_Custom_AnalogIn_19_Hystereses |  | 10000840
[8 empty] | 10000871 | Para_Custom_AnalogIn_19_LimitHi | Para_Custom_AnalogIn_19_LimitHi | 2074 | Para_Custom_AnalogIn_19_LimitHi |  | 10000871
[8 empty] | 10002852 | Para_Custom_AnalogIn_19_LimitHiHi | Para_Custom_AnalogIn_19_LimitHiHi | 2075 | Para_Custom_AnalogIn_19_LimitHiHi |  | 10002852
[8 empty] | 10000901 | Para_Custom_AnalogIn_19_LimitLo | Para_Custom_AnalogIn_19_LimitLo | 2076 | Para_Custom_AnalogIn_19_LimitLo |  | 10000901
[8 empty] | 10002860 | Para_Custom_AnalogIn_19_LimitLoLo | Para_Custom_AnalogIn_19_LimitLoLo | 2077 | Para_Custom_AnalogIn_19_LimitLoLo |  | 10002860
[8 empty] | 10000924 | Para_Custom_AnalogIn_19_ScaleMax | Para_Custom_AnalogIn_19_ScaleMax | 2078 | Para_Custom_AnalogIn_19_ScaleMax |  | 10000924
[8 empty] | 10000935 | Para_Custom_AnalogIn_19_ScaleMin | Para_Custom_AnalogIn_19_ScaleMin | 2079 | Para_Custom_AnalogIn_19_ScaleMin |  | 10000935
[8 empty] | 10000708 | Para_Custom_AnalogIn_1_CustAnaIn_MinMaxActive1 | Para_Custom_AnalogIn_1_CustAnaIn_MinMaxActive1 | 2080 | Para_Custom_AnalogIn_1_CustAnaIn_MinMaxActive1 |  | 10000708
[8 empty] | 10008501 | Para_Custom_AnalogIn_1_CustAnaIn_Typ1 | Para_Custom_AnalogIn_1_CustAnaIn_Typ1 | 2081 | Para_Custom_AnalogIn_1_CustAnaIn_Typ1 |  | 10008501
[8 empty] | 10000830 | Para_Custom_AnalogIn_1_Hystereses | Para_Custom_AnalogIn_1_Hystereses | 2082 | Para_Custom_AnalogIn_1_Hystereses |  | 10000830
[8 empty] | 10000859 | Para_Custom_AnalogIn_1_LimitHi | Para_Custom_AnalogIn_1_LimitHi | 2083 | Para_Custom_AnalogIn_1_LimitHi |  | 10000859
[8 empty] | 10000062 | Para_Custom_AnalogIn_1_LimitHiHi | Para_Custom_AnalogIn_1_LimitHiHi | 2084 | Para_Custom_AnalogIn_1_LimitHiHi |  | 10000062
[8 empty] | 10000890 | Para_Custom_AnalogIn_1_LimitLo | Para_Custom_AnalogIn_1_LimitLo | 2085 | Para_Custom_AnalogIn_1_LimitLo |  | 10000890
[8 empty] | 10000065 | Para_Custom_AnalogIn_1_LimitLoLo | Para_Custom_AnalogIn_1_LimitLoLo | 2086 | Para_Custom_AnalogIn_1_LimitLoLo |  | 10000065
[8 empty] | 10000155 | Para_Custom_AnalogIn_20_CustAnaIn_Active20 | Para_Custom_AnalogIn_20_CustAnaIn_Active20 | 2087 | Para_Custom_AnalogIn_20_CustAnaIn_Active20 |  | 10000155
[8 empty] | 10000720 | Para_Custom_AnalogIn_20_CustAnaIn_MinMaxActive20 | Para_Custom_AnalogIn_20_CustAnaIn_MinMaxActive20 | 2088 | Para_Custom_AnalogIn_20_CustAnaIn_MinMaxActive20 |  | 10000720
[8 empty] | 10001165 | Para_Custom_AnalogIn_20_CustAnaIn_Set4mA20 | Para_Custom_AnalogIn_20_CustAnaIn_Set4mA20 | 2089 | Para_Custom_AnalogIn_20_CustAnaIn_Set4mA20 |  | 10001165
[8 empty] | 10008602 | Para_Custom_AnalogIn_20_CustAnaIn_Typ20 | Para_Custom_AnalogIn_20_CustAnaIn_Typ20 | 2090 | Para_Custom_AnalogIn_20_CustAnaIn_Typ20 |  | 10008602
[8 empty] | 10000839 | Para_Custom_AnalogIn_20_Hystereses | Para_Custom_AnalogIn_20_Hystereses | 2091 | Para_Custom_AnalogIn_20_Hystereses |  | 10000839
[8 empty] | 10000869 | Para_Custom_AnalogIn_20_LimitHi | Para_Custom_AnalogIn_20_LimitHi | 2092 | Para_Custom_AnalogIn_20_LimitHi |  | 10000869
[8 empty] | 10002847 | Para_Custom_AnalogIn_20_LimitHiHi | Para_Custom_AnalogIn_20_LimitHiHi | 2093 | Para_Custom_AnalogIn_20_LimitHiHi |  | 10002847
[8 empty] | 10000899 | Para_Custom_AnalogIn_20_LimitLo | Para_Custom_AnalogIn_20_LimitLo | 2094 | Para_Custom_AnalogIn_20_LimitLo |  | 10000899
[8 empty] | 10002856 | Para_Custom_AnalogIn_20_LimitLoLo | Para_Custom_AnalogIn_20_LimitLoLo | 2095 | Para_Custom_AnalogIn_20_LimitLoLo |  | 10002856
[8 empty] | 10000918 | Para_Custom_AnalogIn_20_ScaleMax | Para_Custom_AnalogIn_20_ScaleMax | 2096 | Para_Custom_AnalogIn_20_ScaleMax |  | 10000918
[8 empty] | 10000937 | Para_Custom_AnalogIn_20_ScaleMin | Para_Custom_AnalogIn_20_ScaleMin | 2097 | Para_Custom_AnalogIn_20_ScaleMin |  | 10000937
[8 empty] | 10000156 | Para_Custom_AnalogIn_21_CustAnaIn_Active21 | Para_Custom_AnalogIn_21_CustAnaIn_Active21 | 2098 | Para_Custom_AnalogIn_21_CustAnaIn_Active21 |  | 10000156
[8 empty] | 10000722 | Para_Custom_AnalogIn_21_CustAnaIn_MinMaxActive21 | Para_Custom_AnalogIn_21_CustAnaIn_MinMaxActive21 | 2099 | Para_Custom_AnalogIn_21_CustAnaIn_MinMaxActive21 |  | 10000722
[8 empty] | 10001164 | Para_Custom_AnalogIn_21_CustAnaIn_Set4mA21 | Para_Custom_AnalogIn_21_CustAnaIn_Set4mA21 | 2100 | Para_Custom_AnalogIn_21_CustAnaIn_Set4mA21 |  | 10001164
[8 empty] | 10008601 | Para_Custom_AnalogIn_21_CustAnaIn_Typ21 | Para_Custom_AnalogIn_21_CustAnaIn_Typ21 | 2101 | Para_Custom_AnalogIn_21_CustAnaIn_Typ21 |  | 10008601
[8 empty] | 10000845 | Para_Custom_AnalogIn_21_Hystereses | Para_Custom_AnalogIn_21_Hystereses | 2102 | Para_Custom_AnalogIn_21_Hystereses |  | 10000845
[8 empty] | 10000873 | Para_Custom_AnalogIn_21_LimitHi | Para_Custom_AnalogIn_21_LimitHi | 2103 | Para_Custom_AnalogIn_21_LimitHi |  | 10000873
[8 empty] | 10002855 | Para_Custom_AnalogIn_21_LimitHiHi | Para_Custom_AnalogIn_21_LimitHiHi | 2104 | Para_Custom_AnalogIn_21_LimitHiHi |  | 10002855
[8 empty] | 10000902 | Para_Custom_AnalogIn_21_LimitLo | Para_Custom_AnalogIn_21_LimitLo | 2105 | Para_Custom_AnalogIn_21_LimitLo |  | 10000902
[8 empty] | 10002866 | Para_Custom_AnalogIn_21_LimitLoLo | Para_Custom_AnalogIn_21_LimitLoLo | 2106 | Para_Custom_AnalogIn_21_LimitLoLo |  | 10002866
[8 empty] | 10000922 | Para_Custom_AnalogIn_21_ScaleMax | Para_Custom_AnalogIn_21_ScaleMax | 2107 | Para_Custom_AnalogIn_21_ScaleMax |  | 10000922
[8 empty] | 10000938 | Para_Custom_AnalogIn_21_ScaleMin | Para_Custom_AnalogIn_21_ScaleMin | 2108 | Para_Custom_AnalogIn_21_ScaleMin |  | 10000938
[8 empty] | 10000158 | Para_Custom_AnalogIn_22_CustAnaIn_Active22 | Para_Custom_AnalogIn_22_CustAnaIn_Active22 | 2109 | Para_Custom_AnalogIn_22_CustAnaIn_Active22 |  | 10000158
[8 empty] | 10000726 | Para_Custom_AnalogIn_22_CustAnaIn_MinMaxActive22 | Para_Custom_AnalogIn_22_CustAnaIn_MinMaxActive22 | 2110 | Para_Custom_AnalogIn_22_CustAnaIn_MinMaxActive22 |  | 10000726
[8 empty] | 10001160 | Para_Custom_AnalogIn_22_CustAnaIn_Set4mA22 | Para_Custom_AnalogIn_22_CustAnaIn_Set4mA22 | 2111 | Para_Custom_AnalogIn_22_CustAnaIn_Set4mA22 |  | 10001160
[8 empty] | 10008600 | Para_Custom_AnalogIn_22_CustAnaIn_Typ22 | Para_Custom_AnalogIn_22_CustAnaIn_Typ22 | 2112 | Para_Custom_AnalogIn_22_CustAnaIn_Typ22 |  | 10008600
[8 empty] | 10000842 | Para_Custom_AnalogIn_22_Hystereses | Para_Custom_AnalogIn_22_Hystereses | 2113 | Para_Custom_AnalogIn_22_Hystereses |  | 10000842
[8 empty] | 10000874 | Para_Custom_AnalogIn_22_LimitHi | Para_Custom_AnalogIn_22_LimitHi | 2114 | Para_Custom_AnalogIn_22_LimitHi |  | 10000874
[8 empty] | 10002859 | Para_Custom_AnalogIn_22_LimitHiHi | Para_Custom_AnalogIn_22_LimitHiHi | 2115 | Para_Custom_AnalogIn_22_LimitHiHi |  | 10002859
[8 empty] | 10000900 | Para_Custom_AnalogIn_22_LimitLo | Para_Custom_AnalogIn_22_LimitLo | 2116 | Para_Custom_AnalogIn_22_LimitLo |  | 10000900
[8 empty] | 10002861 | Para_Custom_AnalogIn_22_LimitLoLo | Para_Custom_AnalogIn_22_LimitLoLo | 2117 | Para_Custom_AnalogIn_22_LimitLoLo |  | 10002861
[8 empty] | 10000925 | Para_Custom_AnalogIn_22_ScaleMax | Para_Custom_AnalogIn_22_ScaleMax | 2118 | Para_Custom_AnalogIn_22_ScaleMax |  | 10000925
[8 empty] | 10000936 | Para_Custom_AnalogIn_22_ScaleMin | Para_Custom_AnalogIn_22_ScaleMin | 2119 | Para_Custom_AnalogIn_22_ScaleMin |  | 10000936
[8 empty] | 10000662 | Para_Custom_AnalogIn_23_CustAnaIn_Active23 | Para_Custom_AnalogIn_23_CustAnaIn_Active23 | 2120 | Para_Custom_AnalogIn_23_CustAnaIn_Active23 |  | 10000662
[8 empty] | 10000724 | Para_Custom_AnalogIn_23_CustAnaIn_MinMaxActive23 | Para_Custom_AnalogIn_23_CustAnaIn_MinMaxActive23 | 2121 | Para_Custom_AnalogIn_23_CustAnaIn_MinMaxActive23 |  | 10000724
[8 empty] | 10001158 | Para_Custom_AnalogIn_23_CustAnaIn_Set4mA23 | Para_Custom_AnalogIn_23_CustAnaIn_Set4mA23 | 2122 | Para_Custom_AnalogIn_23_CustAnaIn_Set4mA23 |  | 10001158
[8 empty] | 10008605 | Para_Custom_AnalogIn_23_CustAnaIn_Typ23 | Para_Custom_AnalogIn_23_CustAnaIn_Typ23 | 2123 | Para_Custom_AnalogIn_23_CustAnaIn_Typ23 |  | 10008605
[8 empty] | 10000844 | Para_Custom_AnalogIn_23_Hystereses | Para_Custom_AnalogIn_23_Hystereses | 2124 | Para_Custom_AnalogIn_23_Hystereses |  | 10000844
[8 empty] | 10000872 | Para_Custom_AnalogIn_23_LimitHi | Para_Custom_AnalogIn_23_LimitHi | 2125 | Para_Custom_AnalogIn_23_LimitHi |  | 10000872
[8 empty] | 10002869 | Para_Custom_AnalogIn_23_LimitHiHi | Para_Custom_AnalogIn_23_LimitHiHi | 2126 | Para_Custom_AnalogIn_23_LimitHiHi |  | 10002869
[8 empty] | 10000906 | Para_Custom_AnalogIn_23_LimitLo | Para_Custom_AnalogIn_23_LimitLo | 2127 | Para_Custom_AnalogIn_23_LimitLo |  | 10000906
[8 empty] | 10002871 | Para_Custom_AnalogIn_23_LimitLoLo | Para_Custom_AnalogIn_23_LimitLoLo | 2128 | Para_Custom_AnalogIn_23_LimitLoLo |  | 10002871
[8 empty] | 10000923 | Para_Custom_AnalogIn_23_ScaleMax | Para_Custom_AnalogIn_23_ScaleMax | 2129 | Para_Custom_AnalogIn_23_ScaleMax |  | 10000923
[8 empty] | 10000939 | Para_Custom_AnalogIn_23_ScaleMin | Para_Custom_AnalogIn_23_ScaleMin | 2130 | Para_Custom_AnalogIn_23_ScaleMin |  | 10000939
[8 empty] | 10000682 | Para_Custom_AnalogIn_24_CustAnaIn_Active24 | Para_Custom_AnalogIn_24_CustAnaIn_Active24 | 2131 | Para_Custom_AnalogIn_24_CustAnaIn_Active24 |  | 10000682
[8 empty] | 10000805 | Para_Custom_AnalogIn_24_CustAnaIn_MinMaxActive24 | Para_Custom_AnalogIn_24_CustAnaIn_MinMaxActive24 | 2132 | Para_Custom_AnalogIn_24_CustAnaIn_MinMaxActive24 |  | 10000805
[8 empty] | 10001157 | Para_Custom_AnalogIn_24_CustAnaIn_Set4mA24 | Para_Custom_AnalogIn_24_CustAnaIn_Set4mA24 | 2133 | Para_Custom_AnalogIn_24_CustAnaIn_Set4mA24 |  | 10001157
[8 empty] | 10008606 | Para_Custom_AnalogIn_24_CustAnaIn_Typ24 | Para_Custom_AnalogIn_24_CustAnaIn_Typ24 | 2134 | Para_Custom_AnalogIn_24_CustAnaIn_Typ24 |  | 10008606
[8 empty] | 10000843 | Para_Custom_AnalogIn_24_Hystereses | Para_Custom_AnalogIn_24_Hystereses | 2135 | Para_Custom_AnalogIn_24_Hystereses |  | 10000843
[8 empty] | 10000875 | Para_Custom_AnalogIn_24_LimitHi | Para_Custom_AnalogIn_24_LimitHi | 2136 | Para_Custom_AnalogIn_24_LimitHi |  | 10000875
[8 empty] | 10002870 | Para_Custom_AnalogIn_24_LimitHiHi | Para_Custom_AnalogIn_24_LimitHiHi | 2137 | Para_Custom_AnalogIn_24_LimitHiHi |  | 10002870
[8 empty] | 10000905 | Para_Custom_AnalogIn_24_LimitLo | Para_Custom_AnalogIn_24_LimitLo | 2138 | Para_Custom_AnalogIn_24_LimitLo |  | 10000905
[8 empty] | 10002868 | Para_Custom_AnalogIn_24_LimitLoLo | Para_Custom_AnalogIn_24_LimitLoLo | 2139 | Para_Custom_AnalogIn_24_LimitLoLo |  | 10002868
[8 empty] | 10000926 | Para_Custom_AnalogIn_24_ScaleMax | Para_Custom_AnalogIn_24_ScaleMax | 2140 | Para_Custom_AnalogIn_24_ScaleMax |  | 10000926
[8 empty] | 10000943 | Para_Custom_AnalogIn_24_ScaleMin | Para_Custom_AnalogIn_24_ScaleMin | 2141 | Para_Custom_AnalogIn_24_ScaleMin |  | 10000943
[8 empty] | 10000702 | Para_Custom_AnalogIn_25_CustAnaIn_Active25 | Para_Custom_AnalogIn_25_CustAnaIn_Active25 | 2142 | Para_Custom_AnalogIn_25_CustAnaIn_Active25 |  | 10000702
[8 empty] | 10000988 | Para_Custom_AnalogIn_25_CustAnaIn_MinMaxActive25 | Para_Custom_AnalogIn_25_CustAnaIn_MinMaxActive25 | 2143 | Para_Custom_AnalogIn_25_CustAnaIn_MinMaxActive25 |  | 10000988
[8 empty] | 10001155 | Para_Custom_AnalogIn_25_CustAnaIn_Set4mA25 | Para_Custom_AnalogIn_25_CustAnaIn_Set4mA25 | 2144 | Para_Custom_AnalogIn_25_CustAnaIn_Set4mA25 |  | 10001155
[8 empty] | 10008603 | Para_Custom_AnalogIn_25_CustAnaIn_Typ25 | Para_Custom_AnalogIn_25_CustAnaIn_Typ25 | 2145 | Para_Custom_AnalogIn_25_CustAnaIn_Typ25 |  | 10008603
[8 empty] | 10000847 | Para_Custom_AnalogIn_25_Hystereses | Para_Custom_AnalogIn_25_Hystereses | 2146 | Para_Custom_AnalogIn_25_Hystereses |  | 10000847
[8 empty] | 10000877 | Para_Custom_AnalogIn_25_LimitHi | Para_Custom_AnalogIn_25_LimitHi | 2147 | Para_Custom_AnalogIn_25_LimitHi |  | 10000877
[8 empty] | 10002878 | Para_Custom_AnalogIn_25_LimitHiHi | Para_Custom_AnalogIn_25_LimitHiHi | 2148 | Para_Custom_AnalogIn_25_LimitHiHi |  | 10002878
[8 empty] | 10000907 | Para_Custom_AnalogIn_25_LimitLo | Para_Custom_AnalogIn_25_LimitLo | 2149 | Para_Custom_AnalogIn_25_LimitLo |  | 10000907
[8 empty] | 10002876 | Para_Custom_AnalogIn_25_LimitLoLo | Para_Custom_AnalogIn_25_LimitLoLo | 2150 | Para_Custom_AnalogIn_25_LimitLoLo |  | 10002876
[8 empty] | 10000927 | Para_Custom_AnalogIn_25_ScaleMax | Para_Custom_AnalogIn_25_ScaleMax | 2151 | Para_Custom_AnalogIn_25_ScaleMax |  | 10000927
[8 empty] | 10000940 | Para_Custom_AnalogIn_25_ScaleMin | Para_Custom_AnalogIn_25_ScaleMin | 2152 | Para_Custom_AnalogIn_25_ScaleMin |  | 10000940
[8 empty] | 10000704 | Para_Custom_AnalogIn_26_CustAnaIn_Active26 | Para_Custom_AnalogIn_26_CustAnaIn_Active26 | 2153 | Para_Custom_AnalogIn_26_CustAnaIn_Active26 |  | 10000704
[8 empty] | 10000996 | Para_Custom_AnalogIn_26_CustAnaIn_MinMaxActive26 | Para_Custom_AnalogIn_26_CustAnaIn_MinMaxActive26 | 2154 | Para_Custom_AnalogIn_26_CustAnaIn_MinMaxActive26 |  | 10000996
[8 empty] | 10001141 | Para_Custom_AnalogIn_26_CustAnaIn_Set4mA26 | Para_Custom_AnalogIn_26_CustAnaIn_Set4mA26 | 2155 | Para_Custom_AnalogIn_26_CustAnaIn_Set4mA26 |  | 10001141
[8 empty] | 10008604 | Para_Custom_AnalogIn_26_CustAnaIn_Typ26 | Para_Custom_AnalogIn_26_CustAnaIn_Typ26 | 2156 | Para_Custom_AnalogIn_26_CustAnaIn_Typ26 |  | 10008604
[8 empty] | 10000848 | Para_Custom_AnalogIn_26_Hystereses | Para_Custom_AnalogIn_26_Hystereses | 2157 | Para_Custom_AnalogIn_26_Hystereses |  | 10000848
[8 empty] | 10000876 | Para_Custom_AnalogIn_26_LimitHi | Para_Custom_AnalogIn_26_LimitHi | 2158 | Para_Custom_AnalogIn_26_LimitHi |  | 10000876
[8 empty] | 10002875 | Para_Custom_AnalogIn_26_LimitHiHi | Para_Custom_AnalogIn_26_LimitHiHi | 2159 | Para_Custom_AnalogIn_26_LimitHiHi |  | 10002875
[8 empty] | 10000904 | Para_Custom_AnalogIn_26_LimitLo | Para_Custom_AnalogIn_26_LimitLo | 2160 | Para_Custom_AnalogIn_26_LimitLo |  | 10000904
[8 empty] | 10002880 | Para_Custom_AnalogIn_26_LimitLoLo | Para_Custom_AnalogIn_26_LimitLoLo | 2161 | Para_Custom_AnalogIn_26_LimitLoLo |  | 10002880
[8 empty] | 10000928 | Para_Custom_AnalogIn_26_ScaleMax | Para_Custom_AnalogIn_26_ScaleMax | 2162 | Para_Custom_AnalogIn_26_ScaleMax |  | 10000928
[8 empty] | 10000941 | Para_Custom_AnalogIn_26_ScaleMin | Para_Custom_AnalogIn_26_ScaleMin | 2163 | Para_Custom_AnalogIn_26_ScaleMin |  | 10000941
[8 empty] | 10000706 | Para_Custom_AnalogIn_27_CustAnaIn_Active27 | Para_Custom_AnalogIn_27_CustAnaIn_Active27 | 2164 | Para_Custom_AnalogIn_27_CustAnaIn_Active27 |  | 10000706
[8 empty] | 10000992 | Para_Custom_AnalogIn_27_CustAnaIn_MinMaxActive27 | Para_Custom_AnalogIn_27_CustAnaIn_MinMaxActive27 | 2165 | Para_Custom_AnalogIn_27_CustAnaIn_MinMaxActive27 |  | 10000992
[8 empty] | 10001159 | Para_Custom_AnalogIn_27_CustAnaIn_Set4mA27 | Para_Custom_AnalogIn_27_CustAnaIn_Set4mA27 | 2166 | Para_Custom_AnalogIn_27_CustAnaIn_Set4mA27 |  | 10001159
[8 empty] | 10008608 | Para_Custom_AnalogIn_27_CustAnaIn_Typ27 | Para_Custom_AnalogIn_27_CustAnaIn_Typ27 | 2167 | Para_Custom_AnalogIn_27_CustAnaIn_Typ27 |  | 10008608
[8 empty] | 10000846 | Para_Custom_AnalogIn_27_Hystereses | Para_Custom_AnalogIn_27_Hystereses | 2168 | Para_Custom_AnalogIn_27_Hystereses |  | 10000846
[8 empty] | 10000878 | Para_Custom_AnalogIn_27_LimitHi | Para_Custom_AnalogIn_27_LimitHi | 2169 | Para_Custom_AnalogIn_27_LimitHi |  | 10000878
[8 empty] | 10002886 | Para_Custom_AnalogIn_27_LimitHiHi | Para_Custom_AnalogIn_27_LimitHiHi | 2170 | Para_Custom_AnalogIn_27_LimitHiHi |  | 10002886
[8 empty] | 10000908 | Para_Custom_AnalogIn_27_LimitLo | Para_Custom_AnalogIn_27_LimitLo | 2171 | Para_Custom_AnalogIn_27_LimitLo |  | 10000908
[8 empty] | 10002888 | Para_Custom_AnalogIn_27_LimitLoLo | Para_Custom_AnalogIn_27_LimitLoLo | 2172 | Para_Custom_AnalogIn_27_LimitLoLo |  | 10002888
[8 empty] | 10000929 | Para_Custom_AnalogIn_27_ScaleMax | Para_Custom_AnalogIn_27_ScaleMax | 2173 | Para_Custom_AnalogIn_27_ScaleMax |  | 10000929
[8 empty] | 10000944 | Para_Custom_AnalogIn_27_ScaleMin | Para_Custom_AnalogIn_27_ScaleMin | 2174 | Para_Custom_AnalogIn_27_ScaleMin |  | 10000944
[8 empty] | 10000705 | Para_Custom_AnalogIn_28_CustAnaIn_Active28 | Para_Custom_AnalogIn_28_CustAnaIn_Active28 | 2175 | Para_Custom_AnalogIn_28_CustAnaIn_Active28 |  | 10000705
[8 empty] | 10000999 | Para_Custom_AnalogIn_28_CustAnaIn_MinMaxActive28 | Para_Custom_AnalogIn_28_CustAnaIn_MinMaxActive28 | 2176 | Para_Custom_AnalogIn_28_CustAnaIn_MinMaxActive28 |  | 10000999
[8 empty] | 10001151 | Para_Custom_AnalogIn_28_CustAnaIn_Set4mA28 | Para_Custom_AnalogIn_28_CustAnaIn_Set4mA28 | 2177 | Para_Custom_AnalogIn_28_CustAnaIn_Set4mA28 |  | 10001151
[8 empty] | 10008607 | Para_Custom_AnalogIn_28_CustAnaIn_Typ28 | Para_Custom_AnalogIn_28_CustAnaIn_Typ28 | 2178 | Para_Custom_AnalogIn_28_CustAnaIn_Typ28 |  | 10008607
[8 empty] | 10000849 | Para_Custom_AnalogIn_28_Hystereses | Para_Custom_AnalogIn_28_Hystereses | 2179 | Para_Custom_AnalogIn_28_Hystereses |  | 10000849
[8 empty] | 10000882 | Para_Custom_AnalogIn_28_LimitHi | Para_Custom_AnalogIn_28_LimitHi | 2180 | Para_Custom_AnalogIn_28_LimitHi |  | 10000882
[8 empty] | 10002884 | Para_Custom_AnalogIn_28_LimitHiHi | Para_Custom_AnalogIn_28_LimitHiHi | 2181 | Para_Custom_AnalogIn_28_LimitHiHi |  | 10002884
[8 empty] | 10000909 | Para_Custom_AnalogIn_28_LimitLo | Para_Custom_AnalogIn_28_LimitLo | 2182 | Para_Custom_AnalogIn_28_LimitLo |  | 10000909
[8 empty] | 10002883 | Para_Custom_AnalogIn_28_LimitLoLo | Para_Custom_AnalogIn_28_LimitLoLo | 2183 | Para_Custom_AnalogIn_28_LimitLoLo |  | 10002883
[8 empty] | 10000931 | Para_Custom_AnalogIn_28_ScaleMax | Para_Custom_AnalogIn_28_ScaleMax | 2184 | Para_Custom_AnalogIn_28_ScaleMax |  | 10000931
[8 empty] | 10000947 | Para_Custom_AnalogIn_28_ScaleMin | Para_Custom_AnalogIn_28_ScaleMin | 2185 | Para_Custom_AnalogIn_28_ScaleMin |  | 10000947
[8 empty] | 10000707 | Para_Custom_AnalogIn_29_CustAnaIn_Active29 | Para_Custom_AnalogIn_29_CustAnaIn_Active29 | 2186 | Para_Custom_AnalogIn_29_CustAnaIn_Active29 |  | 10000707
[8 empty] | 10000994 | Para_Custom_AnalogIn_29_CustAnaIn_MinMaxActive29 | Para_Custom_AnalogIn_29_CustAnaIn_MinMaxActive29 | 2187 | Para_Custom_AnalogIn_29_CustAnaIn_MinMaxActive29 |  | 10000994
[8 empty] | 10001154 | Para_Custom_AnalogIn_29_CustAnaIn_Set4mA29 | Para_Custom_AnalogIn_29_CustAnaIn_Set4mA29 | 2188 | Para_Custom_AnalogIn_29_CustAnaIn_Set4mA29 |  | 10001154
[8 empty] | 10008609 | Para_Custom_AnalogIn_29_CustAnaIn_Typ29 | Para_Custom_AnalogIn_29_CustAnaIn_Typ29 | 2189 | Para_Custom_AnalogIn_29_CustAnaIn_Typ29 |  | 10008609
[8 empty] | 10000850 | Para_Custom_AnalogIn_29_Hystereses | Para_Custom_AnalogIn_29_Hystereses | 2190 | Para_Custom_AnalogIn_29_Hystereses |  | 10000850
[8 empty] | 10000880 | Para_Custom_AnalogIn_29_LimitHi | Para_Custom_AnalogIn_29_LimitHi | 2191 | Para_Custom_AnalogIn_29_LimitHi |  | 10000880
[8 empty] | 10002891 | Para_Custom_AnalogIn_29_LimitHiHi | Para_Custom_AnalogIn_29_LimitHiHi | 2192 | Para_Custom_AnalogIn_29_LimitHiHi |  | 10002891
[8 empty] | 10000915 | Para_Custom_AnalogIn_29_LimitLo | Para_Custom_AnalogIn_29_LimitLo | 2193 | Para_Custom_AnalogIn_29_LimitLo |  | 10000915
[8 empty] | 10002893 | Para_Custom_AnalogIn_29_LimitLoLo | Para_Custom_AnalogIn_29_LimitLoLo | 2194 | Para_Custom_AnalogIn_29_LimitLoLo |  | 10002893
[8 empty] | 10000930 | Para_Custom_AnalogIn_29_ScaleMax | Para_Custom_AnalogIn_29_ScaleMax | 2195 | Para_Custom_AnalogIn_29_ScaleMax |  | 10000930
[8 empty] | 10000942 | Para_Custom_AnalogIn_29_ScaleMin | Para_Custom_AnalogIn_29_ScaleMin | 2196 | Para_Custom_AnalogIn_29_ScaleMin |  | 10000942
[8 empty] | 10000721 | Para_Custom_AnalogIn_2_CustAnaIn_MinMaxActive2 | Para_Custom_AnalogIn_2_CustAnaIn_MinMaxActive2 | 2197 | Para_Custom_AnalogIn_2_CustAnaIn_MinMaxActive2 |  | 10000721
[8 empty] | 10008599 | Para_Custom_AnalogIn_2_CustAnaIn_Typ2 | Para_Custom_AnalogIn_2_CustAnaIn_Typ2 | 2198 | Para_Custom_AnalogIn_2_CustAnaIn_Typ2 |  | 10008599
[8 empty] | 10000841 | Para_Custom_AnalogIn_2_Hystereses | Para_Custom_AnalogIn_2_Hystereses | 2199 | Para_Custom_AnalogIn_2_Hystereses |  | 10000841
[8 empty] | 10000870 | Para_Custom_AnalogIn_2_LimitHi | Para_Custom_AnalogIn_2_LimitHi | 2200 | Para_Custom_AnalogIn_2_LimitHi |  | 10000870
[8 empty] | 10000063 | Para_Custom_AnalogIn_2_LimitHiHi | Para_Custom_AnalogIn_2_LimitHiHi | 2201 | Para_Custom_AnalogIn_2_LimitHiHi |  | 10000063
[8 empty] | 10000903 | Para_Custom_AnalogIn_2_LimitLo | Para_Custom_AnalogIn_2_LimitLo | 2202 | Para_Custom_AnalogIn_2_LimitLo |  | 10000903
[8 empty] | 10000061 | Para_Custom_AnalogIn_2_LimitLoLo | Para_Custom_AnalogIn_2_LimitLoLo | 2203 | Para_Custom_AnalogIn_2_LimitLoLo |  | 10000061
[8 empty] | 10000703 | Para_Custom_AnalogIn_30_CustAnaIn_Active30 | Para_Custom_AnalogIn_30_CustAnaIn_Active30 | 2204 | Para_Custom_AnalogIn_30_CustAnaIn_Active30 |  | 10000703
[8 empty] | 10000998 | Para_Custom_AnalogIn_30_CustAnaIn_MinMaxActive30 | Para_Custom_AnalogIn_30_CustAnaIn_MinMaxActive30 | 2205 | Para_Custom_AnalogIn_30_CustAnaIn_MinMaxActive30 |  | 10000998
[8 empty] | 10001156 | Para_Custom_AnalogIn_30_CustAnaIn_Set4mA30 | Para_Custom_AnalogIn_30_CustAnaIn_Set4mA30 | 2206 | Para_Custom_AnalogIn_30_CustAnaIn_Set4mA30 |  | 10001156
[8 empty] | 10008612 | Para_Custom_AnalogIn_30_CustAnaIn_Typ30 | Para_Custom_AnalogIn_30_CustAnaIn_Typ30 | 2207 | Para_Custom_AnalogIn_30_CustAnaIn_Typ30 |  | 10008612
[8 empty] | 10000851 | Para_Custom_AnalogIn_30_Hystereses | Para_Custom_AnalogIn_30_Hystereses | 2208 | Para_Custom_AnalogIn_30_Hystereses |  | 10000851
[8 empty] | 10000881 | Para_Custom_AnalogIn_30_LimitHi | Para_Custom_AnalogIn_30_LimitHi | 2209 | Para_Custom_AnalogIn_30_LimitHi |  | 10000881
[8 empty] | 10002894 | Para_Custom_AnalogIn_30_LimitHiHi | Para_Custom_AnalogIn_30_LimitHiHi | 2210 | Para_Custom_AnalogIn_30_LimitHiHi |  | 10002894
[8 empty] | 10000912 | Para_Custom_AnalogIn_30_LimitLo | Para_Custom_AnalogIn_30_LimitLo | 2211 | Para_Custom_AnalogIn_30_LimitLo |  | 10000912
[8 empty] | 10002896 | Para_Custom_AnalogIn_30_LimitLoLo | Para_Custom_AnalogIn_30_LimitLoLo | 2212 | Para_Custom_AnalogIn_30_LimitLoLo |  | 10002896
[8 empty] | 10000933 | Para_Custom_AnalogIn_30_ScaleMax | Para_Custom_AnalogIn_30_ScaleMax | 2213 | Para_Custom_AnalogIn_30_ScaleMax |  | 10000933
[8 empty] | 10000946 | Para_Custom_AnalogIn_30_ScaleMin | Para_Custom_AnalogIn_30_ScaleMin | 2214 | Para_Custom_AnalogIn_30_ScaleMin |  | 10000946
[8 empty] | 10001215 | Para_Custom_AnalogIn_31_CustAnaIn_Active31 | Para_Custom_AnalogIn_31_CustAnaIn_Active31 | 2215 | Para_Custom_AnalogIn_31_CustAnaIn_Active31 |  | 10001215
[8 empty] | 10001245 | Para_Custom_AnalogIn_31_CustAnaIn_MinMaxActive31 | Para_Custom_AnalogIn_31_CustAnaIn_MinMaxActive31 | 2216 | Para_Custom_AnalogIn_31_CustAnaIn_MinMaxActive31 |  | 10001245
[8 empty] | 10001150 | Para_Custom_AnalogIn_31_CustAnaIn_Set4mA31 | Para_Custom_AnalogIn_31_CustAnaIn_Set4mA31 | 2217 | Para_Custom_AnalogIn_31_CustAnaIn_Set4mA31 |  | 10001150
[8 empty] | 10008611 | Para_Custom_AnalogIn_31_CustAnaIn_Typ31 | Para_Custom_AnalogIn_31_CustAnaIn_Typ31 | 2218 | Para_Custom_AnalogIn_31_CustAnaIn_Typ31 |  | 10008611
[8 empty] | 10000147 | Para_Custom_AnalogIn_31_Hystereses | Para_Custom_AnalogIn_31_Hystereses | 2219 | Para_Custom_AnalogIn_31_Hystereses |  | 10000147
[8 empty] | 10000148 | Para_Custom_AnalogIn_31_LimitHi | Para_Custom_AnalogIn_31_LimitHi | 2220 | Para_Custom_AnalogIn_31_LimitHi |  | 10000148
[8 empty] | 10002902 | Para_Custom_AnalogIn_31_LimitHiHi | Para_Custom_AnalogIn_31_LimitHiHi | 2221 | Para_Custom_AnalogIn_31_LimitHiHi |  | 10002902
[8 empty] | 10000145 | Para_Custom_AnalogIn_31_LimitLo | Para_Custom_AnalogIn_31_LimitLo | 2222 | Para_Custom_AnalogIn_31_LimitLo |  | 10000145
[8 empty] | 10002897 | Para_Custom_AnalogIn_31_LimitLoLo | Para_Custom_AnalogIn_31_LimitLoLo | 2223 | Para_Custom_AnalogIn_31_LimitLoLo |  | 10002897
[8 empty] | 10000715 | Para_Custom_AnalogIn_31_ScaleMax | Para_Custom_AnalogIn_31_ScaleMax | 2224 | Para_Custom_AnalogIn_31_ScaleMax |  | 10000715
[8 empty] | 10000978 | Para_Custom_AnalogIn_31_ScaleMin | Para_Custom_AnalogIn_31_ScaleMin | 2225 | Para_Custom_AnalogIn_31_ScaleMin |  | 10000978
[8 empty] | 10001214 | Para_Custom_AnalogIn_32_CustAnaIn_Active32 | Para_Custom_AnalogIn_32_CustAnaIn_Active32 | 2226 | Para_Custom_AnalogIn_32_CustAnaIn_Active32 |  | 10001214
[8 empty] | 10001249 | Para_Custom_AnalogIn_32_CustAnaIn_MinMaxActive32 | Para_Custom_AnalogIn_32_CustAnaIn_MinMaxActive32 | 2227 | Para_Custom_AnalogIn_32_CustAnaIn_MinMaxActive32 |  | 10001249
[8 empty] | 10001152 | Para_Custom_AnalogIn_32_CustAnaIn_Set4mA32 | Para_Custom_AnalogIn_32_CustAnaIn_Set4mA32 | 2228 | Para_Custom_AnalogIn_32_CustAnaIn_Set4mA32 |  | 10001152
[8 empty] | 10008613 | Para_Custom_AnalogIn_32_CustAnaIn_Typ32 | Para_Custom_AnalogIn_32_CustAnaIn_Typ32 | 2229 | Para_Custom_AnalogIn_32_CustAnaIn_Typ32 |  | 10008613
[8 empty] | 10000981 | Para_Custom_AnalogIn_32_Hystereses | Para_Custom_AnalogIn_32_Hystereses | 2230 | Para_Custom_AnalogIn_32_Hystereses |  | 10000981
[8 empty] | 10000983 | Para_Custom_AnalogIn_32_LimitHi | Para_Custom_AnalogIn_32_LimitHi | 2231 | Para_Custom_AnalogIn_32_LimitHi |  | 10000983
[8 empty] | 10002903 | Para_Custom_AnalogIn_32_LimitHiHi | Para_Custom_AnalogIn_32_LimitHiHi | 2232 | Para_Custom_AnalogIn_32_LimitHiHi |  | 10002903
[8 empty] | 10000984 | Para_Custom_AnalogIn_32_LimitLo | Para_Custom_AnalogIn_32_LimitLo | 2233 | Para_Custom_AnalogIn_32_LimitLo |  | 10000984
[8 empty] | 10002906 | Para_Custom_AnalogIn_32_LimitLoLo | Para_Custom_AnalogIn_32_LimitLoLo | 2234 | Para_Custom_AnalogIn_32_LimitLoLo |  | 10002906
[8 empty] | 10000985 | Para_Custom_AnalogIn_32_ScaleMax | Para_Custom_AnalogIn_32_ScaleMax | 2235 | Para_Custom_AnalogIn_32_ScaleMax |  | 10000985
[8 empty] | 10000982 | Para_Custom_AnalogIn_32_ScaleMin | Para_Custom_AnalogIn_32_ScaleMin | 2236 | Para_Custom_AnalogIn_32_ScaleMin |  | 10000982
[8 empty] | 10001213 | Para_Custom_AnalogIn_33_CustAnaIn_Active33 | Para_Custom_AnalogIn_33_CustAnaIn_Active33 | 2237 | Para_Custom_AnalogIn_33_CustAnaIn_Active33 |  | 10001213
[8 empty] | 10001251 | Para_Custom_AnalogIn_33_CustAnaIn_MinMaxActive33 | Para_Custom_AnalogIn_33_CustAnaIn_MinMaxActive33 | 2238 | Para_Custom_AnalogIn_33_CustAnaIn_MinMaxActive33 |  | 10001251
[8 empty] | 10001153 | Para_Custom_AnalogIn_33_CustAnaIn_Set4mA33 | Para_Custom_AnalogIn_33_CustAnaIn_Set4mA33 | 2239 | Para_Custom_AnalogIn_33_CustAnaIn_Set4mA33 |  | 10001153
[8 empty] | 10008614 | Para_Custom_AnalogIn_33_CustAnaIn_Typ33 | Para_Custom_AnalogIn_33_CustAnaIn_Typ33 | 2240 | Para_Custom_AnalogIn_33_CustAnaIn_Typ33 |  | 10008614
[8 empty] | 10000987 | Para_Custom_AnalogIn_33_Hystereses | Para_Custom_AnalogIn_33_Hystereses | 2241 | Para_Custom_AnalogIn_33_Hystereses |  | 10000987
[8 empty] | 10000986 | Para_Custom_AnalogIn_33_LimitHi | Para_Custom_AnalogIn_33_LimitHi | 2242 | Para_Custom_AnalogIn_33_LimitHi |  | 10000986
[8 empty] | 10002905 | Para_Custom_AnalogIn_33_LimitHiHi | Para_Custom_AnalogIn_33_LimitHiHi | 2243 | Para_Custom_AnalogIn_33_LimitHiHi |  | 10002905
[8 empty] | 10000990 | Para_Custom_AnalogIn_33_LimitLo | Para_Custom_AnalogIn_33_LimitLo | 2244 | Para_Custom_AnalogIn_33_LimitLo |  | 10000990
[8 empty] | 10002908 | Para_Custom_AnalogIn_33_LimitLoLo | Para_Custom_AnalogIn_33_LimitLoLo | 2245 | Para_Custom_AnalogIn_33_LimitLoLo |  | 10002908
[8 empty] | 10000989 | Para_Custom_AnalogIn_33_ScaleMax | Para_Custom_AnalogIn_33_ScaleMax | 2246 | Para_Custom_AnalogIn_33_ScaleMax |  | 10000989
[8 empty] | 10001032 | Para_Custom_AnalogIn_33_ScaleMin | Para_Custom_AnalogIn_33_ScaleMin | 2247 | Para_Custom_AnalogIn_33_ScaleMin |  | 10001032
[8 empty] | 10001217 | Para_Custom_AnalogIn_34_CustAnaIn_Active34 | Para_Custom_AnalogIn_34_CustAnaIn_Active34 | 2248 | Para_Custom_AnalogIn_34_CustAnaIn_Active34 |  | 10001217
[8 empty] | 10001246 | Para_Custom_AnalogIn_34_CustAnaIn_MinMaxActive34 | Para_Custom_AnalogIn_34_CustAnaIn_MinMaxActive34 | 2249 | Para_Custom_AnalogIn_34_CustAnaIn_MinMaxActive34 |  | 10001246
[8 empty] | 10001148 | Para_Custom_AnalogIn_34_CustAnaIn_Set4mA34 | Para_Custom_AnalogIn_34_CustAnaIn_Set4mA34 | 2250 | Para_Custom_AnalogIn_34_CustAnaIn_Set4mA34 |  | 10001148
[8 empty] | 10008615 | Para_Custom_AnalogIn_34_CustAnaIn_Typ34 | Para_Custom_AnalogIn_34_CustAnaIn_Typ34 | 2251 | Para_Custom_AnalogIn_34_CustAnaIn_Typ34 |  | 10008615
[8 empty] | 10001106 | Para_Custom_AnalogIn_34_Hystereses | Para_Custom_AnalogIn_34_Hystereses | 2252 | Para_Custom_AnalogIn_34_Hystereses |  | 10001106
[8 empty] | 10001107 | Para_Custom_AnalogIn_34_LimitHi | Para_Custom_AnalogIn_34_LimitHi | 2253 | Para_Custom_AnalogIn_34_LimitHi |  | 10001107
[8 empty] | 10002913 | Para_Custom_AnalogIn_34_LimitHiHi | Para_Custom_AnalogIn_34_LimitHiHi | 2254 | Para_Custom_AnalogIn_34_LimitHiHi |  | 10002913
[8 empty] | 10001109 | Para_Custom_AnalogIn_34_LimitLo | Para_Custom_AnalogIn_34_LimitLo | 2255 | Para_Custom_AnalogIn_34_LimitLo |  | 10001109
[8 empty] | 10002911 | Para_Custom_AnalogIn_34_LimitLoLo | Para_Custom_AnalogIn_34_LimitLoLo | 2256 | Para_Custom_AnalogIn_34_LimitLoLo |  | 10002911
[8 empty] | 10001105 | Para_Custom_AnalogIn_34_ScaleMax | Para_Custom_AnalogIn_34_ScaleMax | 2257 | Para_Custom_AnalogIn_34_ScaleMax |  | 10001105
[8 empty] | 10001108 | Para_Custom_AnalogIn_34_ScaleMin | Para_Custom_AnalogIn_34_ScaleMin | 2258 | Para_Custom_AnalogIn_34_ScaleMin |  | 10001108
[8 empty] | 10001218 | Para_Custom_AnalogIn_35_CustAnaIn_Active35 | Para_Custom_AnalogIn_35_CustAnaIn_Active35 | 2259 | Para_Custom_AnalogIn_35_CustAnaIn_Active35 |  | 10001218
[8 empty] | 10001244 | Para_Custom_AnalogIn_35_CustAnaIn_MinMaxActive35 | Para_Custom_AnalogIn_35_CustAnaIn_MinMaxActive35 | 2260 | Para_Custom_AnalogIn_35_CustAnaIn_MinMaxActive35 |  | 10001244
[8 empty] | 10001147 | Para_Custom_AnalogIn_35_CustAnaIn_Set4mA35 | Para_Custom_AnalogIn_35_CustAnaIn_Set4mA35 | 2261 | Para_Custom_AnalogIn_35_CustAnaIn_Set4mA35 |  | 10001147
[8 empty] | 10008616 | Para_Custom_AnalogIn_35_CustAnaIn_Typ35 | Para_Custom_AnalogIn_35_CustAnaIn_Typ35 | 2262 | Para_Custom_AnalogIn_35_CustAnaIn_Typ35 |  | 10008616
[8 empty] | 10001110 | Para_Custom_AnalogIn_35_Hystereses | Para_Custom_AnalogIn_35_Hystereses | 2263 | Para_Custom_AnalogIn_35_Hystereses |  | 10001110
[8 empty] | 10001112 | Para_Custom_AnalogIn_35_LimitHi | Para_Custom_AnalogIn_35_LimitHi | 2264 | Para_Custom_AnalogIn_35_LimitHi |  | 10001112
[8 empty] | 10002915 | Para_Custom_AnalogIn_35_LimitHiHi | Para_Custom_AnalogIn_35_LimitHiHi | 2265 | Para_Custom_AnalogIn_35_LimitHiHi |  | 10002915
[8 empty] | 10001113 | Para_Custom_AnalogIn_35_LimitLo | Para_Custom_AnalogIn_35_LimitLo | 2266 | Para_Custom_AnalogIn_35_LimitLo |  | 10001113
[8 empty] | 10002917 | Para_Custom_AnalogIn_35_LimitLoLo | Para_Custom_AnalogIn_35_LimitLoLo | 2267 | Para_Custom_AnalogIn_35_LimitLoLo |  | 10002917
[8 empty] | 10001111 | Para_Custom_AnalogIn_35_ScaleMax | Para_Custom_AnalogIn_35_ScaleMax | 2268 | Para_Custom_AnalogIn_35_ScaleMax |  | 10001111
[8 empty] | 10001115 | Para_Custom_AnalogIn_35_ScaleMin | Para_Custom_AnalogIn_35_ScaleMin | 2269 | Para_Custom_AnalogIn_35_ScaleMin |  | 10001115
[8 empty] | 10001219 | Para_Custom_AnalogIn_36_CustAnaIn_Active36 | Para_Custom_AnalogIn_36_CustAnaIn_Active36 | 2270 | Para_Custom_AnalogIn_36_CustAnaIn_Active36 |  | 10001219
[8 empty] | 10001247 | Para_Custom_AnalogIn_36_CustAnaIn_MinMaxActive36 | Para_Custom_AnalogIn_36_CustAnaIn_MinMaxActive36 | 2271 | Para_Custom_AnalogIn_36_CustAnaIn_MinMaxActive36 |  | 10001247
[8 empty] | 10001149 | Para_Custom_AnalogIn_36_CustAnaIn_Set4mA36 | Para_Custom_AnalogIn_36_CustAnaIn_Set4mA36 | 2272 | Para_Custom_AnalogIn_36_CustAnaIn_Set4mA36 |  | 10001149
[8 empty] | 10008622 | Para_Custom_AnalogIn_36_CustAnaIn_Typ36 | Para_Custom_AnalogIn_36_CustAnaIn_Typ36 | 2273 | Para_Custom_AnalogIn_36_CustAnaIn_Typ36 |  | 10008622
[8 empty] | 10001116 | Para_Custom_AnalogIn_36_Hystereses | Para_Custom_AnalogIn_36_Hystereses | 2274 | Para_Custom_AnalogIn_36_Hystereses |  | 10001116
[8 empty] | 10001114 | Para_Custom_AnalogIn_36_LimitHi | Para_Custom_AnalogIn_36_LimitHi | 2275 | Para_Custom_AnalogIn_36_LimitHi |  | 10001114
[8 empty] | 10002926 | Para_Custom_AnalogIn_36_LimitHiHi | Para_Custom_AnalogIn_36_LimitHiHi | 2276 | Para_Custom_AnalogIn_36_LimitHiHi |  | 10002926
[8 empty] | 10001117 | Para_Custom_AnalogIn_36_LimitLo | Para_Custom_AnalogIn_36_LimitLo | 2277 | Para_Custom_AnalogIn_36_LimitLo |  | 10001117
[8 empty] | 10002920 | Para_Custom_AnalogIn_36_LimitLoLo | Para_Custom_AnalogIn_36_LimitLoLo | 2278 | Para_Custom_AnalogIn_36_LimitLoLo |  | 10002920
[8 empty] | 10001118 | Para_Custom_AnalogIn_36_ScaleMax | Para_Custom_AnalogIn_36_ScaleMax | 2279 | Para_Custom_AnalogIn_36_ScaleMax |  | 10001118
[8 empty] | 10001119 | Para_Custom_AnalogIn_36_ScaleMin | Para_Custom_AnalogIn_36_ScaleMin | 2280 | Para_Custom_AnalogIn_36_ScaleMin |  | 10001119
[8 empty] | 10001220 | Para_Custom_AnalogIn_37_CustAnaIn_Active37 | Para_Custom_AnalogIn_37_CustAnaIn_Active37 | 2281 | Para_Custom_AnalogIn_37_CustAnaIn_Active37 |  | 10001220
[8 empty] | 10001250 | Para_Custom_AnalogIn_37_CustAnaIn_MinMaxActive37 | Para_Custom_AnalogIn_37_CustAnaIn_MinMaxActive37 | 2282 | Para_Custom_AnalogIn_37_CustAnaIn_MinMaxActive37 |  | 10001250
[8 empty] | 10001143 | Para_Custom_AnalogIn_37_CustAnaIn_Set4mA37 | Para_Custom_AnalogIn_37_CustAnaIn_Set4mA37 | 2283 | Para_Custom_AnalogIn_37_CustAnaIn_Set4mA37 |  | 10001143
[8 empty] | 10008617 | Para_Custom_AnalogIn_37_CustAnaIn_Typ37 | Para_Custom_AnalogIn_37_CustAnaIn_Typ37 | 2284 | Para_Custom_AnalogIn_37_CustAnaIn_Typ37 |  | 10008617
[8 empty] | 10001121 | Para_Custom_AnalogIn_37_Hystereses | Para_Custom_AnalogIn_37_Hystereses | 2285 | Para_Custom_AnalogIn_37_Hystereses |  | 10001121
[8 empty] | 10001125 | Para_Custom_AnalogIn_37_LimitHi | Para_Custom_AnalogIn_37_LimitHi | 2286 | Para_Custom_AnalogIn_37_LimitHi |  | 10001125
[8 empty] | 10002922 | Para_Custom_AnalogIn_37_LimitHiHi | Para_Custom_AnalogIn_37_LimitHiHi | 2287 | Para_Custom_AnalogIn_37_LimitHiHi |  | 10002922
[8 empty] | 10001120 | Para_Custom_AnalogIn_37_LimitLo | Para_Custom_AnalogIn_37_LimitLo | 2288 | Para_Custom_AnalogIn_37_LimitLo |  | 10001120
[8 empty] | 10002923 | Para_Custom_AnalogIn_37_LimitLoLo | Para_Custom_AnalogIn_37_LimitLoLo | 2289 | Para_Custom_AnalogIn_37_LimitLoLo |  | 10002923
[8 empty] | 10001124 | Para_Custom_AnalogIn_37_ScaleMax | Para_Custom_AnalogIn_37_ScaleMax | 2290 | Para_Custom_AnalogIn_37_ScaleMax |  | 10001124
[8 empty] | 10001123 | Para_Custom_AnalogIn_37_ScaleMin | Para_Custom_AnalogIn_37_ScaleMin | 2291 | Para_Custom_AnalogIn_37_ScaleMin |  | 10001123
[8 empty] | 10001222 | Para_Custom_AnalogIn_38_CustAnaIn_Active38 | Para_Custom_AnalogIn_38_CustAnaIn_Active38 | 2292 | Para_Custom_AnalogIn_38_CustAnaIn_Active38 |  | 10001222
[8 empty] | 10001248 | Para_Custom_AnalogIn_38_CustAnaIn_MinMaxActive38 | Para_Custom_AnalogIn_38_CustAnaIn_MinMaxActive38 | 2293 | Para_Custom_AnalogIn_38_CustAnaIn_MinMaxActive38 |  | 10001248
[8 empty] | 10001145 | Para_Custom_AnalogIn_38_CustAnaIn_Set4mA38 | Para_Custom_AnalogIn_38_CustAnaIn_Set4mA38 | 2294 | Para_Custom_AnalogIn_38_CustAnaIn_Set4mA38 |  | 10001145
[8 empty] | 10008620 | Para_Custom_AnalogIn_38_CustAnaIn_Typ38 | Para_Custom_AnalogIn_38_CustAnaIn_Typ38 | 2295 | Para_Custom_AnalogIn_38_CustAnaIn_Typ38 |  | 10008620
[8 empty] | 10001129 | Para_Custom_AnalogIn_38_Hystereses | Para_Custom_AnalogIn_38_Hystereses | 2296 | Para_Custom_AnalogIn_38_Hystereses |  | 10001129
[8 empty] | 10001126 | Para_Custom_AnalogIn_38_LimitHi | Para_Custom_AnalogIn_38_LimitHi | 2297 | Para_Custom_AnalogIn_38_LimitHi |  | 10001126
[8 empty] | 10002930 | Para_Custom_AnalogIn_38_LimitHiHi | Para_Custom_AnalogIn_38_LimitHiHi | 2298 | Para_Custom_AnalogIn_38_LimitHiHi |  | 10002930
[8 empty] | 10001128 | Para_Custom_AnalogIn_38_LimitLo | Para_Custom_AnalogIn_38_LimitLo | 2299 | Para_Custom_AnalogIn_38_LimitLo |  | 10001128
[8 empty] | 10002927 | Para_Custom_AnalogIn_38_LimitLoLo | Para_Custom_AnalogIn_38_LimitLoLo | 2300 | Para_Custom_AnalogIn_38_LimitLoLo |  | 10002927
[8 empty] | 10001127 | Para_Custom_AnalogIn_38_ScaleMax | Para_Custom_AnalogIn_38_ScaleMax | 2301 | Para_Custom_AnalogIn_38_ScaleMax |  | 10001127
[8 empty] | 10001130 | Para_Custom_AnalogIn_38_ScaleMin | Para_Custom_AnalogIn_38_ScaleMin | 2302 | Para_Custom_AnalogIn_38_ScaleMin |  | 10001130
[8 empty] | 10001224 | Para_Custom_AnalogIn_39_CustAnaIn_Active39 | Para_Custom_AnalogIn_39_CustAnaIn_Active39 | 2303 | Para_Custom_AnalogIn_39_CustAnaIn_Active39 |  | 10001224
[8 empty] | 10001252 | Para_Custom_AnalogIn_39_CustAnaIn_MinMaxActive39 | Para_Custom_AnalogIn_39_CustAnaIn_MinMaxActive39 | 2304 | Para_Custom_AnalogIn_39_CustAnaIn_MinMaxActive39 |  | 10001252
[8 empty] | 10001144 | Para_Custom_AnalogIn_39_CustAnaIn_Set4mA39 | Para_Custom_AnalogIn_39_CustAnaIn_Set4mA39 | 2305 | Para_Custom_AnalogIn_39_CustAnaIn_Set4mA39 |  | 10001144
[8 empty] | 10008621 | Para_Custom_AnalogIn_39_CustAnaIn_Typ39 | Para_Custom_AnalogIn_39_CustAnaIn_Typ39 | 2306 | Para_Custom_AnalogIn_39_CustAnaIn_Typ39 |  | 10008621
[8 empty] | 10001008 | Para_Custom_AnalogIn_39_Hystereses | Para_Custom_AnalogIn_39_Hystereses | 2307 | Para_Custom_AnalogIn_39_Hystereses |  | 10001008
[8 empty] | 10001010 | Para_Custom_AnalogIn_39_LimitHi | Para_Custom_AnalogIn_39_LimitHi | 2308 | Para_Custom_AnalogIn_39_LimitHi |  | 10001010
[8 empty] | 10002933 | Para_Custom_AnalogIn_39_LimitHiHi | Para_Custom_AnalogIn_39_LimitHiHi | 2309 | Para_Custom_AnalogIn_39_LimitHiHi |  | 10002933
[8 empty] | 10001012 | Para_Custom_AnalogIn_39_LimitLo | Para_Custom_AnalogIn_39_LimitLo | 2310 | Para_Custom_AnalogIn_39_LimitLo |  | 10001012
[8 empty] | 10002932 | Para_Custom_AnalogIn_39_LimitLoLo | Para_Custom_AnalogIn_39_LimitLoLo | 2311 | Para_Custom_AnalogIn_39_LimitLoLo |  | 10002932
[8 empty] | 10001011 | Para_Custom_AnalogIn_39_ScaleMax | Para_Custom_AnalogIn_39_ScaleMax | 2312 | Para_Custom_AnalogIn_39_ScaleMax |  | 10001011
[8 empty] | 10001014 | Para_Custom_AnalogIn_39_ScaleMin | Para_Custom_AnalogIn_39_ScaleMin | 2313 | Para_Custom_AnalogIn_39_ScaleMin |  | 10001014
[8 empty] | 10000997 | Para_Custom_AnalogIn_3_CustAnaIn_MinMaxActive3 | Para_Custom_AnalogIn_3_CustAnaIn_MinMaxActive3 | 2314 | Para_Custom_AnalogIn_3_CustAnaIn_MinMaxActive3 |  | 10000997
[8 empty] | 10008610 | Para_Custom_AnalogIn_3_CustAnaIn_Typ3 | Para_Custom_AnalogIn_3_CustAnaIn_Typ3 | 2315 | Para_Custom_AnalogIn_3_CustAnaIn_Typ3 |  | 10008610
[8 empty] | 10000856 | Para_Custom_AnalogIn_3_Hystereses | Para_Custom_AnalogIn_3_Hystereses | 2316 | Para_Custom_AnalogIn_3_Hystereses |  | 10000856
[8 empty] | 10000879 | Para_Custom_AnalogIn_3_LimitHi | Para_Custom_AnalogIn_3_LimitHi | 2317 | Para_Custom_AnalogIn_3_LimitHi |  | 10000879
[8 empty] | 10000064 | Para_Custom_AnalogIn_3_LimitHiHi | Para_Custom_AnalogIn_3_LimitHiHi | 2318 | Para_Custom_AnalogIn_3_LimitHiHi |  | 10000064
[8 empty] | 10000911 | Para_Custom_AnalogIn_3_LimitLo | Para_Custom_AnalogIn_3_LimitLo | 2319 | Para_Custom_AnalogIn_3_LimitLo |  | 10000911
[8 empty] | 10000066 | Para_Custom_AnalogIn_3_LimitLoLo | Para_Custom_AnalogIn_3_LimitLoLo | 2320 | Para_Custom_AnalogIn_3_LimitLoLo |  | 10000066
[8 empty] | 10001221 | Para_Custom_AnalogIn_40_CustAnaIn_Active40 | Para_Custom_AnalogIn_40_CustAnaIn_Active40 | 2321 | Para_Custom_AnalogIn_40_CustAnaIn_Active40 |  | 10001221
[8 empty] | 10001256 | Para_Custom_AnalogIn_40_CustAnaIn_MinMaxActive40 | Para_Custom_AnalogIn_40_CustAnaIn_MinMaxActive40 | 2322 | Para_Custom_AnalogIn_40_CustAnaIn_MinMaxActive40 |  | 10001256
[8 empty] | 10001146 | Para_Custom_AnalogIn_40_CustAnaIn_Set4mA40 | Para_Custom_AnalogIn_40_CustAnaIn_Set4mA40 | 2323 | Para_Custom_AnalogIn_40_CustAnaIn_Set4mA40 |  | 10001146
[8 empty] | 10008618 | Para_Custom_AnalogIn_40_CustAnaIn_Typ40 | Para_Custom_AnalogIn_40_CustAnaIn_Typ40 | 2324 | Para_Custom_AnalogIn_40_CustAnaIn_Typ40 |  | 10008618
[8 empty] | 10001016 | Para_Custom_AnalogIn_40_Hystereses | Para_Custom_AnalogIn_40_Hystereses | 2325 | Para_Custom_AnalogIn_40_Hystereses |  | 10001016
[8 empty] | 10001015 | Para_Custom_AnalogIn_40_LimitHi | Para_Custom_AnalogIn_40_LimitHi | 2326 | Para_Custom_AnalogIn_40_LimitHi |  | 10001015
[8 empty] | 10002936 | Para_Custom_AnalogIn_40_LimitHiHi | Para_Custom_AnalogIn_40_LimitHiHi | 2327 | Para_Custom_AnalogIn_40_LimitHiHi |  | 10002936
[8 empty] | 10001013 | Para_Custom_AnalogIn_40_LimitLo | Para_Custom_AnalogIn_40_LimitLo | 2328 | Para_Custom_AnalogIn_40_LimitLo |  | 10001013
[8 empty] | 10002938 | Para_Custom_AnalogIn_40_LimitLoLo | Para_Custom_AnalogIn_40_LimitLoLo | 2329 | Para_Custom_AnalogIn_40_LimitLoLo |  | 10002938
[8 empty] | 10001017 | Para_Custom_AnalogIn_40_ScaleMax | Para_Custom_AnalogIn_40_ScaleMax | 2330 | Para_Custom_AnalogIn_40_ScaleMax |  | 10001017
[8 empty] | 10001020 | Para_Custom_AnalogIn_40_ScaleMin | Para_Custom_AnalogIn_40_ScaleMin | 2331 | Para_Custom_AnalogIn_40_ScaleMin |  | 10001020
[8 empty] | 10001223 | Para_Custom_AnalogIn_41_CustAnaIn_Active41 | Para_Custom_AnalogIn_41_CustAnaIn_Active41 | 2332 | Para_Custom_AnalogIn_41_CustAnaIn_Active41 |  | 10001223
[8 empty] | 10001254 | Para_Custom_AnalogIn_41_CustAnaIn_MinMaxActive41 | Para_Custom_AnalogIn_41_CustAnaIn_MinMaxActive41 | 2333 | Para_Custom_AnalogIn_41_CustAnaIn_MinMaxActive41 |  | 10001254
[8 empty] | 10001140 | Para_Custom_AnalogIn_41_CustAnaIn_Set4mA41 | Para_Custom_AnalogIn_41_CustAnaIn_Set4mA41 | 2334 | Para_Custom_AnalogIn_41_CustAnaIn_Set4mA41 |  | 10001140
[8 empty] | 10008619 | Para_Custom_AnalogIn_41_CustAnaIn_Typ41 | Para_Custom_AnalogIn_41_CustAnaIn_Typ41 | 2335 | Para_Custom_AnalogIn_41_CustAnaIn_Typ41 |  | 10008619
[8 empty] | 10001021 | Para_Custom_AnalogIn_41_Hystereses | Para_Custom_AnalogIn_41_Hystereses | 2336 | Para_Custom_AnalogIn_41_Hystereses |  | 10001021
[8 empty] | 10001019 | Para_Custom_AnalogIn_41_LimitHi | Para_Custom_AnalogIn_41_LimitHi | 2337 | Para_Custom_AnalogIn_41_LimitHi |  | 10001019
[8 empty] | 10002943 | Para_Custom_AnalogIn_41_LimitHiHi | Para_Custom_AnalogIn_41_LimitHiHi | 2338 | Para_Custom_AnalogIn_41_LimitHiHi |  | 10002943
[8 empty] | 10001022 | Para_Custom_AnalogIn_41_LimitLo | Para_Custom_AnalogIn_41_LimitLo | 2339 | Para_Custom_AnalogIn_41_LimitLo |  | 10001022
[8 empty] | 10002946 | Para_Custom_AnalogIn_41_LimitLoLo | Para_Custom_AnalogIn_41_LimitLoLo | 2340 | Para_Custom_AnalogIn_41_LimitLoLo |  | 10002946
[8 empty] | 10001023 | Para_Custom_AnalogIn_41_ScaleMax | Para_Custom_AnalogIn_41_ScaleMax | 2341 | Para_Custom_AnalogIn_41_ScaleMax |  | 10001023
[8 empty] | 10001018 | Para_Custom_AnalogIn_41_ScaleMin | Para_Custom_AnalogIn_41_ScaleMin | 2342 | Para_Custom_AnalogIn_41_ScaleMin |  | 10001018
[8 empty] | 10001226 | Para_Custom_AnalogIn_42_CustAnaIn_Active42 | Para_Custom_AnalogIn_42_CustAnaIn_Active42 | 2343 | Para_Custom_AnalogIn_42_CustAnaIn_Active42 |  | 10001226
[8 empty] | 10001253 | Para_Custom_AnalogIn_42_CustAnaIn_MinMaxActive42 | Para_Custom_AnalogIn_42_CustAnaIn_MinMaxActive42 | 2344 | Para_Custom_AnalogIn_42_CustAnaIn_MinMaxActive42 |  | 10001253
[8 empty] | 10001142 | Para_Custom_AnalogIn_42_CustAnaIn_Set4mA42 | Para_Custom_AnalogIn_42_CustAnaIn_Set4mA42 | 2345 | Para_Custom_AnalogIn_42_CustAnaIn_Set4mA42 |  | 10001142
[8 empty] | 10008627 | Para_Custom_AnalogIn_42_CustAnaIn_Typ42 | Para_Custom_AnalogIn_42_CustAnaIn_Typ42 | 2346 | Para_Custom_AnalogIn_42_CustAnaIn_Typ42 |  | 10008627
[8 empty] | 10001042 | Para_Custom_AnalogIn_42_Hystereses | Para_Custom_AnalogIn_42_Hystereses | 2347 | Para_Custom_AnalogIn_42_Hystereses |  | 10001042
[8 empty] | 10001043 | Para_Custom_AnalogIn_42_LimitHi | Para_Custom_AnalogIn_42_LimitHi | 2348 | Para_Custom_AnalogIn_42_LimitHi |  | 10001043
[8 empty] | 10002940 | Para_Custom_AnalogIn_42_LimitHiHi | Para_Custom_AnalogIn_42_LimitHiHi | 2349 | Para_Custom_AnalogIn_42_LimitHiHi |  | 10002940
[8 empty] | 10001044 | Para_Custom_AnalogIn_42_LimitLo | Para_Custom_AnalogIn_42_LimitLo | 2350 | Para_Custom_AnalogIn_42_LimitLo |  | 10001044
[8 empty] | 10002945 | Para_Custom_AnalogIn_42_LimitLoLo | Para_Custom_AnalogIn_42_LimitLoLo | 2351 | Para_Custom_AnalogIn_42_LimitLoLo |  | 10002945
[8 empty] | 10001049 | Para_Custom_AnalogIn_42_ScaleMax | Para_Custom_AnalogIn_42_ScaleMax | 2352 | Para_Custom_AnalogIn_42_ScaleMax |  | 10001049
[8 empty] | 10001046 | Para_Custom_AnalogIn_42_ScaleMin | Para_Custom_AnalogIn_42_ScaleMin | 2353 | Para_Custom_AnalogIn_42_ScaleMin |  | 10001046
[8 empty] | 10001227 | Para_Custom_AnalogIn_43_CustAnaIn_Active43 | Para_Custom_AnalogIn_43_CustAnaIn_Active43 | 2354 | Para_Custom_AnalogIn_43_CustAnaIn_Active43 |  | 10001227
[8 empty] | 10001257 | Para_Custom_AnalogIn_43_CustAnaIn_MinMaxActive43 | Para_Custom_AnalogIn_43_CustAnaIn_MinMaxActive43 | 2355 | Para_Custom_AnalogIn_43_CustAnaIn_MinMaxActive43 |  | 10001257
[8 empty] | 10001171 | Para_Custom_AnalogIn_43_CustAnaIn_Set4mA43 | Para_Custom_AnalogIn_43_CustAnaIn_Set4mA43 | 2356 | Para_Custom_AnalogIn_43_CustAnaIn_Set4mA43 |  | 10001171
[8 empty] | 10008623 | Para_Custom_AnalogIn_43_CustAnaIn_Typ43 | Para_Custom_AnalogIn_43_CustAnaIn_Typ43 | 2357 | Para_Custom_AnalogIn_43_CustAnaIn_Typ43 |  | 10008623
[8 empty] | 10001047 | Para_Custom_AnalogIn_43_Hystereses | Para_Custom_AnalogIn_43_Hystereses | 2358 | Para_Custom_AnalogIn_43_Hystereses |  | 10001047
[8 empty] | 10001045 | Para_Custom_AnalogIn_43_LimitHi | Para_Custom_AnalogIn_43_LimitHi | 2359 | Para_Custom_AnalogIn_43_LimitHi |  | 10001045
[8 empty] | 10002948 | Para_Custom_AnalogIn_43_LimitHiHi | Para_Custom_AnalogIn_43_LimitHiHi | 2360 | Para_Custom_AnalogIn_43_LimitHiHi |  | 10002948
[8 empty] | 10001053 | Para_Custom_AnalogIn_43_LimitLo | Para_Custom_AnalogIn_43_LimitLo | 2361 | Para_Custom_AnalogIn_43_LimitLo |  | 10001053
[8 empty] | 10002957 | Para_Custom_AnalogIn_43_LimitLoLo | Para_Custom_AnalogIn_43_LimitLoLo | 2362 | Para_Custom_AnalogIn_43_LimitLoLo |  | 10002957
[8 empty] | 10001051 | Para_Custom_AnalogIn_43_ScaleMax | Para_Custom_AnalogIn_43_ScaleMax | 2363 | Para_Custom_AnalogIn_43_ScaleMax |  | 10001051
[8 empty] | 10001048 | Para_Custom_AnalogIn_43_ScaleMin | Para_Custom_AnalogIn_43_ScaleMin | 2364 | Para_Custom_AnalogIn_43_ScaleMin |  | 10001048
[8 empty] | 10001228 | Para_Custom_AnalogIn_44_CustAnaIn_Active44 | Para_Custom_AnalogIn_44_CustAnaIn_Active44 | 2365 | Para_Custom_AnalogIn_44_CustAnaIn_Active44 |  | 10001228
[8 empty] | 10001260 | Para_Custom_AnalogIn_44_CustAnaIn_MinMaxActive44 | Para_Custom_AnalogIn_44_CustAnaIn_MinMaxActive44 | 2366 | Para_Custom_AnalogIn_44_CustAnaIn_MinMaxActive44 |  | 10001260
[8 empty] | 10001167 | Para_Custom_AnalogIn_44_CustAnaIn_Set4mA44 | Para_Custom_AnalogIn_44_CustAnaIn_Set4mA44 | 2367 | Para_Custom_AnalogIn_44_CustAnaIn_Set4mA44 |  | 10001167
[8 empty] | 10008626 | Para_Custom_AnalogIn_44_CustAnaIn_Typ44 | Para_Custom_AnalogIn_44_CustAnaIn_Typ44 | 2368 | Para_Custom_AnalogIn_44_CustAnaIn_Typ44 |  | 10008626
[8 empty] | 10001050 | Para_Custom_AnalogIn_44_Hystereses | Para_Custom_AnalogIn_44_Hystereses | 2369 | Para_Custom_AnalogIn_44_Hystereses |  | 10001050
[8 empty] | 10001052 | Para_Custom_AnalogIn_44_LimitHi | Para_Custom_AnalogIn_44_LimitHi | 2370 | Para_Custom_AnalogIn_44_LimitHi |  | 10001052
[8 empty] | 10002956 | Para_Custom_AnalogIn_44_LimitHiHi | Para_Custom_AnalogIn_44_LimitHiHi | 2371 | Para_Custom_AnalogIn_44_LimitHiHi |  | 10002956
[8 empty] | 10001055 | Para_Custom_AnalogIn_44_LimitLo | Para_Custom_AnalogIn_44_LimitLo | 2372 | Para_Custom_AnalogIn_44_LimitLo |  | 10001055
[8 empty] | 10002958 | Para_Custom_AnalogIn_44_LimitLoLo | Para_Custom_AnalogIn_44_LimitLoLo | 2373 | Para_Custom_AnalogIn_44_LimitLoLo |  | 10002958
[8 empty] | 10001057 | Para_Custom_AnalogIn_44_ScaleMax | Para_Custom_AnalogIn_44_ScaleMax | 2374 | Para_Custom_AnalogIn_44_ScaleMax |  | 10001057
[8 empty] | 10001059 | Para_Custom_AnalogIn_44_ScaleMin | Para_Custom_AnalogIn_44_ScaleMin | 2375 | Para_Custom_AnalogIn_44_ScaleMin |  | 10001059
[8 empty] | 10001225 | Para_Custom_AnalogIn_45_CustAnaIn_Active45 | Para_Custom_AnalogIn_45_CustAnaIn_Active45 | 2376 | Para_Custom_AnalogIn_45_CustAnaIn_Active45 |  | 10001225
[8 empty] | 10001255 | Para_Custom_AnalogIn_45_CustAnaIn_MinMaxActive45 | Para_Custom_AnalogIn_45_CustAnaIn_MinMaxActive45 | 2377 | Para_Custom_AnalogIn_45_CustAnaIn_MinMaxActive45 |  | 10001255
[8 empty] | 10001169 | Para_Custom_AnalogIn_45_CustAnaIn_Set4mA45 | Para_Custom_AnalogIn_45_CustAnaIn_Set4mA45 | 2378 | Para_Custom_AnalogIn_45_CustAnaIn_Set4mA45 |  | 10001169
[8 empty] | 10008624 | Para_Custom_AnalogIn_45_CustAnaIn_Typ45 | Para_Custom_AnalogIn_45_CustAnaIn_Typ45 | 2379 | Para_Custom_AnalogIn_45_CustAnaIn_Typ45 |  | 10008624
[8 empty] | 10001058 | Para_Custom_AnalogIn_45_Hystereses | Para_Custom_AnalogIn_45_Hystereses | 2380 | Para_Custom_AnalogIn_45_Hystereses |  | 10001058
[8 empty] | 10001054 | Para_Custom_AnalogIn_45_LimitHi | Para_Custom_AnalogIn_45_LimitHi | 2381 | Para_Custom_AnalogIn_45_LimitHi |  | 10001054
[8 empty] | 10002950 | Para_Custom_AnalogIn_45_LimitHiHi | Para_Custom_AnalogIn_45_LimitHiHi | 2382 | Para_Custom_AnalogIn_45_LimitHiHi |  | 10002950
[8 empty] | 10001060 | Para_Custom_AnalogIn_45_LimitLo | Para_Custom_AnalogIn_45_LimitLo | 2383 | Para_Custom_AnalogIn_45_LimitLo |  | 10001060
[8 empty] | 10002954 | Para_Custom_AnalogIn_45_LimitLoLo | Para_Custom_AnalogIn_45_LimitLoLo | 2384 | Para_Custom_AnalogIn_45_LimitLoLo |  | 10002954
[8 empty] | 10001062 | Para_Custom_AnalogIn_45_ScaleMax | Para_Custom_AnalogIn_45_ScaleMax | 2385 | Para_Custom_AnalogIn_45_ScaleMax |  | 10001062
[8 empty] | 10001056 | Para_Custom_AnalogIn_45_ScaleMin | Para_Custom_AnalogIn_45_ScaleMin | 2386 | Para_Custom_AnalogIn_45_ScaleMin |  | 10001056
[8 empty] | 10001229 | Para_Custom_AnalogIn_46_CustAnaIn_Active46 | Para_Custom_AnalogIn_46_CustAnaIn_Active46 | 2387 | Para_Custom_AnalogIn_46_CustAnaIn_Active46 |  | 10001229
[8 empty] | 10001258 | Para_Custom_AnalogIn_46_CustAnaIn_MinMaxActive46 | Para_Custom_AnalogIn_46_CustAnaIn_MinMaxActive46 | 2388 | Para_Custom_AnalogIn_46_CustAnaIn_MinMaxActive46 |  | 10001258
[8 empty] | 10001168 | Para_Custom_AnalogIn_46_CustAnaIn_Set4mA46 | Para_Custom_AnalogIn_46_CustAnaIn_Set4mA46 | 2389 | Para_Custom_AnalogIn_46_CustAnaIn_Set4mA46 |  | 10001168
[8 empty] | 10008628 | Para_Custom_AnalogIn_46_CustAnaIn_Typ46 | Para_Custom_AnalogIn_46_CustAnaIn_Typ46 | 2390 | Para_Custom_AnalogIn_46_CustAnaIn_Typ46 |  | 10008628
[8 empty] | 10001061 | Para_Custom_AnalogIn_46_Hystereses | Para_Custom_AnalogIn_46_Hystereses | 2391 | Para_Custom_AnalogIn_46_Hystereses |  | 10001061
[8 empty] | 10001064 | Para_Custom_AnalogIn_46_LimitHi | Para_Custom_AnalogIn_46_LimitHi | 2392 | Para_Custom_AnalogIn_46_LimitHi |  | 10001064
[8 empty] | 10002961 | Para_Custom_AnalogIn_46_LimitHiHi | Para_Custom_AnalogIn_46_LimitHiHi | 2393 | Para_Custom_AnalogIn_46_LimitHiHi |  | 10002961
[8 empty] | 10001063 | Para_Custom_AnalogIn_46_LimitLo | Para_Custom_AnalogIn_46_LimitLo | 2394 | Para_Custom_AnalogIn_46_LimitLo |  | 10001063
[8 empty] | 10002964 | Para_Custom_AnalogIn_46_LimitLoLo | Para_Custom_AnalogIn_46_LimitLoLo | 2395 | Para_Custom_AnalogIn_46_LimitLoLo |  | 10002964
[8 empty] | 10001065 | Para_Custom_AnalogIn_46_ScaleMax | Para_Custom_AnalogIn_46_ScaleMax | 2396 | Para_Custom_AnalogIn_46_ScaleMax |  | 10001065
[8 empty] | 10001066 | Para_Custom_AnalogIn_46_ScaleMin | Para_Custom_AnalogIn_46_ScaleMin | 2397 | Para_Custom_AnalogIn_46_ScaleMin |  | 10001066
[8 empty] | 10001230 | Para_Custom_AnalogIn_47_CustAnaIn_Active47 | Para_Custom_AnalogIn_47_CustAnaIn_Active47 | 2398 | Para_Custom_AnalogIn_47_CustAnaIn_Active47 |  | 10001230
[8 empty] | 10001259 | Para_Custom_AnalogIn_47_CustAnaIn_MinMaxActive47 | Para_Custom_AnalogIn_47_CustAnaIn_MinMaxActive47 | 2399 | Para_Custom_AnalogIn_47_CustAnaIn_MinMaxActive47 |  | 10001259
[8 empty] | 10001163 | Para_Custom_AnalogIn_47_CustAnaIn_Set4mA47 | Para_Custom_AnalogIn_47_CustAnaIn_Set4mA47 | 2400 | Para_Custom_AnalogIn_47_CustAnaIn_Set4mA47 |  | 10001163
[8 empty] | 10008629 | Para_Custom_AnalogIn_47_CustAnaIn_Typ47 | Para_Custom_AnalogIn_47_CustAnaIn_Typ47 | 2401 | Para_Custom_AnalogIn_47_CustAnaIn_Typ47 |  | 10008629
[8 empty] | 10001070 | Para_Custom_AnalogIn_47_Hystereses | Para_Custom_AnalogIn_47_Hystereses | 2402 | Para_Custom_AnalogIn_47_Hystereses |  | 10001070
[8 empty] | 10001069 | Para_Custom_AnalogIn_47_LimitHi | Para_Custom_AnalogIn_47_LimitHi | 2403 | Para_Custom_AnalogIn_47_LimitHi |  | 10001069
[8 empty] | 10002967 | Para_Custom_AnalogIn_47_LimitHiHi | Para_Custom_AnalogIn_47_LimitHiHi | 2404 | Para_Custom_AnalogIn_47_LimitHiHi |  | 10002967
[8 empty] | 10001067 | Para_Custom_AnalogIn_47_LimitLo | Para_Custom_AnalogIn_47_LimitLo | 2405 | Para_Custom_AnalogIn_47_LimitLo |  | 10001067
[8 empty] | 10002966 | Para_Custom_AnalogIn_47_LimitLoLo | Para_Custom_AnalogIn_47_LimitLoLo | 2406 | Para_Custom_AnalogIn_47_LimitLoLo |  | 10002966
[8 empty] | 10001071 | Para_Custom_AnalogIn_47_ScaleMax | Para_Custom_AnalogIn_47_ScaleMax | 2407 | Para_Custom_AnalogIn_47_ScaleMax |  | 10001071
[8 empty] | 10001068 | Para_Custom_AnalogIn_47_ScaleMin | Para_Custom_AnalogIn_47_ScaleMin | 2408 | Para_Custom_AnalogIn_47_ScaleMin |  | 10001068
[8 empty] | 10001231 | Para_Custom_AnalogIn_48_CustAnaIn_Active48 | Para_Custom_AnalogIn_48_CustAnaIn_Active48 | 2409 | Para_Custom_AnalogIn_48_CustAnaIn_Active48 |  | 10001231
[8 empty] | 10001261 | Para_Custom_AnalogIn_48_CustAnaIn_MinMaxActive48 | Para_Custom_AnalogIn_48_CustAnaIn_MinMaxActive48 | 2410 | Para_Custom_AnalogIn_48_CustAnaIn_MinMaxActive48 |  | 10001261
[8 empty] | 10001172 | Para_Custom_AnalogIn_48_CustAnaIn_Set4mA48 | Para_Custom_AnalogIn_48_CustAnaIn_Set4mA48 | 2411 | Para_Custom_AnalogIn_48_CustAnaIn_Set4mA48 |  | 10001172
[8 empty] | 10008630 | Para_Custom_AnalogIn_48_CustAnaIn_Typ48 | Para_Custom_AnalogIn_48_CustAnaIn_Typ48 | 2412 | Para_Custom_AnalogIn_48_CustAnaIn_Typ48 |  | 10008630
[8 empty] | 10001077 | Para_Custom_AnalogIn_48_Hystereses | Para_Custom_AnalogIn_48_Hystereses | 2413 | Para_Custom_AnalogIn_48_Hystereses |  | 10001077
[8 empty] | 10001074 | Para_Custom_AnalogIn_48_LimitHi | Para_Custom_AnalogIn_48_LimitHi | 2414 | Para_Custom_AnalogIn_48_LimitHi |  | 10001074
[8 empty] | 10002968 | Para_Custom_AnalogIn_48_LimitHiHi | Para_Custom_AnalogIn_48_LimitHiHi | 2415 | Para_Custom_AnalogIn_48_LimitHiHi |  | 10002968
[8 empty] | 10001079 | Para_Custom_AnalogIn_48_LimitLo | Para_Custom_AnalogIn_48_LimitLo | 2416 | Para_Custom_AnalogIn_48_LimitLo |  | 10001079
[8 empty] | 10002971 | Para_Custom_AnalogIn_48_LimitLoLo | Para_Custom_AnalogIn_48_LimitLoLo | 2417 | Para_Custom_AnalogIn_48_LimitLoLo |  | 10002971
[8 empty] | 10001078 | Para_Custom_AnalogIn_48_ScaleMax | Para_Custom_AnalogIn_48_ScaleMax | 2418 | Para_Custom_AnalogIn_48_ScaleMax |  | 10001078
[8 empty] | 10001080 | Para_Custom_AnalogIn_48_ScaleMin | Para_Custom_AnalogIn_48_ScaleMin | 2419 | Para_Custom_AnalogIn_48_ScaleMin |  | 10001080
[8 empty] | 10001232 | Para_Custom_AnalogIn_49_CustAnaIn_Active49 | Para_Custom_AnalogIn_49_CustAnaIn_Active49 | 2420 | Para_Custom_AnalogIn_49_CustAnaIn_Active49 |  | 10001232
[8 empty] | 10001263 | Para_Custom_AnalogIn_49_CustAnaIn_MinMaxActive49 | Para_Custom_AnalogIn_49_CustAnaIn_MinMaxActive49 | 2421 | Para_Custom_AnalogIn_49_CustAnaIn_MinMaxActive49 |  | 10001263
[8 empty] | 10001170 | Para_Custom_AnalogIn_49_CustAnaIn_Set4mA49 | Para_Custom_AnalogIn_49_CustAnaIn_Set4mA49 | 2422 | Para_Custom_AnalogIn_49_CustAnaIn_Set4mA49 |  | 10001170
[8 empty] | 10008631 | Para_Custom_AnalogIn_49_CustAnaIn_Typ49 | Para_Custom_AnalogIn_49_CustAnaIn_Typ49 | 2423 | Para_Custom_AnalogIn_49_CustAnaIn_Typ49 |  | 10008631
[8 empty] | 10001081 | Para_Custom_AnalogIn_49_Hystereses | Para_Custom_AnalogIn_49_Hystereses | 2424 | Para_Custom_AnalogIn_49_Hystereses |  | 10001081
[8 empty] | 10001083 | Para_Custom_AnalogIn_49_LimitHi | Para_Custom_AnalogIn_49_LimitHi | 2425 | Para_Custom_AnalogIn_49_LimitHi |  | 10001083
[8 empty] | 10002973 | Para_Custom_AnalogIn_49_LimitHiHi | Para_Custom_AnalogIn_49_LimitHiHi | 2426 | Para_Custom_AnalogIn_49_LimitHiHi |  | 10002973
[8 empty] | 10001084 | Para_Custom_AnalogIn_49_LimitLo | Para_Custom_AnalogIn_49_LimitLo | 2427 | Para_Custom_AnalogIn_49_LimitLo |  | 10001084
[8 empty] | 10002979 | Para_Custom_AnalogIn_49_LimitLoLo | Para_Custom_AnalogIn_49_LimitLoLo | 2428 | Para_Custom_AnalogIn_49_LimitLoLo |  | 10002979
[8 empty] | 10001082 | Para_Custom_AnalogIn_49_ScaleMax | Para_Custom_AnalogIn_49_ScaleMax | 2429 | Para_Custom_AnalogIn_49_ScaleMax |  | 10001082
[8 empty] | 10001087 | Para_Custom_AnalogIn_49_ScaleMin | Para_Custom_AnalogIn_49_ScaleMin | 2430 | Para_Custom_AnalogIn_49_ScaleMin |  | 10001087
[8 empty] | 10001000 | Para_Custom_AnalogIn_4_CustAnaIn_MinMaxActive4 | Para_Custom_AnalogIn_4_CustAnaIn_MinMaxActive4 | 2431 | Para_Custom_AnalogIn_4_CustAnaIn_MinMaxActive4 |  | 10001000
[8 empty] | 10008625 | Para_Custom_AnalogIn_4_CustAnaIn_Typ4 | Para_Custom_AnalogIn_4_CustAnaIn_Typ4 | 2432 | Para_Custom_AnalogIn_4_CustAnaIn_Typ4 |  | 10008625
[8 empty] | 10000854 | Para_Custom_AnalogIn_4_Hystereses | Para_Custom_AnalogIn_4_Hystereses | 2433 | Para_Custom_AnalogIn_4_Hystereses |  | 10000854
[8 empty] | 10000884 | Para_Custom_AnalogIn_4_LimitHi | Para_Custom_AnalogIn_4_LimitHi | 2434 | Para_Custom_AnalogIn_4_LimitHi |  | 10000884
[8 empty] | 10000070 | Para_Custom_AnalogIn_4_LimitHiHi | Para_Custom_AnalogIn_4_LimitHiHi | 2435 | Para_Custom_AnalogIn_4_LimitHiHi |  | 10000070
[8 empty] | 10000914 | Para_Custom_AnalogIn_4_LimitLo | Para_Custom_AnalogIn_4_LimitLo | 2436 | Para_Custom_AnalogIn_4_LimitLo |  | 10000914
[8 empty] | 10000069 | Para_Custom_AnalogIn_4_LimitLoLo | Para_Custom_AnalogIn_4_LimitLoLo | 2437 | Para_Custom_AnalogIn_4_LimitLoLo |  | 10000069
[8 empty] | 10001234 | Para_Custom_AnalogIn_50_CustAnaIn_Active50 | Para_Custom_AnalogIn_50_CustAnaIn_Active50 | 2438 | Para_Custom_AnalogIn_50_CustAnaIn_Active50 |  | 10001234
[8 empty] | 10001266 | Para_Custom_AnalogIn_50_CustAnaIn_MinMaxActive50 | Para_Custom_AnalogIn_50_CustAnaIn_MinMaxActive50 | 2439 | Para_Custom_AnalogIn_50_CustAnaIn_MinMaxActive50 |  | 10001266
[8 empty] | 10001175 | Para_Custom_AnalogIn_50_CustAnaIn_Set4mA50 | Para_Custom_AnalogIn_50_CustAnaIn_Set4mA50 | 2440 | Para_Custom_AnalogIn_50_CustAnaIn_Set4mA50 |  | 10001175
[8 empty] | 10008633 | Para_Custom_AnalogIn_50_CustAnaIn_Typ50 | Para_Custom_AnalogIn_50_CustAnaIn_Typ50 | 2441 | Para_Custom_AnalogIn_50_CustAnaIn_Typ50 |  | 10008633
[8 empty] | 10001085 | Para_Custom_AnalogIn_50_Hystereses | Para_Custom_AnalogIn_50_Hystereses | 2442 | Para_Custom_AnalogIn_50_Hystereses |  | 10001085
[8 empty] | 10001089 | Para_Custom_AnalogIn_50_LimitHi | Para_Custom_AnalogIn_50_LimitHi | 2443 | Para_Custom_AnalogIn_50_LimitHi |  | 10001089
[8 empty] | 10002974 | Para_Custom_AnalogIn_50_LimitHiHi | Para_Custom_AnalogIn_50_LimitHiHi | 2444 | Para_Custom_AnalogIn_50_LimitHiHi |  | 10002974
[8 empty] | 10001086 | Para_Custom_AnalogIn_50_LimitLo | Para_Custom_AnalogIn_50_LimitLo | 2445 | Para_Custom_AnalogIn_50_LimitLo |  | 10001086
[8 empty] | 10002978 | Para_Custom_AnalogIn_50_LimitLoLo | Para_Custom_AnalogIn_50_LimitLoLo | 2446 | Para_Custom_AnalogIn_50_LimitLoLo |  | 10002978
[8 empty] | 10001088 | Para_Custom_AnalogIn_50_ScaleMax | Para_Custom_AnalogIn_50_ScaleMax | 2447 | Para_Custom_AnalogIn_50_ScaleMax |  | 10001088
[8 empty] | 10001092 | Para_Custom_AnalogIn_50_ScaleMin | Para_Custom_AnalogIn_50_ScaleMin | 2448 | Para_Custom_AnalogIn_50_ScaleMin |  | 10001092
[8 empty] | 10001233 | Para_Custom_AnalogIn_51_CustAnaIn_Active51 | Para_Custom_AnalogIn_51_CustAnaIn_Active51 | 2449 | Para_Custom_AnalogIn_51_CustAnaIn_Active51 |  | 10001233
[8 empty] | 10001267 | Para_Custom_AnalogIn_51_CustAnaIn_MinMaxActive51 | Para_Custom_AnalogIn_51_CustAnaIn_MinMaxActive51 | 2450 | Para_Custom_AnalogIn_51_CustAnaIn_MinMaxActive51 |  | 10001267
[8 empty] | 10001174 | Para_Custom_AnalogIn_51_CustAnaIn_Set4mA51 | Para_Custom_AnalogIn_51_CustAnaIn_Set4mA51 | 2451 | Para_Custom_AnalogIn_51_CustAnaIn_Set4mA51 |  | 10001174
[8 empty] | 10008634 | Para_Custom_AnalogIn_51_CustAnaIn_Typ51 | Para_Custom_AnalogIn_51_CustAnaIn_Typ51 | 2452 | Para_Custom_AnalogIn_51_CustAnaIn_Typ51 |  | 10008634
[8 empty] | 10001091 | Para_Custom_AnalogIn_51_Hystereses | Para_Custom_AnalogIn_51_Hystereses | 2453 | Para_Custom_AnalogIn_51_Hystereses |  | 10001091
[8 empty] | 10001090 | Para_Custom_AnalogIn_51_LimitHi | Para_Custom_AnalogIn_51_LimitHi | 2454 | Para_Custom_AnalogIn_51_LimitHi |  | 10001090
[8 empty] | 10002988 | Para_Custom_AnalogIn_51_LimitHiHi | Para_Custom_AnalogIn_51_LimitHiHi | 2455 | Para_Custom_AnalogIn_51_LimitHiHi |  | 10002988
[8 empty] | 10001094 | Para_Custom_AnalogIn_51_LimitLo | Para_Custom_AnalogIn_51_LimitLo | 2456 | Para_Custom_AnalogIn_51_LimitLo |  | 10001094
[8 empty] | 10002987 | Para_Custom_AnalogIn_51_LimitLoLo | Para_Custom_AnalogIn_51_LimitLoLo | 2457 | Para_Custom_AnalogIn_51_LimitLoLo |  | 10002987
[8 empty] | 10001093 | Para_Custom_AnalogIn_51_ScaleMax | Para_Custom_AnalogIn_51_ScaleMax | 2458 | Para_Custom_AnalogIn_51_ScaleMax |  | 10001093
[8 empty] | 10001095 | Para_Custom_AnalogIn_51_ScaleMin | Para_Custom_AnalogIn_51_ScaleMin | 2459 | Para_Custom_AnalogIn_51_ScaleMin |  | 10001095
[8 empty] | 10001237 | Para_Custom_AnalogIn_52_CustAnaIn_Active52 | Para_Custom_AnalogIn_52_CustAnaIn_Active52 | 2460 | Para_Custom_AnalogIn_52_CustAnaIn_Active52 |  | 10001237
[8 empty] | 10001268 | Para_Custom_AnalogIn_52_CustAnaIn_MinMaxActive52 | Para_Custom_AnalogIn_52_CustAnaIn_MinMaxActive52 | 2461 | Para_Custom_AnalogIn_52_CustAnaIn_MinMaxActive52 |  | 10001268
[8 empty] | 10001279 | Para_Custom_AnalogIn_52_CustAnaIn_Set4mA52 | Para_Custom_AnalogIn_52_CustAnaIn_Set4mA52 | 2462 | Para_Custom_AnalogIn_52_CustAnaIn_Set4mA52 |  | 10001279
[8 empty] | 10008636 | Para_Custom_AnalogIn_52_CustAnaIn_Typ52 | Para_Custom_AnalogIn_52_CustAnaIn_Typ52 | 2463 | Para_Custom_AnalogIn_52_CustAnaIn_Typ52 |  | 10008636
[8 empty] | 10001097 | Para_Custom_AnalogIn_52_Hystereses | Para_Custom_AnalogIn_52_Hystereses | 2464 | Para_Custom_AnalogIn_52_Hystereses |  | 10001097
[8 empty] | 10001098 | Para_Custom_AnalogIn_52_LimitHi | Para_Custom_AnalogIn_52_LimitHi | 2465 | Para_Custom_AnalogIn_52_LimitHi |  | 10001098
[8 empty] | 10002981 | Para_Custom_AnalogIn_52_LimitHiHi | Para_Custom_AnalogIn_52_LimitHiHi | 2466 | Para_Custom_AnalogIn_52_LimitHiHi |  | 10002981
[8 empty] | 10001096 | Para_Custom_AnalogIn_52_LimitLo | Para_Custom_AnalogIn_52_LimitLo | 2467 | Para_Custom_AnalogIn_52_LimitLo |  | 10001096
[8 empty] | 10002992 | Para_Custom_AnalogIn_52_LimitLoLo | Para_Custom_AnalogIn_52_LimitLoLo | 2468 | Para_Custom_AnalogIn_52_LimitLoLo |  | 10002992
[8 empty] | 10001099 | Para_Custom_AnalogIn_52_ScaleMax | Para_Custom_AnalogIn_52_ScaleMax | 2469 | Para_Custom_AnalogIn_52_ScaleMax |  | 10001099
[8 empty] | 10001102 | Para_Custom_AnalogIn_52_ScaleMin | Para_Custom_AnalogIn_52_ScaleMin | 2470 | Para_Custom_AnalogIn_52_ScaleMin |  | 10001102
[8 empty] | 10001239 | Para_Custom_AnalogIn_53_CustAnaIn_Active53 | Para_Custom_AnalogIn_53_CustAnaIn_Active53 | 2471 | Para_Custom_AnalogIn_53_CustAnaIn_Active53 |  | 10001239
[8 empty] | 10001269 | Para_Custom_AnalogIn_53_CustAnaIn_MinMaxActive53 | Para_Custom_AnalogIn_53_CustAnaIn_MinMaxActive53 | 2472 | Para_Custom_AnalogIn_53_CustAnaIn_MinMaxActive53 |  | 10001269
[8 empty] | 10001173 | Para_Custom_AnalogIn_53_CustAnaIn_Set4mA53 | Para_Custom_AnalogIn_53_CustAnaIn_Set4mA53 | 2473 | Para_Custom_AnalogIn_53_CustAnaIn_Set4mA53 |  | 10001173
[8 empty] | 10008638 | Para_Custom_AnalogIn_53_CustAnaIn_Typ53 | Para_Custom_AnalogIn_53_CustAnaIn_Typ53 | 2474 | Para_Custom_AnalogIn_53_CustAnaIn_Typ53 |  | 10008638
[8 empty] | 10001104 | Para_Custom_AnalogIn_53_Hystereses | Para_Custom_AnalogIn_53_Hystereses | 2475 | Para_Custom_AnalogIn_53_Hystereses |  | 10001104
[8 empty] | 10001122 | Para_Custom_AnalogIn_53_LimitHi | Para_Custom_AnalogIn_53_LimitHi | 2476 | Para_Custom_AnalogIn_53_LimitHi |  | 10001122
[8 empty] | 10002994 | Para_Custom_AnalogIn_53_LimitHiHi | Para_Custom_AnalogIn_53_LimitHiHi | 2477 | Para_Custom_AnalogIn_53_LimitHiHi |  | 10002994
[8 empty] | 10001100 | Para_Custom_AnalogIn_53_LimitLo | Para_Custom_AnalogIn_53_LimitLo | 2478 | Para_Custom_AnalogIn_53_LimitLo |  | 10001100
[8 empty] | 10002990 | Para_Custom_AnalogIn_53_LimitLoLo | Para_Custom_AnalogIn_53_LimitLoLo | 2479 | Para_Custom_AnalogIn_53_LimitLoLo |  | 10002990
[8 empty] | 10001101 | Para_Custom_AnalogIn_53_ScaleMax | Para_Custom_AnalogIn_53_ScaleMax | 2480 | Para_Custom_AnalogIn_53_ScaleMax |  | 10001101
[8 empty] | 10001103 | Para_Custom_AnalogIn_53_ScaleMin | Para_Custom_AnalogIn_53_ScaleMin | 2481 | Para_Custom_AnalogIn_53_ScaleMin |  | 10001103
[8 empty] | 10001235 | Para_Custom_AnalogIn_54_CustAnaIn_Active54 | Para_Custom_AnalogIn_54_CustAnaIn_Active54 | 2482 | Para_Custom_AnalogIn_54_CustAnaIn_Active54 |  | 10001235
[8 empty] | 10001265 | Para_Custom_AnalogIn_54_CustAnaIn_MinMaxActive54 | Para_Custom_AnalogIn_54_CustAnaIn_MinMaxActive54 | 2483 | Para_Custom_AnalogIn_54_CustAnaIn_MinMaxActive54 |  | 10001265
[8 empty] | 10001262 | Para_Custom_AnalogIn_54_CustAnaIn_Set4mA54 | Para_Custom_AnalogIn_54_CustAnaIn_Set4mA54 | 2484 | Para_Custom_AnalogIn_54_CustAnaIn_Set4mA54 |  | 10001262
[8 empty] | 10008639 | Para_Custom_AnalogIn_54_CustAnaIn_Typ54 | Para_Custom_AnalogIn_54_CustAnaIn_Typ54 | 2485 | Para_Custom_AnalogIn_54_CustAnaIn_Typ54 |  | 10008639
[8 empty] | 10001178 | Para_Custom_AnalogIn_54_Hystereses | Para_Custom_AnalogIn_54_Hystereses | 2486 | Para_Custom_AnalogIn_54_Hystereses |  | 10001178
[8 empty] | 10001179 | Para_Custom_AnalogIn_54_LimitHi | Para_Custom_AnalogIn_54_LimitHi | 2487 | Para_Custom_AnalogIn_54_LimitHi |  | 10001179
[8 empty] | 10002986 | Para_Custom_AnalogIn_54_LimitHiHi | Para_Custom_AnalogIn_54_LimitHiHi | 2488 | Para_Custom_AnalogIn_54_LimitHiHi |  | 10002986
[8 empty] | 10001181 | Para_Custom_AnalogIn_54_LimitLo | Para_Custom_AnalogIn_54_LimitLo | 2489 | Para_Custom_AnalogIn_54_LimitLo |  | 10001181
[8 empty] | 10002997 | Para_Custom_AnalogIn_54_LimitLoLo | Para_Custom_AnalogIn_54_LimitLoLo | 2490 | Para_Custom_AnalogIn_54_LimitLoLo |  | 10002997
[8 empty] | 10001182 | Para_Custom_AnalogIn_54_ScaleMax | Para_Custom_AnalogIn_54_ScaleMax | 2491 | Para_Custom_AnalogIn_54_ScaleMax |  | 10001182
[8 empty] | 10001183 | Para_Custom_AnalogIn_54_ScaleMin | Para_Custom_AnalogIn_54_ScaleMin | 2492 | Para_Custom_AnalogIn_54_ScaleMin |  | 10001183
[8 empty] | 10001240 | Para_Custom_AnalogIn_55_CustAnaIn_Active55 | Para_Custom_AnalogIn_55_CustAnaIn_Active55 | 2493 | Para_Custom_AnalogIn_55_CustAnaIn_Active55 |  | 10001240
[8 empty] | 10001270 | Para_Custom_AnalogIn_55_CustAnaIn_MinMaxActive55 | Para_Custom_AnalogIn_55_CustAnaIn_MinMaxActive55 | 2494 | Para_Custom_AnalogIn_55_CustAnaIn_MinMaxActive55 |  | 10001270
[8 empty] | 10001177 | Para_Custom_AnalogIn_55_CustAnaIn_Set4mA55 | Para_Custom_AnalogIn_55_CustAnaIn_Set4mA55 | 2495 | Para_Custom_AnalogIn_55_CustAnaIn_Set4mA55 |  | 10001177
[8 empty] | 10008640 | Para_Custom_AnalogIn_55_CustAnaIn_Typ55 | Para_Custom_AnalogIn_55_CustAnaIn_Typ55 | 2496 | Para_Custom_AnalogIn_55_CustAnaIn_Typ55 |  | 10008640
[8 empty] | 10001184 | Para_Custom_AnalogIn_55_Hystereses | Para_Custom_AnalogIn_55_Hystereses | 2497 | Para_Custom_AnalogIn_55_Hystereses |  | 10001184
[8 empty] | 10001189 | Para_Custom_AnalogIn_55_LimitHi | Para_Custom_AnalogIn_55_LimitHi | 2498 | Para_Custom_AnalogIn_55_LimitHi |  | 10001189
[8 empty] | 10002998 | Para_Custom_AnalogIn_55_LimitHiHi | Para_Custom_AnalogIn_55_LimitHiHi | 2499 | Para_Custom_AnalogIn_55_LimitHiHi |  | 10002998
[8 empty] | 10001186 | Para_Custom_AnalogIn_55_LimitLo | Para_Custom_AnalogIn_55_LimitLo | 2500 | Para_Custom_AnalogIn_55_LimitLo |  | 10001186
[8 empty] | 10003000 | Para_Custom_AnalogIn_55_LimitLoLo | Para_Custom_AnalogIn_55_LimitLoLo | 2501 | Para_Custom_AnalogIn_55_LimitLoLo |  | 10003000
[8 empty] | 10001187 | Para_Custom_AnalogIn_55_ScaleMax | Para_Custom_AnalogIn_55_ScaleMax | 2502 | Para_Custom_AnalogIn_55_ScaleMax |  | 10001187
[8 empty] | 10001185 | Para_Custom_AnalogIn_55_ScaleMin | Para_Custom_AnalogIn_55_ScaleMin | 2503 | Para_Custom_AnalogIn_55_ScaleMin |  | 10001185
[8 empty] | 10001236 | Para_Custom_AnalogIn_56_CustAnaIn_Active56 | Para_Custom_AnalogIn_56_CustAnaIn_Active56 | 2504 | Para_Custom_AnalogIn_56_CustAnaIn_Active56 |  | 10001236
[8 empty] | 10001272 | Para_Custom_AnalogIn_56_CustAnaIn_MinMaxActive56 | Para_Custom_AnalogIn_56_CustAnaIn_MinMaxActive56 | 2505 | Para_Custom_AnalogIn_56_CustAnaIn_MinMaxActive56 |  | 10001272
[8 empty] | 10001176 | Para_Custom_AnalogIn_56_CustAnaIn_Set4mA56 | Para_Custom_AnalogIn_56_CustAnaIn_Set4mA56 | 2506 | Para_Custom_AnalogIn_56_CustAnaIn_Set4mA56 |  | 10001176
[8 empty] | 10008637 | Para_Custom_AnalogIn_56_CustAnaIn_Typ56 | Para_Custom_AnalogIn_56_CustAnaIn_Typ56 | 2507 | Para_Custom_AnalogIn_56_CustAnaIn_Typ56 |  | 10008637
[8 empty] | 10001190 | Para_Custom_AnalogIn_56_Hystereses | Para_Custom_AnalogIn_56_Hystereses | 2508 | Para_Custom_AnalogIn_56_Hystereses |  | 10001190
[8 empty] | 10001191 | Para_Custom_AnalogIn_56_LimitHi | Para_Custom_AnalogIn_56_LimitHi | 2509 | Para_Custom_AnalogIn_56_LimitHi |  | 10001191
[8 empty] | 10003001 | Para_Custom_AnalogIn_56_LimitHiHi | Para_Custom_AnalogIn_56_LimitHiHi | 2510 | Para_Custom_AnalogIn_56_LimitHiHi |  | 10003001
[8 empty] | 10001188 | Para_Custom_AnalogIn_56_LimitLo | Para_Custom_AnalogIn_56_LimitLo | 2511 | Para_Custom_AnalogIn_56_LimitLo |  | 10001188
[8 empty] | 10003004 | Para_Custom_AnalogIn_56_LimitLoLo | Para_Custom_AnalogIn_56_LimitLoLo | 2512 | Para_Custom_AnalogIn_56_LimitLoLo |  | 10003004
[8 empty] | 10001192 | Para_Custom_AnalogIn_56_ScaleMax | Para_Custom_AnalogIn_56_ScaleMax | 2513 | Para_Custom_AnalogIn_56_ScaleMax |  | 10001192
[8 empty] | 10001193 | Para_Custom_AnalogIn_56_ScaleMin | Para_Custom_AnalogIn_56_ScaleMin | 2514 | Para_Custom_AnalogIn_56_ScaleMin |  | 10001193
[8 empty] | 10001238 | Para_Custom_AnalogIn_57_CustAnaIn_Active57 | Para_Custom_AnalogIn_57_CustAnaIn_Active57 | 2515 | Para_Custom_AnalogIn_57_CustAnaIn_Active57 |  | 10001238
[8 empty] | 10001271 | Para_Custom_AnalogIn_57_CustAnaIn_MinMaxActive57 | Para_Custom_AnalogIn_57_CustAnaIn_MinMaxActive57 | 2516 | Para_Custom_AnalogIn_57_CustAnaIn_MinMaxActive57 |  | 10001271
[8 empty] | 10001180 | Para_Custom_AnalogIn_57_CustAnaIn_Set4mA57 | Para_Custom_AnalogIn_57_CustAnaIn_Set4mA57 | 2517 | Para_Custom_AnalogIn_57_CustAnaIn_Set4mA57 |  | 10001180
[8 empty] | 10008635 | Para_Custom_AnalogIn_57_CustAnaIn_Typ57 | Para_Custom_AnalogIn_57_CustAnaIn_Typ57 | 2518 | Para_Custom_AnalogIn_57_CustAnaIn_Typ57 |  | 10008635
[8 empty] | 10001194 | Para_Custom_AnalogIn_57_Hystereses | Para_Custom_AnalogIn_57_Hystereses | 2519 | Para_Custom_AnalogIn_57_Hystereses |  | 10001194
[8 empty] | 10001195 | Para_Custom_AnalogIn_57_LimitHi | Para_Custom_AnalogIn_57_LimitHi | 2520 | Para_Custom_AnalogIn_57_LimitHi |  | 10001195
[8 empty] | 10003007 | Para_Custom_AnalogIn_57_LimitHiHi | Para_Custom_AnalogIn_57_LimitHiHi | 2521 | Para_Custom_AnalogIn_57_LimitHiHi |  | 10003007
[8 empty] | 10001197 | Para_Custom_AnalogIn_57_LimitLo | Para_Custom_AnalogIn_57_LimitLo | 2522 | Para_Custom_AnalogIn_57_LimitLo |  | 10001197
[8 empty] | 10003009 | Para_Custom_AnalogIn_57_LimitLoLo | Para_Custom_AnalogIn_57_LimitLoLo | 2523 | Para_Custom_AnalogIn_57_LimitLoLo |  | 10003009
[8 empty] | 10001196 | Para_Custom_AnalogIn_57_ScaleMax | Para_Custom_AnalogIn_57_ScaleMax | 2524 | Para_Custom_AnalogIn_57_ScaleMax |  | 10001196
[8 empty] | 10001199 | Para_Custom_AnalogIn_57_ScaleMin | Para_Custom_AnalogIn_57_ScaleMin | 2525 | Para_Custom_AnalogIn_57_ScaleMin |  | 10001199
[8 empty] | 10001241 | Para_Custom_AnalogIn_58_CustAnaIn_Active58 | Para_Custom_AnalogIn_58_CustAnaIn_Active58 | 2526 | Para_Custom_AnalogIn_58_CustAnaIn_Active58 |  | 10001241
[8 empty] | 10001273 | Para_Custom_AnalogIn_58_CustAnaIn_MinMaxActive58 | Para_Custom_AnalogIn_58_CustAnaIn_MinMaxActive58 | 2527 | Para_Custom_AnalogIn_58_CustAnaIn_MinMaxActive58 |  | 10001273
[8 empty] | 10001264 | Para_Custom_AnalogIn_58_CustAnaIn_Set4mA58 | Para_Custom_AnalogIn_58_CustAnaIn_Set4mA58 | 2528 | Para_Custom_AnalogIn_58_CustAnaIn_Set4mA58 |  | 10001264
[8 empty] | 10008641 | Para_Custom_AnalogIn_58_CustAnaIn_Typ58 | Para_Custom_AnalogIn_58_CustAnaIn_Typ58 | 2529 | Para_Custom_AnalogIn_58_CustAnaIn_Typ58 |  | 10008641
[8 empty] | 10001200 | Para_Custom_AnalogIn_58_Hystereses | Para_Custom_AnalogIn_58_Hystereses | 2530 | Para_Custom_AnalogIn_58_Hystereses |  | 10001200
[8 empty] | 10001198 | Para_Custom_AnalogIn_58_LimitHi | Para_Custom_AnalogIn_58_LimitHi | 2531 | Para_Custom_AnalogIn_58_LimitHi |  | 10001198
[8 empty] | 10003005 | Para_Custom_AnalogIn_58_LimitHiHi | Para_Custom_AnalogIn_58_LimitHiHi | 2532 | Para_Custom_AnalogIn_58_LimitHiHi |  | 10003005
[8 empty] | 10001202 | Para_Custom_AnalogIn_58_LimitLo | Para_Custom_AnalogIn_58_LimitLo | 2533 | Para_Custom_AnalogIn_58_LimitLo |  | 10001202
[8 empty] | 10003008 | Para_Custom_AnalogIn_58_LimitLoLo | Para_Custom_AnalogIn_58_LimitLoLo | 2534 | Para_Custom_AnalogIn_58_LimitLoLo |  | 10003008
[8 empty] | 10001203 | Para_Custom_AnalogIn_58_ScaleMax | Para_Custom_AnalogIn_58_ScaleMax | 2535 | Para_Custom_AnalogIn_58_ScaleMax |  | 10001203
[8 empty] | 10001201 | Para_Custom_AnalogIn_58_ScaleMin | Para_Custom_AnalogIn_58_ScaleMin | 2536 | Para_Custom_AnalogIn_58_ScaleMin |  | 10001201
[8 empty] | 10001243 | Para_Custom_AnalogIn_59_CustAnaIn_Active59 | Para_Custom_AnalogIn_59_CustAnaIn_Active59 | 2537 | Para_Custom_AnalogIn_59_CustAnaIn_Active59 |  | 10001243
[8 empty] | 10001277 | Para_Custom_AnalogIn_59_CustAnaIn_MinMaxActive59 | Para_Custom_AnalogIn_59_CustAnaIn_MinMaxActive59 | 2538 | Para_Custom_AnalogIn_59_CustAnaIn_MinMaxActive59 |  | 10001277
[8 empty] | 10001275 | Para_Custom_AnalogIn_59_CustAnaIn_Set4mA59 | Para_Custom_AnalogIn_59_CustAnaIn_Set4mA59 | 2539 | Para_Custom_AnalogIn_59_CustAnaIn_Set4mA59 |  | 10001275
[8 empty] | 10008642 | Para_Custom_AnalogIn_59_CustAnaIn_Typ59 | Para_Custom_AnalogIn_59_CustAnaIn_Typ59 | 2540 | Para_Custom_AnalogIn_59_CustAnaIn_Typ59 |  | 10008642
[8 empty] | 10001205 | Para_Custom_AnalogIn_59_Hystereses | Para_Custom_AnalogIn_59_Hystereses | 2541 | Para_Custom_AnalogIn_59_Hystereses |  | 10001205
[8 empty] | 10001208 | Para_Custom_AnalogIn_59_LimitHi | Para_Custom_AnalogIn_59_LimitHi | 2542 | Para_Custom_AnalogIn_59_LimitHi |  | 10001208
[8 empty] | 10003010 | Para_Custom_AnalogIn_59_LimitHiHi | Para_Custom_AnalogIn_59_LimitHiHi | 2543 | Para_Custom_AnalogIn_59_LimitHiHi |  | 10003010
[8 empty] | 10001206 | Para_Custom_AnalogIn_59_LimitLo | Para_Custom_AnalogIn_59_LimitLo | 2544 | Para_Custom_AnalogIn_59_LimitLo |  | 10001206
[8 empty] | 10003013 | Para_Custom_AnalogIn_59_LimitLoLo | Para_Custom_AnalogIn_59_LimitLoLo | 2545 | Para_Custom_AnalogIn_59_LimitLoLo |  | 10003013
[8 empty] | 10001204 | Para_Custom_AnalogIn_59_ScaleMax | Para_Custom_AnalogIn_59_ScaleMax | 2546 | Para_Custom_AnalogIn_59_ScaleMax |  | 10001204
[8 empty] | 10001209 | Para_Custom_AnalogIn_59_ScaleMin | Para_Custom_AnalogIn_59_ScaleMin | 2547 | Para_Custom_AnalogIn_59_ScaleMin |  | 10001209
[8 empty] | 10001003 | Para_Custom_AnalogIn_5_CustAnaIn_MinMaxActive5 | Para_Custom_AnalogIn_5_CustAnaIn_MinMaxActive5 | 2548 | Para_Custom_AnalogIn_5_CustAnaIn_MinMaxActive5 |  | 10001003
[8 empty] | 10008632 | Para_Custom_AnalogIn_5_CustAnaIn_Typ5 | Para_Custom_AnalogIn_5_CustAnaIn_Typ5 | 2549 | Para_Custom_AnalogIn_5_CustAnaIn_Typ5 |  | 10008632
[8 empty] | 10000853 | Para_Custom_AnalogIn_5_Hystereses | Para_Custom_AnalogIn_5_Hystereses | 2550 | Para_Custom_AnalogIn_5_Hystereses |  | 10000853
[8 empty] | 10000883 | Para_Custom_AnalogIn_5_LimitHi | Para_Custom_AnalogIn_5_LimitHi | 2551 | Para_Custom_AnalogIn_5_LimitHi |  | 10000883
[8 empty] | 10000067 | Para_Custom_AnalogIn_5_LimitHiHi | Para_Custom_AnalogIn_5_LimitHiHi | 2552 | Para_Custom_AnalogIn_5_LimitHiHi |  | 10000067
[8 empty] | 10000916 | Para_Custom_AnalogIn_5_LimitLo | Para_Custom_AnalogIn_5_LimitLo | 2553 | Para_Custom_AnalogIn_5_LimitLo |  | 10000916
[8 empty] | 10000068 | Para_Custom_AnalogIn_5_LimitLoLo | Para_Custom_AnalogIn_5_LimitLoLo | 2554 | Para_Custom_AnalogIn_5_LimitLoLo |  | 10000068
[8 empty] | 10001242 | Para_Custom_AnalogIn_60_CustAnaIn_Active60 | Para_Custom_AnalogIn_60_CustAnaIn_Active60 | 2555 | Para_Custom_AnalogIn_60_CustAnaIn_Active60 |  | 10001242
[8 empty] | 10001274 | Para_Custom_AnalogIn_60_CustAnaIn_MinMaxActive60 | Para_Custom_AnalogIn_60_CustAnaIn_MinMaxActive60 | 2556 | Para_Custom_AnalogIn_60_CustAnaIn_MinMaxActive60 |  | 10001274
[8 empty] | 10001278 | Para_Custom_AnalogIn_60_CustAnaIn_Set4mA60 | Para_Custom_AnalogIn_60_CustAnaIn_Set4mA60 | 2557 | Para_Custom_AnalogIn_60_CustAnaIn_Set4mA60 |  | 10001278
[8 empty] | 10008647 | Para_Custom_AnalogIn_60_CustAnaIn_Typ60 | Para_Custom_AnalogIn_60_CustAnaIn_Typ60 | 2558 | Para_Custom_AnalogIn_60_CustAnaIn_Typ60 |  | 10008647
[8 empty] | 10001207 | Para_Custom_AnalogIn_60_Hystereses | Para_Custom_AnalogIn_60_Hystereses | 2559 | Para_Custom_AnalogIn_60_Hystereses |  | 10001207
[8 empty] | 10001210 | Para_Custom_AnalogIn_60_LimitHi | Para_Custom_AnalogIn_60_LimitHi | 2560 | Para_Custom_AnalogIn_60_LimitHi |  | 10001210
[8 empty] | 10003011 | Para_Custom_AnalogIn_60_LimitHiHi | Para_Custom_AnalogIn_60_LimitHiHi | 2561 | Para_Custom_AnalogIn_60_LimitHiHi |  | 10003011
[8 empty] | 10001211 | Para_Custom_AnalogIn_60_LimitLo | Para_Custom_AnalogIn_60_LimitLo | 2562 | Para_Custom_AnalogIn_60_LimitLo |  | 10001211
[8 empty] | 10003012 | Para_Custom_AnalogIn_60_LimitLoLo | Para_Custom_AnalogIn_60_LimitLoLo | 2563 | Para_Custom_AnalogIn_60_LimitLoLo |  | 10003012
[8 empty] | 10001216 | Para_Custom_AnalogIn_60_ScaleMax | Para_Custom_AnalogIn_60_ScaleMax | 2564 | Para_Custom_AnalogIn_60_ScaleMax |  | 10001216
[8 empty] | 10001212 | Para_Custom_AnalogIn_60_ScaleMin | Para_Custom_AnalogIn_60_ScaleMin | 2565 | Para_Custom_AnalogIn_60_ScaleMin |  | 10001212
[8 empty] | 10001036 | Para_Custom_AnalogIn_6_CustAnaIn_MinMaxActive6 | Para_Custom_AnalogIn_6_CustAnaIn_MinMaxActive6 | 2566 | Para_Custom_AnalogIn_6_CustAnaIn_MinMaxActive6 |  | 10001036
[8 empty] | 10008644 | Para_Custom_AnalogIn_6_CustAnaIn_Typ6 | Para_Custom_AnalogIn_6_CustAnaIn_Typ6 | 2567 | Para_Custom_AnalogIn_6_CustAnaIn_Typ6 |  | 10008644
[8 empty] | 10000852 | Para_Custom_AnalogIn_6_Hystereses | Para_Custom_AnalogIn_6_Hystereses | 2568 | Para_Custom_AnalogIn_6_Hystereses |  | 10000852
[8 empty] | 10000886 | Para_Custom_AnalogIn_6_LimitHi | Para_Custom_AnalogIn_6_LimitHi | 2569 | Para_Custom_AnalogIn_6_LimitHi |  | 10000886
[8 empty] | 10002798 | Para_Custom_AnalogIn_6_LimitHiHi | Para_Custom_AnalogIn_6_LimitHiHi | 2570 | Para_Custom_AnalogIn_6_LimitHiHi |  | 10002798
[8 empty] | 10000910 | Para_Custom_AnalogIn_6_LimitLo | Para_Custom_AnalogIn_6_LimitLo | 2571 | Para_Custom_AnalogIn_6_LimitLo |  | 10000910
[8 empty] | 10002803 | Para_Custom_AnalogIn_6_LimitLoLo | Para_Custom_AnalogIn_6_LimitLoLo | 2572 | Para_Custom_AnalogIn_6_LimitLoLo |  | 10002803
[8 empty] | 10001038 | Para_Custom_AnalogIn_7_CustAnaIn_MinMaxActive7 | Para_Custom_AnalogIn_7_CustAnaIn_MinMaxActive7 | 2573 | Para_Custom_AnalogIn_7_CustAnaIn_MinMaxActive7 |  | 10001038
[8 empty] | 10008643 | Para_Custom_AnalogIn_7_CustAnaIn_Typ7 | Para_Custom_AnalogIn_7_CustAnaIn_Typ7 | 2574 | Para_Custom_AnalogIn_7_CustAnaIn_Typ7 |  | 10008643
[8 empty] | 10000858 | Para_Custom_AnalogIn_7_Hystereses | Para_Custom_AnalogIn_7_Hystereses | 2575 | Para_Custom_AnalogIn_7_Hystereses |  | 10000858
[8 empty] | 10000887 | Para_Custom_AnalogIn_7_LimitHi | Para_Custom_AnalogIn_7_LimitHi | 2576 | Para_Custom_AnalogIn_7_LimitHi |  | 10000887
[8 empty] | 10002796 | Para_Custom_AnalogIn_7_LimitHiHi | Para_Custom_AnalogIn_7_LimitHiHi | 2577 | Para_Custom_AnalogIn_7_LimitHiHi |  | 10002796
[8 empty] | 10000913 | Para_Custom_AnalogIn_7_LimitLo | Para_Custom_AnalogIn_7_LimitLo | 2578 | Para_Custom_AnalogIn_7_LimitLo |  | 10000913
[8 empty] | 10002801 | Para_Custom_AnalogIn_7_LimitLoLo | Para_Custom_AnalogIn_7_LimitLoLo | 2579 | Para_Custom_AnalogIn_7_LimitLoLo |  | 10002801
[8 empty] | 10001073 | Para_Custom_AnalogIn_8_CustAnaIn_MinMaxActive8 | Para_Custom_AnalogIn_8_CustAnaIn_MinMaxActive8 | 2580 | Para_Custom_AnalogIn_8_CustAnaIn_MinMaxActive8 |  | 10001073
[8 empty] | 10008645 | Para_Custom_AnalogIn_8_CustAnaIn_Typ8 | Para_Custom_AnalogIn_8_CustAnaIn_Typ8 | 2581 | Para_Custom_AnalogIn_8_CustAnaIn_Typ8 |  | 10008645
[8 empty] | 10000857 | Para_Custom_AnalogIn_8_Hystereses | Para_Custom_AnalogIn_8_Hystereses | 2582 | Para_Custom_AnalogIn_8_Hystereses |  | 10000857
[8 empty] | 10000885 | Para_Custom_AnalogIn_8_LimitHi | Para_Custom_AnalogIn_8_LimitHi | 2583 | Para_Custom_AnalogIn_8_LimitHi |  | 10000885
[8 empty] | 10002802 | Para_Custom_AnalogIn_8_LimitHiHi | Para_Custom_AnalogIn_8_LimitHiHi | 2584 | Para_Custom_AnalogIn_8_LimitHiHi |  | 10002802
[8 empty] | 10000917 | Para_Custom_AnalogIn_8_LimitLo | Para_Custom_AnalogIn_8_LimitLo | 2585 | Para_Custom_AnalogIn_8_LimitLo |  | 10000917
[8 empty] | 10002811 | Para_Custom_AnalogIn_8_LimitLoLo | Para_Custom_AnalogIn_8_LimitLoLo | 2586 | Para_Custom_AnalogIn_8_LimitLoLo |  | 10002811
[8 empty] | 10000828 | Para_Custom_AnalogIn_9_CustAnaIn_MinMaxActive9 | Para_Custom_AnalogIn_9_CustAnaIn_MinMaxActive9 | 2587 | Para_Custom_AnalogIn_9_CustAnaIn_MinMaxActive9 |  | 10000828
[8 empty] | 10008646 | Para_Custom_AnalogIn_9_CustAnaIn_Typ9 | Para_Custom_AnalogIn_9_CustAnaIn_Typ9 | 2588 | Para_Custom_AnalogIn_9_CustAnaIn_Typ9 |  | 10008646
[8 empty] | 10000855 | Para_Custom_AnalogIn_9_Hystereses | Para_Custom_AnalogIn_9_Hystereses | 2589 | Para_Custom_AnalogIn_9_Hystereses |  | 10000855
[8 empty] | 10000889 | Para_Custom_AnalogIn_9_LimitHi | Para_Custom_AnalogIn_9_LimitHi | 2590 | Para_Custom_AnalogIn_9_LimitHi |  | 10000889
[8 empty] | 10002810 | Para_Custom_AnalogIn_9_LimitHiHi | Para_Custom_AnalogIn_9_LimitHiHi | 2591 | Para_Custom_AnalogIn_9_LimitHiHi |  | 10002810
[8 empty] | 10000921 | Para_Custom_AnalogIn_9_LimitLo | Para_Custom_AnalogIn_9_LimitLo | 2592 | Para_Custom_AnalogIn_9_LimitLo |  | 10000921
[8 empty] | 10002812 | Para_Custom_AnalogIn_9_LimitLoLo | Para_Custom_AnalogIn_9_LimitLoLo | 2593 | Para_Custom_AnalogIn_9_LimitLoLo |  | 10002812
[8 empty] | 10003017 | Para_Custom_AnalogOut_AO10_HardwareScaleMax | Para_Custom_AnalogOut_AO10_HardwareScaleMax | 2594 | Para_Custom_AnalogOut_AO10_HardwareScaleMax |  | 10003017
[8 empty] | 10003032 | Para_Custom_AnalogOut_AO10_HardwareScaleMin | Para_Custom_AnalogOut_AO10_HardwareScaleMin | 2595 | Para_Custom_AnalogOut_AO10_HardwareScaleMin |  | 10003032
[8 empty] | 10000948 | Para_Custom_AnalogOut_AO10_ScaleMax | Para_Custom_AnalogOut_AO10_ScaleMax | 2596 | Para_Custom_AnalogOut_AO10_ScaleMax |  | 10000948
[8 empty] | 10000965 | Para_Custom_AnalogOut_AO10_ScaleMin | Para_Custom_AnalogOut_AO10_ScaleMin | 2597 | Para_Custom_AnalogOut_AO10_ScaleMin |  | 10000965
[8 empty] | 10003018 | Para_Custom_AnalogOut_AO11_HardwareScaleMax | Para_Custom_AnalogOut_AO11_HardwareScaleMax | 2598 | Para_Custom_AnalogOut_AO11_HardwareScaleMax |  | 10003018
[8 empty] | 10003033 | Para_Custom_AnalogOut_AO11_HardwareScaleMin | Para_Custom_AnalogOut_AO11_HardwareScaleMin | 2599 | Para_Custom_AnalogOut_AO11_HardwareScaleMin |  | 10003033
[8 empty] | 10000952 | Para_Custom_AnalogOut_AO11_ScaleMax | Para_Custom_AnalogOut_AO11_ScaleMax | 2600 | Para_Custom_AnalogOut_AO11_ScaleMax |  | 10000952
[8 empty] | 10000962 | Para_Custom_AnalogOut_AO11_ScaleMin | Para_Custom_AnalogOut_AO11_ScaleMin | 2601 | Para_Custom_AnalogOut_AO11_ScaleMin |  | 10000962
[8 empty] | 10003016 | Para_Custom_AnalogOut_AO12_HardwareScaleMax | Para_Custom_AnalogOut_AO12_HardwareScaleMax | 2602 | Para_Custom_AnalogOut_AO12_HardwareScaleMax |  | 10003016
[8 empty] | 10003035 | Para_Custom_AnalogOut_AO12_HardwareScaleMin | Para_Custom_AnalogOut_AO12_HardwareScaleMin | 2603 | Para_Custom_AnalogOut_AO12_HardwareScaleMin |  | 10003035
[8 empty] | 10000951 | Para_Custom_AnalogOut_AO12_ScaleMax | Para_Custom_AnalogOut_AO12_ScaleMax | 2604 | Para_Custom_AnalogOut_AO12_ScaleMax |  | 10000951
[8 empty] | 10000969 | Para_Custom_AnalogOut_AO12_ScaleMin | Para_Custom_AnalogOut_AO12_ScaleMin | 2605 | Para_Custom_AnalogOut_AO12_ScaleMin |  | 10000969
[8 empty] | 10003020 | Para_Custom_AnalogOut_AO13_HardwareScaleMax | Para_Custom_AnalogOut_AO13_HardwareScaleMax | 2606 | Para_Custom_AnalogOut_AO13_HardwareScaleMax |  | 10003020
[8 empty] | 10003036 | Para_Custom_AnalogOut_AO13_HardwareScaleMin | Para_Custom_AnalogOut_AO13_HardwareScaleMin | 2607 | Para_Custom_AnalogOut_AO13_HardwareScaleMin |  | 10003036
[8 empty] | 10000949 | Para_Custom_AnalogOut_AO13_ScaleMax | Para_Custom_AnalogOut_AO13_ScaleMax | 2608 | Para_Custom_AnalogOut_AO13_ScaleMax |  | 10000949
[8 empty] | 10000967 | Para_Custom_AnalogOut_AO13_ScaleMin | Para_Custom_AnalogOut_AO13_ScaleMin | 2609 | Para_Custom_AnalogOut_AO13_ScaleMin |  | 10000967
[8 empty] | 10003022 | Para_Custom_AnalogOut_AO14_HardwareScaleMax | Para_Custom_AnalogOut_AO14_HardwareScaleMax | 2610 | Para_Custom_AnalogOut_AO14_HardwareScaleMax |  | 10003022
[8 empty] | 10003039 | Para_Custom_AnalogOut_AO14_HardwareScaleMin | Para_Custom_AnalogOut_AO14_HardwareScaleMin | 2611 | Para_Custom_AnalogOut_AO14_HardwareScaleMin |  | 10003039
[8 empty] | 10000953 | Para_Custom_AnalogOut_AO14_ScaleMax | Para_Custom_AnalogOut_AO14_ScaleMax | 2612 | Para_Custom_AnalogOut_AO14_ScaleMax |  | 10000953
[8 empty] | 10000968 | Para_Custom_AnalogOut_AO14_ScaleMin | Para_Custom_AnalogOut_AO14_ScaleMin | 2613 | Para_Custom_AnalogOut_AO14_ScaleMin |  | 10000968
[8 empty] | 10003019 | Para_Custom_AnalogOut_AO15_HardwareScaleMax | Para_Custom_AnalogOut_AO15_HardwareScaleMax | 2614 | Para_Custom_AnalogOut_AO15_HardwareScaleMax |  | 10003019
[8 empty] | 10003038 | Para_Custom_AnalogOut_AO15_HardwareScaleMin | Para_Custom_AnalogOut_AO15_HardwareScaleMin | 2615 | Para_Custom_AnalogOut_AO15_HardwareScaleMin |  | 10003038
[8 empty] | 10000950 | Para_Custom_AnalogOut_AO15_ScaleMax | Para_Custom_AnalogOut_AO15_ScaleMax | 2616 | Para_Custom_AnalogOut_AO15_ScaleMax |  | 10000950
[8 empty] | 10000970 | Para_Custom_AnalogOut_AO15_ScaleMin | Para_Custom_AnalogOut_AO15_ScaleMin | 2617 | Para_Custom_AnalogOut_AO15_ScaleMin |  | 10000970
[8 empty] | 10003023 | Para_Custom_AnalogOut_AO16_HardwareScaleMax | Para_Custom_AnalogOut_AO16_HardwareScaleMax | 2618 | Para_Custom_AnalogOut_AO16_HardwareScaleMax |  | 10003023
[8 empty] | 10003041 | Para_Custom_AnalogOut_AO16_HardwareScaleMin | Para_Custom_AnalogOut_AO16_HardwareScaleMin | 2619 | Para_Custom_AnalogOut_AO16_HardwareScaleMin |  | 10003041
[8 empty] | 10000956 | Para_Custom_AnalogOut_AO16_ScaleMax | Para_Custom_AnalogOut_AO16_ScaleMax | 2620 | Para_Custom_AnalogOut_AO16_ScaleMax |  | 10000956
[8 empty] | 10000964 | Para_Custom_AnalogOut_AO16_ScaleMin | Para_Custom_AnalogOut_AO16_ScaleMin | 2621 | Para_Custom_AnalogOut_AO16_ScaleMin |  | 10000964
[8 empty] | 10003062 | Para_Custom_AnalogOut_AO1_HardwareScaleMax | Para_Custom_AnalogOut_AO1_HardwareScaleMax | 2622 | Para_Custom_AnalogOut_AO1_HardwareScaleMax |  | 10003062
[8 empty] | 10003065 | Para_Custom_AnalogOut_AO1_HardwareScaleMin | Para_Custom_AnalogOut_AO1_HardwareScaleMin | 2623 | Para_Custom_AnalogOut_AO1_HardwareScaleMin |  | 10003065
[8 empty] | 10000945 | Para_Custom_AnalogOut_AO1_ScaleMax | Para_Custom_AnalogOut_AO1_ScaleMax | 2624 | Para_Custom_AnalogOut_AO1_ScaleMax |  | 10000945
[8 empty] | 10000966 | Para_Custom_AnalogOut_AO1_ScaleMin | Para_Custom_AnalogOut_AO1_ScaleMin | 2625 | Para_Custom_AnalogOut_AO1_ScaleMin |  | 10000966
[8 empty] | 10003064 | Para_Custom_AnalogOut_AO2_HardwareScaleMax | Para_Custom_AnalogOut_AO2_HardwareScaleMax | 2626 | Para_Custom_AnalogOut_AO2_HardwareScaleMax |  | 10003064
[8 empty] | 10003021 | Para_Custom_AnalogOut_AO2_HardwareScaleMin | Para_Custom_AnalogOut_AO2_HardwareScaleMin | 2627 | Para_Custom_AnalogOut_AO2_HardwareScaleMin |  | 10003021
[8 empty] | 10000954 | Para_Custom_AnalogOut_AO2_ScaleMax | Para_Custom_AnalogOut_AO2_ScaleMax | 2628 | Para_Custom_AnalogOut_AO2_ScaleMax |  | 10000954
[8 empty] | 10000972 | Para_Custom_AnalogOut_AO2_ScaleMin | Para_Custom_AnalogOut_AO2_ScaleMin | 2629 | Para_Custom_AnalogOut_AO2_ScaleMin |  | 10000972
[8 empty] | 10003063 | Para_Custom_AnalogOut_AO3_HardwareScaleMax | Para_Custom_AnalogOut_AO3_HardwareScaleMax | 2630 | Para_Custom_AnalogOut_AO3_HardwareScaleMax |  | 10003063
[8 empty] | 10003027 | Para_Custom_AnalogOut_AO3_HardwareScaleMin | Para_Custom_AnalogOut_AO3_HardwareScaleMin | 2631 | Para_Custom_AnalogOut_AO3_HardwareScaleMin |  | 10003027
[8 empty] | 10000955 | Para_Custom_AnalogOut_AO3_ScaleMax | Para_Custom_AnalogOut_AO3_ScaleMax | 2632 | Para_Custom_AnalogOut_AO3_ScaleMax |  | 10000955
[8 empty] | 10000971 | Para_Custom_AnalogOut_AO3_ScaleMin | Para_Custom_AnalogOut_AO3_ScaleMin | 2633 | Para_Custom_AnalogOut_AO3_ScaleMin |  | 10000971
[8 empty] | 10003066 | Para_Custom_AnalogOut_AO4_HardwareScaleMax | Para_Custom_AnalogOut_AO4_HardwareScaleMax | 2634 | Para_Custom_AnalogOut_AO4_HardwareScaleMax |  | 10003066
[8 empty] | 10003024 | Para_Custom_AnalogOut_AO4_HardwareScaleMin | Para_Custom_AnalogOut_AO4_HardwareScaleMin | 2635 | Para_Custom_AnalogOut_AO4_HardwareScaleMin |  | 10003024
[8 empty] | 10000959 | Para_Custom_AnalogOut_AO4_ScaleMax | Para_Custom_AnalogOut_AO4_ScaleMax | 2636 | Para_Custom_AnalogOut_AO4_ScaleMax |  | 10000959
[8 empty] | 10000973 | Para_Custom_AnalogOut_AO4_ScaleMin | Para_Custom_AnalogOut_AO4_ScaleMin | 2637 | Para_Custom_AnalogOut_AO4_ScaleMin |  | 10000973
[8 empty] | 10003067 | Para_Custom_AnalogOut_AO5_HardwareScaleMax | Para_Custom_AnalogOut_AO5_HardwareScaleMax | 2638 | Para_Custom_AnalogOut_AO5_HardwareScaleMax |  | 10003067
[8 empty] | 10003028 | Para_Custom_AnalogOut_AO5_HardwareScaleMin | Para_Custom_AnalogOut_AO5_HardwareScaleMin | 2639 | Para_Custom_AnalogOut_AO5_HardwareScaleMin |  | 10003028
[8 empty] | 10000958 | Para_Custom_AnalogOut_AO5_ScaleMax | Para_Custom_AnalogOut_AO5_ScaleMax | 2640 | Para_Custom_AnalogOut_AO5_ScaleMax |  | 10000958
[8 empty] | 10000975 | Para_Custom_AnalogOut_AO5_ScaleMin | Para_Custom_AnalogOut_AO5_ScaleMin | 2641 | Para_Custom_AnalogOut_AO5_ScaleMin |  | 10000975
[8 empty] | 10003068 | Para_Custom_AnalogOut_AO6_HardwareScaleMax | Para_Custom_AnalogOut_AO6_HardwareScaleMax | 2642 | Para_Custom_AnalogOut_AO6_HardwareScaleMax |  | 10003068
[8 empty] | 10003026 | Para_Custom_AnalogOut_AO6_HardwareScaleMin | Para_Custom_AnalogOut_AO6_HardwareScaleMin | 2643 | Para_Custom_AnalogOut_AO6_HardwareScaleMin |  | 10003026
[8 empty] | 10000957 | Para_Custom_AnalogOut_AO6_ScaleMax | Para_Custom_AnalogOut_AO6_ScaleMax | 2644 | Para_Custom_AnalogOut_AO6_ScaleMax |  | 10000957
[8 empty] | 10000974 | Para_Custom_AnalogOut_AO6_ScaleMin | Para_Custom_AnalogOut_AO6_ScaleMin | 2645 | Para_Custom_AnalogOut_AO6_ScaleMin |  | 10000974
[8 empty] | 10003069 | Para_Custom_AnalogOut_AO7_HardwareScaleMax | Para_Custom_AnalogOut_AO7_HardwareScaleMax | 2646 | Para_Custom_AnalogOut_AO7_HardwareScaleMax |  | 10003069
[8 empty] | 10003025 | Para_Custom_AnalogOut_AO7_HardwareScaleMin | Para_Custom_AnalogOut_AO7_HardwareScaleMin | 2647 | Para_Custom_AnalogOut_AO7_HardwareScaleMin |  | 10003025
[8 empty] | 10000960 | Para_Custom_AnalogOut_AO7_ScaleMax | Para_Custom_AnalogOut_AO7_ScaleMax | 2648 | Para_Custom_AnalogOut_AO7_ScaleMax |  | 10000960
[8 empty] | 10000976 | Para_Custom_AnalogOut_AO7_ScaleMin | Para_Custom_AnalogOut_AO7_ScaleMin | 2649 | Para_Custom_AnalogOut_AO7_ScaleMin |  | 10000976
[8 empty] | 10003070 | Para_Custom_AnalogOut_AO8_HardwareScaleMax | Para_Custom_AnalogOut_AO8_HardwareScaleMax | 2650 | Para_Custom_AnalogOut_AO8_HardwareScaleMax |  | 10003070
[8 empty] | 10003029 | Para_Custom_AnalogOut_AO8_HardwareScaleMin | Para_Custom_AnalogOut_AO8_HardwareScaleMin | 2651 | Para_Custom_AnalogOut_AO8_HardwareScaleMin |  | 10003029
[8 empty] | 10000961 | Para_Custom_AnalogOut_AO8_ScaleMax | Para_Custom_AnalogOut_AO8_ScaleMax | 2652 | Para_Custom_AnalogOut_AO8_ScaleMax |  | 10000961
[8 empty] | 10000979 | Para_Custom_AnalogOut_AO8_ScaleMin | Para_Custom_AnalogOut_AO8_ScaleMin | 2653 | Para_Custom_AnalogOut_AO8_ScaleMin |  | 10000979
[8 empty] | 10003071 | Para_Custom_AnalogOut_AO9_HardwareScaleMax | Para_Custom_AnalogOut_AO9_HardwareScaleMax | 2654 | Para_Custom_AnalogOut_AO9_HardwareScaleMax |  | 10003071
[8 empty] | 10003034 | Para_Custom_AnalogOut_AO9_HardwareScaleMin | Para_Custom_AnalogOut_AO9_HardwareScaleMin | 2655 | Para_Custom_AnalogOut_AO9_HardwareScaleMin |  | 10003034
[8 empty] | 10000963 | Para_Custom_AnalogOut_AO9_ScaleMax | Para_Custom_AnalogOut_AO9_ScaleMax | 2656 | Para_Custom_AnalogOut_AO9_ScaleMax |  | 10000963
[8 empty] | 10000977 | Para_Custom_AnalogOut_AO9_ScaleMin | Para_Custom_AnalogOut_AO9_ScaleMin | 2657 | Para_Custom_AnalogOut_AO9_ScaleMin |  | 10000977
[8 empty] | 10000980 | Para_Custom_Status_AuxCust_Active1 | Para_Custom_Status_AuxCust_Active1 | 2658 | Para_Custom_Status_AuxCust_Active1 |  | 10000980
[8 empty] | 10001033 | Para_Custom_Status_AuxCust_Active10 | Para_Custom_Status_AuxCust_Active10 | 2659 | Para_Custom_Status_AuxCust_Active10 |  | 10001033
[8 empty] | 10008481 | Para_Custom_Status_AuxCust_Active11 | Para_Custom_Status_AuxCust_Active11 | 2660 | Para_Custom_Status_AuxCust_Active11 |  | 10008481
[8 empty] | 10008487 | Para_Custom_Status_AuxCust_Active12 | Para_Custom_Status_AuxCust_Active12 | 2661 | Para_Custom_Status_AuxCust_Active12 |  | 10008487
[8 empty] | 10008484 | Para_Custom_Status_AuxCust_Active13 | Para_Custom_Status_AuxCust_Active13 | 2662 | Para_Custom_Status_AuxCust_Active13 |  | 10008484
[8 empty] | 10008483 | Para_Custom_Status_AuxCust_Active14 | Para_Custom_Status_AuxCust_Active14 | 2663 | Para_Custom_Status_AuxCust_Active14 |  | 10008483
[8 empty] | 10008459 | Para_Custom_Status_AuxCust_Active15 | Para_Custom_Status_AuxCust_Active15 | 2664 | Para_Custom_Status_AuxCust_Active15 |  | 10008459
[8 empty] | 10008482 | Para_Custom_Status_AuxCust_Active16 | Para_Custom_Status_AuxCust_Active16 | 2665 | Para_Custom_Status_AuxCust_Active16 |  | 10008482
[8 empty] | 10008460 | Para_Custom_Status_AuxCust_Active17 | Para_Custom_Status_AuxCust_Active17 | 2666 | Para_Custom_Status_AuxCust_Active17 |  | 10008460
[8 empty] | 10008461 | Para_Custom_Status_AuxCust_Active18 | Para_Custom_Status_AuxCust_Active18 | 2667 | Para_Custom_Status_AuxCust_Active18 |  | 10008461
[8 empty] | 10008462 | Para_Custom_Status_AuxCust_Active19 | Para_Custom_Status_AuxCust_Active19 | 2668 | Para_Custom_Status_AuxCust_Active19 |  | 10008462
[8 empty] | 10001024 | Para_Custom_Status_AuxCust_Active2 | Para_Custom_Status_AuxCust_Active2 | 2669 | Para_Custom_Status_AuxCust_Active2 |  | 10001024
[8 empty] | 10008463 | Para_Custom_Status_AuxCust_Active20 | Para_Custom_Status_AuxCust_Active20 | 2670 | Para_Custom_Status_AuxCust_Active20 |  | 10008463
[8 empty] | 10008464 | Para_Custom_Status_AuxCust_Active21 | Para_Custom_Status_AuxCust_Active21 | 2671 | Para_Custom_Status_AuxCust_Active21 |  | 10008464
[8 empty] | 10008466 | Para_Custom_Status_AuxCust_Active22 | Para_Custom_Status_AuxCust_Active22 | 2672 | Para_Custom_Status_AuxCust_Active22 |  | 10008466
[8 empty] | 10008465 | Para_Custom_Status_AuxCust_Active23 | Para_Custom_Status_AuxCust_Active23 | 2673 | Para_Custom_Status_AuxCust_Active23 |  | 10008465
[8 empty] | 10008468 | Para_Custom_Status_AuxCust_Active24 | Para_Custom_Status_AuxCust_Active24 | 2674 | Para_Custom_Status_AuxCust_Active24 |  | 10008468
[8 empty] | 10008467 | Para_Custom_Status_AuxCust_Active25 | Para_Custom_Status_AuxCust_Active25 | 2675 | Para_Custom_Status_AuxCust_Active25 |  | 10008467
[8 empty] | 10008469 | Para_Custom_Status_AuxCust_Active26 | Para_Custom_Status_AuxCust_Active26 | 2676 | Para_Custom_Status_AuxCust_Active26 |  | 10008469
[8 empty] | 10008470 | Para_Custom_Status_AuxCust_Active27 | Para_Custom_Status_AuxCust_Active27 | 2677 | Para_Custom_Status_AuxCust_Active27 |  | 10008470
[8 empty] | 10008473 | Para_Custom_Status_AuxCust_Active28 | Para_Custom_Status_AuxCust_Active28 | 2678 | Para_Custom_Status_AuxCust_Active28 |  | 10008473
[8 empty] | 10008472 | Para_Custom_Status_AuxCust_Active29 | Para_Custom_Status_AuxCust_Active29 | 2679 | Para_Custom_Status_AuxCust_Active29 |  | 10008472
[8 empty] | 10001026 | Para_Custom_Status_AuxCust_Active3 | Para_Custom_Status_AuxCust_Active3 | 2680 | Para_Custom_Status_AuxCust_Active3 |  | 10001026
[8 empty] | 10008475 | Para_Custom_Status_AuxCust_Active30 | Para_Custom_Status_AuxCust_Active30 | 2681 | Para_Custom_Status_AuxCust_Active30 |  | 10008475
[8 empty] | 10008471 | Para_Custom_Status_AuxCust_Active31 | Para_Custom_Status_AuxCust_Active31 | 2682 | Para_Custom_Status_AuxCust_Active31 |  | 10008471
[8 empty] | 10008474 | Para_Custom_Status_AuxCust_Active32 | Para_Custom_Status_AuxCust_Active32 | 2683 | Para_Custom_Status_AuxCust_Active32 |  | 10008474
[8 empty] | 10008476 | Para_Custom_Status_AuxCust_Active33 | Para_Custom_Status_AuxCust_Active33 | 2684 | Para_Custom_Status_AuxCust_Active33 |  | 10008476
[8 empty] | 10008478 | Para_Custom_Status_AuxCust_Active34 | Para_Custom_Status_AuxCust_Active34 | 2685 | Para_Custom_Status_AuxCust_Active34 |  | 10008478
[8 empty] | 10008477 | Para_Custom_Status_AuxCust_Active35 | Para_Custom_Status_AuxCust_Active35 | 2686 | Para_Custom_Status_AuxCust_Active35 |  | 10008477
[8 empty] | 10008479 | Para_Custom_Status_AuxCust_Active36 | Para_Custom_Status_AuxCust_Active36 | 2687 | Para_Custom_Status_AuxCust_Active36 |  | 10008479
[8 empty] | 10008480 | Para_Custom_Status_AuxCust_Active37 | Para_Custom_Status_AuxCust_Active37 | 2688 | Para_Custom_Status_AuxCust_Active37 |  | 10008480
[8 empty] | 10008485 | Para_Custom_Status_AuxCust_Active38 | Para_Custom_Status_AuxCust_Active38 | 2689 | Para_Custom_Status_AuxCust_Active38 |  | 10008485
[8 empty] | 10008486 | Para_Custom_Status_AuxCust_Active39 | Para_Custom_Status_AuxCust_Active39 | 2690 | Para_Custom_Status_AuxCust_Active39 |  | 10008486
[8 empty] | 10001028 | Para_Custom_Status_AuxCust_Active4 | Para_Custom_Status_AuxCust_Active4 | 2691 | Para_Custom_Status_AuxCust_Active4 |  | 10001028
[8 empty] | 10008488 | Para_Custom_Status_AuxCust_Active40 | Para_Custom_Status_AuxCust_Active40 | 2692 | Para_Custom_Status_AuxCust_Active40 |  | 10008488
[8 empty] | 10001025 | Para_Custom_Status_AuxCust_Active5 | Para_Custom_Status_AuxCust_Active5 | 2693 | Para_Custom_Status_AuxCust_Active5 |  | 10001025
[8 empty] | 10001030 | Para_Custom_Status_AuxCust_Active6 | Para_Custom_Status_AuxCust_Active6 | 2694 | Para_Custom_Status_AuxCust_Active6 |  | 10001030
[8 empty] | 10001027 | Para_Custom_Status_AuxCust_Active7 | Para_Custom_Status_AuxCust_Active7 | 2695 | Para_Custom_Status_AuxCust_Active7 |  | 10001027
[8 empty] | 10001031 | Para_Custom_Status_AuxCust_Active8 | Para_Custom_Status_AuxCust_Active8 | 2696 | Para_Custom_Status_AuxCust_Active8 |  | 10001031
[8 empty] | 10001029 | Para_Custom_Status_AuxCust_Active9 | Para_Custom_Status_AuxCust_Active9 | 2697 | Para_Custom_Status_AuxCust_Active9 |  | 10001029
[8 empty] | 10008541 | Para_Cylinder_Bearing_Pc_T_CBearing_Sig_Lo | Para_Cylinder_Bearing_Pc_T_CBearing_Sig_Lo | 2698 | Para_Cylinder_Bearing_Pc_T_CBearing_Sig_Lo |  | 10008541
[8 empty] | 10000122 | Para_Cylinder_Bearing_T_CBearing_Exist | Para_Cylinder_Bearing_T_CBearing_Exist | 2699 | Para_Cylinder_Bearing_T_CBearing_Exist |  | 10000122
[8 empty] | 10000123 | Para_Cylinder_Bearing_T_CBearing_Hi | Para_Cylinder_Bearing_T_CBearing_Hi | 2700 | Para_Cylinder_Bearing_T_CBearing_Hi |  | 10000123
[8 empty] | 10008586 | Para_Cylinder_Bearing_T_CBearing_Hi_Offset | Para_Cylinder_Bearing_T_CBearing_Hi_Offset | 2701 | Para_Cylinder_Bearing_T_CBearing_Hi_Offset |  | 10008586
[8 empty] | 10000124 | Para_Cylinder_Bearing_T_CBearing_HiHi | Para_Cylinder_Bearing_T_CBearing_HiHi | 2702 | Para_Cylinder_Bearing_T_CBearing_HiHi |  | 10000124
[8 empty] | 10000121 | Para_Cylinder_Bearing_T_CBearing_MDev_HiHi | Para_Cylinder_Bearing_T_CBearing_MDev_HiHi | 2703 | Para_Cylinder_Bearing_T_CBearing_MDev_HiHi |  | 10000121
[8 empty] | 10000157 | Para_Cylinder_Bearing_T_MBearing_Exist | Para_Cylinder_Bearing_T_MBearing_Exist | 2704 | Para_Cylinder_Bearing_T_MBearing_Exist |  | 10000157
[8 empty] | 10000328 | Para_Cylinder_Bearing_T_MBearing_Hi | Para_Cylinder_Bearing_T_MBearing_Hi | 2705 | Para_Cylinder_Bearing_T_MBearing_Hi |  | 10000328
[8 empty] | 10000327 | Para_Cylinder_Bearing_T_MBearing_HiHi | Para_Cylinder_Bearing_T_MBearing_HiHi | 2706 | Para_Cylinder_Bearing_T_MBearing_HiHi |  | 10000327
[8 empty] | 10000334 | Para_Cylinder_Bearing_T_MBearing_MDev_HiHi | Para_Cylinder_Bearing_T_MBearing_MDev_HiHi | 2707 | Para_Cylinder_Bearing_T_MBearing_MDev_HiHi |  | 10000334
[8 empty] | 10002614 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset1 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset1 | 2708 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset1 |  | 10002614
[8 empty] | 10002633 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset10 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset10 | 2709 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset10 |  | 10002633
[8 empty] | 10002641 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset11 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset11 | 2710 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset11 |  | 10002641
[8 empty] | 10002639 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset12 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset12 | 2711 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset12 |  | 10002639
[8 empty] | 10002647 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset13 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset13 | 2712 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset13 |  | 10002647
[8 empty] | 10002649 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset14 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset14 | 2713 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset14 |  | 10002649
[8 empty] | 10002648 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset15 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset15 | 2714 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset15 |  | 10002648
[8 empty] | 10002652 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset16 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset16 | 2715 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset16 |  | 10002652
[8 empty] | 10002655 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset17 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset17 | 2716 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset17 |  | 10002655
[8 empty] | 10002657 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset18 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset18 | 2717 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset18 |  | 10002657
[8 empty] | 10002658 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset19 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset19 | 2718 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset19 |  | 10002658
[8 empty] | 10002619 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset2 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset2 | 2719 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset2 |  | 10002619
[8 empty] | 10002659 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset20 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset20 | 2720 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset20 |  | 10002659
[8 empty] | 10002666 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset21 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset21 | 2721 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset21 |  | 10002666
[8 empty] | 10002665 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset22 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset22 | 2722 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset22 |  | 10002665
[8 empty] | 10002667 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset23 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset23 | 2723 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset23 |  | 10002667
[8 empty] | 10002668 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset24 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset24 | 2724 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset24 |  | 10002668
[8 empty] | 10002622 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset3 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset3 | 2725 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset3 |  | 10002622
[8 empty] | 10002627 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset4 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset4 | 2726 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset4 |  | 10002627
[8 empty] | 10002618 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset5 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset5 | 2727 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset5 |  | 10002618
[8 empty] | 10002626 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset6 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset6 | 2728 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset6 |  | 10002626
[8 empty] | 10002640 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset7 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset7 | 2729 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset7 |  | 10002640
[8 empty] | 10002632 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset8 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset8 | 2730 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset8 |  | 10002632
[8 empty] | 10002645 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset9 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset9 | 2731 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset9 |  | 10002645
[8 empty] | 10003015 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset_Active | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset_Active | 2732 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset_Active |  | 10003015
[8 empty] | 10000535 | Para_Cylinder_Ignition_CA_AdvTimeLim | Para_Cylinder_Ignition_CA_AdvTimeLim | 2733 | Para_Cylinder_Ignition_CA_AdvTimeLim |  | 10000535
[8 empty] | 10000536 | Para_Cylinder_Ignition_CA_Ign_OP_Power1 | Para_Cylinder_Ignition_CA_Ign_OP_Power1 | 2734 | Para_Cylinder_Ignition_CA_Ign_OP_Power1 |  | 10000536
[8 empty] | 10000533 | Para_Cylinder_Ignition_CA_Ign_OP_Power2 | Para_Cylinder_Ignition_CA_Ign_OP_Power2 | 2735 | Para_Cylinder_Ignition_CA_Ign_OP_Power2 |  | 10000533
[8 empty] | 10000539 | Para_Cylinder_Ignition_CA_Ign_OP_Power3 | Para_Cylinder_Ignition_CA_Ign_OP_Power3 | 2736 | Para_Cylinder_Ignition_CA_Ign_OP_Power3 |  | 10000539
[8 empty] | 10000537 | Para_Cylinder_Ignition_CA_Ign_OP_Power4 | Para_Cylinder_Ignition_CA_Ign_OP_Power4 | 2737 | Para_Cylinder_Ignition_CA_Ign_OP_Power4 |  | 10000537
[8 empty] | 10000538 | Para_Cylinder_Ignition_CA_Ign_OP_Speed1 | Para_Cylinder_Ignition_CA_Ign_OP_Speed1 | 2738 | Para_Cylinder_Ignition_CA_Ign_OP_Speed1 |  | 10000538
[8 empty] | 10000541 | Para_Cylinder_Ignition_CA_Ign_OP_Speed2 | Para_Cylinder_Ignition_CA_Ign_OP_Speed2 | 2739 | Para_Cylinder_Ignition_CA_Ign_OP_Speed2 |  | 10000541
[8 empty] | 10000542 | Para_Cylinder_Ignition_CA_Ign_OP_Speed3 | Para_Cylinder_Ignition_CA_Ign_OP_Speed3 | 2740 | Para_Cylinder_Ignition_CA_Ign_OP_Speed3 |  | 10000542
[8 empty] | 10000543 | Para_Cylinder_Ignition_CA_Ign_OP_Speed4 | Para_Cylinder_Ignition_CA_Ign_OP_Speed4 | 2741 | Para_Cylinder_Ignition_CA_Ign_OP_Speed4 |  | 10000543
[8 empty] | 10000544 | Para_Cylinder_Ignition_CA_RetTimeLim | Para_Cylinder_Ignition_CA_RetTimeLim | 2742 | Para_Cylinder_Ignition_CA_RetTimeLim |  | 10000544
[8 empty] | 10000545 | Para_Cylinder_Ignition_MisfCont | Para_Cylinder_Ignition_MisfCont | 2743 | Para_Cylinder_Ignition_MisfCont |  | 10000545
[8 empty] | 10000540 | Para_Cylinder_Ignition_MORIS_CoilType0_Current | Para_Cylinder_Ignition_MORIS_CoilType0_Current | 2744 | Para_Cylinder_Ignition_MORIS_CoilType0_Current |  | 10000540
[8 empty] | 10000546 | Para_Cylinder_Ignition_MORIS_CoilType0_Time | Para_Cylinder_Ignition_MORIS_CoilType0_Time | 2745 | Para_Cylinder_Ignition_MORIS_CoilType0_Time |  | 10000546
[8 empty] | 10000548 | Para_Cylinder_Ignition_MORIS_SparkChar1_Current | Para_Cylinder_Ignition_MORIS_SparkChar1_Current | 2746 | Para_Cylinder_Ignition_MORIS_SparkChar1_Current |  | 10000548
[8 empty] | 10000554 | Para_Cylinder_Ignition_MORIS_SparkChar1_Time | Para_Cylinder_Ignition_MORIS_SparkChar1_Time | 2747 | Para_Cylinder_Ignition_MORIS_SparkChar1_Time |  | 10000554
[8 empty] | 10000547 | Para_Cylinder_Ignition_MORIS_SparkChar2_Current | Para_Cylinder_Ignition_MORIS_SparkChar2_Current | 2748 | Para_Cylinder_Ignition_MORIS_SparkChar2_Current |  | 10000547
[8 empty] | 10000552 | Para_Cylinder_Ignition_MORIS_SparkChar2_Time | Para_Cylinder_Ignition_MORIS_SparkChar2_Time | 2749 | Para_Cylinder_Ignition_MORIS_SparkChar2_Time |  | 10000552
[8 empty] | 10000550 | Para_Cylinder_Ignition_MORIS_SparkChar3_Current | Para_Cylinder_Ignition_MORIS_SparkChar3_Current | 2750 | Para_Cylinder_Ignition_MORIS_SparkChar3_Current |  | 10000550
[8 empty] | 10000555 | Para_Cylinder_Ignition_MORIS_SparkChar3_Time | Para_Cylinder_Ignition_MORIS_SparkChar3_Time | 2751 | Para_Cylinder_Ignition_MORIS_SparkChar3_Time |  | 10000555
[8 empty] | 10000549 | Para_Cylinder_Ignition_MORIS_SparkChar4_Current | Para_Cylinder_Ignition_MORIS_SparkChar4_Current | 2752 | Para_Cylinder_Ignition_MORIS_SparkChar4_Current |  | 10000549
[8 empty] | 10000556 | Para_Cylinder_Ignition_MORIS_SparkChar4_Time | Para_Cylinder_Ignition_MORIS_SparkChar4_Time | 2753 | Para_Cylinder_Ignition_MORIS_SparkChar4_Time |  | 10000556
[8 empty] | 10000551 | Para_Cylinder_Ignition_MORIS_SparkChar5_Current | Para_Cylinder_Ignition_MORIS_SparkChar5_Current | 2754 | Para_Cylinder_Ignition_MORIS_SparkChar5_Current |  | 10000551
[8 empty] | 10000558 | Para_Cylinder_Ignition_MORIS_SparkChar5_Time | Para_Cylinder_Ignition_MORIS_SparkChar5_Time | 2755 | Para_Cylinder_Ignition_MORIS_SparkChar5_Time |  | 10000558
[8 empty] | 10000553 | Para_Cylinder_Ignition_MORIS_SparkChar6_Current | Para_Cylinder_Ignition_MORIS_SparkChar6_Current | 2756 | Para_Cylinder_Ignition_MORIS_SparkChar6_Current |  | 10000553
[8 empty] | 10008595 | Para_Cylinder_Ignition_MORIS_VarSparkDur_DynSparkDuration | Para_Cylinder_Ignition_MORIS_VarSparkDur_DynSparkDuration | 2757 | Para_Cylinder_Ignition_MORIS_VarSparkDur_DynSparkDuration |  | 10008595
[8 empty] | 10008597 | Para_Cylinder_Ignition_MORIS_VarSparkDur_P_Act_DynSpark_Limit_Nom | Para_Cylinder_Ignition_MORIS_VarSparkDur_P_Act_DynSpark_Limit_Nom | 2758 | Para_Cylinder_Ignition_MORIS_VarSparkDur_P_Act_DynSpark_Limit_Nom |  | 10008597
[8 empty] | 10008598 | Para_Cylinder_Ignition_MORIS_VarSparkDur_usDurationIdle | Para_Cylinder_Ignition_MORIS_VarSparkDur_usDurationIdle | 2759 | Para_Cylinder_Ignition_MORIS_VarSparkDur_usDurationIdle |  | 10008598
[8 empty] | 10008547 | Para_Cylinder_Knock_CA_IP_Knck_Max | Para_Cylinder_Knock_CA_IP_Knck_Max | 2760 | Para_Cylinder_Knock_CA_IP_Knck_Max |  | 10008547
[8 empty] | 10008542 | Para_Cylinder_Knock_Kno_Int_MinLim | Para_Cylinder_Knock_Kno_Int_MinLim | 2761 | Para_Cylinder_Knock_Kno_Int_MinLim |  | 10008542
[8 empty] | 10008544 | Para_Cylinder_Knock_Kno_IP_Scale_StP | Para_Cylinder_Knock_Kno_IP_Scale_StP | 2762 | Para_Cylinder_Knock_Kno_IP_Scale_StP |  | 10008544
[8 empty] | 10008549 | Para_Cylinder_Knock_Kno_P2s_Inc_EnP | Para_Cylinder_Knock_Kno_P2s_Inc_EnP | 2763 | Para_Cylinder_Knock_Kno_P2s_Inc_EnP |  | 10008549
[8 empty] | 10008545 | Para_Cylinder_Knock_Kno_P2s_Inc_StP | Para_Cylinder_Knock_Kno_P2s_Inc_StP | 2764 | Para_Cylinder_Knock_Kno_P2s_Inc_StP |  | 10008545
[8 empty] | 10008550 | Para_Cylinder_Knock_Kno_Pmax_CylMax | Para_Cylinder_Knock_Kno_Pmax_CylMax | 2765 | Para_Cylinder_Knock_Kno_Pmax_CylMax |  | 10008550
[8 empty] | 10008543 | Para_Cylinder_Knock_Kno_Pmax_Red_EnP_dlt | Para_Cylinder_Knock_Kno_Pmax_Red_EnP_dlt | 2766 | Para_Cylinder_Knock_Kno_Pmax_Red_EnP_dlt |  | 10008543
[8 empty] | 10008540 | Para_Cylinder_Knock_Kno_Pmax_Red_StP | Para_Cylinder_Knock_Kno_Pmax_Red_StP | 2767 | Para_Cylinder_Knock_Kno_Pmax_Red_StP |  | 10008540
[8 empty] | 10008590 | Para_Cylinder_Knock_PBC_Pr_PBC_Knck_Heavy | Para_Cylinder_Knock_PBC_Pr_PBC_Knck_Heavy | 2768 | Para_Cylinder_Knock_PBC_Pr_PBC_Knck_Heavy |  | 10008590
[8 empty] | 10001413 | Para_Cylinder_Knock_PBC_Pr_PBC_Knck_Lim | Para_Cylinder_Knock_PBC_Pr_PBC_Knck_Lim | 2769 | Para_Cylinder_Knock_PBC_Pr_PBC_Knck_Lim |  | 10001413
[8 empty] | 10008546 | Para_Cylinder_Knock_Pmax_Knck_Max | Para_Cylinder_Knock_Pmax_Knck_Max | 2770 | Para_Cylinder_Knock_Pmax_Knck_Max |  | 10008546
[8 empty] | 10008548 | Para_Cylinder_Knock_Pr_P2s_Knck_Max | Para_Cylinder_Knock_Pr_P2s_Knck_Max | 2771 | Para_Cylinder_Knock_Pr_P2s_Knck_Max |  | 10008548
[8 empty] | 10000688 | Para_Cylinder_Monic1_delay | Para_Cylinder_Monic1_delay | 2772 | Para_Cylinder_Monic1_delay |  | 10000688
[8 empty] | 10000689 | Para_Cylinder_Monic1_limit | Para_Cylinder_Monic1_limit | 2773 | Para_Cylinder_Monic1_limit |  | 10000689
[8 empty] | 10000691 | Para_Cylinder_Monic2_delay | Para_Cylinder_Monic2_delay | 2774 | Para_Cylinder_Monic2_delay |  | 10000691
[8 empty] | 10000687 | Para_Cylinder_Monic2_limit | Para_Cylinder_Monic2_limit | 2775 | Para_Cylinder_Monic2_limit |  | 10000687
[8 empty] | 10000683 | Para_Cylinder_Monic3_delay | Para_Cylinder_Monic3_delay | 2776 | Para_Cylinder_Monic3_delay |  | 10000683
[8 empty] | 10000684 | Para_Cylinder_Monic3_limit | Para_Cylinder_Monic3_limit | 2777 | Para_Cylinder_Monic3_limit |  | 10000684
[8 empty] | 10000686 | Para_Cylinder_Monic4_delay | Para_Cylinder_Monic4_delay | 2778 | Para_Cylinder_Monic4_delay |  | 10000686
[8 empty] | 10000685 | Para_Cylinder_Monic4_limit | Para_Cylinder_Monic4_limit | 2779 | Para_Cylinder_Monic4_limit |  | 10000685
[8 empty] | 10000681 | Para_Cylinder_Monic_Ign_LimitMonitorActive1 | Para_Cylinder_Monic_Ign_LimitMonitorActive1 | 2780 | Para_Cylinder_Monic_Ign_LimitMonitorActive1 |  | 10000681
[8 empty] | 10000679 | Para_Cylinder_Monic_Ign_LimitMonitorActive2 | Para_Cylinder_Monic_Ign_LimitMonitorActive2 | 2781 | Para_Cylinder_Monic_Ign_LimitMonitorActive2 |  | 10000679
[8 empty] | 10000675 | Para_Cylinder_Monic_Ign_LimitMonitorActive3 | Para_Cylinder_Monic_Ign_LimitMonitorActive3 | 2782 | Para_Cylinder_Monic_Ign_LimitMonitorActive3 |  | 10000675
[8 empty] | 10000680 | Para_Cylinder_Monic_Ign_LimitMonitorActive4 | Para_Cylinder_Monic_Ign_LimitMonitorActive4 | 2783 | Para_Cylinder_Monic_Ign_LimitMonitorActive4 |  | 10000680
[8 empty] | 10008897 | Para_Cylinder_PBC_CoVControl_CoV_Set100 | Para_Cylinder_PBC_CoVControl_CoV_Set100 | 2784 | Para_Cylinder_PBC_CoVControl_CoV_Set100 |  | 10008897
[8 empty] | 10008898 | Para_Cylinder_PBC_CoVControl_CoV_Set50 | Para_Cylinder_PBC_CoVControl_CoV_Set50 | 2785 | Para_Cylinder_PBC_CoVControl_CoV_Set50 |  | 10008898
[8 empty] | 10008896 | Para_Cylinder_PBC_CoVControl_CoVCtr_Act | Para_Cylinder_PBC_CoVControl_CoVCtr_Act | 2786 | Para_Cylinder_PBC_CoVControl_CoVCtr_Act |  | 10008896
[8 empty] | 10008902 | Para_Cylinder_PBC_CoVControl_CoVCtr_ki | Para_Cylinder_PBC_CoVControl_CoVCtr_ki | 2787 | Para_Cylinder_PBC_CoVControl_CoVCtr_ki |  | 10008902
[8 empty] | 10008901 | Para_Cylinder_PBC_CoVControl_CoVCtr_kp | Para_Cylinder_PBC_CoVControl_CoVCtr_kp | 2788 | Para_Cylinder_PBC_CoVControl_CoVCtr_kp |  | 10008901
[8 empty] | 10008899 | Para_Cylinder_PBC_CoVControl_Pr_CoV_p2s_Range | Para_Cylinder_PBC_CoVControl_Pr_CoV_p2s_Range | 2789 | Para_Cylinder_PBC_CoVControl_Pr_CoV_p2s_Range |  | 10008899
[8 empty] | 10008884 | Para_Cylinder_PBC_MFB50Control_CA_MFB50_ITPOfs_early | Para_Cylinder_PBC_MFB50Control_CA_MFB50_ITPOfs_early | 2790 | Para_Cylinder_PBC_MFB50Control_CA_MFB50_ITPOfs_early |  | 10008884
[8 empty] | 10008883 | Para_Cylinder_PBC_MFB50Control_CA_MFB50_ITPOfs_late | Para_Cylinder_PBC_MFB50Control_CA_MFB50_ITPOfs_late | 2791 | Para_Cylinder_PBC_MFB50Control_CA_MFB50_ITPOfs_late |  | 10008883
[8 empty] | 10008878 | Para_Cylinder_PBC_MFB50Control_CA_MFB50_set100 | Para_Cylinder_PBC_MFB50Control_CA_MFB50_set100 | 2792 | Para_Cylinder_PBC_MFB50Control_CA_MFB50_set100 |  | 10008878
[8 empty] | 10008881 | Para_Cylinder_PBC_MFB50Control_CA_MFB50_set50 | Para_Cylinder_PBC_MFB50Control_CA_MFB50_set50 | 2793 | Para_Cylinder_PBC_MFB50Control_CA_MFB50_set50 |  | 10008881
[8 empty] | 10008886 | Para_Cylinder_PBC_MFB50Control_MFB50_ITP_ratio | Para_Cylinder_PBC_MFB50Control_MFB50_ITP_ratio | 2794 | Para_Cylinder_PBC_MFB50Control_MFB50_ITP_ratio |  | 10008886
[8 empty] | 10002793 | Para_Cylinder_PBC_MFB50Control_MFB50Contr_Ena | Para_Cylinder_PBC_MFB50Control_MFB50Contr_Ena | 2795 | Para_Cylinder_PBC_MFB50Control_MFB50Contr_Ena |  | 10002793
[8 empty] | 10008885 | Para_Cylinder_PBC_MFB50Control_MFB50Ctr_ki | Para_Cylinder_PBC_MFB50Control_MFB50Ctr_ki | 2796 | Para_Cylinder_PBC_MFB50Control_MFB50Ctr_ki |  | 10008885
[8 empty] | 10008882 | Para_Cylinder_PBC_MFB50Control_MFB50Ctr_kp | Para_Cylinder_PBC_MFB50Control_MFB50Ctr_kp | 2797 | Para_Cylinder_PBC_MFB50Control_MFB50Ctr_kp |  | 10008882
[8 empty] | 10000144 | Para_Cylinder_PBC_Num_IMEP_Misf_Lim | Para_Cylinder_PBC_Num_IMEP_Misf_Lim | 2798 | Para_Cylinder_PBC_Num_IMEP_Misf_Lim |  | 10000144
[8 empty] | 10008524 | Para_Cylinder_PBC_P_PBC_Act_Hys | Para_Cylinder_PBC_P_PBC_Act_Hys | 2799 | Para_Cylinder_PBC_P_PBC_Act_Hys |  | 10008524
[8 empty] | 10008527 | Para_Cylinder_PBC_P_PBC_Act_SP | Para_Cylinder_PBC_P_PBC_Act_SP | 2800 | Para_Cylinder_PBC_P_PBC_Act_SP |  | 10008527
[8 empty] | 10008526 | Para_Cylinder_PBC_Pr_CPP_AbsLim_LHE | Para_Cylinder_PBC_Pr_CPP_AbsLim_LHE | 2801 | Para_Cylinder_PBC_Pr_CPP_AbsLim_LHE |  | 10008526
[8 empty] | 10008656 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_cur_gradient | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_cur_gradient | 2802 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_cur_gradient |  | 10008656
[8 empty] | 10008651 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_duration | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_duration | 2803 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_duration |  | 10008651
[8 empty] | 10008653 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_set_current | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_set_current | 2804 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_set_current |  | 10008653
[8 empty] | 10008654 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_set_duration | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_set_duration | 2805 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_set_duration |  | 10008654
[8 empty] | 10008659 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time1 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time1 | 2806 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time1 |  | 10008659
[8 empty] | 10008669 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time10 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time10 | 2807 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time10 |  | 10008669
[8 empty] | 10008667 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time11 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time11 | 2808 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time11 |  | 10008667
[8 empty] | 10008670 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time12 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time12 | 2809 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time12 |  | 10008670
[8 empty] | 10008671 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time13 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time13 | 2810 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time13 |  | 10008671
[8 empty] | 10008672 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time14 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time14 | 2811 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time14 |  | 10008672
[8 empty] | 10008673 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time15 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time15 | 2812 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time15 |  | 10008673
[8 empty] | 10008676 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time16 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time16 | 2813 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time16 |  | 10008676
[8 empty] | 10008674 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time17 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time17 | 2814 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time17 |  | 10008674
[8 empty] | 10008675 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time18 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time18 | 2815 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time18 |  | 10008675
[8 empty] | 10008677 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time19 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time19 | 2816 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time19 |  | 10008677
[8 empty] | 10008660 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time2 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time2 | 2817 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time2 |  | 10008660
[8 empty] | 10008678 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time20 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time20 | 2818 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time20 |  | 10008678
[8 empty] | 10008680 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time21 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time21 | 2819 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time21 |  | 10008680
[8 empty] | 10008681 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time22 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time22 | 2820 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time22 |  | 10008681
[8 empty] | 10008679 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time23 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time23 | 2821 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time23 |  | 10008679
[8 empty] | 10008682 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time24 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time24 | 2822 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time24 |  | 10008682
[8 empty] | 10008661 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time3 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time3 | 2823 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time3 |  | 10008661
[8 empty] | 10008663 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time4 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time4 | 2824 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time4 |  | 10008663
[8 empty] | 10008662 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time5 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time5 | 2825 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time5 |  | 10008662
[8 empty] | 10008664 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time6 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time6 | 2826 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time6 |  | 10008664
[8 empty] | 10008665 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time7 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time7 | 2827 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time7 |  | 10008665
[8 empty] | 10008668 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time8 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time8 | 2828 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time8 |  | 10008668
[8 empty] | 10008666 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time9 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time9 | 2829 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time9 |  | 10008666
[8 empty] | 10008657 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_var_limit_Idle | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_var_limit_Idle | 2830 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_var_limit_Idle |  | 10008657
[8 empty] | 10008658 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_var_limit_Load | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_var_limit_Load | 2831 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_var_limit_Load |  | 10008658
[8 empty] | 10008655 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_var_limit_Start | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_var_limit_Start | 2832 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_var_limit_Start |  | 10008655
[8 empty] | 10008700 | Para_Cylinder_PI_CorrectCurrCtr_SA_PI_currCtr_delay | Para_Cylinder_PI_CorrectCurrCtr_SA_PI_currCtr_delay | 2833 | Para_Cylinder_PI_CorrectCurrCtr_SA_PI_currCtr_delay |  | 10008700
[8 empty] | 10008696 | Para_Cylinder_PI_CorrectCurrCtr_SA_PI_currCtr_duration | Para_Cylinder_PI_CorrectCurrCtr_SA_PI_currCtr_duration | 2834 | Para_Cylinder_PI_CorrectCurrCtr_SA_PI_currCtr_duration |  | 10008696
[8 empty] | 10008698 | Para_Cylinder_PI_CorrectCurrCtr_SA_PI_currCtr_level | Para_Cylinder_PI_CorrectCurrCtr_SA_PI_currCtr_level | 2835 | Para_Cylinder_PI_CorrectCurrCtr_SA_PI_currCtr_level |  | 10008698
[8 empty] | 10008699 | Para_Cylinder_PI_CorrectCurrCtr_SA_PI_currCtr_rate | Para_Cylinder_PI_CorrectCurrCtr_SA_PI_currCtr_rate | 2836 | Para_Cylinder_PI_CorrectCurrCtr_SA_PI_currCtr_rate |  | 10008699
[8 empty] | 10008683 | Para_Cylinder_PI_CurrentProfile_SA_PI_curr1_current | Para_Cylinder_PI_CurrentProfile_SA_PI_curr1_current | 2837 | Para_Cylinder_PI_CurrentProfile_SA_PI_curr1_current |  | 10008683
[8 empty] | 10008687 | Para_Cylinder_PI_CurrentProfile_SA_PI_curr1_duration | Para_Cylinder_PI_CurrentProfile_SA_PI_curr1_duration | 2838 | Para_Cylinder_PI_CurrentProfile_SA_PI_curr1_duration |  | 10008687
[8 empty] | 10008685 | Para_Cylinder_PI_CurrentProfile_SA_PI_curr2_current | Para_Cylinder_PI_CurrentProfile_SA_PI_curr2_current | 2839 | Para_Cylinder_PI_CurrentProfile_SA_PI_curr2_current |  | 10008685
[8 empty] | 10008690 | Para_Cylinder_PI_CurrentProfile_SA_PI_curr2_duration | Para_Cylinder_PI_CurrentProfile_SA_PI_curr2_duration | 2840 | Para_Cylinder_PI_CurrentProfile_SA_PI_curr2_duration |  | 10008690
[8 empty] | 10008684 | Para_Cylinder_PI_CurrentProfile_SA_PI_curr3_current | Para_Cylinder_PI_CurrentProfile_SA_PI_curr3_current | 2841 | Para_Cylinder_PI_CurrentProfile_SA_PI_curr3_current |  | 10008684
[8 empty] | 10008689 | Para_Cylinder_PI_CurrentProfile_SA_PI_curr3_duration | Para_Cylinder_PI_CurrentProfile_SA_PI_curr3_duration | 2842 | Para_Cylinder_PI_CurrentProfile_SA_PI_curr3_duration |  | 10008689
[8 empty] | 10008686 | Para_Cylinder_PI_CurrentProfile_SA_PI_curr4_current | Para_Cylinder_PI_CurrentProfile_SA_PI_curr4_current | 2843 | Para_Cylinder_PI_CurrentProfile_SA_PI_curr4_current |  | 10008686
[8 empty] | 10008691 | Para_Cylinder_PI_CurrentRecovery_SA_PI_recov_current | Para_Cylinder_PI_CurrentRecovery_SA_PI_recov_current | 2844 | Para_Cylinder_PI_CurrentRecovery_SA_PI_recov_current |  | 10008691
[8 empty] | 10008688 | Para_Cylinder_PI_CurrentRecovery_SA_PI_recov_delay | Para_Cylinder_PI_CurrentRecovery_SA_PI_recov_delay | 2845 | Para_Cylinder_PI_CurrentRecovery_SA_PI_recov_delay |  | 10008688
[8 empty] | 10008692 | Para_Cylinder_PI_CurrentRecovery_SA_PI_recov_duration | Para_Cylinder_PI_CurrentRecovery_SA_PI_recov_duration | 2846 | Para_Cylinder_PI_CurrentRecovery_SA_PI_recov_duration |  | 10008692
[8 empty] | 10008701 | Para_Cylinder_PI_Demagnet_PIDemagActive | Para_Cylinder_PI_Demagnet_PIDemagActive | 2847 | Para_Cylinder_PI_Demagnet_PIDemagActive |  | 10008701
[8 empty] | 10008702 | Para_Cylinder_PI_Demagnet_SA_PI_demag_delay | Para_Cylinder_PI_Demagnet_SA_PI_demag_delay | 2848 | Para_Cylinder_PI_Demagnet_SA_PI_demag_delay |  | 10008702
[8 empty] | 10008650 | Para_Cylinder_PI_Demagnet_SA_PI_demag_duration | Para_Cylinder_PI_Demagnet_SA_PI_demag_duration | 2849 | Para_Cylinder_PI_Demagnet_SA_PI_demag_duration |  | 10008650
[8 empty] | 10008652 | Para_Cylinder_PI_Demagnet_SA_PI_demag_up_limit | Para_Cylinder_PI_Demagnet_SA_PI_demag_up_limit | 2850 | Para_Cylinder_PI_Demagnet_SA_PI_demag_up_limit |  | 10008652
[8 empty] | 10002608 | Para_Cylinder_PI_MisfCyl_Max_Norm | Para_Cylinder_PI_MisfCyl_Max_Norm | 2851 | Para_Cylinder_PI_MisfCyl_Max_Norm |  | 10002608
[8 empty] | 10002623 | Para_Cylinder_PI_P_MisfCtr_Hys_Norm | Para_Cylinder_PI_P_MisfCtr_Hys_Norm | 2852 | Para_Cylinder_PI_P_MisfCtr_Hys_Norm |  | 10002623
[8 empty] | 10002615 | Para_Cylinder_PI_P_MisfCtr_SP_Norm | Para_Cylinder_PI_P_MisfCtr_SP_Norm | 2853 | Para_Cylinder_PI_P_MisfCtr_SP_Norm |  | 10002615
[8 empty] | 10008697 | Para_Cylinder_PI_PullInCurrCheck_SA_PI_pudet_duration | Para_Cylinder_PI_PullInCurrCheck_SA_PI_pudet_duration | 2854 | Para_Cylinder_PI_PullInCurrCheck_SA_PI_pudet_duration |  | 10008697
[8 empty] | 10008694 | Para_Cylinder_PI_PullInCurrCheck_SA_PI_pudet_level | Para_Cylinder_PI_PullInCurrCheck_SA_PI_pudet_level | 2855 | Para_Cylinder_PI_PullInCurrCheck_SA_PI_pudet_level |  | 10008694
[8 empty] | 10008693 | Para_Cylinder_PI_PullInCurrCheck_SA_PI_pudet_st_time | Para_Cylinder_PI_PullInCurrCheck_SA_PI_pudet_st_time | 2856 | Para_Cylinder_PI_PullInCurrCheck_SA_PI_pudet_st_time |  | 10008693
[8 empty] | 10008695 | Para_Cylinder_PI_SA_CyclPIOnDuringMisf | Para_Cylinder_PI_SA_CyclPIOnDuringMisf | 2857 | Para_Cylinder_PI_SA_CyclPIOnDuringMisf |  | 10008695
[8 empty] | 10000690 | Para_Cylinder_PI_SA_PIValveType | Para_Cylinder_PI_SA_PIValveType | 2858 | Para_Cylinder_PI_SA_PIValveType |  | 10000690
[8 empty] | 10002670 | Para_Cylinder_PI_ti_OpTi_MisCyl_Trig | Para_Cylinder_PI_ti_OpTi_MisCyl_Trig | 2859 | Para_Cylinder_PI_ti_OpTi_MisCyl_Trig |  | 10002670
[8 empty] | 10002612 | Para_Cylinder_PI_ti_OpTi_MisfCyl | Para_Cylinder_PI_ti_OpTi_MisfCyl | 2860 | Para_Cylinder_PI_ti_OpTi_MisfCyl |  | 10002612
[8 empty] | 10000492 | Para_Electrical_GeneratCtr_ChoiceSet_PF_CosPCtr_PF_Set1 | Para_Electrical_GeneratCtr_ChoiceSet_PF_CosPCtr_PF_Set1 | 2861 | Para_Electrical_GeneratCtr_ChoiceSet_PF_CosPCtr_PF_Set1 |  | 10000492
[8 empty] | 10000577 | Para_Electrical_GeneratCtr_PF_Customer_Selected | Para_Electrical_GeneratCtr_PF_Customer_Selected | 2862 | Para_Electrical_GeneratCtr_PF_Customer_Selected |  | 10000577
[8 empty] | 10008791 | Para_Electrical_GeneratCtr_QLimit_Q_OverExc_Lim | Para_Electrical_GeneratCtr_QLimit_Q_OverExc_Lim | 2863 | Para_Electrical_GeneratCtr_QLimit_Q_OverExc_Lim |  | 10008791
[8 empty] | 10008792 | Para_Electrical_GeneratCtr_QLimit_Q_UnderExc_Lim | Para_Electrical_GeneratCtr_QLimit_Q_UnderExc_Lim | 2864 | Para_Electrical_GeneratCtr_QLimit_Q_UnderExc_Lim |  | 10008792
[8 empty] | 10000500 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h0 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h0 | 2865 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h0 |  | 10000500
[8 empty] | 10000499 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h1 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h1 | 2866 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h1 |  | 10000499
[8 empty] | 10000503 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h2 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h2 | 2867 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h2 |  | 10000503
[8 empty] | 10000501 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h3 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h3 | 2868 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h3 |  | 10000501
[8 empty] | 10000507 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h4 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h4 | 2869 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h4 |  | 10000507
[8 empty] | 10000506 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h5 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h5 | 2870 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h5 |  | 10000506
[8 empty] | 10000496 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m0 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m0 | 2871 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m0 |  | 10000496
[8 empty] | 10000505 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m1 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m1 | 2872 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m1 |  | 10000505
[8 empty] | 10000504 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m2 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m2 | 2873 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m2 |  | 10000504
[8 empty] | 10000502 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m3 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m3 | 2874 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m3 |  | 10000502
[8 empty] | 10000508 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m4 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m4 | 2875 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m4 |  | 10000508
[8 empty] | 10000511 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m5 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m5 | 2876 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m5 |  | 10000511
[8 empty] | 10000490 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set0 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set0 | 2877 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set0 |  | 10000490
[8 empty] | 10000493 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set1 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set1 | 2878 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set1 |  | 10000493
[8 empty] | 10000495 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set2 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set2 | 2879 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set2 |  | 10000495
[8 empty] | 10000494 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set3 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set3 | 2880 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set3 |  | 10000494
[8 empty] | 10000498 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set4 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set4 | 2881 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set4 |  | 10000498
[8 empty] | 10000497 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set5 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set5 | 2882 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set5 |  | 10000497
[8 empty] | 10000568 | Para_Electrical_GeneratCtr_Voltage_F_Gen_Match_Max | Para_Electrical_GeneratCtr_Voltage_F_Gen_Match_Max | 2883 | Para_Electrical_GeneratCtr_Voltage_F_Gen_Match_Max |  | 10000568
[8 empty] | 10000567 | Para_Electrical_GeneratCtr_Voltage_F_Gen_Match_Min | Para_Electrical_GeneratCtr_Voltage_F_Gen_Match_Min | 2884 | Para_Electrical_GeneratCtr_Voltage_F_Gen_Match_Min |  | 10000567
[8 empty] | 10000514 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map0 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map0 | 2885 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map0 |  | 10000514
[8 empty] | 10000520 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map10 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map10 | 2886 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map10 |  | 10000520
[8 empty] | 10000518 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map2 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map2 | 2887 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map2 |  | 10000518
[8 empty] | 10000522 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map4 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map4 | 2888 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map4 |  | 10000522
[8 empty] | 10000515 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map6 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map6 | 2889 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map6 |  | 10000515
[8 empty] | 10000519 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map8 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map8 | 2890 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map8 |  | 10000519
[8 empty] | 10000510 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set0 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set0 | 2891 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set0 |  | 10000510
[8 empty] | 10000513 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set1 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set1 | 2892 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set1 |  | 10000513
[8 empty] | 10000509 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set2 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set2 | 2893 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set2 |  | 10000509
[8 empty] | 10000512 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set3 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set3 | 2894 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set3 |  | 10000512
[8 empty] | 10000517 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set4 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set4 | 2895 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set4 |  | 10000517
[8 empty] | 10000516 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set5 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set5 | 2896 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set5 |  | 10000516
[8 empty] | 10001326 | Para_Electrical_GeneratCtr_Voltage_U_adj_gcb_ext_hilo_a | Para_Electrical_GeneratCtr_Voltage_U_adj_gcb_ext_hilo_a | 2897 | Para_Electrical_GeneratCtr_Voltage_U_adj_gcb_ext_hilo_a |  | 10001326
[8 empty] | 10001288 | Para_Electrical_GeneratCtr_Voltage_U_adj_gcb_mmd_calc_a | Para_Electrical_GeneratCtr_Voltage_U_adj_gcb_mmd_calc_a | 2898 | Para_Electrical_GeneratCtr_Voltage_U_adj_gcb_mmd_calc_a |  | 10001288
[8 empty] | 10001328 | Para_Electrical_GeneratCtr_Voltage_U_adj_mcb_ext_hilo_a | Para_Electrical_GeneratCtr_Voltage_U_adj_mcb_ext_hilo_a | 2899 | Para_Electrical_GeneratCtr_Voltage_U_adj_mcb_ext_hilo_a |  | 10001328
[8 empty] | 10001315 | Para_Electrical_GeneratCtr_Voltage_U_adj_mcb_mmd_calc_a | Para_Electrical_GeneratCtr_Voltage_U_adj_mcb_mmd_calc_a | 2900 | Para_Electrical_GeneratCtr_Voltage_U_adj_mcb_mmd_calc_a |  | 10001315
[8 empty] | 10000578 | Para_Electrical_GeneratCtr_Voltage_U_Gen_match_delta | Para_Electrical_GeneratCtr_Voltage_U_Gen_match_delta | 2901 | Para_Electrical_GeneratCtr_Voltage_U_Gen_match_delta |  | 10000578
[8 empty] | 10000574 | Para_Electrical_GeneratCtr_Voltage_U_Gen_P_Ena | Para_Electrical_GeneratCtr_Voltage_U_Gen_P_Ena | 2902 | Para_Electrical_GeneratCtr_Voltage_U_Gen_P_Ena |  | 10000574
[8 empty] | 10000132 | Para_Electrical_GeneratCtr_Voltage_U_Gen_Rmp_Inc | Para_Electrical_GeneratCtr_Voltage_U_Gen_Rmp_Inc | 2903 | Para_Electrical_GeneratCtr_Voltage_U_Gen_Rmp_Inc |  | 10000132
[8 empty] | 10000573 | Para_Electrical_GeneratCtr_Voltage_U_Gen_spd_match | Para_Electrical_GeneratCtr_Voltage_U_Gen_spd_match | 2904 | Para_Electrical_GeneratCtr_Voltage_U_Gen_spd_match |  | 10000573
[8 empty] | 10002540 | Para_Electrical_Generator_F_GenBear_DE1_Active | Para_Electrical_Generator_F_GenBear_DE1_Active | 2905 | Para_Electrical_Generator_F_GenBear_DE1_Active |  | 10002540
[8 empty] | 10002544 | Para_Electrical_Generator_F_GenBear_DE2_Active | Para_Electrical_Generator_F_GenBear_DE2_Active | 2906 | Para_Electrical_Generator_F_GenBear_DE2_Active |  | 10002544
[8 empty] | 10002549 | Para_Electrical_Generator_F_GenBear_NDE1_Active | Para_Electrical_Generator_F_GenBear_NDE1_Active | 2907 | Para_Electrical_Generator_F_GenBear_NDE1_Active |  | 10002549
[8 empty] | 10002547 | Para_Electrical_Generator_F_GenBear_NDE2_Active | Para_Electrical_Generator_F_GenBear_NDE2_Active | 2908 | Para_Electrical_Generator_F_GenBear_NDE2_Active |  | 10002547
[8 empty] | 10002562 | Para_Electrical_Generator_F_GenBear_ScalMax | Para_Electrical_Generator_F_GenBear_ScalMax | 2909 | Para_Electrical_Generator_F_GenBear_ScalMax |  | 10002562
[8 empty] | 10002553 | Para_Electrical_Generator_F_GenBear_ScalMin | Para_Electrical_Generator_F_GenBear_ScalMin | 2910 | Para_Electrical_Generator_F_GenBear_ScalMin |  | 10002553
[8 empty] | 10008789 | Para_Electrical_Generator_T_GenAirIn2_Active | Para_Electrical_Generator_T_GenAirIn2_Active | 2911 | Para_Electrical_Generator_T_GenAirIn2_Active |  | 10008789
[8 empty] | 10008790 | Para_Electrical_Generator_T_Pred_GenAirIn_Rate | Para_Electrical_Generator_T_Pred_GenAirIn_Rate | 2912 | Para_Electrical_Generator_T_Pred_GenAirIn_Rate |  | 10008790
[8 empty] | 10008793 | Para_Electrical_Generator_T_Pred_GenAirIn_Start | Para_Electrical_Generator_T_Pred_GenAirIn_Start | 2913 | Para_Electrical_Generator_T_Pred_GenAirIn_Start |  | 10008793
[8 empty] | 10000694 | Para_Electrical_Generator_ti_Gen_VoltReg_Fail | Para_Electrical_Generator_ti_Gen_VoltReg_Fail | 2914 | Para_Electrical_Generator_ti_Gen_VoltReg_Fail |  | 10000694
[8 empty] | 10002558 | Para_Electrical_Generator_tiF_GenBear_Hi | Para_Electrical_Generator_tiF_GenBear_Hi | 2915 | Para_Electrical_Generator_tiF_GenBear_Hi |  | 10002558
[8 empty] | 10002555 | Para_Electrical_Generator_tiF_GenBear_HiHi | Para_Electrical_Generator_tiF_GenBear_HiHi | 2916 | Para_Electrical_Generator_tiF_GenBear_HiHi |  | 10002555
[8 empty] | 10000586 | Para_Electrical_Generator_tiP_Gen_Reverse | Para_Electrical_Generator_tiP_Gen_Reverse | 2917 | Para_Electrical_Generator_tiP_Gen_Reverse |  | 10000586
[8 empty] | 10000580 | Para_Electrical_Generator_tiP_Gen_Reverse2 | Para_Electrical_Generator_tiP_Gen_Reverse2 | 2918 | Para_Electrical_Generator_tiP_Gen_Reverse2 |  | 10000580
[8 empty] | 10000581 | Para_Electrical_Generator_tiP_Reverse_Mon_Ena | Para_Electrical_Generator_tiP_Reverse_Mon_Ena | 2919 | Para_Electrical_Generator_tiP_Reverse_Mon_Ena |  | 10000581
[8 empty] | 10000583 | Para_Electrical_Generator_tiPF_CosPCtr_del | Para_Electrical_Generator_tiPF_CosPCtr_del | 2920 | Para_Electrical_Generator_tiPF_CosPCtr_del |  | 10000583
[8 empty] | 10000576 | Para_Electrical_Generator_U_Gen_Contr_Sel | Para_Electrical_Generator_U_Gen_Contr_Sel | 2921 | Para_Electrical_Generator_U_Gen_Contr_Sel |  | 10000576
[8 empty] | 10000582 | Para_Electrical_Generator_U_Gen_Nom_2 | Para_Electrical_Generator_U_Gen_Nom_2 | 2922 | Para_Electrical_Generator_U_Gen_Nom_2 |  | 10000582
[8 empty] | 10000521 | Para_Electrical_Grid_GridCodeDyn_GrC_CapStop | Para_Electrical_Grid_GridCodeDyn_GrC_CapStop | 2923 | Para_Electrical_Grid_GridCodeDyn_GrC_CapStop |  | 10000521
[8 empty] | 10002773 | Para_Electrical_Grid_GridCodeDyn_GrC_Prof_Active0 | Para_Electrical_Grid_GridCodeDyn_GrC_Prof_Active0 | 2924 | Para_Electrical_Grid_GridCodeDyn_GrC_Prof_Active0 |  | 10002773
[8 empty] | 10002775 | Para_Electrical_Grid_GridCodeDyn_GrC_Prof_Active1 | Para_Electrical_Grid_GridCodeDyn_GrC_Prof_Active1 | 2925 | Para_Electrical_Grid_GridCodeDyn_GrC_Prof_Active1 |  | 10002775
[8 empty] | 10002777 | Para_Electrical_Grid_GridCodeDyn_GrC_Prof_Active2 | Para_Electrical_Grid_GridCodeDyn_GrC_Prof_Active2 | 2926 | Para_Electrical_Grid_GridCodeDyn_GrC_Prof_Active2 |  | 10002777
[8 empty] | 10000525 | Para_Electrical_Grid_GridCodeDyn_GridCode_Active | Para_Electrical_Grid_GridCodeDyn_GridCode_Active | 2927 | Para_Electrical_Grid_GridCodeDyn_GridCode_Active |  | 10000525
[8 empty] | 10008879 | Para_Electrical_Grid_GridCodeDyn_GridCode_Prof23_Active | Para_Electrical_Grid_GridCodeDyn_GridCode_Prof23_Active | 2928 | Para_Electrical_Grid_GridCodeDyn_GridCode_Prof23_Active |  | 10008879
[8 empty] | 10000105 | Para_Electrical_Grid_GridCodeDyn_GridCodeMonitoringOnly | Para_Electrical_Grid_GridCodeDyn_GridCodeMonitoringOnly | 2929 | Para_Electrical_Grid_GridCodeDyn_GridCodeMonitoringOnly |  | 10000105
[8 empty] | 10002785 | Para_Electrical_Grid_GridCodeDyn_ti_GrC_Prof0 | Para_Electrical_Grid_GridCodeDyn_ti_GrC_Prof0 | 2930 | Para_Electrical_Grid_GridCodeDyn_ti_GrC_Prof0 |  | 10002785
[8 empty] | 10002786 | Para_Electrical_Grid_GridCodeDyn_ti_GrC_Prof1 | Para_Electrical_Grid_GridCodeDyn_ti_GrC_Prof1 | 2931 | Para_Electrical_Grid_GridCodeDyn_ti_GrC_Prof1 |  | 10002786
[8 empty] | 10002778 | Para_Electrical_Grid_GridCodeDyn_ti_GrC_Prof2 | Para_Electrical_Grid_GridCodeDyn_ti_GrC_Prof2 | 2932 | Para_Electrical_Grid_GridCodeDyn_ti_GrC_Prof2 |  | 10002778
[8 empty] | 10002788 | Para_Electrical_Grid_GridCodeDyn_U_GrC_Prof_Norm0 | Para_Electrical_Grid_GridCodeDyn_U_GrC_Prof_Norm0 | 2933 | Para_Electrical_Grid_GridCodeDyn_U_GrC_Prof_Norm0 |  | 10002788
[8 empty] | 10002780 | Para_Electrical_Grid_GridCodeDyn_U_GrC_Prof_Norm1 | Para_Electrical_Grid_GridCodeDyn_U_GrC_Prof_Norm1 | 2934 | Para_Electrical_Grid_GridCodeDyn_U_GrC_Prof_Norm1 |  | 10002780
[8 empty] | 10002787 | Para_Electrical_Grid_GridCodeDyn_U_GrC_Prof_Norm2 | Para_Electrical_Grid_GridCodeDyn_U_GrC_Prof_Norm2 | 2935 | Para_Electrical_Grid_GridCodeDyn_U_GrC_Prof_Norm2 |  | 10002787
[8 empty] | 10008938 | Para_Electrical_Grid_GridCodeStatic_DEIE_Active | Para_Electrical_Grid_GridCodeStatic_DEIE_Active | 2936 | Para_Electrical_Grid_GridCodeStatic_DEIE_Active |  | 10008938
[8 empty] | 10008749 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_Droop_FC_neg | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_Droop_FC_neg | 2937 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_Droop_FC_neg |  | 10008749
[8 empty] | 10008747 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_Droop_FC_pos | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_Droop_FC_pos | 2938 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_Droop_FC_pos |  | 10008747
[8 empty] | 10008757 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_F_FC_Deadband_neg | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_F_FC_Deadband_neg | 2939 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_F_FC_Deadband_neg |  | 10008757
[8 empty] | 10008754 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_F_FC_Deadband_pos | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_F_FC_Deadband_pos | 2940 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_F_FC_Deadband_pos |  | 10008754
[8 empty] | 10008756 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_F_FC_Dlt_neg | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_F_FC_Dlt_neg | 2941 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_F_FC_Dlt_neg |  | 10008756
[8 empty] | 10008758 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_F_FC_Dlt_pos | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_F_FC_Dlt_pos | 2942 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_F_FC_Dlt_pos |  | 10008758
[8 empty] | 10008780 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_Calc_PRamp_FC_active | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_Calc_PRamp_FC_active | 2943 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_Calc_PRamp_FC_active |  | 10008780
[8 empty] | 10008776 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_PRamp_FC_DecGrad_Norm | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_PRamp_FC_DecGrad_Norm | 2944 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_PRamp_FC_DecGrad_Norm |  | 10008776
[8 empty] | 10008777 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_PRamp_FC_ExtInp | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_PRamp_FC_ExtInp | 2945 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_PRamp_FC_ExtInp |  | 10008777
[8 empty] | 10008775 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_PRamp_FC_IncGrad_Norm | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_PRamp_FC_IncGrad_Norm | 2946 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_PRamp_FC_IncGrad_Norm |  | 10008775
[8 empty] | 10008774 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_PRamp_FC_SetCOn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_PRamp_FC_SetCOn | 2947 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_PRamp_FC_SetCOn |  | 10008774
[8 empty] | 10008781 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_tiSetTime_FC_PRamp | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_tiSetTime_FC_PRamp | 2948 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_tiSetTime_FC_PRamp |  | 10008781
[8 empty] | 10008746 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_Set_FC_COn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_Set_FC_COn | 2949 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_Set_FC_COn |  | 10008746
[8 empty] | 10008752 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_Set_FC_ExtInp | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_Set_FC_ExtInp | 2950 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_Set_FC_ExtInp |  | 10008752
[8 empty] | 10008750 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_Set_FC_Input | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_Set_FC_Input | 2951 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_Set_FC_Input |  | 10008750
[8 empty] | 10008755 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_SetMarg_FC_neg | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_SetMarg_FC_neg | 2952 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_SetMarg_FC_neg |  | 10008755
[8 empty] | 10008753 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_SetMarg_FC_pos | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_SetMarg_FC_pos | 2953 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_SetMarg_FC_pos |  | 10008753
[8 empty] | 10008751 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_SetMarg_FC_StaInp | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_SetMarg_FC_StaInp | 2954 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_SetMarg_FC_StaInp |  | 10008751
[8 empty] | 10008779 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TestFunction_FAct_FC_ManualTest | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TestFunction_FAct_FC_ManualTest | 2955 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TestFunction_FAct_FC_ManualTest |  | 10008779
[8 empty] | 10008778 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TestFunction_FNom_FC_ManualTest | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TestFunction_FNom_FC_ManualTest | 2956 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TestFunction_FNom_FC_ManualTest |  | 10008778
[8 empty] | 10008761 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TestFunction_Set_FC_Testmode | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TestFunction_Set_FC_Testmode | 2957 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TestFunction_Set_FC_Testmode |  | 10008761
[8 empty] | 10008744 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_F_FC_Deadband_TAF_neg | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_F_FC_Deadband_TAF_neg | 2958 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_F_FC_Deadband_TAF_neg |  | 10008744
[8 empty] | 10008748 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_F_FC_Deadband_TAF_pos | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_F_FC_Deadband_TAF_pos | 2959 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_F_FC_Deadband_TAF_pos |  | 10008748
[8 empty] | 10008745 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_P_SetMarg_FC_TAF | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_P_SetMarg_FC_TAF | 2960 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_P_SetMarg_FC_TAF |  | 10008745
[8 empty] | 10008762 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_HFRCOn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_HFRCOn | 2961 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_HFRCOn |  | 10008762
[8 empty] | 10008759 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_PORCOn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_PORCOn | 2962 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_PORCOn |  | 10008759
[8 empty] | 10008770 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_RRCOn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_RRCOn | 2963 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_RRCOn |  | 10008770
[8 empty] | 10008764 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_SORCOn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_SORCOn | 2964 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_SORCOn |  | 10008764
[8 empty] | 10008773 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_SRCOn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_SRCOn | 2965 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_SRCOn |  | 10008773
[8 empty] | 10008760 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_TimeActFunctCOn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_TimeActFunctCOn | 2966 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_TimeActFunctCOn |  | 10008760
[8 empty] | 10008766 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_TOR2COn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_TOR2COn | 2967 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_TOR2COn |  | 10008766
[8 empty] | 10008768 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_TORCOn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_TORCOn | 2968 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_TORCOn |  | 10008768
[8 empty] | 10008763 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_POR | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_POR | 2969 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_POR |  | 10008763
[8 empty] | 10008772 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_RR | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_RR | 2970 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_RR |  | 10008772
[8 empty] | 10008767 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_SOR | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_SOR | 2971 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_SOR |  | 10008767
[8 empty] | 10008771 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_SR | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_SR | 2972 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_SR |  | 10008771
[8 empty] | 10008765 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_TOR | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_TOR | 2973 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_TOR |  | 10008765
[8 empty] | 10008769 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_TOR2 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_TOR2 | 2974 | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_TOR2 |  | 10008769
[8 empty] | 10008937 | Para_Electrical_Grid_GridCodeStatic_PowerLimit_P_DEIE_ScalMax | Para_Electrical_Grid_GridCodeStatic_PowerLimit_P_DEIE_ScalMax | 2975 | Para_Electrical_Grid_GridCodeStatic_PowerLimit_P_DEIE_ScalMax |  | 10008937
[8 empty] | 10008934 | Para_Electrical_Grid_GridCodeStatic_PowerLimit_P_DEIE_ScalMin | Para_Electrical_Grid_GridCodeStatic_PowerLimit_P_DEIE_ScalMin | 2976 | Para_Electrical_Grid_GridCodeStatic_PowerLimit_P_DEIE_ScalMin |  | 10008934
[8 empty] | 10008939 | Para_Electrical_Grid_GridCodeStatic_tiDelayDEIE | Para_Electrical_Grid_GridCodeStatic_tiDelayDEIE | 2977 | Para_Electrical_Grid_GridCodeStatic_tiDelayDEIE |  | 10008939
[8 empty] | 10000216 | Para_Electrical_Grid_Synchronization_ADL_Enable | Para_Electrical_Grid_Synchronization_ADL_Enable | 2978 | Para_Electrical_Grid_Synchronization_ADL_Enable |  | 10000216
[8 empty] | 10008356 | Para_Electrical_Grid_Synchronization_BB_ClosCondLimits_Active | Para_Electrical_Grid_Synchronization_BB_ClosCondLimits_Active | 2979 | Para_Electrical_Grid_Synchronization_BB_ClosCondLimits_Active |  | 10008356
[8 empty] | 10000214 | Para_Electrical_Grid_Synchronization_BS_Acc_Active | Para_Electrical_Grid_Synchronization_BS_Acc_Active | 2980 | Para_Electrical_Grid_Synchronization_BS_Acc_Active |  | 10000214
[8 empty] | 10000211 | Para_Electrical_Grid_Synchronization_BS_Enable | Para_Electrical_Grid_Synchronization_BS_Enable | 2981 | Para_Electrical_Grid_Synchronization_BS_Enable |  | 10000211
[8 empty] | 10000217 | Para_Electrical_Grid_Synchronization_BS_OnlyMan | Para_Electrical_Grid_Synchronization_BS_OnlyMan | 2982 | Para_Electrical_Grid_Synchronization_BS_OnlyMan |  | 10000217
[8 empty] | 10000203 | Para_Electrical_Grid_Synchronization_C_CB_Enable | Para_Electrical_Grid_Synchronization_C_CB_Enable | 2983 | Para_Electrical_Grid_Synchronization_C_CB_Enable |  | 10000203
[8 empty] | 10000232 | Para_Electrical_Grid_Synchronization_EngOpAfterMIF_Enable | Para_Electrical_Grid_Synchronization_EngOpAfterMIF_Enable | 2984 | Para_Electrical_Grid_Synchronization_EngOpAfterMIF_Enable |  | 10000232
[8 empty] | 10008377 | Para_Electrical_Grid_Synchronization_F_BB_ClosCond_Hy | Para_Electrical_Grid_Synchronization_F_BB_ClosCond_Hy | 2985 | Para_Electrical_Grid_Synchronization_F_BB_ClosCond_Hy |  | 10008377
[8 empty] | 10008375 | Para_Electrical_Grid_Synchronization_F_BB_ClosCond_LimHi | Para_Electrical_Grid_Synchronization_F_BB_ClosCond_LimHi | 2986 | Para_Electrical_Grid_Synchronization_F_BB_ClosCond_LimHi |  | 10008375
[8 empty] | 10008374 | Para_Electrical_Grid_Synchronization_F_BB_ClosCond_LimLo | Para_Electrical_Grid_Synchronization_F_BB_ClosCond_LimLo | 2987 | Para_Electrical_Grid_Synchronization_F_BB_ClosCond_LimLo |  | 10008374
[8 empty] | 10003014 | Para_Electrical_Grid_Synchronization_GCB_MainsCutOff_Active | Para_Electrical_Grid_Synchronization_GCB_MainsCutOff_Active | 2988 | Para_Electrical_Grid_Synchronization_GCB_MainsCutOff_Active |  | 10003014
[8 empty] | 10000235 | Para_Electrical_Grid_Synchronization_GenDeexit_Enable | Para_Electrical_Grid_Synchronization_GenDeexit_Enable | 2989 | Para_Electrical_Grid_Synchronization_GenDeexit_Enable |  | 10000235
[8 empty] | 10000208 | Para_Electrical_Grid_Synchronization_IslandOp_Enable | Para_Electrical_Grid_Synchronization_IslandOp_Enable | 2990 | Para_Electrical_Grid_Synchronization_IslandOp_Enable |  | 10000208
[8 empty] | 10000207 | Para_Electrical_Grid_Synchronization_MCB_Ctr_Cust | Para_Electrical_Grid_Synchronization_MCB_Ctr_Cust | 2991 | Para_Electrical_Grid_Synchronization_MCB_Ctr_Cust |  | 10000207
[8 empty] | 10000204 | Para_Electrical_Grid_Synchronization_MCB_Enable | Para_Electrical_Grid_Synchronization_MCB_Enable | 2992 | Para_Electrical_Grid_Synchronization_MCB_Enable |  | 10000204
[8 empty] | 10000206 | Para_Electrical_Grid_Synchronization_MCB_ReSw2Mns_Enable | Para_Electrical_Grid_Synchronization_MCB_ReSw2Mns_Enable | 2993 | Para_Electrical_Grid_Synchronization_MCB_ReSw2Mns_Enable |  | 10000206
[8 empty] | 10000210 | Para_Electrical_Grid_Synchronization_MCB_SyMMD2 | Para_Electrical_Grid_Synchronization_MCB_SyMMD2 | 2994 | Para_Electrical_Grid_Synchronization_MCB_SyMMD2 |  | 10000210
[8 empty] | 10000228 | Para_Electrical_Grid_Synchronization_MIF_Enable | Para_Electrical_Grid_Synchronization_MIF_Enable | 2995 | Para_Electrical_Grid_Synchronization_MIF_Enable |  | 10000228
[8 empty] | 10000205 | Para_Electrical_Grid_Synchronization_Mns_Enable | Para_Electrical_Grid_Synchronization_Mns_Enable | 2996 | Para_Electrical_Grid_Synchronization_Mns_Enable |  | 10000205
[8 empty] | 10000200 | Para_Electrical_Grid_Synchronization_MSy | Para_Electrical_Grid_Synchronization_MSy | 2997 | Para_Electrical_Grid_Synchronization_MSy |  | 10000200
[8 empty] | 10000213 | Para_Electrical_Grid_Synchronization_N_BS_Acc_LimHi | Para_Electrical_Grid_Synchronization_N_BS_Acc_LimHi | 2998 | Para_Electrical_Grid_Synchronization_N_BS_Acc_LimHi |  | 10000213
[8 empty] | 10000209 | Para_Electrical_Grid_Synchronization_OnlyIsland_Enable | Para_Electrical_Grid_Synchronization_OnlyIsland_Enable | 2999 | Para_Electrical_Grid_Synchronization_OnlyIsland_Enable |  | 10000209
[8 empty] | 10000196 | Para_Electrical_Grid_Synchronization_SyActive | Para_Electrical_Grid_Synchronization_SyActive | 3000 | Para_Electrical_Grid_Synchronization_SyActive |  | 10000196
[8 empty] | 10008378 | Para_Electrical_Grid_Synchronization_tiBB_ClosCond_Delay | Para_Electrical_Grid_Synchronization_tiBB_ClosCond_Delay | 3001 | Para_Electrical_Grid_Synchronization_tiBB_ClosCond_Delay |  | 10008378
[8 empty] | 10008379 | Para_Electrical_Grid_Synchronization_tiBB_ClosCondAftMnsFail_Delay | Para_Electrical_Grid_Synchronization_tiBB_ClosCondAftMnsFail_Delay | 3002 | Para_Electrical_Grid_Synchronization_tiBB_ClosCondAftMnsFail_Delay |  | 10008379
[8 empty] | 10000523 | Para_Electrical_Grid_Synchronization_tiMainsOkDelay | Para_Electrical_Grid_Synchronization_tiMainsOkDelay | 3003 | Para_Electrical_Grid_Synchronization_tiMainsOkDelay |  | 10000523
[8 empty] | 10008440 | Para_Electrical_Grid_Synchronization_tiMCB_COf_GCB_OpF | Para_Electrical_Grid_Synchronization_tiMCB_COf_GCB_OpF | 3004 | Para_Electrical_Grid_Synchronization_tiMCB_COf_GCB_OpF |  | 10008440
[8 empty] | 10000230 | Para_Electrical_Grid_Synchronization_tiMIF | Para_Electrical_Grid_Synchronization_tiMIF | 3005 | Para_Electrical_Grid_Synchronization_tiMIF |  | 10000230
[8 empty] | 10008376 | Para_Electrical_Grid_Synchronization_U_BB_ClosCond_Hy_Norm | Para_Electrical_Grid_Synchronization_U_BB_ClosCond_Hy_Norm | 3006 | Para_Electrical_Grid_Synchronization_U_BB_ClosCond_Hy_Norm |  | 10008376
[8 empty] | 10008372 | Para_Electrical_Grid_Synchronization_U_BB_ClosCond_LimHi_Norm | Para_Electrical_Grid_Synchronization_U_BB_ClosCond_LimHi_Norm | 3007 | Para_Electrical_Grid_Synchronization_U_BB_ClosCond_LimHi_Norm |  | 10008372
[8 empty] | 10008373 | Para_Electrical_Grid_Synchronization_U_BB_ClosCond_LimLo_Norm | Para_Electrical_Grid_Synchronization_U_BB_ClosCond_LimLo_Norm | 3008 | Para_Electrical_Grid_Synchronization_U_BB_ClosCond_LimLo_Norm |  | 10008373
[8 empty] | 10000237 | Para_Electrical_Grid_Synchronization_U_Gen_DeEx_LimLo | Para_Electrical_Grid_Synchronization_U_Gen_DeEx_LimLo | 3009 | Para_Electrical_Grid_Synchronization_U_Gen_DeEx_LimLo |  | 10000237
[8 empty] | 10000622 | Para_Electrical_MMD_MMD1_Ang_DiffMax1 | Para_Electrical_MMD_MMD1_Ang_DiffMax1 | 3010 | Para_Electrical_MMD_MMD1_Ang_DiffMax1 |  | 10000622
[8 empty] | 10000624 | Para_Electrical_MMD_MMD1_Ang_PhiSync11 | Para_Electrical_MMD_MMD1_Ang_PhiSync11 | 3011 | Para_Electrical_MMD_MMD1_Ang_PhiSync11 |  | 10000624
[8 empty] | 10000608 | Para_Electrical_MMD_MMD1_Aron_Act1 | Para_Electrical_MMD_MMD1_Aron_Act1 | 3012 | Para_Electrical_MMD_MMD1_Aron_Act1 |  | 10000608
[8 empty] | 10000607 | Para_Electrical_MMD_MMD1_Bus3PhaseCircuit_Act1 | Para_Electrical_MMD_MMD1_Bus3PhaseCircuit_Act1 | 3013 | Para_Electrical_MMD_MMD1_Bus3PhaseCircuit_Act1 |  | 10000607
[8 empty] | 10000611 | Para_Electrical_MMD_MMD1_F_DiffMin1 | Para_Electrical_MMD_MMD1_F_DiffMin1 | 3014 | Para_Electrical_MMD_MMD1_F_DiffMin1 |  | 10000611
[8 empty] | 10000617 | Para_Electrical_MMD_MMD1_F_Nom1 | Para_Electrical_MMD_MMD1_F_Nom1 | 3015 | Para_Electrical_MMD_MMD1_F_Nom1 |  | 10000617
[8 empty] | 10000618 | Para_Electrical_MMD_MMD1_F_Over1 | Para_Electrical_MMD_MMD1_F_Over1 | 3016 | Para_Electrical_MMD_MMD1_F_Over1 |  | 10000618
[8 empty] | 10000623 | Para_Electrical_MMD_MMD1_F_Under1 | Para_Electrical_MMD_MMD1_F_Under1 | 3017 | Para_Electrical_MMD_MMD1_F_Under1 |  | 10000623
[8 empty] | 10000613 | Para_Electrical_MMD_MMD1_Gen3PhaseCircuit_Act1 | Para_Electrical_MMD_MMD1_Gen3PhaseCircuit_Act1 | 3018 | Para_Electrical_MMD_MMD1_Gen3PhaseCircuit_Act1 |  | 10000613
[8 empty] | 10000609 | Para_Electrical_MMD_MMD1_I_CurrRange1 | Para_Electrical_MMD_MMD1_I_CurrRange1 | 3019 | Para_Electrical_MMD_MMD1_I_CurrRange1 |  | 10000609
[8 empty] | 10000610 | Para_Electrical_MMD_MMD1_I_GenNom1 | Para_Electrical_MMD_MMD1_I_GenNom1 | 3020 | Para_Electrical_MMD_MMD1_I_GenNom1 |  | 10000610
[8 empty] | 10000612 | Para_Electrical_MMD_MMD1_I_Short1 | Para_Electrical_MMD_MMD1_I_Short1 | 3021 | Para_Electrical_MMD_MMD1_I_Short1 |  | 10000612
[8 empty] | 10000605 | Para_Electrical_MMD_MMD1_MMDSynch_Act1 | Para_Electrical_MMD_MMD1_MMDSynch_Act1 | 3022 | Para_Electrical_MMD_MMD1_MMDSynch_Act1 |  | 10000605
[8 empty] | 10000615 | Para_Electrical_MMD_MMD1_Mul_U_Bus1 | Para_Electrical_MMD_MMD1_Mul_U_Bus1 | 3023 | Para_Electrical_MMD_MMD1_Mul_U_Bus1 |  | 10000615
[8 empty] | 10000621 | Para_Electrical_MMD_MMD1_Ti_F_OverDel1 | Para_Electrical_MMD_MMD1_Ti_F_OverDel1 | 3024 | Para_Electrical_MMD_MMD1_Ti_F_OverDel1 |  | 10000621
[8 empty] | 10000628 | Para_Electrical_MMD_MMD1_Ti_F_UnderDel1 | Para_Electrical_MMD_MMD1_Ti_F_UnderDel1 | 3025 | Para_Electrical_MMD_MMD1_Ti_F_UnderDel1 |  | 10000628
[8 empty] | 10000616 | Para_Electrical_MMD_MMD1_Ti_I_ShortDel1 | Para_Electrical_MMD_MMD1_Ti_I_ShortDel1 | 3026 | Para_Electrical_MMD_MMD1_Ti_I_ShortDel1 |  | 10000616
[8 empty] | 10000632 | Para_Electrical_MMD_MMD1_Ti_U_AsymDel1 | Para_Electrical_MMD_MMD1_Ti_U_AsymDel1 | 3027 | Para_Electrical_MMD_MMD1_Ti_U_AsymDel1 |  | 10000632
[8 empty] | 10000619 | Para_Electrical_MMD_MMD1_Ti_V_Over1 | Para_Electrical_MMD_MMD1_Ti_V_Over1 | 3028 | Para_Electrical_MMD_MMD1_Ti_V_Over1 |  | 10000619
[8 empty] | 10000626 | Para_Electrical_MMD_MMD1_Ti_V_Under1 | Para_Electrical_MMD_MMD1_Ti_V_Under1 | 3029 | Para_Electrical_MMD_MMD1_Ti_V_Under1 |  | 10000626
[8 empty] | 10000631 | Para_Electrical_MMD_MMD1_Ti_V_Under21 | Para_Electrical_MMD_MMD1_Ti_V_Under21 | 3030 | Para_Electrical_MMD_MMD1_Ti_V_Under21 |  | 10000631
[8 empty] | 10000629 | Para_Electrical_MMD_MMD1_U_Asym1 | Para_Electrical_MMD_MMD1_U_Asym1 | 3031 | Para_Electrical_MMD_MMD1_U_Asym1 |  | 10000629
[8 empty] | 10000634 | Para_Electrical_MMD_MMD1_U_BusNom1 | Para_Electrical_MMD_MMD1_U_BusNom1 | 3032 | Para_Electrical_MMD_MMD1_U_BusNom1 |  | 10000634
[8 empty] | 10000633 | Para_Electrical_MMD_MMD1_U_DeadBus1 | Para_Electrical_MMD_MMD1_U_DeadBus1 | 3033 | Para_Electrical_MMD_MMD1_U_DeadBus1 |  | 10000633
[8 empty] | 10000630 | Para_Electrical_MMD_MMD1_U_DeadSync1 | Para_Electrical_MMD_MMD1_U_DeadSync1 | 3034 | Para_Electrical_MMD_MMD1_U_DeadSync1 |  | 10000630
[8 empty] | 10000637 | Para_Electrical_MMD_MMD1_U_DiffMax1 | Para_Electrical_MMD_MMD1_U_DiffMax1 | 3035 | Para_Electrical_MMD_MMD1_U_DiffMax1 |  | 10000637
[8 empty] | 10000614 | Para_Electrical_MMD_MMD1_U_Gen_Nom1 | Para_Electrical_MMD_MMD1_U_Gen_Nom1 | 3036 | Para_Electrical_MMD_MMD1_U_Gen_Nom1 |  | 10000614
[8 empty] | 10000639 | Para_Electrical_MMD_MMD1_U_Range1 | Para_Electrical_MMD_MMD1_U_Range1 | 3037 | Para_Electrical_MMD_MMD1_U_Range1 |  | 10000639
[8 empty] | 10000635 | Para_Electrical_MMD_MMD1_U_RangeBus1 | Para_Electrical_MMD_MMD1_U_RangeBus1 | 3038 | Para_Electrical_MMD_MMD1_U_RangeBus1 |  | 10000635
[8 empty] | 10000636 | Para_Electrical_MMD_MMD1_U_RangeSync11 | Para_Electrical_MMD_MMD1_U_RangeSync11 | 3039 | Para_Electrical_MMD_MMD1_U_RangeSync11 |  | 10000636
[8 empty] | 10000641 | Para_Electrical_MMD_MMD1_U_RangeSync21 | Para_Electrical_MMD_MMD1_U_RangeSync21 | 3040 | Para_Electrical_MMD_MMD1_U_RangeSync21 |  | 10000641
[8 empty] | 10000638 | Para_Electrical_MMD_MMD1_U_SyncNom1 | Para_Electrical_MMD_MMD1_U_SyncNom1 | 3041 | Para_Electrical_MMD_MMD1_U_SyncNom1 |  | 10000638
[8 empty] | 10000620 | Para_Electrical_MMD_MMD1_V_Over1 | Para_Electrical_MMD_MMD1_V_Over1 | 3042 | Para_Electrical_MMD_MMD1_V_Over1 |  | 10000620
[8 empty] | 10000627 | Para_Electrical_MMD_MMD1_V_Under1 | Para_Electrical_MMD_MMD1_V_Under1 | 3043 | Para_Electrical_MMD_MMD1_V_Under1 |  | 10000627
[8 empty] | 10000625 | Para_Electrical_MMD_MMD1_V_Under21 | Para_Electrical_MMD_MMD1_V_Under21 | 3044 | Para_Electrical_MMD_MMD1_V_Under21 |  | 10000625
[8 empty] | 10000728 | Para_Electrical_MMD_MMD2_Act | Para_Electrical_MMD_MMD2_Act | 3045 | Para_Electrical_MMD_MMD2_Act |  | 10000728
[8 empty] | 10000657 | Para_Electrical_MMD_MMD2_Ang_DiffMax2 | Para_Electrical_MMD_MMD2_Ang_DiffMax2 | 3046 | Para_Electrical_MMD_MMD2_Ang_DiffMax2 |  | 10000657
[8 empty] | 10000659 | Para_Electrical_MMD_MMD2_Ang_PhiSync12 | Para_Electrical_MMD_MMD2_Ang_PhiSync12 | 3047 | Para_Electrical_MMD_MMD2_Ang_PhiSync12 |  | 10000659
[8 empty] | 10000642 | Para_Electrical_MMD_MMD2_Aron_Act2 | Para_Electrical_MMD_MMD2_Aron_Act2 | 3048 | Para_Electrical_MMD_MMD2_Aron_Act2 |  | 10000642
[8 empty] | 10000645 | Para_Electrical_MMD_MMD2_Bus3PhaseCircuit_Act2 | Para_Electrical_MMD_MMD2_Bus3PhaseCircuit_Act2 | 3049 | Para_Electrical_MMD_MMD2_Bus3PhaseCircuit_Act2 |  | 10000645
[8 empty] | 10000643 | Para_Electrical_MMD_MMD2_F_DiffMin2 | Para_Electrical_MMD_MMD2_F_DiffMin2 | 3050 | Para_Electrical_MMD_MMD2_F_DiffMin2 |  | 10000643
[8 empty] | 10000652 | Para_Electrical_MMD_MMD2_F_Nom2 | Para_Electrical_MMD_MMD2_F_Nom2 | 3051 | Para_Electrical_MMD_MMD2_F_Nom2 |  | 10000652
[8 empty] | 10000653 | Para_Electrical_MMD_MMD2_F_Over2 | Para_Electrical_MMD_MMD2_F_Over2 | 3052 | Para_Electrical_MMD_MMD2_F_Over2 |  | 10000653
[8 empty] | 10000661 | Para_Electrical_MMD_MMD2_F_Under2 | Para_Electrical_MMD_MMD2_F_Under2 | 3053 | Para_Electrical_MMD_MMD2_F_Under2 |  | 10000661
[8 empty] | 10000649 | Para_Electrical_MMD_MMD2_Gen3PhaseCircuit_Act2 | Para_Electrical_MMD_MMD2_Gen3PhaseCircuit_Act2 | 3054 | Para_Electrical_MMD_MMD2_Gen3PhaseCircuit_Act2 |  | 10000649
[8 empty] | 10000646 | Para_Electrical_MMD_MMD2_I_CurrRange2 | Para_Electrical_MMD_MMD2_I_CurrRange2 | 3055 | Para_Electrical_MMD_MMD2_I_CurrRange2 |  | 10000646
[8 empty] | 10000644 | Para_Electrical_MMD_MMD2_I_GenNom2 | Para_Electrical_MMD_MMD2_I_GenNom2 | 3056 | Para_Electrical_MMD_MMD2_I_GenNom2 |  | 10000644
[8 empty] | 10000647 | Para_Electrical_MMD_MMD2_I_Short2 | Para_Electrical_MMD_MMD2_I_Short2 | 3057 | Para_Electrical_MMD_MMD2_I_Short2 |  | 10000647
[8 empty] | 10000640 | Para_Electrical_MMD_MMD2_MMDSynch_Act2 | Para_Electrical_MMD_MMD2_MMDSynch_Act2 | 3058 | Para_Electrical_MMD_MMD2_MMDSynch_Act2 |  | 10000640
[8 empty] | 10000650 | Para_Electrical_MMD_MMD2_Mul_U_Bus2 | Para_Electrical_MMD_MMD2_Mul_U_Bus2 | 3059 | Para_Electrical_MMD_MMD2_Mul_U_Bus2 |  | 10000650
[8 empty] | 10000655 | Para_Electrical_MMD_MMD2_Mul_U_Sync12 | Para_Electrical_MMD_MMD2_Mul_U_Sync12 | 3060 | Para_Electrical_MMD_MMD2_Mul_U_Sync12 |  | 10000655
[8 empty] | 10000651 | Para_Electrical_MMD_MMD2_Ti_F_OverDel2 | Para_Electrical_MMD_MMD2_Ti_F_OverDel2 | 3061 | Para_Electrical_MMD_MMD2_Ti_F_OverDel2 |  | 10000651
[8 empty] | 10000660 | Para_Electrical_MMD_MMD2_Ti_F_UnderDel2 | Para_Electrical_MMD_MMD2_Ti_F_UnderDel2 | 3062 | Para_Electrical_MMD_MMD2_Ti_F_UnderDel2 |  | 10000660
[8 empty] | 10000648 | Para_Electrical_MMD_MMD2_Ti_I_ShortDel2 | Para_Electrical_MMD_MMD2_Ti_I_ShortDel2 | 3063 | Para_Electrical_MMD_MMD2_Ti_I_ShortDel2 |  | 10000648
[8 empty] | 10000669 | Para_Electrical_MMD_MMD2_Ti_U_AsymDel2 | Para_Electrical_MMD_MMD2_Ti_U_AsymDel2 | 3064 | Para_Electrical_MMD_MMD2_Ti_U_AsymDel2 |  | 10000669
[8 empty] | 10000658 | Para_Electrical_MMD_MMD2_Ti_V_Over2 | Para_Electrical_MMD_MMD2_Ti_V_Over2 | 3065 | Para_Electrical_MMD_MMD2_Ti_V_Over2 |  | 10000658
[8 empty] | 10000667 | Para_Electrical_MMD_MMD2_Ti_V_Under2 | Para_Electrical_MMD_MMD2_Ti_V_Under2 | 3066 | Para_Electrical_MMD_MMD2_Ti_V_Under2 |  | 10000667
[8 empty] | 10000665 | Para_Electrical_MMD_MMD2_Ti_V_Under22 | Para_Electrical_MMD_MMD2_Ti_V_Under22 | 3067 | Para_Electrical_MMD_MMD2_Ti_V_Under22 |  | 10000665
[8 empty] | 10000666 | Para_Electrical_MMD_MMD2_U_Asym2 | Para_Electrical_MMD_MMD2_U_Asym2 | 3068 | Para_Electrical_MMD_MMD2_U_Asym2 |  | 10000666
[8 empty] | 10000673 | Para_Electrical_MMD_MMD2_U_BusNom2 | Para_Electrical_MMD_MMD2_U_BusNom2 | 3069 | Para_Electrical_MMD_MMD2_U_BusNom2 |  | 10000673
[8 empty] | 10000674 | Para_Electrical_MMD_MMD2_U_DeadBus2 | Para_Electrical_MMD_MMD2_U_DeadBus2 | 3070 | Para_Electrical_MMD_MMD2_U_DeadBus2 |  | 10000674
[8 empty] | 10000668 | Para_Electrical_MMD_MMD2_U_DeadSync2 | Para_Electrical_MMD_MMD2_U_DeadSync2 | 3071 | Para_Electrical_MMD_MMD2_U_DeadSync2 |  | 10000668
[8 empty] | 10000671 | Para_Electrical_MMD_MMD2_U_DiffMax2 | Para_Electrical_MMD_MMD2_U_DiffMax2 | 3072 | Para_Electrical_MMD_MMD2_U_DiffMax2 |  | 10000671
[8 empty] | 10000654 | Para_Electrical_MMD_MMD2_U_Gen_Nom2 | Para_Electrical_MMD_MMD2_U_Gen_Nom2 | 3073 | Para_Electrical_MMD_MMD2_U_Gen_Nom2 |  | 10000654
[8 empty] | 10000670 | Para_Electrical_MMD_MMD2_U_Range2 | Para_Electrical_MMD_MMD2_U_Range2 | 3074 | Para_Electrical_MMD_MMD2_U_Range2 |  | 10000670
[8 empty] | 10000677 | Para_Electrical_MMD_MMD2_U_RangeBus2 | Para_Electrical_MMD_MMD2_U_RangeBus2 | 3075 | Para_Electrical_MMD_MMD2_U_RangeBus2 |  | 10000677
[8 empty] | 10000678 | Para_Electrical_MMD_MMD2_U_RangeSync12 | Para_Electrical_MMD_MMD2_U_RangeSync12 | 3076 | Para_Electrical_MMD_MMD2_U_RangeSync12 |  | 10000678
[8 empty] | 10000676 | Para_Electrical_MMD_MMD2_U_RangeSync22 | Para_Electrical_MMD_MMD2_U_RangeSync22 | 3077 | Para_Electrical_MMD_MMD2_U_RangeSync22 |  | 10000676
[8 empty] | 10000672 | Para_Electrical_MMD_MMD2_U_SyncNom2 | Para_Electrical_MMD_MMD2_U_SyncNom2 | 3078 | Para_Electrical_MMD_MMD2_U_SyncNom2 |  | 10000672
[8 empty] | 10000656 | Para_Electrical_MMD_MMD2_V_Over2 | Para_Electrical_MMD_MMD2_V_Over2 | 3079 | Para_Electrical_MMD_MMD2_V_Over2 |  | 10000656
[8 empty] | 10000664 | Para_Electrical_MMD_MMD2_V_Under2 | Para_Electrical_MMD_MMD2_V_Under2 | 3080 | Para_Electrical_MMD_MMD2_V_Under2 |  | 10000664
[8 empty] | 10000663 | Para_Electrical_MMD_MMD2_V_Under22 | Para_Electrical_MMD_MMD2_V_Under22 | 3081 | Para_Electrical_MMD_MMD2_V_Under22 |  | 10000663
[8 empty] | 10049888 | Para_emission_bco_scr_emline1_exist | Para_emission_bco_scr_emline1_exist | 3082 | Para_emission_bco_scr_emline1_exist |  | 10049888
[8 empty] | 10049889 | Para_emission_bem_avgcalc_start | Para_emission_bem_avgcalc_start | 3083 | Para_emission_bem_avgcalc_start |  | 10049889
[8 empty] | 10049890 | Para_emission_bem_avgcalc_steadystate | Para_emission_bem_avgcalc_steadystate | 3084 | Para_emission_bem_avgcalc_steadystate |  | 10049890
[8 empty] | 10049892 | Para_emission_bno2_scr_emline1_exist | Para_emission_bno2_scr_emline1_exist | 3085 | Para_emission_bno2_scr_emline1_exist |  | 10049892
[8 empty] | 10049891 | Para_emission_bno_scr_emline1_exist | Para_emission_bno_scr_emline1_exist | 3086 | Para_emission_bno_scr_emline1_exist |  | 10049891
[8 empty] | 10049893 | Para_emission_bnoxs_heating_active | Para_emission_bnoxs_heating_active | 3087 | Para_emission_bnoxs_heating_active |  | 10049893
[8 empty] | 10049894 | Para_emission_bscr_active | Para_emission_bscr_active | 3088 | Para_emission_bscr_active |  | 10049894
[8 empty] | 10049895 | Para_emission_bt_scr_catin_exist | Para_emission_bt_scr_catin_exist | 3089 | Para_emission_bt_scr_catin_exist |  | 10049895
[8 empty] | 10049896 | Para_emission_bt_scr_catout_exist | Para_emission_bt_scr_catout_exist | 3090 | Para_emission_bt_scr_catout_exist |  | 10049896
[8 empty] | 10049897 | Para_emission_iidx_em_avgmon_option | Para_emission_iidx_em_avgmon_option | 3091 | Para_emission_iidx_em_avgmon_option |  | 10049897
[8 empty] | 10049898 | Para_emission_iidx_noxs_config | Para_emission_iidx_noxs_config | 3092 | Para_emission_iidx_noxs_config |  | 10049898
[8 empty] | 10049899 | Para_emission_iidx_scr_extemoption | Para_emission_iidx_scr_extemoption | 3093 | Para_emission_iidx_scr_extemoption |  | 10049899
[8 empty] | 10049900 | Para_emission_inoxs_lifetime | Para_emission_inoxs_lifetime | 3094 | Para_emission_inoxs_lifetime | h | 10049900
[8 empty] | 10049901 | Para_emission_rco_em_catout_mg_hi | Para_emission_rco_em_catout_mg_hi | 3095 | Para_emission_rco_em_catout_mg_hi | mg/Nm3 | 10049901
[8 empty] | 10049902 | Para_emission_rnox_em_catout_mg_hi | Para_emission_rnox_em_catout_mg_hi | 3096 | Para_emission_rnox_em_catout_mg_hi | mg/Nm3 | 10049902
[8 empty] | 10049903 | Para_emission_rnox_em_catout_mg_hitol | Para_emission_rnox_em_catout_mg_hitol | 3097 | Para_emission_rnox_em_catout_mg_hitol | mg/Nm3 | 10049903
[8 empty] | 10049904 | Para_emission_rnox_em_catout_mg_set | Para_emission_rnox_em_catout_mg_set | 3098 | Para_emission_rnox_em_catout_mg_set | mg/Nm3 | 10049904
[8 empty] | 10049905 | Para_emission_rnox_em_engout_mg_hi | Para_emission_rnox_em_engout_mg_hi | 3099 | Para_emission_rnox_em_engout_mg_hi | mg/Nm3 | 10049905
[8 empty] | 10049906 | Para_emission_rnox_em_engout_mg_hitol | Para_emission_rnox_em_engout_mg_hitol | 3100 | Para_emission_rnox_em_engout_mg_hitol | mg/Nm3 | 10049906
[8 empty] | 10049907 | Para_emission_rnox_em_engout_mg_set | Para_emission_rnox_em_engout_mg_set | 3101 | Para_emission_rnox_em_engout_mg_set | mg/Nm3 | 10049907
[8 empty] | 10049908 | Para_emission_rnox_noxs_catout_offs | Para_emission_rnox_noxs_catout_offs | 3102 | Para_emission_rnox_noxs_catout_offs | ppm | 10049908
[8 empty] | 10049909 | Para_emission_rnox_noxs_engout_a_offs | Para_emission_rnox_noxs_engout_a_offs | 3103 | Para_emission_rnox_noxs_engout_a_offs | ppm | 10049909
[8 empty] | 10049910 | Para_emission_rnox_noxs_engout_b_offs | Para_emission_rnox_noxs_engout_b_offs | 3104 | Para_emission_rnox_noxs_engout_b_offs | ppm | 10049910
[8 empty] | 10049911 | Para_emission_rnox_noxs_engout_dev_hi | Para_emission_rnox_noxs_engout_dev_hi | 3105 | Para_emission_rnox_noxs_engout_dev_hi | ppm | 10049911
[8 empty] | 10049912 | Para_emission_rnox_noxs_engout_offs | Para_emission_rnox_noxs_engout_offs | 3106 | Para_emission_rnox_noxs_engout_offs | ppm | 10049912
[8 empty] | 10049913 | Para_emission_ro2_noxs_catout_offs | Para_emission_ro2_noxs_catout_offs | 3107 | Para_emission_ro2_noxs_catout_offs | % | 10049913
[8 empty] | 10049914 | Para_emission_ro2_noxs_engout_a_offs | Para_emission_ro2_noxs_engout_a_offs | 3108 | Para_emission_ro2_noxs_engout_a_offs | % | 10049914
[8 empty] | 10049915 | Para_emission_ro2_noxs_engout_b_offs | Para_emission_ro2_noxs_engout_b_offs | 3109 | Para_emission_ro2_noxs_engout_b_offs | % | 10049915
[8 empty] | 10049916 | Para_emission_ro2_noxs_engout_dev_hi | Para_emission_ro2_noxs_engout_dev_hi | 3110 | Para_emission_ro2_noxs_engout_dev_hi | % | 10049916
[8 empty] | 10049917 | Para_emission_ro2_noxs_engout_offs | Para_emission_ro2_noxs_engout_offs | 3111 | Para_emission_ro2_noxs_engout_offs | % | 10049917
[8 empty] | 10049918 | Para_emission_ro2_reference | Para_emission_ro2_reference | 3112 | Para_emission_ro2_reference | % | 10049918
[8 empty] | 10049919 | Para_emission_rp_scr_ureadosingunit_release | Para_emission_rp_scr_ureadosingunit_release | 3113 | Para_emission_rp_scr_ureadosingunit_release | %Pnom | 10049919
[8 empty] | 10049920 | Para_emission_rratio_no2_nox_catout | Para_emission_rratio_no2_nox_catout | 3114 | Para_emission_rratio_no2_nox_catout | % | 10049920
[8 empty] | 10049921 | Para_emission_rratio_no2_nox_engout | Para_emission_rratio_no2_nox_engout | 3115 | Para_emission_rratio_no2_nox_engout | % | 10049921
[8 empty] | 10049922 | Para_emission_rt_scr_catin_hi | Para_emission_rt_scr_catin_hi | 3116 | Para_emission_rt_scr_catin_hi | °C | 10049922
[8 empty] | 10049923 | Para_emission_rt_scr_catout_hi | Para_emission_rt_scr_catout_hi | 3117 | Para_emission_rt_scr_catout_hi | °C | 10049923
[8 empty] | 10049924 | Para_emission_rt_scr_ureadosingunit_release | Para_emission_rt_scr_ureadosingunit_release | 3118 | Para_emission_rt_scr_ureadosingunit_release | °C | 10049924
[8 empty] | 10049925 | Para_emission_tiem_avgcalc_timebase | Para_emission_tiem_avgcalc_timebase | 3119 | Para_emission_tiem_avgcalc_timebase | min | 10049925
[8 empty] | 10049926 | Para_emission_tiscr_eac_durationstartup | Para_emission_tiscr_eac_durationstartup | 3120 | Para_emission_tiscr_eac_durationstartup | s | 10049926
[8 empty] | 10049927 | Para_emission_tiscr_emline_purgingwaiting | Para_emission_tiscr_emline_purgingwaiting | 3121 | Para_emission_tiscr_emline_purgingwaiting | s | 10049927
[8 empty] | 17218 | Para_EngDat_AccessNr | Para_EngDat_AccessNr | 3122 | Para_EngDat_AccessNr |  | 17218
[8 empty] | 17219 | Para_EngDat_Act2StageTC | Para_EngDat_Act2StageTC | 3123 | Para_EngDat_Act2StageTC |  | 17219
[8 empty] | 17220 | Para_EngDat_Act3WayKat | Para_EngDat_Act3WayKat | 3124 | Para_EngDat_Act3WayKat |  | 17220
[8 empty] | 17221 | Para_EngDat_ActAutGas | Para_EngDat_ActAutGas | 3125 | Para_EngDat_ActAutGas |  | 17221
[8 empty] | 17222 | Para_EngDat_ActAuxCool | Para_EngDat_ActAuxCool | 3126 | Para_EngDat_ActAuxCool |  | 17222
[8 empty] | 17223 | Para_EngDat_ActAuxVent | Para_EngDat_ActAuxVent | 3127 | Para_EngDat_ActAuxVent |  | 17223
[8 empty] | 17224 | Para_EngDat_ActCodinox | Para_EngDat_ActCodinox | 3128 | Para_EngDat_ActCodinox |  | 17224
[8 empty] | 17225 | Para_EngDat_ActExhReactor | Para_EngDat_ActExhReactor | 3129 | Para_EngDat_ActExhReactor |  | 17225
[8 empty] | 17226 | Para_EngDat_ActGasMix_NEx | Para_EngDat_ActGasMix_NEx | 3130 | Para_EngDat_ActGasMix_NEx |  | 17226
[8 empty] | 17227 | Para_EngDat_ActHumidity | Para_EngDat_ActHumidity | 3131 | Para_EngDat_ActHumidity |  | 17227
[8 empty] | 17228 | Para_EngDat_ActIC900 | Para_EngDat_ActIC900 | 3132 | Para_EngDat_ActIC900 |  | 17228
[8 empty] | 17229 | Para_EngDat_ActIsolatedOp | Para_EngDat_ActIsolatedOp | 3133 | Para_EngDat_ActIsolatedOp |  | 17229
[8 empty] | 17230 | Para_EngDat_ActKLS90_NEx | Para_EngDat_ActKLS90_NEx | 3134 | Para_EngDat_ActKLS90_NEx |  | 17230
[8 empty] | 17231 | Para_EngDat_ActKLS98 | Para_EngDat_ActKLS98 | 3135 | Para_EngDat_ActKLS98 |  | 17231
[8 empty] | 17232 | Para_EngDat_ActKLS98Misf_NEx | Para_EngDat_ActKLS98Misf_NEx | 3136 | Para_EngDat_ActKLS98Misf_NEx |  | 17232
[8 empty] | 17233 | Para_EngDat_ActLIVC | Para_EngDat_ActLIVC | 3137 | Para_EngDat_ActLIVC |  | 17233
[8 empty] | 17234 | Para_EngDat_ActMixTempCtr | Para_EngDat_ActMixTempCtr | 3138 | Para_EngDat_ActMixTempCtr |  | 17234
[8 empty] | 17235 | Para_EngDat_ActMMU2_NEx | Para_EngDat_ActMMU2_NEx | 3139 | Para_EngDat_ActMMU2_NEx |  | 17235
[8 empty] | 17236 | Para_EngDat_ActMonic | Para_EngDat_ActMonic | 3140 | Para_EngDat_ActMonic |  | 17236
[8 empty] | 17237 | Para_EngDat_ActNOx | Para_EngDat_ActNOx | 3141 | Para_EngDat_ActNOx |  | 17237
[8 empty] | 17238 | Para_EngDat_ActOilCount | Para_EngDat_ActOilCount | 3142 | Para_EngDat_ActOilCount |  | 17238
[8 empty] | 17239 | Para_EngDat_ActOutDoorTemp | Para_EngDat_ActOutDoorTemp | 3143 | Para_EngDat_ActOutDoorTemp |  | 17239
[8 empty] | 17240 | Para_EngDat_ActOxyKat | Para_EngDat_ActOxyKat | 3144 | Para_EngDat_ActOxyKat |  | 17240
[8 empty] | 17241 | Para_EngDat_ActPFCtr | Para_EngDat_ActPFCtr | 3145 | Para_EngDat_ActPFCtr |  | 17241
[8 empty] | 17242 | Para_EngDat_ActPlantCtr1 | Para_EngDat_ActPlantCtr1 | 3146 | Para_EngDat_ActPlantCtr1 |  | 17242
[8 empty] | 17243 | Para_EngDat_ActPlantCtr10 | Para_EngDat_ActPlantCtr10 | 3147 | Para_EngDat_ActPlantCtr10 |  | 17243
[8 empty] | 17244 | Para_EngDat_ActPlantCtr11 | Para_EngDat_ActPlantCtr11 | 3148 | Para_EngDat_ActPlantCtr11 |  | 17244
[8 empty] | 17245 | Para_EngDat_ActPlantCtr12 | Para_EngDat_ActPlantCtr12 | 3149 | Para_EngDat_ActPlantCtr12 |  | 17245
[8 empty] | 17246 | Para_EngDat_ActPlantCtr13 | Para_EngDat_ActPlantCtr13 | 3150 | Para_EngDat_ActPlantCtr13 |  | 17246
[8 empty] | 17247 | Para_EngDat_ActPlantCtr14 | Para_EngDat_ActPlantCtr14 | 3151 | Para_EngDat_ActPlantCtr14 |  | 17247
[8 empty] | 17248 | Para_EngDat_ActPlantCtr15 | Para_EngDat_ActPlantCtr15 | 3152 | Para_EngDat_ActPlantCtr15 |  | 17248
[8 empty] | 17249 | Para_EngDat_ActPlantCtr16 | Para_EngDat_ActPlantCtr16 | 3153 | Para_EngDat_ActPlantCtr16 |  | 17249
[8 empty] | 17250 | Para_EngDat_ActPlantCtr2 | Para_EngDat_ActPlantCtr2 | 3154 | Para_EngDat_ActPlantCtr2 |  | 17250
[8 empty] | 17251 | Para_EngDat_ActPlantCtr3 | Para_EngDat_ActPlantCtr3 | 3155 | Para_EngDat_ActPlantCtr3 |  | 17251
[8 empty] | 17252 | Para_EngDat_ActPlantCtr4 | Para_EngDat_ActPlantCtr4 | 3156 | Para_EngDat_ActPlantCtr4 |  | 17252
[8 empty] | 17253 | Para_EngDat_ActPlantCtr5 | Para_EngDat_ActPlantCtr5 | 3157 | Para_EngDat_ActPlantCtr5 |  | 17253
[8 empty] | 17254 | Para_EngDat_ActPlantCtr6 | Para_EngDat_ActPlantCtr6 | 3158 | Para_EngDat_ActPlantCtr6 |  | 17254
[8 empty] | 17255 | Para_EngDat_ActPlantCtr7 | Para_EngDat_ActPlantCtr7 | 3159 | Para_EngDat_ActPlantCtr7 |  | 17255
[8 empty] | 17256 | Para_EngDat_ActPlantCtr8 | Para_EngDat_ActPlantCtr8 | 3160 | Para_EngDat_ActPlantCtr8 |  | 17256
[8 empty] | 17257 | Para_EngDat_ActPreChambGasComp | Para_EngDat_ActPreChambGasComp | 3161 | Para_EngDat_ActPreChambGasComp |  | 17257
[8 empty] | 17258 | Para_EngDat_ActPRedTempIntakeAir | Para_EngDat_ActPRedTempIntakeAir | 3162 | Para_EngDat_ActPRedTempIntakeAir |  | 17258
[8 empty] | 17259 | Para_EngDat_ActPRedTurboSpeed | Para_EngDat_ActPRedTurboSpeed | 3163 | Para_EngDat_ActPRedTurboSpeed |  | 17259
[8 empty] | 17260 | Para_EngDat_ActReceiveDataBus1 | Para_EngDat_ActReceiveDataBus1 | 3164 | Para_EngDat_ActReceiveDataBus1 |  | 17260
[8 empty] | 17261 | Para_EngDat_ActReceiveDataBus2 | Para_EngDat_ActReceiveDataBus2 | 3165 | Para_EngDat_ActReceiveDataBus2 |  | 17261
[8 empty] | 17262 | Para_EngDat_ActReserveAnalog | Para_EngDat_ActReserveAnalog | 3166 | Para_EngDat_ActReserveAnalog |  | 17262
[8 empty] | 17263 | Para_EngDat_ActReservePar | Para_EngDat_ActReservePar | 3167 | Para_EngDat_ActReservePar |  | 17263
[8 empty] | 17264 | Para_EngDat_ActRoomTemp | Para_EngDat_ActRoomTemp | 3168 | Para_EngDat_ActRoomTemp |  | 17264
[8 empty] | 17265 | Para_EngDat_ActSAFI | Para_EngDat_ActSAFI | 3169 | Para_EngDat_ActSAFI |  | 17265
[8 empty] | 17266 | Para_EngDat_ActSpecGM | Para_EngDat_ActSpecGM | 3170 | Para_EngDat_ActSpecGM |  | 17266
[8 empty] | 17267 | Para_EngDat_ActSpecialGas | Para_EngDat_ActSpecialGas | 3171 | Para_EngDat_ActSpecialGas |  | 17267
[8 empty] | 17268 | Para_EngDat_ActTecJet | Para_EngDat_ActTecJet | 3172 | Para_EngDat_ActTecJet |  | 17268
[8 empty] | 17269 | Para_EngDat_ActTempIntakeAir | Para_EngDat_ActTempIntakeAir | 3173 | Para_EngDat_ActTempIntakeAir |  | 17269
[8 empty] | 17270 | Para_EngDat_ActTurboBypass | Para_EngDat_ActTurboBypass | 3174 | Para_EngDat_ActTurboBypass |  | 17270
[8 empty] | 17271 | Para_EngDat_ActTurboSpeedA | Para_EngDat_ActTurboSpeedA | 3175 | Para_EngDat_ActTurboSpeedA |  | 17271
[8 empty] | 17272 | Para_EngDat_ActTurboSpeedB | Para_EngDat_ActTurboSpeedB | 3176 | Para_EngDat_ActTurboSpeedB |  | 17272
[8 empty] | 17273 | Para_EngDat_ActTurboSpeedLPA | Para_EngDat_ActTurboSpeedLPA | 3177 | Para_EngDat_ActTurboSpeedLPA |  | 17273
[8 empty] | 17274 | Para_EngDat_ActTurboSpeedLPB | Para_EngDat_ActTurboSpeedLPB | 3178 | Para_EngDat_ActTurboSpeedLPB |  | 17274
[8 empty] | 17275 | Para_EngDat_ActUniIO | Para_EngDat_ActUniIO | 3179 | Para_EngDat_ActUniIO |  | 17275
[8 empty] | 17276 | Para_EngDat_ActWasteGate | Para_EngDat_ActWasteGate | 3180 | Para_EngDat_ActWasteGate |  | 17276
[8 empty] | 17277 | Para_EngDat_ApplicationName_NEx | Para_EngDat_ApplicationName_NEx | 3181 | Para_EngDat_ApplicationName_NEx |  | 17277
[8 empty] | 17278 | Para_EngDat_ApplicationType_NEx | Para_EngDat_ApplicationType_NEx | 3182 | Para_EngDat_ApplicationType_NEx |  | 17278
[8 empty] | 17279 | Para_EngDat_BasisUpdateVers_NEx | Para_EngDat_BasisUpdateVers_NEx | 3183 | Para_EngDat_BasisUpdateVers_NEx |  | 17279
[8 empty] | 17280 | Para_EngDat_CompRate | Para_EngDat_CompRate | 3184 | Para_EngDat_CompRate |  | 17280
[8 empty] | 221 | Para_EngDat_EngineNr_NEx | Para_EngDat_EngineNr_NEx | 3185 | Para_EngDat_EngineNr_NEx |  | 221
[8 empty] | 1239 | Para_EngDat_EngineType_NEx | Para_EngDat_EngineType_NEx | 3186 | Para_EngDat_EngineType_NEx |  | 1239
[8 empty] | 17281 | Para_EngDat_GroupAccessNr | Para_EngDat_GroupAccessNr | 3187 | Para_EngDat_GroupAccessNr |  | 17281
[8 empty] | 17282 | Para_EngDat_GroupAccessNr2 | Para_EngDat_GroupAccessNr2 | 3188 | Para_EngDat_GroupAccessNr2 |  | 17282
[8 empty] | 17283 | Para_EngDat_GroupAccessNr3 | Para_EngDat_GroupAccessNr3 | 3189 | Para_EngDat_GroupAccessNr3 |  | 17283
[8 empty] | 17284 | Para_EngDat_LanguageID_NEx | Para_EngDat_LanguageID_NEx | 3190 | Para_EngDat_LanguageID_NEx |  | 17284
[8 empty] | 17285 | Para_EngDat_ModBusSlaveIDLink1 | Para_EngDat_ModBusSlaveIDLink1 | 3191 | Para_EngDat_ModBusSlaveIDLink1 |  | 17285
[8 empty] | 17286 | Para_EngDat_ModBusSlaveIDLink2 | Para_EngDat_ModBusSlaveIDLink2 | 3192 | Para_EngDat_ModBusSlaveIDLink2 |  | 17286
[8 empty] | 17287 | Para_EngDat_ModInertia | Para_EngDat_ModInertia | 3193 | Para_EngDat_ModInertia |  | 17287
[8 empty] | 17288 | Para_EngDat_NumbGasmixer | Para_EngDat_NumbGasmixer | 3194 | Para_EngDat_NumbGasmixer |  | 17288
[8 empty] | 17289 | Para_EngDat_NumbGasTrain | Para_EngDat_NumbGasTrain | 3195 | Para_EngDat_NumbGasTrain |  | 17289
[8 empty] | 17290 | Para_EngDat_NumbGasTyp | Para_EngDat_NumbGasTyp | 3196 | Para_EngDat_NumbGasTyp |  | 17290
[8 empty] | 17291 | Para_EngDat_NumbTecjet | Para_EngDat_NumbTecjet | 3197 | Para_EngDat_NumbTecjet |  | 17291
[8 empty] | 17292 | Para_EngDat_NumbTurboBypass | Para_EngDat_NumbTurboBypass | 3198 | Para_EngDat_NumbTurboBypass |  | 17292
[8 empty] | 19474 | Para_EngDat_Tempc_NEx | Para_EngDat_Tempc_NEx | 3199 | Para_EngDat_Tempc_NEx |  | 19474
[8 empty] | 19475 | Para_EngDat_Tempt_NEx | Para_EngDat_Tempt_NEx | 3200 | Para_EngDat_Tempt_NEx |  | 19475
[8 empty] | 19476 | Para_EngDat_Tempu_NEx | Para_EngDat_Tempu_NEx | 3201 | Para_EngDat_Tempu_NEx |  | 19476
[8 empty] | 17293 | Para_EngDat_TurboBypass4_20mA | Para_EngDat_TurboBypass4_20mA | 3202 | Para_EngDat_TurboBypass4_20mA |  | 17293
[8 empty] | 17294 | Para_EngDat_VersRPS_NEx | Para_EngDat_VersRPS_NEx | 3203 | Para_EngDat_VersRPS_NEx |  | 17294
[8 empty] | 17295 | Para_EngDat_VersSPS_NEx | Para_EngDat_VersSPS_NEx | 3204 | Para_EngDat_VersSPS_NEx | version | 17295
[8 empty] | 17296 | Para_EngDat_VersVIS_NEx | Para_EngDat_VersVIS_NEx | 3205 | Para_EngDat_VersVIS_NEx |  | 17296
[8 empty] | 17297 | Para_EngDat_VisuUpdateVers_NEx | Para_EngDat_VisuUpdateVers_NEx | 3206 | Para_EngDat_VisuUpdateVers_NEx |  | 17297
[8 empty] | 10000588 | Para_Engine_ChargeTempCtr_DComp | Para_Engine_ChargeTempCtr_DComp | 3207 | Para_Engine_ChargeTempCtr_DComp |  | 10000588
[8 empty] | 10000591 | Para_Engine_ChargeTempCtr_deadband | Para_Engine_ChargeTempCtr_deadband | 3208 | Para_Engine_ChargeTempCtr_deadband |  | 10000591
[8 empty] | 10000597 | Para_Engine_ChargeTempCtr_dW_down | Para_Engine_ChargeTempCtr_dW_down | 3209 | Para_Engine_ChargeTempCtr_dW_down |  | 10000597
[8 empty] | 10000599 | Para_Engine_ChargeTempCtr_dW_up | Para_Engine_ChargeTempCtr_dW_up | 3210 | Para_Engine_ChargeTempCtr_dW_up |  | 10000599
[8 empty] | 10000604 | Para_Engine_ChargeTempCtr_dY_max | Para_Engine_ChargeTempCtr_dY_max | 3211 | Para_Engine_ChargeTempCtr_dY_max |  | 10000604
[8 empty] | 10000592 | Para_Engine_ChargeTempCtr_IComp | Para_Engine_ChargeTempCtr_IComp | 3212 | Para_Engine_ChargeTempCtr_IComp |  | 10000592
[8 empty] | 10000818 | Para_Engine_ChargeTempCtr_Kp_manualAdjust | Para_Engine_ChargeTempCtr_Kp_manualAdjust | 3213 | Para_Engine_ChargeTempCtr_Kp_manualAdjust |  | 10000818
[8 empty] | 10000594 | Para_Engine_ChargeTempCtr_nvert | Para_Engine_ChargeTempCtr_nvert | 3214 | Para_Engine_ChargeTempCtr_nvert |  | 10000594
[8 empty] | 10000598 | Para_Engine_ChargeTempCtr_PComp | Para_Engine_ChargeTempCtr_PComp | 3215 | Para_Engine_ChargeTempCtr_PComp |  | 10000598
[8 empty] | 10008345 | Para_Engine_ChargeTempCtr_Pos_ChC_Valve_ScalMax | Para_Engine_ChargeTempCtr_Pos_ChC_Valve_ScalMax | 3216 | Para_Engine_ChargeTempCtr_Pos_ChC_Valve_ScalMax |  | 10008345
[8 empty] | 10008346 | Para_Engine_ChargeTempCtr_Pos_ChC_Valve_ScalMin | Para_Engine_ChargeTempCtr_Pos_ChC_Valve_ScalMin | 3217 | Para_Engine_ChargeTempCtr_Pos_ChC_Valve_ScalMin |  | 10008346
[8 empty] | 10008340 | Para_Engine_ChargeTempCtr_Pos_ChCValve | Para_Engine_ChargeTempCtr_Pos_ChCValve | 3218 | Para_Engine_ChargeTempCtr_Pos_ChCValve |  | 10008340
[8 empty] | 10000826 | Para_Engine_ChargeTempCtr_t_min_pulse_down | Para_Engine_ChargeTempCtr_t_min_pulse_down | 3219 | Para_Engine_ChargeTempCtr_t_min_pulse_down |  | 10000826
[8 empty] | 10000822 | Para_Engine_ChargeTempCtr_t_min_pulse_up | Para_Engine_ChargeTempCtr_t_min_pulse_up | 3220 | Para_Engine_ChargeTempCtr_t_min_pulse_up |  | 10000822
[8 empty] | 10000823 | Para_Engine_ChargeTempCtr_t_period_down | Para_Engine_ChargeTempCtr_t_period_down | 3221 | Para_Engine_ChargeTempCtr_t_period_down |  | 10000823
[8 empty] | 10000825 | Para_Engine_ChargeTempCtr_t_period_up | Para_Engine_ChargeTempCtr_t_period_up | 3222 | Para_Engine_ChargeTempCtr_t_period_up |  | 10000825
[8 empty] | 10000827 | Para_Engine_ChargeTempCtr_Tn_manualAdjust | Para_Engine_ChargeTempCtr_Tn_manualAdjust | 3223 | Para_Engine_ChargeTempCtr_Tn_manualAdjust |  | 10000827
[8 empty] | 10000824 | Para_Engine_ChargeTempCtr_Tv_manualAdjust | Para_Engine_ChargeTempCtr_Tv_manualAdjust | 3224 | Para_Engine_ChargeTempCtr_Tv_manualAdjust |  | 10000824
[8 empty] | 10000596 | Para_Engine_ChargeTempCtr_WMax | Para_Engine_ChargeTempCtr_WMax | 3225 | Para_Engine_ChargeTempCtr_WMax |  | 10000596
[8 empty] | 10000595 | Para_Engine_ChargeTempCtr_WMin | Para_Engine_ChargeTempCtr_WMin | 3226 | Para_Engine_ChargeTempCtr_WMin |  | 10000595
[8 empty] | 10000602 | Para_Engine_ChargeTempCtr_Y_block | Para_Engine_ChargeTempCtr_Y_block | 3227 | Para_Engine_ChargeTempCtr_Y_block |  | 10000602
[8 empty] | 10000600 | Para_Engine_ChargeTempCtr_YMax | Para_Engine_ChargeTempCtr_YMax | 3228 | Para_Engine_ChargeTempCtr_YMax |  | 10000600
[8 empty] | 10000601 | Para_Engine_ChargeTempCtr_YMin | Para_Engine_ChargeTempCtr_YMin | 3229 | Para_Engine_ChargeTempCtr_YMin |  | 10000601
[8 empty] | 10000279 | Para_Engine_Charging_AirFilterDiffPress_DPr_AirFilt_Exist | Para_Engine_Charging_AirFilterDiffPress_DPr_AirFilt_Exist | 3230 | Para_Engine_Charging_AirFilterDiffPress_DPr_AirFilt_Exist |  | 10000279
[8 empty] | 10008589 | Para_Engine_Charging_AirFilterDiffPress_DPr_AirFilt_Hi_incr | Para_Engine_Charging_AirFilterDiffPress_DPr_AirFilt_Hi_incr | 3231 | Para_Engine_Charging_AirFilterDiffPress_DPr_AirFilt_Hi_incr |  | 10008589
[8 empty] | 10008588 | Para_Engine_Charging_AirFilterDiffPress_DPr_AirFilt_Lo | Para_Engine_Charging_AirFilterDiffPress_DPr_AirFilt_Lo | 3232 | Para_Engine_Charging_AirFilterDiffPress_DPr_AirFilt_Lo |  | 10008588
[8 empty] | 10003061 | Para_Engine_Charging_Pos_CBV_Ref_WG | Para_Engine_Charging_Pos_CBV_Ref_WG | 3233 | Para_Engine_Charging_Pos_CBV_Ref_WG |  | 10003061
[8 empty] | 10008584 | Para_Engine_Charging_Pressure_DPr_Ch_FA_Hi | Para_Engine_Charging_Pressure_DPr_Ch_FA_Hi | 3234 | Para_Engine_Charging_Pressure_DPr_Ch_FA_Hi |  | 10008584
[8 empty] | 10008585 | Para_Engine_Charging_Pressure_DPr_Ch_HPCooler_Hi | Para_Engine_Charging_Pressure_DPr_Ch_HPCooler_Hi | 3235 | Para_Engine_Charging_Pressure_DPr_Ch_HPCooler_Hi |  | 10008585
[8 empty] | 10008579 | Para_Engine_Charging_Pressure_DPr_Ch_LPCooler_Hi | Para_Engine_Charging_Pressure_DPr_Ch_LPCooler_Hi | 3236 | Para_Engine_Charging_Pressure_DPr_Ch_LPCooler_Hi |  | 10008579
[8 empty] | 10008582 | Para_Engine_Charging_Pressure_Pr_Ch_P1LP_A_Exist | Para_Engine_Charging_Pressure_Pr_Ch_P1LP_A_Exist | 3237 | Para_Engine_Charging_Pressure_Pr_Ch_P1LP_A_Exist |  | 10008582
[8 empty] | 10008577 | Para_Engine_Charging_Pressure_Pr_Ch_P1LP_B_Exist | Para_Engine_Charging_Pressure_Pr_Ch_P1LP_B_Exist | 3238 | Para_Engine_Charging_Pressure_Pr_Ch_P1LP_B_Exist |  | 10008577
[8 empty] | 10008583 | Para_Engine_Charging_Pressure_Pr_Ch_P1LPScalMax | Para_Engine_Charging_Pressure_Pr_Ch_P1LPScalMax | 3239 | Para_Engine_Charging_Pressure_Pr_Ch_P1LPScalMax |  | 10008583
[8 empty] | 10008581 | Para_Engine_Charging_Pressure_Pr_Ch_P1LPScalMin | Para_Engine_Charging_Pressure_Pr_Ch_P1LPScalMin | 3240 | Para_Engine_Charging_Pressure_Pr_Ch_P1LPScalMin |  | 10008581
[8 empty] | 10008558 | Para_Engine_Charging_Pressure_Pr_Ch_P2bFA_Exist | Para_Engine_Charging_Pressure_Pr_Ch_P2bFA_Exist | 3241 | Para_Engine_Charging_Pressure_Pr_Ch_P2bFA_Exist |  | 10008558
[8 empty] | 10008561 | Para_Engine_Charging_Pressure_Pr_Ch_P2bFAScalMax | Para_Engine_Charging_Pressure_Pr_Ch_P2bFAScalMax | 3242 | Para_Engine_Charging_Pressure_Pr_Ch_P2bFAScalMax |  | 10008561
[8 empty] | 10008562 | Para_Engine_Charging_Pressure_Pr_Ch_P2bFAScalMin | Para_Engine_Charging_Pressure_Pr_Ch_P2bFAScalMin | 3243 | Para_Engine_Charging_Pressure_Pr_Ch_P2bFAScalMin |  | 10008562
[8 empty] | 10008706 | Para_Engine_Charging_Pressure_Pr_Ch_P2HP_A_Exist | Para_Engine_Charging_Pressure_Pr_Ch_P2HP_A_Exist | 3244 | Para_Engine_Charging_Pressure_Pr_Ch_P2HP_A_Exist |  | 10008706
[8 empty] | 10008707 | Para_Engine_Charging_Pressure_Pr_Ch_P2HP_B_Exist | Para_Engine_Charging_Pressure_Pr_Ch_P2HP_B_Exist | 3245 | Para_Engine_Charging_Pressure_Pr_Ch_P2HP_B_Exist |  | 10008707
[8 empty] | 10008574 | Para_Engine_Charging_Pressure_Pr_Ch_P2HP_Exist | Para_Engine_Charging_Pressure_Pr_Ch_P2HP_Exist | 3246 | Para_Engine_Charging_Pressure_Pr_Ch_P2HP_Exist |  | 10008574
[8 empty] | 10008572 | Para_Engine_Charging_Pressure_Pr_Ch_P2HPScalMax | Para_Engine_Charging_Pressure_Pr_Ch_P2HPScalMax | 3247 | Para_Engine_Charging_Pressure_Pr_Ch_P2HPScalMax |  | 10008572
[8 empty] | 10008575 | Para_Engine_Charging_Pressure_Pr_Ch_P2HPScalMin | Para_Engine_Charging_Pressure_Pr_Ch_P2HPScalMin | 3248 | Para_Engine_Charging_Pressure_Pr_Ch_P2HPScalMin |  | 10008575
[8 empty] | 10008711 | Para_Engine_Charging_Pressure_Pr_Ch_P2LP_A_Exist | Para_Engine_Charging_Pressure_Pr_Ch_P2LP_A_Exist | 3249 | Para_Engine_Charging_Pressure_Pr_Ch_P2LP_A_Exist |  | 10008711
[8 empty] | 10008709 | Para_Engine_Charging_Pressure_Pr_Ch_P2LP_B_Exist | Para_Engine_Charging_Pressure_Pr_Ch_P2LP_B_Exist | 3250 | Para_Engine_Charging_Pressure_Pr_Ch_P2LP_B_Exist |  | 10008709
[8 empty] | 10008576 | Para_Engine_Charging_Pressure_Pr_Ch_P2LP_Exist | Para_Engine_Charging_Pressure_Pr_Ch_P2LP_Exist | 3251 | Para_Engine_Charging_Pressure_Pr_Ch_P2LP_Exist |  | 10008576
[8 empty] | 10008580 | Para_Engine_Charging_Pressure_Pr_Ch_P2LPScalMax | Para_Engine_Charging_Pressure_Pr_Ch_P2LPScalMax | 3252 | Para_Engine_Charging_Pressure_Pr_Ch_P2LPScalMax |  | 10008580
[8 empty] | 10008578 | Para_Engine_Charging_Pressure_Pr_Ch_P2LPScalMin | Para_Engine_Charging_Pressure_Pr_Ch_P2LPScalMin | 3253 | Para_Engine_Charging_Pressure_Pr_Ch_P2LPScalMin |  | 10008578
[8 empty] | 10008710 | Para_Engine_Charging_Temp_T_Ch_T1LP_A_Exist | Para_Engine_Charging_Temp_T_Ch_T1LP_A_Exist | 3254 | Para_Engine_Charging_Temp_T_Ch_T1LP_A_Exist |  | 10008710
[8 empty] | 10008712 | Para_Engine_Charging_Temp_T_Ch_T1LP_B_Exist | Para_Engine_Charging_Temp_T_Ch_T1LP_B_Exist | 3255 | Para_Engine_Charging_Temp_T_Ch_T1LP_B_Exist |  | 10008712
[8 empty] | 10008708 | Para_Engine_Charging_Temp_T_Ch_T1LP_Exist | Para_Engine_Charging_Temp_T_Ch_T1LP_Exist | 3256 | Para_Engine_Charging_Temp_T_Ch_T1LP_Exist |  | 10008708
[8 empty] | 10008713 | Para_Engine_Charging_Temp_T_Ch_T1LP_Hi | Para_Engine_Charging_Temp_T_Ch_T1LP_Hi | 3257 | Para_Engine_Charging_Temp_T_Ch_T1LP_Hi |  | 10008713
[8 empty] | 10008530 | Para_Engine_Charging_tiWG_SS_Del | Para_Engine_Charging_tiWG_SS_Del | 3258 | Para_Engine_Charging_tiWG_SS_Del |  | 10008530
[8 empty] | 10008529 | Para_Engine_Charging_WG_Check_Ena | Para_Engine_Charging_WG_Check_Ena | 3259 | Para_Engine_Charging_WG_Check_Ena |  | 10008529
[8 empty] | 10003058 | Para_Engine_Charging_WG_Man | Para_Engine_Charging_WG_Man | 3260 | Para_Engine_Charging_WG_Man |  | 10003058
[8 empty] | 10001037 | Para_Engine_Coupling_Comm1_Baud | Para_Engine_Coupling_Comm1_Baud | 3261 | Para_Engine_Coupling_Comm1_Baud |  | 10001037
[8 empty] | 10001034 | Para_Engine_Coupling_Comm1_Parity | Para_Engine_Coupling_Comm1_Parity | 3262 | Para_Engine_Coupling_Comm1_Parity |  | 10001034
[8 empty] | 10001280 | Para_Engine_Coupling_Comm1_PB_SlaveID1 | Para_Engine_Coupling_Comm1_PB_SlaveID1 | 3263 | Para_Engine_Coupling_Comm1_PB_SlaveID1 |  | 10001280
[8 empty] | 10001290 | Para_Engine_Coupling_Comm1_PB_SlaveID2 | Para_Engine_Coupling_Comm1_PB_SlaveID2 | 3264 | Para_Engine_Coupling_Comm1_PB_SlaveID2 |  | 10001290
[8 empty] | 10001302 | Para_Engine_Coupling_Comm1_PN_SlaveID1 | Para_Engine_Coupling_Comm1_PN_SlaveID1 | 3265 | Para_Engine_Coupling_Comm1_PN_SlaveID1 |  | 10001302
[8 empty] | 10001041 | Para_Engine_Coupling_Comm1_Stopbit | Para_Engine_Coupling_Comm1_Stopbit | 3266 | Para_Engine_Coupling_Comm1_Stopbit |  | 10001041
[8 empty] | 10001035 | Para_Engine_Coupling_Comm2_Baud | Para_Engine_Coupling_Comm2_Baud | 3267 | Para_Engine_Coupling_Comm2_Baud |  | 10001035
[8 empty] | 10001039 | Para_Engine_Coupling_Comm2_Parity | Para_Engine_Coupling_Comm2_Parity | 3268 | Para_Engine_Coupling_Comm2_Parity |  | 10001039
[8 empty] | 10001289 | Para_Engine_Coupling_Comm2_PB_SlaveID1 | Para_Engine_Coupling_Comm2_PB_SlaveID1 | 3269 | Para_Engine_Coupling_Comm2_PB_SlaveID1 |  | 10001289
[8 empty] | 10001291 | Para_Engine_Coupling_Comm2_PB_SlaveID2 | Para_Engine_Coupling_Comm2_PB_SlaveID2 | 3270 | Para_Engine_Coupling_Comm2_PB_SlaveID2 |  | 10001291
[8 empty] | 10001331 | Para_Engine_Coupling_Comm2_PN_SlaveID1 | Para_Engine_Coupling_Comm2_PN_SlaveID1 | 3271 | Para_Engine_Coupling_Comm2_PN_SlaveID1 |  | 10001331
[8 empty] | 10001040 | Para_Engine_Coupling_Comm2_Stopbit | Para_Engine_Coupling_Comm2_Stopbit | 3272 | Para_Engine_Coupling_Comm2_Stopbit |  | 10001040
[8 empty] | 10000130 | Para_Engine_Coupling_Comm_IPaddr_first_TCP | Para_Engine_Coupling_Comm_IPaddr_first_TCP | 3273 | Para_Engine_Coupling_Comm_IPaddr_first_TCP |  | 10000130
[8 empty] | 10000489 | Para_Engine_Coupling_Comm_IPaddr_fourth_TCP | Para_Engine_Coupling_Comm_IPaddr_fourth_TCP | 3274 | Para_Engine_Coupling_Comm_IPaddr_fourth_TCP |  | 10000489
[8 empty] | 10000134 | Para_Engine_Coupling_Comm_IPaddr_second_TCP | Para_Engine_Coupling_Comm_IPaddr_second_TCP | 3275 | Para_Engine_Coupling_Comm_IPaddr_second_TCP |  | 10000134
[8 empty] | 10000133 | Para_Engine_Coupling_Comm_IPaddr_third_TCP | Para_Engine_Coupling_Comm_IPaddr_third_TCP | 3276 | Para_Engine_Coupling_Comm_IPaddr_third_TCP |  | 10000133
[8 empty] | 10001076 | Para_Engine_Coupling_Comm_PortID_TCP | Para_Engine_Coupling_Comm_PortID_TCP | 3277 | Para_Engine_Coupling_Comm_PortID_TCP |  | 10001076
[8 empty] | 10001072 | Para_Engine_Coupling_Comm_SlaveID_TCP | Para_Engine_Coupling_Comm_SlaveID_TCP | 3278 | Para_Engine_Coupling_Comm_SlaveID_TCP |  | 10001072
[8 empty] | 10001282 | Para_Engine_Coupling_Comm_SubMask_first_TCP | Para_Engine_Coupling_Comm_SubMask_first_TCP | 3279 | Para_Engine_Coupling_Comm_SubMask_first_TCP |  | 10001282
[8 empty] | 10001285 | Para_Engine_Coupling_Comm_SubMask_fourth_TCP | Para_Engine_Coupling_Comm_SubMask_fourth_TCP | 3280 | Para_Engine_Coupling_Comm_SubMask_fourth_TCP |  | 10001285
[8 empty] | 10001281 | Para_Engine_Coupling_Comm_SubMask_second_TCP | Para_Engine_Coupling_Comm_SubMask_second_TCP | 3281 | Para_Engine_Coupling_Comm_SubMask_second_TCP |  | 10001281
[8 empty] | 10001287 | Para_Engine_Coupling_Comm_SubMask_third_TCP | Para_Engine_Coupling_Comm_SubMask_third_TCP | 3282 | Para_Engine_Coupling_Comm_SubMask_third_TCP |  | 10001287
[8 empty] | 10000562 | Para_Engine_Coupling_Idx_Comm1_Interface | Para_Engine_Coupling_Idx_Comm1_Interface | 3283 | Para_Engine_Coupling_Idx_Comm1_Interface |  | 10000562
[8 empty] | 10000559 | Para_Engine_Coupling_Idx_Comm1_type | Para_Engine_Coupling_Idx_Comm1_type | 3284 | Para_Engine_Coupling_Idx_Comm1_type |  | 10000559
[8 empty] | 10000561 | Para_Engine_Coupling_Idx_Comm2_Interface | Para_Engine_Coupling_Idx_Comm2_Interface | 3285 | Para_Engine_Coupling_Idx_Comm2_Interface |  | 10000561
[8 empty] | 10000566 | Para_Engine_Coupling_Idx_Comm2_type | Para_Engine_Coupling_Idx_Comm2_type | 3286 | Para_Engine_Coupling_Idx_Comm2_type |  | 10000566
[8 empty] | 10008195 | Para_Engine_Coupling_OPC_Rcv_Ena | Para_Engine_Coupling_OPC_Rcv_Ena | 3287 | Para_Engine_Coupling_OPC_Rcv_Ena |  | 10008195
[8 empty] | 10000457 | Para_Engine_EngDat__IgnIC_900Active | Para_Engine_EngDat__IgnIC_900Active | 3288 | Para_Engine_EngDat__IgnIC_900Active |  | 10000457
[8 empty] | 10000221 | Para_Engine_EngDat_AvailabilityTrackingOn | Para_Engine_EngDat_AvailabilityTrackingOn | 3289 | Para_Engine_EngDat_AvailabilityTrackingOn |  | 10000221
[8 empty] | 10000240 | Para_Engine_EngDat_Country | Para_Engine_EngDat_Country | 3290 | Para_Engine_EngDat_Country |  | 10000240
[8 empty] | 10008969 | Para_Engine_EngDat_IdleFrictionMon | Para_Engine_EngDat_IdleFrictionMon | 3291 | Para_Engine_EngDat_IdleFrictionMon |  | 10008969
[8 empty] | 10000460 | Para_Engine_EngDat_IgnMon_Active | Para_Engine_EngDat_IgnMon_Active | 3292 | Para_Engine_EngDat_IgnMon_Active |  | 10000460
[8 empty] | 10000458 | Para_Engine_EngDat_KLS98_Active | Para_Engine_EngDat_KLS98_Active | 3293 | Para_Engine_EngDat_KLS98_Active |  | 10000458
[8 empty] | 10000471 | Para_Engine_EngDat_SA_Active | Para_Engine_EngDat_SA_Active | 3294 | Para_Engine_EngDat_SA_Active |  | 10000471
[8 empty] | 10001305 | Para_Engine_EngDat_SDT_Avg_LoLo | Para_Engine_EngDat_SDT_Avg_LoLo | 3295 | Para_Engine_EngDat_SDT_Avg_LoLo |  | 10001305
[8 empty] | 10008454 | Para_Engine_Island_Greenhouse_Num_Eng_LSL | Para_Engine_Island_Greenhouse_Num_Eng_LSL | 3296 | Para_Engine_Island_Greenhouse_Num_Eng_LSL |  | 10008454
[8 empty] | 10008453 | Para_Engine_Island_Greenhouse_P_drift_GH_Ena | Para_Engine_Island_Greenhouse_P_drift_GH_Ena | 3297 | Para_Engine_Island_Greenhouse_P_drift_GH_Ena |  | 10008453
[8 empty] | 10008455 | Para_Engine_Island_Greenhouse_P_Drift_Rel_Norm | Para_Engine_Island_Greenhouse_P_Drift_Rel_Norm | 3298 | Para_Engine_Island_Greenhouse_P_Drift_Rel_Norm |  | 10008455
[8 empty] | 10008450 | Para_Engine_Island_Greenhouse_P_max_GH_Ena | Para_Engine_Island_Greenhouse_P_max_GH_Ena | 3299 | Para_Engine_Island_Greenhouse_P_max_GH_Ena |  | 10008450
[8 empty] | 10008199 | Para_Engine_Island_Kp_P_Rot_Lam | Para_Engine_Island_Kp_P_Rot_Lam | 3300 | Para_Engine_Island_Kp_P_Rot_Lam |  | 10008199
[8 empty] | 10000569 | Para_Engine_Island_Limit_P_LS_HyLo | Para_Engine_Island_Limit_P_LS_HyLo | 3301 | Para_Engine_Island_Limit_P_LS_HyLo |  | 10000569
[8 empty] | 10000135 | Para_Engine_Island_LoadSh_LSL_Enable | Para_Engine_Island_LoadSh_LSL_Enable | 3302 | Para_Engine_Island_LoadSh_LSL_Enable |  | 10000135
[8 empty] | 10008194 | Para_Engine_Island_P_el_LockTV_Norm | Para_Engine_Island_P_el_LockTV_Norm | 3303 | Para_Engine_Island_P_el_LockTV_Norm |  | 10008194
[8 empty] | 10008197 | Para_Engine_Island_P_el_ReleaseTV_Norm | Para_Engine_Island_P_el_ReleaseTV_Norm | 3304 | Para_Engine_Island_P_el_ReleaseTV_Norm |  | 10008197
[8 empty] | 10008203 | Para_Engine_Island_P_LoadReject_Active | Para_Engine_Island_P_LoadReject_Active | 3305 | Para_Engine_Island_P_LoadReject_Active |  | 10008203
[8 empty] | 10008201 | Para_Engine_Island_P_Rot_Norm_Lam_Trig | Para_Engine_Island_P_Rot_Norm_Lam_Trig | 3306 | Para_Engine_Island_P_Rot_Norm_Lam_Trig |  | 10008201
[8 empty] | 10008200 | Para_Engine_Island_Pr_CBV_Lock | Para_Engine_Island_Pr_CBV_Lock | 3307 | Para_Engine_Island_Pr_CBV_Lock |  | 10008200
[8 empty] | 10008198 | Para_Engine_Island_Pr_CBV_Release | Para_Engine_Island_Pr_CBV_Release | 3308 | Para_Engine_Island_Pr_CBV_Release |  | 10008198
[8 empty] | 10002764 | Para_Engine_Island_Ramp_P_Island_Split_DecGrad_Norm1 | Para_Engine_Island_Ramp_P_Island_Split_DecGrad_Norm1 | 3309 | Para_Engine_Island_Ramp_P_Island_Split_DecGrad_Norm1 |  | 10002764
[8 empty] | 10000570 | Para_Engine_Island_Ramp_P_Island_Split_IncGrad_Norm1 | Para_Engine_Island_Ramp_P_Island_Split_IncGrad_Norm1 | 3310 | Para_Engine_Island_Ramp_P_Island_Split_IncGrad_Norm1 |  | 10000570
[8 empty] | 10000572 | Para_Engine_Leanox_Comp_ZZPKorr | Para_Engine_Leanox_Comp_ZZPKorr | 3311 | Para_Engine_Leanox_Comp_ZZPKorr |  | 10000572
[8 empty] | 10002769 | Para_Engine_Leanox_Gas1_Pr_Leanox_Offset_Isand1 | Para_Engine_Leanox_Gas1_Pr_Leanox_Offset_Isand1 | 3312 | Para_Engine_Leanox_Gas1_Pr_Leanox_Offset_Isand1 |  | 10002769
[8 empty] | 10000590 | Para_Engine_Leanox_Gas1_Pr_P2_Dev_Lim1 | Para_Engine_Leanox_Gas1_Pr_P2_Dev_Lim1 | 3313 | Para_Engine_Leanox_Gas1_Pr_P2_Dev_Lim1 |  | 10000590
[8 empty] | 10003118 | Para_Engine_Leanox_Gas2_Pr_Leanox_Offset_Isand2 | Para_Engine_Leanox_Gas2_Pr_Leanox_Offset_Isand2 | 3314 | Para_Engine_Leanox_Gas2_Pr_Leanox_Offset_Isand2 |  | 10003118
[8 empty] | 10000593 | Para_Engine_Leanox_Gas2_Pr_P2_Dev_Lim2 | Para_Engine_Leanox_Gas2_Pr_P2_Dev_Lim2 | 3315 | Para_Engine_Leanox_Gas2_Pr_P2_Dev_Lim2 |  | 10000593
[8 empty] | 10003117 | Para_Engine_Leanox_Gas3_Pr_Leanox_Offset_Isand3 | Para_Engine_Leanox_Gas3_Pr_Leanox_Offset_Isand3 | 3316 | Para_Engine_Leanox_Gas3_Pr_Leanox_Offset_Isand3 |  | 10003117
[8 empty] | 10000606 | Para_Engine_Leanox_Gas3_Pr_P2_Dev_Lim3 | Para_Engine_Leanox_Gas3_Pr_P2_Dev_Lim3 | 3317 | Para_Engine_Leanox_Gas3_Pr_P2_Dev_Lim3 |  | 10000606
[8 empty] | 10003119 | Para_Engine_Leanox_Gas4_Pr_Leanox_Offset_Isand4 | Para_Engine_Leanox_Gas4_Pr_Leanox_Offset_Isand4 | 3318 | Para_Engine_Leanox_Gas4_Pr_Leanox_Offset_Isand4 |  | 10003119
[8 empty] | 10000603 | Para_Engine_Leanox_Gas4_Pr_P2_Dev_Lim4 | Para_Engine_Leanox_Gas4_Pr_P2_Dev_Lim4 | 3319 | Para_Engine_Leanox_Gas4_Pr_P2_Dev_Lim4 |  | 10000603
[8 empty] | 10000079 | Para_Engine_Leanox_Gasmixer_Gas1_deadband | Para_Engine_Leanox_Gasmixer_Gas1_deadband | 3320 | Para_Engine_Leanox_Gasmixer_Gas1_deadband |  | 10000079
[8 empty] | 10001323 | Para_Engine_Leanox_Gasmixer_Gas1_I | Para_Engine_Leanox_Gasmixer_Gas1_I | 3321 | Para_Engine_Leanox_Gasmixer_Gas1_I |  | 10001323
[8 empty] | 10001314 | Para_Engine_Leanox_Gasmixer_Gas1_P | Para_Engine_Leanox_Gasmixer_Gas1_P | 3322 | Para_Engine_Leanox_Gasmixer_Gas1_P |  | 10001314
[8 empty] | 10001318 | Para_Engine_Leanox_Gasmixer_Gas1_umax | Para_Engine_Leanox_Gasmixer_Gas1_umax | 3323 | Para_Engine_Leanox_Gasmixer_Gas1_umax |  | 10001318
[8 empty] | 10001319 | Para_Engine_Leanox_Gasmixer_Gas1_umin | Para_Engine_Leanox_Gasmixer_Gas1_umin | 3324 | Para_Engine_Leanox_Gasmixer_Gas1_umin |  | 10001319
[8 empty] | 10000077 | Para_Engine_Leanox_Gasmixer_Gas2_deadband | Para_Engine_Leanox_Gasmixer_Gas2_deadband | 3325 | Para_Engine_Leanox_Gasmixer_Gas2_deadband |  | 10000077
[8 empty] | 10000075 | Para_Engine_Leanox_Gasmixer_Gas2_I | Para_Engine_Leanox_Gasmixer_Gas2_I | 3326 | Para_Engine_Leanox_Gasmixer_Gas2_I |  | 10000075
[8 empty] | 10000080 | Para_Engine_Leanox_Gasmixer_Gas2_P | Para_Engine_Leanox_Gasmixer_Gas2_P | 3327 | Para_Engine_Leanox_Gasmixer_Gas2_P |  | 10000080
[8 empty] | 10000078 | Para_Engine_Leanox_Gasmixer_Gas2_umax | Para_Engine_Leanox_Gasmixer_Gas2_umax | 3328 | Para_Engine_Leanox_Gasmixer_Gas2_umax |  | 10000078
[8 empty] | 10000081 | Para_Engine_Leanox_Gasmixer_Gas2_umin | Para_Engine_Leanox_Gasmixer_Gas2_umin | 3329 | Para_Engine_Leanox_Gasmixer_Gas2_umin |  | 10000081
[8 empty] | 10000082 | Para_Engine_Leanox_Gasmixer_Gas3_deadband | Para_Engine_Leanox_Gasmixer_Gas3_deadband | 3330 | Para_Engine_Leanox_Gasmixer_Gas3_deadband |  | 10000082
[8 empty] | 10000085 | Para_Engine_Leanox_Gasmixer_Gas3_I | Para_Engine_Leanox_Gasmixer_Gas3_I | 3331 | Para_Engine_Leanox_Gasmixer_Gas3_I |  | 10000085
[8 empty] | 10000083 | Para_Engine_Leanox_Gasmixer_Gas3_P | Para_Engine_Leanox_Gasmixer_Gas3_P | 3332 | Para_Engine_Leanox_Gasmixer_Gas3_P |  | 10000083
[8 empty] | 10000084 | Para_Engine_Leanox_Gasmixer_Gas3_umax | Para_Engine_Leanox_Gasmixer_Gas3_umax | 3333 | Para_Engine_Leanox_Gasmixer_Gas3_umax |  | 10000084
[8 empty] | 10000086 | Para_Engine_Leanox_Gasmixer_Gas3_umin | Para_Engine_Leanox_Gasmixer_Gas3_umin | 3334 | Para_Engine_Leanox_Gasmixer_Gas3_umin |  | 10000086
[8 empty] | 10000087 | Para_Engine_Leanox_Gasmixer_Gas4_deadband | Para_Engine_Leanox_Gasmixer_Gas4_deadband | 3335 | Para_Engine_Leanox_Gasmixer_Gas4_deadband |  | 10000087
[8 empty] | 10000088 | Para_Engine_Leanox_Gasmixer_Gas4_I | Para_Engine_Leanox_Gasmixer_Gas4_I | 3336 | Para_Engine_Leanox_Gasmixer_Gas4_I |  | 10000088
[8 empty] | 10000090 | Para_Engine_Leanox_Gasmixer_Gas4_P | Para_Engine_Leanox_Gasmixer_Gas4_P | 3337 | Para_Engine_Leanox_Gasmixer_Gas4_P |  | 10000090
[8 empty] | 10001320 | Para_Engine_Leanox_Gasmixer_Gas4_umax | Para_Engine_Leanox_Gasmixer_Gas4_umax | 3338 | Para_Engine_Leanox_Gasmixer_Gas4_umax |  | 10001320
[8 empty] | 10001322 | Para_Engine_Leanox_Gasmixer_Gas4_umin | Para_Engine_Leanox_Gasmixer_Gas4_umin | 3339 | Para_Engine_Leanox_Gasmixer_Gas4_umin |  | 10001322
[8 empty] | 10008887 | Para_Engine_Leanox_IdleLambdaCtr_Gas1_Pr_p2s_LLCtr1 | Para_Engine_Leanox_IdleLambdaCtr_Gas1_Pr_p2s_LLCtr1 | 3340 | Para_Engine_Leanox_IdleLambdaCtr_Gas1_Pr_p2s_LLCtr1 |  | 10008887
[8 empty] | 10008890 | Para_Engine_Leanox_IdleLambdaCtr_Gas2_Pr_p2s_LLCtr2 | Para_Engine_Leanox_IdleLambdaCtr_Gas2_Pr_p2s_LLCtr2 | 3341 | Para_Engine_Leanox_IdleLambdaCtr_Gas2_Pr_p2s_LLCtr2 |  | 10008890
[8 empty] | 10008888 | Para_Engine_Leanox_IdleLambdaCtr_Gas3_Pr_p2s_LLCtr3 | Para_Engine_Leanox_IdleLambdaCtr_Gas3_Pr_p2s_LLCtr3 | 3342 | Para_Engine_Leanox_IdleLambdaCtr_Gas3_Pr_p2s_LLCtr3 |  | 10008888
[8 empty] | 10008892 | Para_Engine_Leanox_IdleLambdaCtr_Gas4_Pr_p2s_LLCtr4 | Para_Engine_Leanox_IdleLambdaCtr_Gas4_Pr_p2s_LLCtr4 | 3343 | Para_Engine_Leanox_IdleLambdaCtr_Gas4_Pr_p2s_LLCtr4 |  | 10008892
[8 empty] | 10008936 | Para_Engine_Leanox_IdleLambdaCtr_Gasmixer_Ki_LeanoxC_GM | Para_Engine_Leanox_IdleLambdaCtr_Gasmixer_Ki_LeanoxC_GM | 3344 | Para_Engine_Leanox_IdleLambdaCtr_Gasmixer_Ki_LeanoxC_GM |  | 10008936
[8 empty] | 10008935 | Para_Engine_Leanox_IdleLambdaCtr_Gasmixer_Kp_LeanoxC_GM | Para_Engine_Leanox_IdleLambdaCtr_Gasmixer_Kp_LeanoxC_GM | 3345 | Para_Engine_Leanox_IdleLambdaCtr_Gasmixer_Kp_LeanoxC_GM |  | 10008935
[8 empty] | 10001325 | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Gas1_Lam_CR_Speed1 | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Gas1_Lam_CR_Speed1 | 3346 | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Gas1_Lam_CR_Speed1 |  | 10001325
[8 empty] | 10001324 | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Gas2_Lam_CR_Speed2 | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Gas2_Lam_CR_Speed2 | 3347 | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Gas2_Lam_CR_Speed2 |  | 10001324
[8 empty] | 10001330 | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Gas3_Lam_CR_Speed3 | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Gas3_Lam_CR_Speed3 | 3348 | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Gas3_Lam_CR_Speed3 |  | 10001330
[8 empty] | 10001332 | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Gas4_Lam_CR_Speed4 | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Gas4_Lam_CR_Speed4 | 3349 | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Gas4_Lam_CR_Speed4 |  | 10001332
[8 empty] | 10008932 | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Ki_LeanoxC_TJ | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Ki_LeanoxC_TJ | 3350 | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Ki_LeanoxC_TJ |  | 10008932
[8 empty] | 10008933 | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Kp_LeanoxC_TJ | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Kp_LeanoxC_TJ | 3351 | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Kp_LeanoxC_TJ |  | 10008933
[8 empty] | 10008889 | Para_Engine_Leanox_IdleLambdaCtr_LLCtr_ki | Para_Engine_Leanox_IdleLambdaCtr_LLCtr_ki | 3352 | Para_Engine_Leanox_IdleLambdaCtr_LLCtr_ki |  | 10008889
[8 empty] | 10008894 | Para_Engine_Leanox_IdleLambdaCtr_LLCtr_kp | Para_Engine_Leanox_IdleLambdaCtr_LLCtr_kp | 3353 | Para_Engine_Leanox_IdleLambdaCtr_LLCtr_kp |  | 10008894
[8 empty] | 10008891 | Para_Engine_Leanox_IdleLambdaCtr_LLLCtr_act | Para_Engine_Leanox_IdleLambdaCtr_LLLCtr_act | 3354 | Para_Engine_Leanox_IdleLambdaCtr_LLLCtr_act |  | 10008891
[8 empty] | 10008895 | Para_Engine_Leanox_IdleLambdaCtr_LLLCtr_delay_Trip | Para_Engine_Leanox_IdleLambdaCtr_LLLCtr_delay_Trip | 3355 | Para_Engine_Leanox_IdleLambdaCtr_LLLCtr_delay_Trip |  | 10008895
[8 empty] | 10008893 | Para_Engine_Leanox_IdleLambdaCtr_Pr_p2s_Win_sy_lfg | Para_Engine_Leanox_IdleLambdaCtr_Pr_p2s_Win_sy_lfg | 3356 | Para_Engine_Leanox_IdleLambdaCtr_Pr_p2s_Win_sy_lfg |  | 10008893
[8 empty] | 10002597 | Para_Engine_Leanox_LambdaFeedFwdCtr_Gas1_Lam_Start_Offs1 | Para_Engine_Leanox_LambdaFeedFwdCtr_Gas1_Lam_Start_Offs1 | 3357 | Para_Engine_Leanox_LambdaFeedFwdCtr_Gas1_Lam_Start_Offs1 |  | 10002597
[8 empty] | 10002600 | Para_Engine_Leanox_LambdaFeedFwdCtr_Gas2_Lam_Start_Offs2 | Para_Engine_Leanox_LambdaFeedFwdCtr_Gas2_Lam_Start_Offs2 | 3358 | Para_Engine_Leanox_LambdaFeedFwdCtr_Gas2_Lam_Start_Offs2 |  | 10002600
[8 empty] | 10002602 | Para_Engine_Leanox_LambdaFeedFwdCtr_Gas3_Lam_Start_Offs3 | Para_Engine_Leanox_LambdaFeedFwdCtr_Gas3_Lam_Start_Offs3 | 3359 | Para_Engine_Leanox_LambdaFeedFwdCtr_Gas3_Lam_Start_Offs3 |  | 10002602
[8 empty] | 10002606 | Para_Engine_Leanox_LambdaFeedFwdCtr_Gas4_Lam_Start_Offs4 | Para_Engine_Leanox_LambdaFeedFwdCtr_Gas4_Lam_Start_Offs4 | 3360 | Para_Engine_Leanox_LambdaFeedFwdCtr_Gas4_Lam_Start_Offs4 |  | 10002606
[8 empty] | 10008877 | Para_Engine_Leanox_LambdaFeedFwdCtr_N_LamOffs_x1 | Para_Engine_Leanox_LambdaFeedFwdCtr_N_LamOffs_x1 | 3361 | Para_Engine_Leanox_LambdaFeedFwdCtr_N_LamOffs_x1 |  | 10008877
[8 empty] | 10008880 | Para_Engine_Leanox_LambdaFeedFwdCtr_N_LamOffs_x2 | Para_Engine_Leanox_LambdaFeedFwdCtr_N_LamOffs_x2 | 3362 | Para_Engine_Leanox_LambdaFeedFwdCtr_N_LamOffs_x2 |  | 10008880
[8 empty] | 10000571 | Para_Engine_Leanox_LeanoxPRED | Para_Engine_Leanox_LeanoxPRED | 3363 | Para_Engine_Leanox_LeanoxPRED |  | 10000571
[8 empty] | 10000585 | Para_Engine_Leanox_LeanoxRamp | Para_Engine_Leanox_LeanoxRamp | 3364 | Para_Engine_Leanox_LeanoxRamp |  | 10000585
[8 empty] | 10002603 | Para_Engine_Leanox_Pr_P2s_Set_0kW | Para_Engine_Leanox_Pr_P2s_Set_0kW | 3365 | Para_Engine_Leanox_Pr_P2s_Set_0kW |  | 10002603
[8 empty] | 10008570 | Para_Engine_PFPDR_Adv_IP_Ena | Para_Engine_PFPDR_Adv_IP_Ena | 3366 | Para_Engine_PFPDR_Adv_IP_Ena |  | 10008570
[8 empty] | 10008565 | Para_Engine_PFPDR_Auto_Ena | Para_Engine_PFPDR_Auto_Ena | 3367 | Para_Engine_PFPDR_Auto_Ena |  | 10008565
[8 empty] | 10008568 | Para_Engine_PFPDR_BH_Auto | Para_Engine_PFPDR_BH_Auto | 3368 | Para_Engine_PFPDR_BH_Auto |  | 10008568
[8 empty] | 10008567 | Para_Engine_PFPDR_CA_IP_EGT | Para_Engine_PFPDR_CA_IP_EGT | 3369 | Para_Engine_PFPDR_CA_IP_EGT |  | 10008567
[8 empty] | 10008569 | Para_Engine_PFPDR_CA_Offs_Lim | Para_Engine_PFPDR_CA_Offs_Lim | 3370 | Para_Engine_PFPDR_CA_Offs_Lim |  | 10008569
[8 empty] | 10008571 | Para_Engine_PFPDR_Ena | Para_Engine_PFPDR_Ena | 3371 | Para_Engine_PFPDR_Ena |  | 10008571
[8 empty] | 10008566 | Para_Engine_PFPDR_Lam_Lim | Para_Engine_PFPDR_Lam_Lim | 3372 | Para_Engine_PFPDR_Lam_Lim |  | 10008566
[8 empty] | 10008573 | Para_Engine_PFPDR_tiSS_Del | Para_Engine_PFPDR_tiSS_Del | 3373 | Para_Engine_PFPDR_tiSS_Del |  | 10008573
[8 empty] | 10000103 | Para_Engine_Power_Ctr_CBV_N | Para_Engine_Power_Ctr_CBV_N | 3374 | Para_Engine_Power_Ctr_CBV_N |  | 10000103
[8 empty] | 10008924 | Para_Engine_Power_Ctr_GEN2_PowCtrl_Ki | Para_Engine_Power_Ctr_GEN2_PowCtrl_Ki | 3375 | Para_Engine_Power_Ctr_GEN2_PowCtrl_Ki |  | 10008924
[8 empty] | 10008923 | Para_Engine_Power_Ctr_GEN2_PowCtrl_Kp | Para_Engine_Power_Ctr_GEN2_PowCtrl_Kp | 3376 | Para_Engine_Power_Ctr_GEN2_PowCtrl_Kp |  | 10008923
[8 empty] | 10001327 | Para_Engine_Power_Ctr_Pr_P2s_CtrLim | Para_Engine_Power_Ctr_Pr_P2s_CtrLim | 3377 | Para_Engine_Power_Ctr_Pr_P2s_CtrLim |  | 10001327
[8 empty] | 10000099 | Para_Engine_Power_Ctr_TV_N | Para_Engine_Power_Ctr_TV_N | 3378 | Para_Engine_Power_Ctr_TV_N |  | 10000099
[8 empty] | 10008457 | Para_Engine_Power_ExtSet_P_Set5_ExtDI_Norm | Para_Engine_Power_ExtSet_P_Set5_ExtDI_Norm | 3379 | Para_Engine_Power_ExtSet_P_Set5_ExtDI_Norm |  | 10008457
[8 empty] | 10008921 | Para_Engine_Power_FastStart_CA_GEN2_fastSt | Para_Engine_Power_FastStart_CA_GEN2_fastSt | 3380 | Para_Engine_Power_FastStart_CA_GEN2_fastSt |  | 10008921
[8 empty] | 10008509 | Para_Engine_Power_FastStart_FastSpeedUp | Para_Engine_Power_FastStart_FastSpeedUp | 3381 | Para_Engine_Power_FastStart_FastSpeedUp |  | 10008509
[8 empty] | 10008510 | Para_Engine_Power_FastStart_FastSync | Para_Engine_Power_FastStart_FastSync | 3382 | Para_Engine_Power_FastStart_FastSync |  | 10008510
[8 empty] | 10008919 | Para_Engine_Power_FastStart_GEN2_preM_Act | Para_Engine_Power_FastStart_GEN2_preM_Act | 3383 | Para_Engine_Power_FastStart_GEN2_preM_Act |  | 10008919
[8 empty] | 10008506 | Para_Engine_Power_FastStart_LowTransNOx_Ena | Para_Engine_Power_FastStart_LowTransNOx_Ena | 3384 | Para_Engine_Power_FastStart_LowTransNOx_Ena |  | 10008506
[8 empty] | 10008532 | Para_Engine_Power_FastStart_P_Ramp_Norm1 | Para_Engine_Power_FastStart_P_Ramp_Norm1 | 3385 | Para_Engine_Power_FastStart_P_Ramp_Norm1 |  | 10008532
[8 empty] | 10008538 | Para_Engine_Power_FastStart_P_Ramp_Norm2 | Para_Engine_Power_FastStart_P_Ramp_Norm2 | 3386 | Para_Engine_Power_FastStart_P_Ramp_Norm2 |  | 10008538
[8 empty] | 10008536 | Para_Engine_Power_FastStart_P_Ramp_Norm3 | Para_Engine_Power_FastStart_P_Ramp_Norm3 | 3387 | Para_Engine_Power_FastStart_P_Ramp_Norm3 |  | 10008536
[8 empty] | 10008539 | Para_Engine_Power_FastStart_P_Ramp_Norm4 | Para_Engine_Power_FastStart_P_Ramp_Norm4 | 3388 | Para_Engine_Power_FastStart_P_Ramp_Norm4 |  | 10008539
[8 empty] | 10008920 | Para_Engine_Power_FastStart_PrR_GEN2_TV_level | Para_Engine_Power_FastStart_PrR_GEN2_TV_level | 3389 | Para_Engine_Power_FastStart_PrR_GEN2_TV_level |  | 10008920
[8 empty] | 10008922 | Para_Engine_Power_FastStart_PrR_GEN2_TV_level_Hy | Para_Engine_Power_FastStart_PrR_GEN2_TV_level_Hy | 3390 | Para_Engine_Power_FastStart_PrR_GEN2_TV_level_Hy |  | 10008922
[8 empty] | 10008531 | Para_Engine_Power_FastStart_ti_Desired1 | Para_Engine_Power_FastStart_ti_Desired1 | 3391 | Para_Engine_Power_FastStart_ti_Desired1 |  | 10008531
[8 empty] | 10008522 | Para_Engine_Power_FastStart_ti_Desired2 | Para_Engine_Power_FastStart_ti_Desired2 | 3392 | Para_Engine_Power_FastStart_ti_Desired2 |  | 10008522
[8 empty] | 10008518 | Para_Engine_Power_FastStart_ti_Desired3 | Para_Engine_Power_FastStart_ti_Desired3 | 3393 | Para_Engine_Power_FastStart_ti_Desired3 |  | 10008518
[8 empty] | 10008519 | Para_Engine_Power_FastStart_ti_Desired4 | Para_Engine_Power_FastStart_ti_Desired4 | 3394 | Para_Engine_Power_FastStart_ti_Desired4 |  | 10008519
[8 empty] | 10008403 | Para_Engine_Power_Limit_P_GhStep_Ena | Para_Engine_Power_Limit_P_GhStep_Ena | 3395 | Para_Engine_Power_Limit_P_GhStep_Ena |  | 10008403
[8 empty] | 10008405 | Para_Engine_Power_Limit_P_GhStep_Lim_Norm0 | Para_Engine_Power_Limit_P_GhStep_Lim_Norm0 | 3396 | Para_Engine_Power_Limit_P_GhStep_Lim_Norm0 |  | 10008405
[8 empty] | 10008406 | Para_Engine_Power_Limit_P_GhStep_Lim_Norm1 | Para_Engine_Power_Limit_P_GhStep_Lim_Norm1 | 3397 | Para_Engine_Power_Limit_P_GhStep_Lim_Norm1 |  | 10008406
[8 empty] | 10008407 | Para_Engine_Power_Limit_P_GhStep_Lim_Norm2 | Para_Engine_Power_Limit_P_GhStep_Lim_Norm2 | 3398 | Para_Engine_Power_Limit_P_GhStep_Lim_Norm2 |  | 10008407
[8 empty] | 10008409 | Para_Engine_Power_Limit_P_GhStep_Lim_Norm3 | Para_Engine_Power_Limit_P_GhStep_Lim_Norm3 | 3399 | Para_Engine_Power_Limit_P_GhStep_Lim_Norm3 |  | 10008409
[8 empty] | 10008408 | Para_Engine_Power_Limit_P_GhStep_Lim_Norm4 | Para_Engine_Power_Limit_P_GhStep_Lim_Norm4 | 3400 | Para_Engine_Power_Limit_P_GhStep_Lim_Norm4 |  | 10008408
[8 empty] | 10001409 | Para_Engine_Power_Limit_P_LimHiHi | Para_Engine_Power_Limit_P_LimHiHi | 3401 | Para_Engine_Power_Limit_P_LimHiHi |  | 10001409
[8 empty] | 10001394 | Para_Engine_Power_RedCrankCase_P_Red_CC | Para_Engine_Power_RedCrankCase_P_Red_CC | 3402 | Para_Engine_Power_RedCrankCase_P_Red_CC |  | 10001394
[8 empty] | 10008456 | Para_Engine_Power_RedExhaust_PID_EGT_I | Para_Engine_Power_RedExhaust_PID_EGT_I | 3403 | Para_Engine_Power_RedExhaust_PID_EGT_I |  | 10008456
[8 empty] | 10008389 | Para_Engine_Power_RedExhaust_PID_EGT_P | Para_Engine_Power_RedExhaust_PID_EGT_P | 3404 | Para_Engine_Power_RedExhaust_PID_EGT_P |  | 10008389
[8 empty] | 10008402 | Para_Engine_Power_RedGCBTemp_P_Red_TempMax_GenCB_Active | Para_Engine_Power_RedGCBTemp_P_Red_TempMax_GenCB_Active | 3405 | Para_Engine_Power_RedGCBTemp_P_Red_TempMax_GenCB_Active |  | 10008402
[8 empty] | 10008404 | Para_Engine_Power_RedGCBTemp_P_Red_TempMax_GenCB_Rate | Para_Engine_Power_RedGCBTemp_P_Red_TempMax_GenCB_Rate | 3406 | Para_Engine_Power_RedGCBTemp_P_Red_TempMax_GenCB_Rate |  | 10008404
[8 empty] | 10008401 | Para_Engine_Power_RedTransformer_P_Red_TransformerWarning_Rate | Para_Engine_Power_RedTransformer_P_Red_TransformerWarning_Rate | 3407 | Para_Engine_Power_RedTransformer_P_Red_TransformerWarning_Rate |  | 10008401
[8 empty] | 10008400 | Para_Engine_Power_RedTransformer_P_Red_TransformerWarning_Sel | Para_Engine_Power_RedTransformer_P_Red_TransformerWarning_Sel | 3408 | Para_Engine_Power_RedTransformer_P_Red_TransformerWarning_Sel |  | 10008400
[8 empty] | 10000700 | Para_Engine_Remote_RemoteReqActive | Para_Engine_Remote_RemoteReqActive | 3409 | Para_Engine_Remote_RemoteReqActive |  | 10000700
[8 empty] | 10000239 | Para_Engine_Remote_ResetRemActive | Para_Engine_Remote_ResetRemActive | 3410 | Para_Engine_Remote_ResetRemActive |  | 10000239
[8 empty] | 10000242 | Para_Engine_Remote_ResetRemRiskClass | Para_Engine_Remote_ResetRemRiskClass | 3411 | Para_Engine_Remote_ResetRemRiskClass |  | 10000242
[8 empty] | 10000695 | Para_Engine_SAFI_SA_Ign_Active | Para_Engine_SAFI_SA_Ign_Active | 3412 | Para_Engine_SAFI_SA_Ign_Active |  | 10000695
[8 empty] | 10000102 | Para_Engine_Speed_Ctr_CBV_IdleOp_D | Para_Engine_Speed_Ctr_CBV_IdleOp_D | 3413 | Para_Engine_Speed_Ctr_CBV_IdleOp_D |  | 10000102
[8 empty] | 10000095 | Para_Engine_Speed_Ctr_CBV_IdleOp_I | Para_Engine_Speed_Ctr_CBV_IdleOp_I | 3414 | Para_Engine_Speed_Ctr_CBV_IdleOp_I |  | 10000095
[8 empty] | 10000100 | Para_Engine_Speed_Ctr_CBV_IdleOp_N | Para_Engine_Speed_Ctr_CBV_IdleOp_N | 3415 | Para_Engine_Speed_Ctr_CBV_IdleOp_N |  | 10000100
[8 empty] | 10000097 | Para_Engine_Speed_Ctr_CBV_IdleOp_P | Para_Engine_Speed_Ctr_CBV_IdleOp_P | 3416 | Para_Engine_Speed_Ctr_CBV_IdleOp_P |  | 10000097
[8 empty] | 10000723 | Para_Engine_Speed_Ctr_CBV_IdleOp_umax | Para_Engine_Speed_Ctr_CBV_IdleOp_umax | 3417 | Para_Engine_Speed_Ctr_CBV_IdleOp_umax |  | 10000723
[8 empty] | 10001286 | Para_Engine_Speed_Ctr_CBV_IdleOp_umin | Para_Engine_Speed_Ctr_CBV_IdleOp_umin | 3418 | Para_Engine_Speed_Ctr_CBV_IdleOp_umin |  | 10001286
[8 empty] | 10000563 | Para_Engine_Speed_Ctr_CBV_IsolatedOp_D | Para_Engine_Speed_Ctr_CBV_IsolatedOp_D | 3419 | Para_Engine_Speed_Ctr_CBV_IsolatedOp_D |  | 10000563
[8 empty] | 10000564 | Para_Engine_Speed_Ctr_CBV_IsolatedOp_I | Para_Engine_Speed_Ctr_CBV_IsolatedOp_I | 3420 | Para_Engine_Speed_Ctr_CBV_IsolatedOp_I |  | 10000564
[8 empty] | 10000106 | Para_Engine_Speed_Ctr_CBV_IsolatedOp_N | Para_Engine_Speed_Ctr_CBV_IsolatedOp_N | 3421 | Para_Engine_Speed_Ctr_CBV_IsolatedOp_N |  | 10000106
[8 empty] | 10000565 | Para_Engine_Speed_Ctr_CBV_IsolatedOp_P | Para_Engine_Speed_Ctr_CBV_IsolatedOp_P | 3422 | Para_Engine_Speed_Ctr_CBV_IsolatedOp_P |  | 10000565
[8 empty] | 10001284 | Para_Engine_Speed_Ctr_CBV_IsolatedOp_umax | Para_Engine_Speed_Ctr_CBV_IsolatedOp_umax | 3423 | Para_Engine_Speed_Ctr_CBV_IsolatedOp_umax |  | 10001284
[8 empty] | 10001283 | Para_Engine_Speed_Ctr_CBV_IsolatedOp_umin | Para_Engine_Speed_Ctr_CBV_IsolatedOp_umin | 3424 | Para_Engine_Speed_Ctr_CBV_IsolatedOp_umin |  | 10001283
[8 empty] | 10001321 | Para_Engine_Speed_Ctr_TV_IdleOp_a | Para_Engine_Speed_Ctr_TV_IdleOp_a | 3425 | Para_Engine_Speed_Ctr_TV_IdleOp_a |  | 10001321
[8 empty] | 10000093 | Para_Engine_Speed_Ctr_TV_IdleOp_D | Para_Engine_Speed_Ctr_TV_IdleOp_D | 3426 | Para_Engine_Speed_Ctr_TV_IdleOp_D |  | 10000093
[8 empty] | 10000098 | Para_Engine_Speed_Ctr_TV_IdleOp_I | Para_Engine_Speed_Ctr_TV_IdleOp_I | 3427 | Para_Engine_Speed_Ctr_TV_IdleOp_I |  | 10000098
[8 empty] | 10000096 | Para_Engine_Speed_Ctr_TV_IdleOp_N | Para_Engine_Speed_Ctr_TV_IdleOp_N | 3428 | Para_Engine_Speed_Ctr_TV_IdleOp_N |  | 10000096
[8 empty] | 10000094 | Para_Engine_Speed_Ctr_TV_IdleOp_P | Para_Engine_Speed_Ctr_TV_IdleOp_P | 3429 | Para_Engine_Speed_Ctr_TV_IdleOp_P |  | 10000094
[8 empty] | 10000089 | Para_Engine_Speed_Ctr_TV_IdleOp_umax | Para_Engine_Speed_Ctr_TV_IdleOp_umax | 3430 | Para_Engine_Speed_Ctr_TV_IdleOp_umax |  | 10000089
[8 empty] | 10000092 | Para_Engine_Speed_Ctr_TV_IdleOp_umin | Para_Engine_Speed_Ctr_TV_IdleOp_umin | 3431 | Para_Engine_Speed_Ctr_TV_IdleOp_umin |  | 10000092
[8 empty] | 10000101 | Para_Engine_Speed_Ctr_TV_IsolatedOp_N | Para_Engine_Speed_Ctr_TV_IsolatedOp_N | 3432 | Para_Engine_Speed_Ctr_TV_IsolatedOp_N |  | 10000101
[8 empty] | 10000692 | Para_Engine_Speed_Limit_N_EngStart_HyHi | Para_Engine_Speed_Limit_N_EngStart_HyHi | 3433 | Para_Engine_Speed_Limit_N_EngStart_HyHi |  | 10000692
[8 empty] | 10000696 | Para_Engine_Speed_Limit_N_EngStart_LimHi | Para_Engine_Speed_Limit_N_EngStart_LimHi | 3434 | Para_Engine_Speed_Limit_N_EngStart_LimHi |  | 10000696
[8 empty] | 10008192 | Para_Engine_Speed_N_Offs_Sync | Para_Engine_Speed_N_Offs_Sync | 3435 | Para_Engine_Speed_N_Offs_Sync |  | 10008192
[8 empty] | 10008517 | Para_Engine_SteadyState_ChargePress_Abs | Para_Engine_SteadyState_ChargePress_Abs | 3436 | Para_Engine_SteadyState_ChargePress_Abs |  | 10008517
[8 empty] | 10008513 | Para_Engine_SteadyState_ChargePress_Rel | Para_Engine_SteadyState_ChargePress_Rel | 3437 | Para_Engine_SteadyState_ChargePress_Rel |  | 10008513
[8 empty] | 10008515 | Para_Engine_SteadyState_ChargePress_ti_Filt | Para_Engine_SteadyState_ChargePress_ti_Filt | 3438 | Para_Engine_SteadyState_ChargePress_ti_Filt |  | 10008515
[8 empty] | 10008507 | Para_Engine_SteadyState_ChargeTemp_Abs | Para_Engine_SteadyState_ChargeTemp_Abs | 3439 | Para_Engine_SteadyState_ChargeTemp_Abs |  | 10008507
[8 empty] | 10008511 | Para_Engine_SteadyState_ChargeTemp_Rel | Para_Engine_SteadyState_ChargeTemp_Rel | 3440 | Para_Engine_SteadyState_ChargeTemp_Rel |  | 10008511
[8 empty] | 10008512 | Para_Engine_SteadyState_ChargeTemp_ti_Filt | Para_Engine_SteadyState_ChargeTemp_ti_Filt | 3441 | Para_Engine_SteadyState_ChargeTemp_ti_Filt |  | 10008512
[8 empty] | 10008788 | Para_Engine_SteadyState_Exhaust_Abs | Para_Engine_SteadyState_Exhaust_Abs | 3442 | Para_Engine_SteadyState_Exhaust_Abs |  | 10008788
[8 empty] | 10008787 | Para_Engine_SteadyState_Exhaust_Rel | Para_Engine_SteadyState_Exhaust_Rel | 3443 | Para_Engine_SteadyState_Exhaust_Rel |  | 10008787
[8 empty] | 10008786 | Para_Engine_SteadyState_Exhaust_ti_Filt | Para_Engine_SteadyState_Exhaust_ti_Filt | 3444 | Para_Engine_SteadyState_Exhaust_ti_Filt |  | 10008786
[8 empty] | 10008516 | Para_Engine_SteadyState_Power_Abs | Para_Engine_SteadyState_Power_Abs | 3445 | Para_Engine_SteadyState_Power_Abs |  | 10008516
[8 empty] | 10008514 | Para_Engine_SteadyState_Power_Rel | Para_Engine_SteadyState_Power_Rel | 3446 | Para_Engine_SteadyState_Power_Rel |  | 10008514
[8 empty] | 10008520 | Para_Engine_SteadyState_Power_ti_Filt | Para_Engine_SteadyState_Power_ti_Filt | 3447 | Para_Engine_SteadyState_Power_ti_Filt |  | 10008520
[8 empty] | 10049928 | Para_enginecontroller_blx2_enable | Para_enginecontroller_blx2_enable | 3448 | Para_enginecontroller_blx2_enable |  | 10049928
[8 empty] | 10049929 | Para_enginecontroller_bp2s_comp_leanoxdrift | Para_enginecontroller_bp2s_comp_leanoxdrift | 3449 | Para_enginecontroller_bp2s_comp_leanoxdrift |  | 10049929
[8 empty] | 10049930 | Para_enginecontroller_ioph_nox_measure_mandatory | Para_enginecontroller_ioph_nox_measure_mandatory | 3450 | Para_enginecontroller_ioph_nox_measure_mandatory | h | 10049930
[8 empty] | 10049931 | Para_enginecontroller_ioph_nox_measure_recommend | Para_enginecontroller_ioph_nox_measure_recommend | 3451 | Para_enginecontroller_ioph_nox_measure_recommend | h | 10049931
[8 empty] | 10049932 | Para_enginecontroller_ioph_p2s_comp_leanoxdrift_reset | Para_enginecontroller_ioph_p2s_comp_leanoxdrift_reset | 3452 | Para_enginecontroller_ioph_p2s_comp_leanoxdrift_reset | h | 10049932
[8 empty] | 10049933 | Para_enginecontroller_ioph_p2s_comp_leanoxdrift_sec2 | Para_enginecontroller_ioph_p2s_comp_leanoxdrift_sec2 | 3453 | Para_enginecontroller_ioph_p2s_comp_leanoxdrift_sec2 | h | 10049933
[8 empty] | 10049940 | Para_enginecontroller_p2s_comp_leanoxdrift_x1 | Para_enginecontroller_p2s_comp_leanoxdrift_x1 | 3454 | Para_enginecontroller_p2s_comp_leanoxdrift_x1 | kW | 10049940
[8 empty] | 10049941 | Para_enginecontroller_p2s_comp_leanoxdrift_x2 | Para_enginecontroller_p2s_comp_leanoxdrift_x2 | 3455 | Para_enginecontroller_p2s_comp_leanoxdrift_x2 | kW | 10049941
[8 empty] | 10049942 | Para_enginecontroller_p2s_comp_leanoxdrift_y1 | Para_enginecontroller_p2s_comp_leanoxdrift_y1 | 3456 | Para_enginecontroller_p2s_comp_leanoxdrift_y1 |  | 10049942
[8 empty] | 10049943 | Para_enginecontroller_p2s_comp_leanoxdrift_y2 | Para_enginecontroller_p2s_comp_leanoxdrift_y2 | 3457 | Para_enginecontroller_p2s_comp_leanoxdrift_y2 |  | 10049943
[8 empty] | 10049934 | Para_enginecontroller_rcoeff_p2s_comp_sector2 | Para_enginecontroller_rcoeff_p2s_comp_sector2 | 3458 | Para_enginecontroller_rcoeff_p2s_comp_sector2 |  | 10049934
[8 empty] | 10049935 | Para_enginecontroller_rlx2_steadystatefactor | Para_enginecontroller_rlx2_steadystatefactor | 3459 | Para_enginecontroller_rlx2_steadystatefactor |  | 10049935
[8 empty] | 10049936 | Para_enginecontroller_rp_p2s_comp_leanoxdrift_sp | Para_enginecontroller_rp_p2s_comp_leanoxdrift_sp | 3460 | Para_enginecontroller_rp_p2s_comp_leanoxdrift_sp | %Pnom | 10049936
[8 empty] | 10049937 | Para_enginecontroller_rpr_lx2_offsetlimit | Para_enginecontroller_rpr_lx2_offsetlimit | 3461 | Para_enginecontroller_rpr_lx2_offsetlimit | mbar | 10049937
[8 empty] | 10049938 | Para_enginecontroller_tifilterconst_nox | Para_enginecontroller_tifilterconst_nox | 3462 | Para_enginecontroller_tifilterconst_nox | s | 10049938
[8 empty] | 10049939 | Para_enginecontroller_tilx2_ctrl_tn | Para_enginecontroller_tilx2_ctrl_tn | 3463 | Para_enginecontroller_tilx2_ctrl_tn | s | 10049939
[8 empty] | 17298 | Para_Exhaust_ActBoil | Para_Exhaust_ActBoil | 3464 | Para_Exhaust_ActBoil |  | 17298
[8 empty] | 17299 | Para_Exhaust_ActExhDevAvg | Para_Exhaust_ActExhDevAvg | 3465 | Para_Exhaust_ActExhDevAvg |  | 17299
[8 empty] | 17300 | Para_Exhaust_ActExhGasScav_NEx | Para_Exhaust_ActExhGasScav_NEx | 3466 | Para_Exhaust_ActExhGasScav_NEx |  | 17300
[8 empty] | 17301 | Para_Exhaust_ActExhMax | Para_Exhaust_ActExhMax | 3467 | Para_Exhaust_ActExhMax |  | 17301
[8 empty] | 17302 | Para_Exhaust_ActExhTemp | Para_Exhaust_ActExhTemp | 3468 | Para_Exhaust_ActExhTemp |  | 17302
[8 empty] | 17303 | Para_Exhaust_ActInHec | Para_Exhaust_ActInHec | 3469 | Para_Exhaust_ActInHec |  | 17303
[8 empty] | 17304 | Para_Exhaust_ActInKat | Para_Exhaust_ActInKat | 3470 | Para_Exhaust_ActInKat |  | 17304
[8 empty] | 17305 | Para_Exhaust_ActKat | Para_Exhaust_ActKat | 3471 | Para_Exhaust_ActKat |  | 17305
[8 empty] | 17306 | Para_Exhaust_ActOutHec | Para_Exhaust_ActOutHec | 3472 | Para_Exhaust_ActOutHec |  | 17306
[8 empty] | 17307 | Para_Exhaust_ActOutKat | Para_Exhaust_ActOutKat | 3473 | Para_Exhaust_ActOutKat |  | 17307
[8 empty] | 17308 | Para_Exhaust_ActTempInTurboCh | Para_Exhaust_ActTempInTurboCh | 3474 | Para_Exhaust_ActTempInTurboCh |  | 17308
[8 empty] | 17309 | Para_Exhaust_ActTempOutHec1 | Para_Exhaust_ActTempOutHec1 | 3475 | Para_Exhaust_ActTempOutHec1 |  | 17309
[8 empty] | 17310 | Para_Exhaust_ActTempOutHec2 | Para_Exhaust_ActTempOutHec2 | 3476 | Para_Exhaust_ActTempOutHec2 |  | 17310
[8 empty] | 10049944 | Para_exhaust_boxicat_exist | Para_exhaust_boxicat_exist | 3477 | Para_exhaust_boxicat_exist |  | 10049944
[8 empty] | 10049945 | Para_exhaust_bpr_oxicat_in_exist | Para_exhaust_bpr_oxicat_in_exist | 3478 | Para_exhaust_bpr_oxicat_in_exist |  | 10049945
[8 empty] | 10049946 | Para_exhaust_bpr_oxicat_in_fast_exist | Para_exhaust_bpr_oxicat_in_fast_exist | 3479 | Para_exhaust_bpr_oxicat_in_fast_exist |  | 10049946
[8 empty] | 10049947 | Para_exhaust_bpr_oxicat_out_exist | Para_exhaust_bpr_oxicat_out_exist | 3480 | Para_exhaust_bpr_oxicat_out_exist |  | 10049947
[8 empty] | 10049948 | Para_exhaust_bt_oxicat_in_exist | Para_exhaust_bt_oxicat_in_exist | 3481 | Para_exhaust_bt_oxicat_in_exist |  | 10049948
[8 empty] | 10049949 | Para_exhaust_bt_oxicat_out_exist | Para_exhaust_bt_oxicat_out_exist | 3482 | Para_exhaust_bt_oxicat_out_exist |  | 10049949
[8 empty] | 10000420 | Para_Exhaust_CODINOX_CO2_PneumVal | Para_Exhaust_CODINOX_CO2_PneumVal | 3483 | Para_Exhaust_CODINOX_CO2_PneumVal |  | 10000420
[8 empty] | 10000396 | Para_Exhaust_CODINOX_tiCO2_ExPSp_StartOffTime | Para_Exhaust_CODINOX_tiCO2_ExPSp_StartOffTime | 3484 | Para_Exhaust_CODINOX_tiCO2_ExPSp_StartOffTime |  | 10000396
[8 empty] | 10000394 | Para_Exhaust_CODINOX_tiCO2_ExPSp_StopOffTime | Para_Exhaust_CODINOX_tiCO2_ExPSp_StopOffTime | 3485 | Para_Exhaust_CODINOX_tiCO2_ExPSp_StopOffTime |  | 10000394
[8 empty] | 10008441 | Para_Exhaust_DiffPressCooler_Pr_Diff_ExGCooler_Active | Para_Exhaust_DiffPressCooler_Pr_Diff_ExGCooler_Active | 3486 | Para_Exhaust_DiffPressCooler_Pr_Diff_ExGCooler_Active |  | 10008441
[8 empty] | 10008442 | Para_Exhaust_DiffPressCooler_Pr_Diff_ExGCooler_Hi | Para_Exhaust_DiffPressCooler_Pr_Diff_ExGCooler_Hi | 3487 | Para_Exhaust_DiffPressCooler_Pr_Diff_ExGCooler_Hi |  | 10008442
[8 empty] | 10008443 | Para_Exhaust_DiffPressCooler_Pr_Diff_ExGCooler_HyHi | Para_Exhaust_DiffPressCooler_Pr_Diff_ExGCooler_HyHi | 3488 | Para_Exhaust_DiffPressCooler_Pr_Diff_ExGCooler_HyHi |  | 10008443
[8 empty] | 10008444 | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_Active | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_Active | 3489 | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_Active |  | 10008444
[8 empty] | 10008447 | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_Hi | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_Hi | 3490 | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_Hi |  | 10008447
[8 empty] | 10008446 | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_Hi1 | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_Hi1 | 3491 | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_Hi1 |  | 10008446
[8 empty] | 10008445 | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_Hi2 | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_Hi2 | 3492 | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_Hi2 |  | 10008445
[8 empty] | 10008449 | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_HyHi | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_HyHi | 3493 | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_HyHi |  | 10008449
[8 empty] | 10008448 | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_Lo | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_Lo | 3494 | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_Lo |  | 10008448
[8 empty] | 10000391 | Para_Exhaust_EGValveEnable | Para_Exhaust_EGValveEnable | 3495 | Para_Exhaust_EGValveEnable |  | 10000391
[8 empty] | 10008292 | Para_Exhaust_HeatExchanger_T_EGaHE1_HyHi_Trip | Para_Exhaust_HeatExchanger_T_EGaHE1_HyHi_Trip | 3496 | Para_Exhaust_HeatExchanger_T_EGaHE1_HyHi_Trip |  | 10008292
[8 empty] | 10008298 | Para_Exhaust_HeatExchanger_T_EGaHE1_HyHi_Warn | Para_Exhaust_HeatExchanger_T_EGaHE1_HyHi_Warn | 3497 | Para_Exhaust_HeatExchanger_T_EGaHE1_HyHi_Warn |  | 10008298
[8 empty] | 10008293 | Para_Exhaust_HeatExchanger_T_EGaHE1_LimHi_Trip | Para_Exhaust_HeatExchanger_T_EGaHE1_LimHi_Trip | 3498 | Para_Exhaust_HeatExchanger_T_EGaHE1_LimHi_Trip |  | 10008293
[8 empty] | 10008295 | Para_Exhaust_HeatExchanger_T_EGaHE1_LimHi_Warn | Para_Exhaust_HeatExchanger_T_EGaHE1_LimHi_Warn | 3499 | Para_Exhaust_HeatExchanger_T_EGaHE1_LimHi_Warn |  | 10008295
[8 empty] | 10008297 | Para_Exhaust_HeatExchanger_T_EGaHE2_HyHi_Trip | Para_Exhaust_HeatExchanger_T_EGaHE2_HyHi_Trip | 3500 | Para_Exhaust_HeatExchanger_T_EGaHE2_HyHi_Trip |  | 10008297
[8 empty] | 10008223 | Para_Exhaust_HeatExchanger_T_EGaHE2_HyHi_Warn | Para_Exhaust_HeatExchanger_T_EGaHE2_HyHi_Warn | 3501 | Para_Exhaust_HeatExchanger_T_EGaHE2_HyHi_Warn |  | 10008223
[8 empty] | 10008294 | Para_Exhaust_HeatExchanger_T_EGaHE2_LimHi_Trip | Para_Exhaust_HeatExchanger_T_EGaHE2_LimHi_Trip | 3502 | Para_Exhaust_HeatExchanger_T_EGaHE2_LimHi_Trip |  | 10008294
[8 empty] | 10008219 | Para_Exhaust_HeatExchanger_T_EGaHE2_LimHi_Warn | Para_Exhaust_HeatExchanger_T_EGaHE2_LimHi_Warn | 3503 | Para_Exhaust_HeatExchanger_T_EGaHE2_LimHi_Warn |  | 10008219
[8 empty] | 10000477 | Para_Exhaust_HeatExchanger_T_PlateHE_InpLimMax | Para_Exhaust_HeatExchanger_T_PlateHE_InpLimMax | 3504 | Para_Exhaust_HeatExchanger_T_PlateHE_InpLimMax |  | 10000477
[8 empty] | 10000480 | Para_Exhaust_HeatExchanger_T_PlateHE_InpLimMin | Para_Exhaust_HeatExchanger_T_PlateHE_InpLimMin | 3505 | Para_Exhaust_HeatExchanger_T_PlateHE_InpLimMin |  | 10000480
[8 empty] | 17311 | Para_Exhaust_NOx_ActCtr | Para_Exhaust_NOx_ActCtr | 3506 | Para_Exhaust_NOx_ActCtr |  | 17311
[8 empty] | 17312 | Para_Exhaust_NOx_ErrorMax | Para_Exhaust_NOx_ErrorMax | 3507 | Para_Exhaust_NOx_ErrorMax | mg/m3 | 17312
[8 empty] | 17313 | Para_Exhaust_NOx_O2ref | Para_Exhaust_NOx_O2ref | 3508 | Para_Exhaust_NOx_O2ref | % | 17313
[8 empty] | 17314 | Para_Exhaust_NOx_Sensor1_ActSensor | Para_Exhaust_NOx_Sensor1_ActSensor | 3509 | Para_Exhaust_NOx_Sensor1_ActSensor |  | 17314
[8 empty] | 17315 | Para_Exhaust_NOx_Sensor1_NOxOffset | Para_Exhaust_NOx_Sensor1_NOxOffset | 3510 | Para_Exhaust_NOx_Sensor1_NOxOffset | ppm | 17315
[8 empty] | 17316 | Para_Exhaust_NOx_Sensor1_O2Offset | Para_Exhaust_NOx_Sensor1_O2Offset | 3511 | Para_Exhaust_NOx_Sensor1_O2Offset | % | 17316
[8 empty] | 17317 | Para_Exhaust_NOx_Sensor2_ActSensor | Para_Exhaust_NOx_Sensor2_ActSensor | 3512 | Para_Exhaust_NOx_Sensor2_ActSensor |  | 17317
[8 empty] | 17318 | Para_Exhaust_NOx_Sensor2_NOxOffset | Para_Exhaust_NOx_Sensor2_NOxOffset | 3513 | Para_Exhaust_NOx_Sensor2_NOxOffset | ppm | 17318
[8 empty] | 17319 | Para_Exhaust_NOx_Sensor2_O2Offset | Para_Exhaust_NOx_Sensor2_O2Offset | 3514 | Para_Exhaust_NOx_Sensor2_O2Offset | % | 17319
[8 empty] | 17320 | Para_Exhaust_NOx_SetNOx | Para_Exhaust_NOx_SetNOx | 3515 | Para_Exhaust_NOx_SetNOx | mg/m3 | 17320
[8 empty] | 10001472 | Para_Exhaust_Pr_EGaHPTC_A_Active | Para_Exhaust_Pr_EGaHPTC_A_Active | 3516 | Para_Exhaust_Pr_EGaHPTC_A_Active |  | 10001472
[8 empty] | 10001476 | Para_Exhaust_Pr_EGaHPTC_B_Active | Para_Exhaust_Pr_EGaHPTC_B_Active | 3517 | Para_Exhaust_Pr_EGaHPTC_B_Active |  | 10001476
[8 empty] | 10001474 | Para_Exhaust_Pr_EGaLPTC_A_Active | Para_Exhaust_Pr_EGaLPTC_A_Active | 3518 | Para_Exhaust_Pr_EGaLPTC_A_Active |  | 10001474
[8 empty] | 10001475 | Para_Exhaust_Pr_EGaLPTC_B_Active | Para_Exhaust_Pr_EGaLPTC_B_Active | 3519 | Para_Exhaust_Pr_EGaLPTC_B_Active |  | 10001475
[8 empty] | 10001473 | Para_Exhaust_Pr_EGbHPTC_A_Active | Para_Exhaust_Pr_EGbHPTC_A_Active | 3520 | Para_Exhaust_Pr_EGbHPTC_A_Active |  | 10001473
[8 empty] | 10001470 | Para_Exhaust_Pr_EGbHPTC_B_Active | Para_Exhaust_Pr_EGbHPTC_B_Active | 3521 | Para_Exhaust_Pr_EGbHPTC_B_Active |  | 10001470
[8 empty] | 17321 | Para_Exhaust_Reactor_Active | Para_Exhaust_Reactor_Active | 3522 | Para_Exhaust_Reactor_Active | % | 17321
[8 empty] | 17322 | Para_Exhaust_Reactor_ActiveHys | Para_Exhaust_Reactor_ActiveHys | 3523 | Para_Exhaust_Reactor_ActiveHys | kW | 17322
[8 empty] | 17323 | Para_Exhaust_Reactor_AdjustRefTemp | Para_Exhaust_Reactor_AdjustRefTemp | 3524 | Para_Exhaust_Reactor_AdjustRefTemp |  | 17323
[8 empty] | 17324 | Para_Exhaust_Reactor_FlapTimer1 | Para_Exhaust_Reactor_FlapTimer1 | 3525 | Para_Exhaust_Reactor_FlapTimer1 | s | 17324
[8 empty] | 17325 | Para_Exhaust_Reactor_FlapTimer2 | Para_Exhaust_Reactor_FlapTimer2 | 3526 | Para_Exhaust_Reactor_FlapTimer2 | s | 17325
[8 empty] | 17326 | Para_Exhaust_Reactor_LimitReactChamb00 | Para_Exhaust_Reactor_LimitReactChamb00 | 3527 | Para_Exhaust_Reactor_LimitReactChamb00 | °C | 17326
[8 empty] | 17327 | Para_Exhaust_Reactor_LimitReactChamb25 | Para_Exhaust_Reactor_LimitReactChamb25 | 3528 | Para_Exhaust_Reactor_LimitReactChamb25 | °C | 17327
[8 empty] | 17328 | Para_Exhaust_Reactor_LimitReactChamb50 | Para_Exhaust_Reactor_LimitReactChamb50 | 3529 | Para_Exhaust_Reactor_LimitReactChamb50 | °C | 17328
[8 empty] | 17329 | Para_Exhaust_Reactor_LimitReactChamb75 | Para_Exhaust_Reactor_LimitReactChamb75 | 3530 | Para_Exhaust_Reactor_LimitReactChamb75 | °C | 17329
[8 empty] | 17330 | Para_Exhaust_Reactor_LimitReactChambStartGasInj | Para_Exhaust_Reactor_LimitReactChambStartGasInj | 3531 | Para_Exhaust_Reactor_LimitReactChambStartGasInj | °C | 17330
[8 empty] | 17331 | Para_Exhaust_Reactor_RelTemp1 | Para_Exhaust_Reactor_RelTemp1 | 3532 | Para_Exhaust_Reactor_RelTemp1 | °C | 17331
[8 empty] | 17332 | Para_Exhaust_Reactor_RelTemp2 | Para_Exhaust_Reactor_RelTemp2 | 3533 | Para_Exhaust_Reactor_RelTemp2 | °C | 17332
[8 empty] | 10002574 | Para_Exhaust_Reactor_Sel_Flap5Pos | Para_Exhaust_Reactor_Sel_Flap5Pos | 3534 | Para_Exhaust_Reactor_Sel_Flap5Pos |  | 10002574
[8 empty] | 10002570 | Para_Exhaust_Reactor_Sel_FlapActEl | Para_Exhaust_Reactor_Sel_FlapActEl | 3535 | Para_Exhaust_Reactor_Sel_FlapActEl |  | 10002570
[8 empty] | 10000115 | Para_Exhaust_Reactor_T_ThR_LimGasHy | Para_Exhaust_Reactor_T_ThR_LimGasHy | 3536 | Para_Exhaust_Reactor_T_ThR_LimGasHy |  | 10000115
[8 empty] | 10000112 | Para_Exhaust_Reactor_T_ThR_LimPInc | Para_Exhaust_Reactor_T_ThR_LimPInc | 3537 | Para_Exhaust_Reactor_T_ThR_LimPInc |  | 10000112
[8 empty] | 10000108 | Para_Exhaust_Reactor_T_ThR_SetwoGas | Para_Exhaust_Reactor_T_ThR_SetwoGas | 3538 | Para_Exhaust_Reactor_T_ThR_SetwoGas |  | 10000108
[8 empty] | 10000110 | Para_Exhaust_Reactor_ThR_NatGas | Para_Exhaust_Reactor_ThR_NatGas | 3539 | Para_Exhaust_Reactor_ThR_NatGas |  | 10000110
[8 empty] | 10000109 | Para_Exhaust_Reactor_ThR_woGas | Para_Exhaust_Reactor_ThR_woGas | 3540 | Para_Exhaust_Reactor_ThR_woGas |  | 10000109
[8 empty] | 10000107 | Para_Exhaust_Reactor_ti_ThR_TimePInc | Para_Exhaust_Reactor_ti_ThR_TimePInc | 3541 | Para_Exhaust_Reactor_ti_ThR_TimePInc |  | 10000107
[8 empty] | 10000113 | Para_Exhaust_Reactor_ti_ThR_ValDurationPInc | Para_Exhaust_Reactor_ti_ThR_ValDurationPInc | 3542 | Para_Exhaust_Reactor_ti_ThR_ValDurationPInc |  | 10000113
[8 empty] | 10000111 | Para_Exhaust_Reactor_ti_ThR_ValIntervalPInc | Para_Exhaust_Reactor_ti_ThR_ValIntervalPInc | 3543 | Para_Exhaust_Reactor_ti_ThR_ValIntervalPInc |  | 10000111
[8 empty] | 10049950 | Para_exhaust_rpr_eg_deflag_fast_hihi | Para_exhaust_rpr_eg_deflag_fast_hihi | 3544 | Para_exhaust_rpr_eg_deflag_fast_hihi |  | 10049950
[8 empty] | 10049951 | Para_exhaust_rpr_oxicat_diff_hi | Para_exhaust_rpr_oxicat_diff_hi | 3545 | Para_exhaust_rpr_oxicat_diff_hi | mbar | 10049951
[8 empty] | 10049952 | Para_exhaust_rt_oxicat_in_hi | Para_exhaust_rt_oxicat_in_hi | 3546 | Para_exhaust_rt_oxicat_in_hi | °C | 10049952
[8 empty] | 10049953 | Para_exhaust_rt_oxicat_out_hihi | Para_exhaust_rt_oxicat_out_hihi | 3547 | Para_exhaust_rt_oxicat_out_hihi | °C | 10049953
[8 empty] | 10000393 | Para_Exhaust_Scavenging_EGScav_ifAuxV_ok | Para_Exhaust_Scavenging_EGScav_ifAuxV_ok | 3548 | Para_Exhaust_Scavenging_EGScav_ifAuxV_ok |  | 10000393
[8 empty] | 10000392 | Para_Exhaust_Scavenging_N2_NoScavGas1 | Para_Exhaust_Scavenging_N2_NoScavGas1 | 3549 | Para_Exhaust_Scavenging_N2_NoScavGas1 |  | 10000392
[8 empty] | 10000395 | Para_Exhaust_Scavenging_N2_NoScavGas2 | Para_Exhaust_Scavenging_N2_NoScavGas2 | 3550 | Para_Exhaust_Scavenging_N2_NoScavGas2 |  | 10000395
[8 empty] | 10002610 | Para_Exhaust_Scavenging_ScavBeStart_Active | Para_Exhaust_Scavenging_ScavBeStart_Active | 3551 | Para_Exhaust_Scavenging_ScavBeStart_Active |  | 10002610
[8 empty] | 10001435 | Para_Exhaust_SCR_Active | Para_Exhaust_SCR_Active | 3552 | Para_Exhaust_SCR_Active |  | 10001435
[8 empty] | 10002686 | Para_Exhaust_SCR_Dosing_Flow_Urea100 | Para_Exhaust_SCR_Dosing_Flow_Urea100 | 3553 | Para_Exhaust_SCR_Dosing_Flow_Urea100 |  | 10002686
[8 empty] | 10001437 | Para_Exhaust_SCR_Dosing_Flow_Urea30 | Para_Exhaust_SCR_Dosing_Flow_Urea30 | 3554 | Para_Exhaust_SCR_Dosing_Flow_Urea30 |  | 10001437
[8 empty] | 10001436 | Para_Exhaust_SCR_Dosing_Flow_Urea40 | Para_Exhaust_SCR_Dosing_Flow_Urea40 | 3555 | Para_Exhaust_SCR_Dosing_Flow_Urea40 |  | 10001436
[8 empty] | 10002676 | Para_Exhaust_SCR_Dosing_Flow_Urea50 | Para_Exhaust_SCR_Dosing_Flow_Urea50 | 3556 | Para_Exhaust_SCR_Dosing_Flow_Urea50 |  | 10002676
[8 empty] | 10002678 | Para_Exhaust_SCR_Dosing_Flow_Urea60 | Para_Exhaust_SCR_Dosing_Flow_Urea60 | 3557 | Para_Exhaust_SCR_Dosing_Flow_Urea60 |  | 10002678
[8 empty] | 10002689 | Para_Exhaust_SCR_Dosing_Flow_Urea70 | Para_Exhaust_SCR_Dosing_Flow_Urea70 | 3558 | Para_Exhaust_SCR_Dosing_Flow_Urea70 |  | 10002689
[8 empty] | 10002690 | Para_Exhaust_SCR_Dosing_Flow_Urea80 | Para_Exhaust_SCR_Dosing_Flow_Urea80 | 3559 | Para_Exhaust_SCR_Dosing_Flow_Urea80 |  | 10002690
[8 empty] | 10002679 | Para_Exhaust_SCR_Dosing_Flow_Urea90 | Para_Exhaust_SCR_Dosing_Flow_Urea90 | 3560 | Para_Exhaust_SCR_Dosing_Flow_Urea90 |  | 10002679
[8 empty] | 10001434 | Para_Exhaust_SCR_Dosing_Flow_Urea_Hi | Para_Exhaust_SCR_Dosing_Flow_Urea_Hi | 3561 | Para_Exhaust_SCR_Dosing_Flow_Urea_Hi |  | 10001434
[8 empty] | 10002687 | Para_Exhaust_SCR_Dosing_Flow_Urea_Offs | Para_Exhaust_SCR_Dosing_Flow_Urea_Offs | 3562 | Para_Exhaust_SCR_Dosing_Flow_Urea_Offs |  | 10002687
[8 empty] | 10002723 | Para_Exhaust_SCR_Dosing_Flow_Urea_ScalMax | Para_Exhaust_SCR_Dosing_Flow_Urea_ScalMax | 3563 | Para_Exhaust_SCR_Dosing_Flow_Urea_ScalMax |  | 10002723
[8 empty] | 10002719 | Para_Exhaust_SCR_Dosing_Flow_Urea_ScalMin | Para_Exhaust_SCR_Dosing_Flow_Urea_ScalMin | 3564 | Para_Exhaust_SCR_Dosing_Flow_Urea_ScalMin |  | 10002719
[8 empty] | 10001428 | Para_Exhaust_SCR_Dosing_Flow_Urea_Set_ScalMax | Para_Exhaust_SCR_Dosing_Flow_Urea_Set_ScalMax | 3565 | Para_Exhaust_SCR_Dosing_Flow_Urea_Set_ScalMax |  | 10001428
[8 empty] | 10001431 | Para_Exhaust_SCR_Dosing_Flow_Urea_Set_ScalMin | Para_Exhaust_SCR_Dosing_Flow_Urea_Set_ScalMin | 3566 | Para_Exhaust_SCR_Dosing_Flow_Urea_Set_ScalMin |  | 10001431
[8 empty] | 10002791 | Para_Exhaust_SCR_Dosing_Flow_UreaGain | Para_Exhaust_SCR_Dosing_Flow_UreaGain | 3567 | Para_Exhaust_SCR_Dosing_Flow_UreaGain |  | 10002791
[8 empty] | 10002700 | Para_Exhaust_SCR_Dosing_Pr_AirSupply_Hi | Para_Exhaust_SCR_Dosing_Pr_AirSupply_Hi | 3568 | Para_Exhaust_SCR_Dosing_Pr_AirSupply_Hi |  | 10002700
[8 empty] | 10002704 | Para_Exhaust_SCR_Dosing_Pr_AirSupply_Lo | Para_Exhaust_SCR_Dosing_Pr_AirSupply_Lo | 3569 | Para_Exhaust_SCR_Dosing_Pr_AirSupply_Lo |  | 10002704
[8 empty] | 10002722 | Para_Exhaust_SCR_Dosing_Pr_AirSupply_ScalMax | Para_Exhaust_SCR_Dosing_Pr_AirSupply_ScalMax | 3570 | Para_Exhaust_SCR_Dosing_Pr_AirSupply_ScalMax |  | 10002722
[8 empty] | 10002730 | Para_Exhaust_SCR_Dosing_Pr_AirSupply_ScalMin | Para_Exhaust_SCR_Dosing_Pr_AirSupply_ScalMin | 3571 | Para_Exhaust_SCR_Dosing_Pr_AirSupply_ScalMin |  | 10002730
[8 empty] | 10001433 | Para_Exhaust_SCR_Dosing_Pr_Urea_Hi | Para_Exhaust_SCR_Dosing_Pr_Urea_Hi | 3572 | Para_Exhaust_SCR_Dosing_Pr_Urea_Hi |  | 10001433
[8 empty] | 10001432 | Para_Exhaust_SCR_Dosing_Pr_Urea_Lo | Para_Exhaust_SCR_Dosing_Pr_Urea_Lo | 3573 | Para_Exhaust_SCR_Dosing_Pr_Urea_Lo |  | 10001432
[8 empty] | 10002727 | Para_Exhaust_SCR_Dosing_Pr_Urea_ScalMax | Para_Exhaust_SCR_Dosing_Pr_Urea_ScalMax | 3574 | Para_Exhaust_SCR_Dosing_Pr_Urea_ScalMax |  | 10002727
[8 empty] | 10002725 | Para_Exhaust_SCR_Dosing_Pr_Urea_ScalMin | Para_Exhaust_SCR_Dosing_Pr_Urea_ScalMin | 3575 | Para_Exhaust_SCR_Dosing_Pr_Urea_ScalMin |  | 10002725
[8 empty] | 10002699 | Para_Exhaust_SCR_Dosing_tiAirCompressed_OfC | Para_Exhaust_SCR_Dosing_tiAirCompressed_OfC | 3576 | Para_Exhaust_SCR_Dosing_tiAirCompressed_OfC |  | 10002699
[8 empty] | 10002698 | Para_Exhaust_SCR_Dosing_tiUreaTank_LevelLow | Para_Exhaust_SCR_Dosing_tiUreaTank_LevelLow | 3577 | Para_Exhaust_SCR_Dosing_tiUreaTank_LevelLow |  | 10002698
[8 empty] | 10002695 | Para_Exhaust_SCR_Dosing_UreaCirculatePump_Exist | Para_Exhaust_SCR_Dosing_UreaCirculatePump_Exist | 3578 | Para_Exhaust_SCR_Dosing_UreaCirculatePump_Exist |  | 10002695
[8 empty] | 10002693 | Para_Exhaust_SCR_Dosing_UreaPump_Service | Para_Exhaust_SCR_Dosing_UreaPump_Service | 3579 | Para_Exhaust_SCR_Dosing_UreaPump_Service |  | 10002693
[8 empty] | 10002746 | Para_Exhaust_SCR_Emission_CEMS_Shutdown | Para_Exhaust_SCR_Emission_CEMS_Shutdown | 3580 | Para_Exhaust_SCR_Emission_CEMS_Shutdown |  | 10002746
[8 empty] | 10002753 | Para_Exhaust_SCR_Emission_CEMS_SteadyState | Para_Exhaust_SCR_Emission_CEMS_SteadyState | 3581 | Para_Exhaust_SCR_Emission_CEMS_SteadyState |  | 10002753
[8 empty] | 10002716 | Para_Exhaust_SCR_Emission_CO_Eng_Out_Set | Para_Exhaust_SCR_Emission_CO_Eng_Out_Set | 3582 | Para_Exhaust_SCR_Emission_CO_Eng_Out_Set |  | 10002716
[8 empty] | 10002756 | Para_Exhaust_SCR_Emission_CO_SCR_Out_Hi | Para_Exhaust_SCR_Emission_CO_SCR_Out_Hi | 3583 | Para_Exhaust_SCR_Emission_CO_SCR_Out_Hi |  | 10002756
[8 empty] | 10001425 | Para_Exhaust_SCR_Emission_CO_SCR_ScalMax | Para_Exhaust_SCR_Emission_CO_SCR_ScalMax | 3584 | Para_Exhaust_SCR_Emission_CO_SCR_ScalMax |  | 10001425
[8 empty] | 10001423 | Para_Exhaust_SCR_Emission_CO_SCR_ScalMin | Para_Exhaust_SCR_Emission_CO_SCR_ScalMin | 3585 | Para_Exhaust_SCR_Emission_CO_SCR_ScalMin |  | 10001423
[8 empty] | 10002758 | Para_Exhaust_SCR_Emission_Idx_NOxS_Config | Para_Exhaust_SCR_Emission_Idx_NOxS_Config | 3586 | Para_Exhaust_SCR_Emission_Idx_NOxS_Config |  | 10002758
[8 empty] | 10002751 | Para_Exhaust_SCR_Emission_NH3_Slip_Ctrl_Active | Para_Exhaust_SCR_Emission_NH3_Slip_Ctrl_Active | 3587 | Para_Exhaust_SCR_Emission_NH3_Slip_Ctrl_Active |  | 10002751
[8 empty] | 10001430 | Para_Exhaust_SCR_Emission_NO2_SCR_ScalMax | Para_Exhaust_SCR_Emission_NO2_SCR_ScalMax | 3588 | Para_Exhaust_SCR_Emission_NO2_SCR_ScalMax |  | 10001430
[8 empty] | 10001429 | Para_Exhaust_SCR_Emission_NO2_SCR_ScalMin | Para_Exhaust_SCR_Emission_NO2_SCR_ScalMin | 3589 | Para_Exhaust_SCR_Emission_NO2_SCR_ScalMin |  | 10001429
[8 empty] | 10001424 | Para_Exhaust_SCR_Emission_NO_Ctrl_SCR_ScalMax | Para_Exhaust_SCR_Emission_NO_Ctrl_SCR_ScalMax | 3590 | Para_Exhaust_SCR_Emission_NO_Ctrl_SCR_ScalMax |  | 10001424
[8 empty] | 10001427 | Para_Exhaust_SCR_Emission_NO_Ctrl_SCR_ScalMin | Para_Exhaust_SCR_Emission_NO_Ctrl_SCR_ScalMin | 3591 | Para_Exhaust_SCR_Emission_NO_Ctrl_SCR_ScalMin |  | 10001427
[8 empty] | 10002742 | Para_Exhaust_SCR_Emission_NO_NH3_Slip_Set | Para_Exhaust_SCR_Emission_NO_NH3_Slip_Set | 3592 | Para_Exhaust_SCR_Emission_NO_NH3_Slip_Set |  | 10002742
[8 empty] | 10001422 | Para_Exhaust_SCR_Emission_NO_SCR_ScalMax | Para_Exhaust_SCR_Emission_NO_SCR_ScalMax | 3593 | Para_Exhaust_SCR_Emission_NO_SCR_ScalMax |  | 10001422
[8 empty] | 10001426 | Para_Exhaust_SCR_Emission_NO_SCR_ScalMin | Para_Exhaust_SCR_Emission_NO_SCR_ScalMin | 3594 | Para_Exhaust_SCR_Emission_NO_SCR_ScalMin |  | 10001426
[8 empty] | 10002715 | Para_Exhaust_SCR_Emission_NOx_Eng_Out_Set | Para_Exhaust_SCR_Emission_NOx_Eng_Out_Set | 3595 | Para_Exhaust_SCR_Emission_NOx_Eng_Out_Set |  | 10002715
[8 empty] | 10002749 | Para_Exhaust_SCR_Emission_NOx_SCR_Out_Hi | Para_Exhaust_SCR_Emission_NOx_SCR_Out_Hi | 3596 | Para_Exhaust_SCR_Emission_NOx_SCR_Out_Hi |  | 10002749
[8 empty] | 10002740 | Para_Exhaust_SCR_Emission_NOx_SCR_Out_Set | Para_Exhaust_SCR_Emission_NOx_SCR_Out_Set | 3597 | Para_Exhaust_SCR_Emission_NOx_SCR_Out_Set |  | 10002740
[8 empty] | 10002709 | Para_Exhaust_SCR_Emission_NOxS_Eng_Out_Hi | Para_Exhaust_SCR_Emission_NOxS_Eng_Out_Hi | 3598 | Para_Exhaust_SCR_Emission_NOxS_Eng_Out_Hi |  | 10002709
[8 empty] | 10002759 | Para_Exhaust_SCR_Emission_tiGasAnalys_Purge_Duration | Para_Exhaust_SCR_Emission_tiGasAnalys_Purge_Duration | 3599 | Para_Exhaust_SCR_Emission_tiGasAnalys_Purge_Duration |  | 10002759
[8 empty] | 10002762 | Para_Exhaust_SCR_Emission_tiGasAnalys_Purge_Intervall | Para_Exhaust_SCR_Emission_tiGasAnalys_Purge_Intervall | 3600 | Para_Exhaust_SCR_Emission_tiGasAnalys_Purge_Intervall |  | 10002762
[8 empty] | 10002768 | Para_Exhaust_SCR_Emission_tiGasAnalys_Waiting | Para_Exhaust_SCR_Emission_tiGasAnalys_Waiting | 3601 | Para_Exhaust_SCR_Emission_tiGasAnalys_Waiting |  | 10002768
[8 empty] | 10002750 | Para_Exhaust_SCR_Emission_tiNO_AboveLimit | Para_Exhaust_SCR_Emission_tiNO_AboveLimit | 3602 | Para_Exhaust_SCR_Emission_tiNO_AboveLimit |  | 10002750
[8 empty] | 10002767 | Para_Exhaust_SCR_Emission_tiReset_SampleGas_Valves | Para_Exhaust_SCR_Emission_tiReset_SampleGas_Valves | 3603 | Para_Exhaust_SCR_Emission_tiReset_SampleGas_Valves |  | 10002767
[8 empty] | 10001438 | Para_Exhaust_SCR_P_LoadEngine_Dosing | Para_Exhaust_SCR_P_LoadEngine_Dosing | 3604 | Para_Exhaust_SCR_P_LoadEngine_Dosing |  | 10001438
[8 empty] | 10002705 | Para_Exhaust_SCR_Pr_SCR_Hi | Para_Exhaust_SCR_Pr_SCR_Hi | 3605 | Para_Exhaust_SCR_Pr_SCR_Hi |  | 10002705
[8 empty] | 10002738 | Para_Exhaust_SCR_Pr_SCR_In_ScalMax | Para_Exhaust_SCR_Pr_SCR_In_ScalMax | 3606 | Para_Exhaust_SCR_Pr_SCR_In_ScalMax |  | 10002738
[8 empty] | 10002737 | Para_Exhaust_SCR_Pr_SCR_In_ScalMin | Para_Exhaust_SCR_Pr_SCR_In_ScalMin | 3607 | Para_Exhaust_SCR_Pr_SCR_In_ScalMin |  | 10002737
[8 empty] | 10001417 | Para_Exhaust_SCR_Pr_SCR_Out_ScalMax | Para_Exhaust_SCR_Pr_SCR_Out_ScalMax | 3608 | Para_Exhaust_SCR_Pr_SCR_Out_ScalMax |  | 10001417
[8 empty] | 10002743 | Para_Exhaust_SCR_Pr_SCR_Out_ScalMin | Para_Exhaust_SCR_Pr_SCR_Out_ScalMin | 3609 | Para_Exhaust_SCR_Pr_SCR_Out_ScalMin |  | 10002743
[8 empty] | 10000220 | Para_Exhaust_SCR_SCR_Release | Para_Exhaust_SCR_SCR_Release | 3610 | Para_Exhaust_SCR_SCR_Release |  | 10000220
[8 empty] | 10002710 | Para_Exhaust_SCR_T_SCR_Avg | Para_Exhaust_SCR_T_SCR_Avg | 3611 | Para_Exhaust_SCR_T_SCR_Avg |  | 10002710
[8 empty] | 10002707 | Para_Exhaust_SCR_T_SCR_In_Hi | Para_Exhaust_SCR_T_SCR_In_Hi | 3612 | Para_Exhaust_SCR_T_SCR_In_Hi |  | 10002707
[8 empty] | 10002733 | Para_Exhaust_SCR_T_SCR_In_ScalMax | Para_Exhaust_SCR_T_SCR_In_ScalMax | 3613 | Para_Exhaust_SCR_T_SCR_In_ScalMax |  | 10002733
[8 empty] | 10002731 | Para_Exhaust_SCR_T_SCR_In_ScalMin | Para_Exhaust_SCR_T_SCR_In_ScalMin | 3614 | Para_Exhaust_SCR_T_SCR_In_ScalMin |  | 10002731
[8 empty] | 10002714 | Para_Exhaust_SCR_T_SCR_Out_Hi | Para_Exhaust_SCR_T_SCR_Out_Hi | 3615 | Para_Exhaust_SCR_T_SCR_Out_Hi |  | 10002714
[8 empty] | 10001419 | Para_Exhaust_SCR_T_SCR_Out_ScalMax | Para_Exhaust_SCR_T_SCR_Out_ScalMax | 3616 | Para_Exhaust_SCR_T_SCR_Out_ScalMax |  | 10001419
[8 empty] | 10001420 | Para_Exhaust_SCR_T_SCR_Out_ScalMin | Para_Exhaust_SCR_T_SCR_Out_ScalMin | 3617 | Para_Exhaust_SCR_T_SCR_Out_ScalMin |  | 10001420
[8 empty] | 10001471 | Para_Exhaust_T_EGaHPTC_A_Active | Para_Exhaust_T_EGaHPTC_A_Active | 3618 | Para_Exhaust_T_EGaHPTC_A_Active |  | 10001471
[8 empty] | 10001469 | Para_Exhaust_T_EGaHPTC_B_Active | Para_Exhaust_T_EGaHPTC_B_Active | 3619 | Para_Exhaust_T_EGaHPTC_B_Active |  | 10001469
[8 empty] | 10001465 | Para_Exhaust_T_EGbHPTC_A_Active | Para_Exhaust_T_EGbHPTC_A_Active | 3620 | Para_Exhaust_T_EGbHPTC_A_Active |  | 10001465
[8 empty] | 10001468 | Para_Exhaust_T_EGbHPTC_B_Active | Para_Exhaust_T_EGbHPTC_B_Active | 3621 | Para_Exhaust_T_EGbHPTC_B_Active |  | 10001468
[8 empty] | 17333 | Para_Exhaust_TCSpeed2Stage_20mA_A | Para_Exhaust_TCSpeed2Stage_20mA_A | 3622 | Para_Exhaust_TCSpeed2Stage_20mA_A |  | 17333
[8 empty] | 17334 | Para_Exhaust_TCSpeed2Stage_20mA_B | Para_Exhaust_TCSpeed2Stage_20mA_B | 3623 | Para_Exhaust_TCSpeed2Stage_20mA_B | 1000/min | 17334
[8 empty] | 17335 | Para_Exhaust_TCSpeed2Stage_4mA_A | Para_Exhaust_TCSpeed2Stage_4mA_A | 3624 | Para_Exhaust_TCSpeed2Stage_4mA_A |  | 17335
[8 empty] | 17336 | Para_Exhaust_TCSpeed2Stage_4mA_B | Para_Exhaust_TCSpeed2Stage_4mA_B | 3625 | Para_Exhaust_TCSpeed2Stage_4mA_B | 1000/min | 17336
[8 empty] | 17337 | Para_Exhaust_TCSpeed2Stage_ActTempOutlet_A | Para_Exhaust_TCSpeed2Stage_ActTempOutlet_A | 3626 | Para_Exhaust_TCSpeed2Stage_ActTempOutlet_A |  | 17337
[8 empty] | 17338 | Para_Exhaust_TCSpeed2Stage_ActTempOutlet_B | Para_Exhaust_TCSpeed2Stage_ActTempOutlet_B | 3627 | Para_Exhaust_TCSpeed2Stage_ActTempOutlet_B |  | 17338
[8 empty] | 17339 | Para_Exhaust_TCSpeed2Stage_IncLimit | Para_Exhaust_TCSpeed2Stage_IncLimit | 3628 | Para_Exhaust_TCSpeed2Stage_IncLimit | 1000/min | 17339
[8 empty] | 17340 | Para_Exhaust_TCSpeed2Stage_Limit | Para_Exhaust_TCSpeed2Stage_Limit | 3629 | Para_Exhaust_TCSpeed2Stage_Limit | 1000/min | 17340
[8 empty] | 17341 | Para_Exhaust_TCSpeed2Stage_LimitHys | Para_Exhaust_TCSpeed2Stage_LimitHys | 3630 | Para_Exhaust_TCSpeed2Stage_LimitHys |  | 17341
[8 empty] | 17342 | Para_Exhaust_TCSpeedA_20mA | Para_Exhaust_TCSpeedA_20mA | 3631 | Para_Exhaust_TCSpeedA_20mA |  | 17342
[8 empty] | 17343 | Para_Exhaust_TCSpeedA_4mA | Para_Exhaust_TCSpeedA_4mA | 3632 | Para_Exhaust_TCSpeedA_4mA |  | 17343
[8 empty] | 17344 | Para_Exhaust_TCSpeedA_Limit | Para_Exhaust_TCSpeedA_Limit | 3633 | Para_Exhaust_TCSpeedA_Limit |  | 17344
[8 empty] | 17345 | Para_Exhaust_TCSpeedA_LimitHys | Para_Exhaust_TCSpeedA_LimitHys | 3634 | Para_Exhaust_TCSpeedA_LimitHys |  | 17345
[8 empty] | 17346 | Para_Exhaust_TCSpeedB_20mA | Para_Exhaust_TCSpeedB_20mA | 3635 | Para_Exhaust_TCSpeedB_20mA |  | 17346
[8 empty] | 17347 | Para_Exhaust_TCSpeedB_4mA | Para_Exhaust_TCSpeedB_4mA | 3636 | Para_Exhaust_TCSpeedB_4mA |  | 17347
[8 empty] | 17348 | Para_Exhaust_TCSpeedB_Limit | Para_Exhaust_TCSpeedB_Limit | 3637 | Para_Exhaust_TCSpeedB_Limit |  | 17348
[8 empty] | 17349 | Para_Exhaust_TCSpeedB_LimitHys | Para_Exhaust_TCSpeedB_LimitHys | 3638 | Para_Exhaust_TCSpeedB_LimitHys |  | 17349
[8 empty] | 17350 | Para_Exhaust_TempBoilHys | Para_Exhaust_TempBoilHys | 3639 | Para_Exhaust_TempBoilHys | °C | 17350
[8 empty] | 17351 | Para_Exhaust_TempBoilInputMax | Para_Exhaust_TempBoilInputMax | 3640 | Para_Exhaust_TempBoilInputMax | °C | 17351
[8 empty] | 17352 | Para_Exhaust_TempBoilInputMin | Para_Exhaust_TempBoilInputMin | 3641 | Para_Exhaust_TempBoilInputMin | °C | 17352
[8 empty] | 17353 | Para_Exhaust_TempBoilTrip | Para_Exhaust_TempBoilTrip | 3642 | Para_Exhaust_TempBoilTrip | °C | 17353
[8 empty] | 17354 | Para_Exhaust_TempBoilWarning | Para_Exhaust_TempBoilWarning | 3643 | Para_Exhaust_TempBoilWarning | °C | 17354
[8 empty] | 17355 | Para_Exhaust_TempExhAvgDevNeg | Para_Exhaust_TempExhAvgDevNeg | 3644 | Para_Exhaust_TempExhAvgDevNeg | °C | 17355
[8 empty] | 17356 | Para_Exhaust_TempExhAvgDevPos | Para_Exhaust_TempExhAvgDevPos | 3645 | Para_Exhaust_TempExhAvgDevPos | °C | 17356
[8 empty] | 19477 | Para_Exhaust_TempExhAvgPnGr40 | Para_Exhaust_TempExhAvgPnGr40 | 3646 | Para_Exhaust_TempExhAvgPnGr40 | °C | 19477
[8 empty] | 17357 | Para_Exhaust_TempExhMaxPnGr40 | Para_Exhaust_TempExhMaxPnGr40 | 3647 | Para_Exhaust_TempExhMaxPnGr40 | °C | 17357
[8 empty] | 17358 | Para_Exhaust_TempExhMaxPnSm40 | Para_Exhaust_TempExhMaxPnSm40 | 3648 | Para_Exhaust_TempExhMaxPnSm40 | °C | 17358
[8 empty] | 17359 | Para_Exhaust_TempInHexHys | Para_Exhaust_TempInHexHys | 3649 | Para_Exhaust_TempInHexHys | °C | 17359
[8 empty] | 17360 | Para_Exhaust_TempInHexMax | Para_Exhaust_TempInHexMax | 3650 | Para_Exhaust_TempInHexMax |  | 17360
[8 empty] | 17361 | Para_Exhaust_TempInKatHys | Para_Exhaust_TempInKatHys | 3651 | Para_Exhaust_TempInKatHys | °C | 17361
[8 empty] | 17362 | Para_Exhaust_TempInKatMax | Para_Exhaust_TempInKatMax | 3652 | Para_Exhaust_TempInKatMax |  | 17362
[8 empty] | 17363 | Para_Exhaust_TempInTurboAlarm | Para_Exhaust_TempInTurboAlarm | 3653 | Para_Exhaust_TempInTurboAlarm |  | 17363
[8 empty] | 17364 | Para_Exhaust_TempInTurboAlarmHys | Para_Exhaust_TempInTurboAlarmHys | 3654 | Para_Exhaust_TempInTurboAlarmHys | °C | 17364
[8 empty] | 17365 | Para_Exhaust_TempInTurboMax | Para_Exhaust_TempInTurboMax | 3655 | Para_Exhaust_TempInTurboMax |  | 17365
[8 empty] | 17366 | Para_Exhaust_TempInTurboMaxHys | Para_Exhaust_TempInTurboMaxHys | 3656 | Para_Exhaust_TempInTurboMaxHys | °C | 17366
[8 empty] | 17367 | Para_Exhaust_TempKatAlarm | Para_Exhaust_TempKatAlarm | 3657 | Para_Exhaust_TempKatAlarm |  | 17367
[8 empty] | 17368 | Para_Exhaust_TempKatAlarmHys | Para_Exhaust_TempKatAlarmHys | 3658 | Para_Exhaust_TempKatAlarmHys | °C | 17368
[8 empty] | 17369 | Para_Exhaust_TempKatdTMax | Para_Exhaust_TempKatdTMax | 3659 | Para_Exhaust_TempKatdTMax |  | 17369
[8 empty] | 17370 | Para_Exhaust_TempKatdTRel | Para_Exhaust_TempKatdTRel | 3660 | Para_Exhaust_TempKatdTRel |  | 17370
[8 empty] | 17371 | Para_Exhaust_TempKatdTRelHys | Para_Exhaust_TempKatdTRelHys | 3661 | Para_Exhaust_TempKatdTRelHys | d°C | 17371
[8 empty] | 17372 | Para_Exhaust_TempKatHys | Para_Exhaust_TempKatHys | 3662 | Para_Exhaust_TempKatHys | d°C | 17372
[8 empty] | 17373 | Para_Exhaust_TempKatMax | Para_Exhaust_TempKatMax | 3663 | Para_Exhaust_TempKatMax |  | 17373
[8 empty] | 17374 | Para_Exhaust_TempOutHexHys | Para_Exhaust_TempOutHexHys | 3664 | Para_Exhaust_TempOutHexHys | °C | 17374
[8 empty] | 17375 | Para_Exhaust_TempOutHexMax | Para_Exhaust_TempOutHexMax | 3665 | Para_Exhaust_TempOutHexMax |  | 17375
[8 empty] | 17376 | Para_Exhaust_TempOutKatHys | Para_Exhaust_TempOutKatHys | 3666 | Para_Exhaust_TempOutKatHys | °C | 17376
[8 empty] | 17377 | Para_Exhaust_TempOutKatMax | Para_Exhaust_TempOutKatMax | 3667 | Para_Exhaust_TempOutKatMax |  | 17377
[8 empty] | 17378 | Para_Exhaust_TimeScavening | Para_Exhaust_TimeScavening | 3668 | Para_Exhaust_TimeScavening |  | 17378
[8 empty] | 10000390 | Para_Exhaust_ValveControl_EGValveRegulation | Para_Exhaust_ValveControl_EGValveRegulation | 3669 | Para_Exhaust_ValveControl_EGValveRegulation |  | 10000390
[8 empty] | 10000410 | Para_Exhaust_ValveControl_Sel_EGVa_Combi | Para_Exhaust_ValveControl_Sel_EGVa_Combi | 3670 | Para_Exhaust_ValveControl_Sel_EGVa_Combi |  | 10000410
[8 empty] | 10000412 | Para_Exhaust_ValveControl_Sel_EGVa_ROTORK | Para_Exhaust_ValveControl_Sel_EGVa_ROTORK | 3671 | Para_Exhaust_ValveControl_Sel_EGVa_ROTORK |  | 10000412
[8 empty] | 10000413 | Para_Exhaust_ValveControl_Sel_EGVa_Torque | Para_Exhaust_ValveControl_Sel_EGVa_Torque | 3672 | Para_Exhaust_ValveControl_Sel_EGVa_Torque |  | 10000413
[8 empty] | 10001276 | Para_Gas_Cnt_Gas_NormM3 | Para_Gas_Cnt_Gas_NormM3 | 3673 | Para_Gas_Cnt_Gas_NormM3 |  | 10001276
[8 empty] | 10001317 | Para_Gas_Cnt_Gas_OpM3 | Para_Gas_Cnt_Gas_OpM3 | 3674 | Para_Gas_Cnt_Gas_OpM3 |  | 10001317
[8 empty] | 10000284 | Para_Gas_Cnt_GasImp_Active | Para_Gas_Cnt_GasImp_Active | 3675 | Para_Gas_Cnt_GasImp_Active |  | 10000284
[8 empty] | 10002637 | Para_Gas_GasData_Gas1_HCR1 | Para_Gas_GasData_Gas1_HCR1 | 3676 | Para_Gas_GasData_Gas1_HCR1 |  | 10002637
[8 empty] | 10000163 | Para_Gas_GasData_Gas1_LHV1 | Para_Gas_GasData_Gas1_LHV1 | 3677 | Para_Gas_GasData_Gas1_LHV1 |  | 10000163
[8 empty] | 10002583 | Para_Gas_GasData_Gas1_MinAirReq1 | Para_Gas_GasData_Gas1_MinAirReq1 | 3678 | Para_Gas_GasData_Gas1_MinAirReq1 |  | 10002583
[8 empty] | 10002577 | Para_Gas_GasData_Gas1_StdGD1 | Para_Gas_GasData_Gas1_StdGD1 | 3679 | Para_Gas_GasData_Gas1_StdGD1 |  | 10002577
[8 empty] | 10002592 | Para_Gas_GasData_Gas2_HCR2 | Para_Gas_GasData_Gas2_HCR2 | 3680 | Para_Gas_GasData_Gas2_HCR2 |  | 10002592
[8 empty] | 10000165 | Para_Gas_GasData_Gas2_LHV2 | Para_Gas_GasData_Gas2_LHV2 | 3681 | Para_Gas_GasData_Gas2_LHV2 |  | 10000165
[8 empty] | 10002631 | Para_Gas_GasData_Gas2_MinAirReq2 | Para_Gas_GasData_Gas2_MinAirReq2 | 3682 | Para_Gas_GasData_Gas2_MinAirReq2 |  | 10002631
[8 empty] | 10002578 | Para_Gas_GasData_Gas2_StdGD2 | Para_Gas_GasData_Gas2_StdGD2 | 3683 | Para_Gas_GasData_Gas2_StdGD2 |  | 10002578
[8 empty] | 10002595 | Para_Gas_GasData_Gas3_HCR3 | Para_Gas_GasData_Gas3_HCR3 | 3684 | Para_Gas_GasData_Gas3_HCR3 |  | 10002595
[8 empty] | 10000164 | Para_Gas_GasData_Gas3_LHV3 | Para_Gas_GasData_Gas3_LHV3 | 3685 | Para_Gas_GasData_Gas3_LHV3 |  | 10000164
[8 empty] | 10002587 | Para_Gas_GasData_Gas3_MinAirReq3 | Para_Gas_GasData_Gas3_MinAirReq3 | 3686 | Para_Gas_GasData_Gas3_MinAirReq3 |  | 10002587
[8 empty] | 10002581 | Para_Gas_GasData_Gas3_StdGD3 | Para_Gas_GasData_Gas3_StdGD3 | 3687 | Para_Gas_GasData_Gas3_StdGD3 |  | 10002581
[8 empty] | 10002593 | Para_Gas_GasData_Gas4_HCR4 | Para_Gas_GasData_Gas4_HCR4 | 3688 | Para_Gas_GasData_Gas4_HCR4 |  | 10002593
[8 empty] | 10000168 | Para_Gas_GasData_Gas4_LHV4 | Para_Gas_GasData_Gas4_LHV4 | 3689 | Para_Gas_GasData_Gas4_LHV4 |  | 10000168
[8 empty] | 10002589 | Para_Gas_GasData_Gas4_MinAirReq4 | Para_Gas_GasData_Gas4_MinAirReq4 | 3690 | Para_Gas_GasData_Gas4_MinAirReq4 |  | 10002589
[8 empty] | 10002588 | Para_Gas_GasData_Gas4_StdGD4 | Para_Gas_GasData_Gas4_StdGD4 | 3691 | Para_Gas_GasData_Gas4_StdGD4 |  | 10002588
[8 empty] | 10000479 | Para_Gas_Gasmixer_Gas1_y1 | Para_Gas_Gasmixer_Gas1_y1 | 3692 | Para_Gas_Gasmixer_Gas1_y1 |  | 10000479
[8 empty] | 10000481 | Para_Gas_Gasmixer_Gas1_y2 | Para_Gas_Gasmixer_Gas1_y2 | 3693 | Para_Gas_Gasmixer_Gas1_y2 |  | 10000481
[8 empty] | 10000482 | Para_Gas_Gasmixer_Gas2_y1 | Para_Gas_Gasmixer_Gas2_y1 | 3694 | Para_Gas_Gasmixer_Gas2_y1 |  | 10000482
[8 empty] | 10000484 | Para_Gas_Gasmixer_Gas2_y2 | Para_Gas_Gasmixer_Gas2_y2 | 3695 | Para_Gas_Gasmixer_Gas2_y2 |  | 10000484
[8 empty] | 10000483 | Para_Gas_Gasmixer_Gas3_y1 | Para_Gas_Gasmixer_Gas3_y1 | 3696 | Para_Gas_Gasmixer_Gas3_y1 |  | 10000483
[8 empty] | 10000486 | Para_Gas_Gasmixer_Gas3_y2 | Para_Gas_Gasmixer_Gas3_y2 | 3697 | Para_Gas_Gasmixer_Gas3_y2 |  | 10000486
[8 empty] | 10000488 | Para_Gas_Gasmixer_Gas4_y1 | Para_Gas_Gasmixer_Gas4_y1 | 3698 | Para_Gas_Gasmixer_Gas4_y1 |  | 10000488
[8 empty] | 10000491 | Para_Gas_Gasmixer_Gas4_y2 | Para_Gas_Gasmixer_Gas4_y2 | 3699 | Para_Gas_Gasmixer_Gas4_y2 |  | 10000491
[8 empty] | 10008784 | Para_Gas_GasMixerSpecial_N_Eng_RunUpLim | Para_Gas_GasMixerSpecial_N_Eng_RunUpLim | 3700 | Para_Gas_GasMixerSpecial_N_Eng_RunUpLim |  | 10008784
[8 empty] | 10008783 | Para_Gas_GasMixerSpecial_Pos_GM_RunUpOffset | Para_Gas_GasMixerSpecial_Pos_GM_RunUpOffset | 3701 | Para_Gas_GasMixerSpecial_Pos_GM_RunUpOffset |  | 10008783
[8 empty] | 10000697 | Para_Gas_GasPropValve_Gas1_Lam_TJ_Power_Offs1 | Para_Gas_GasPropValve_Gas1_Lam_TJ_Power_Offs1 | 3702 | Para_Gas_GasPropValve_Gas1_Lam_TJ_Power_Offs1 |  | 10000697
[8 empty] | 10000575 | Para_Gas_GasPropValve_Gas1_Lam_TJ_Speed_Offs1 | Para_Gas_GasPropValve_Gas1_Lam_TJ_Speed_Offs1 | 3703 | Para_Gas_GasPropValve_Gas1_Lam_TJ_Speed_Offs1 |  | 10000575
[8 empty] | 10003120 | Para_Gas_GasPropValve_Gas1_x1 | Para_Gas_GasPropValve_Gas1_x1 | 3704 | Para_Gas_GasPropValve_Gas1_x1 |  | 10003120
[8 empty] | 10003698 | Para_Gas_GasPropValve_Gas1_x2 | Para_Gas_GasPropValve_Gas1_x2 | 3705 | Para_Gas_GasPropValve_Gas1_x2 |  | 10003698
[8 empty] | 10003718 | Para_Gas_GasPropValve_Gas1_y1 | Para_Gas_GasPropValve_Gas1_y1 | 3706 | Para_Gas_GasPropValve_Gas1_y1 |  | 10003718
[8 empty] | 10003054 | Para_Gas_GasPropValve_Gas1_y2 | Para_Gas_GasPropValve_Gas1_y2 | 3707 | Para_Gas_GasPropValve_Gas1_y2 |  | 10003054
[8 empty] | 10000698 | Para_Gas_GasPropValve_Gas2_Lam_TJ_Power_Offs2 | Para_Gas_GasPropValve_Gas2_Lam_TJ_Power_Offs2 | 3708 | Para_Gas_GasPropValve_Gas2_Lam_TJ_Power_Offs2 |  | 10000698
[8 empty] | 10000579 | Para_Gas_GasPropValve_Gas2_Lam_TJ_Speed_Offs2 | Para_Gas_GasPropValve_Gas2_Lam_TJ_Speed_Offs2 | 3709 | Para_Gas_GasPropValve_Gas2_Lam_TJ_Speed_Offs2 |  | 10000579
[8 empty] | 10003122 | Para_Gas_GasPropValve_Gas2_x1 | Para_Gas_GasPropValve_Gas2_x1 | 3710 | Para_Gas_GasPropValve_Gas2_x1 |  | 10003122
[8 empty] | 10003702 | Para_Gas_GasPropValve_Gas2_x2 | Para_Gas_GasPropValve_Gas2_x2 | 3711 | Para_Gas_GasPropValve_Gas2_x2 |  | 10003702
[8 empty] | 10003050 | Para_Gas_GasPropValve_Gas2_y1 | Para_Gas_GasPropValve_Gas2_y1 | 3712 | Para_Gas_GasPropValve_Gas2_y1 |  | 10003050
[8 empty] | 10003059 | Para_Gas_GasPropValve_Gas2_y2 | Para_Gas_GasPropValve_Gas2_y2 | 3713 | Para_Gas_GasPropValve_Gas2_y2 |  | 10003059
[8 empty] | 10000699 | Para_Gas_GasPropValve_Gas3_Lam_TJ_Power_Offs3 | Para_Gas_GasPropValve_Gas3_Lam_TJ_Power_Offs3 | 3714 | Para_Gas_GasPropValve_Gas3_Lam_TJ_Power_Offs3 |  | 10000699
[8 empty] | 10000587 | Para_Gas_GasPropValve_Gas3_Lam_TJ_Speed_Offs3 | Para_Gas_GasPropValve_Gas3_Lam_TJ_Speed_Offs3 | 3715 | Para_Gas_GasPropValve_Gas3_Lam_TJ_Speed_Offs3 |  | 10000587
[8 empty] | 10003121 | Para_Gas_GasPropValve_Gas3_x1 | Para_Gas_GasPropValve_Gas3_x1 | 3716 | Para_Gas_GasPropValve_Gas3_x1 |  | 10003121
[8 empty] | 10003701 | Para_Gas_GasPropValve_Gas3_x2 | Para_Gas_GasPropValve_Gas3_x2 | 3717 | Para_Gas_GasPropValve_Gas3_x2 |  | 10003701
[8 empty] | 10003056 | Para_Gas_GasPropValve_Gas3_y1 | Para_Gas_GasPropValve_Gas3_y1 | 3718 | Para_Gas_GasPropValve_Gas3_y1 |  | 10003056
[8 empty] | 10003060 | Para_Gas_GasPropValve_Gas3_y2 | Para_Gas_GasPropValve_Gas3_y2 | 3719 | Para_Gas_GasPropValve_Gas3_y2 |  | 10003060
[8 empty] | 10000701 | Para_Gas_GasPropValve_Gas4_Lam_TJ_Power_Offs4 | Para_Gas_GasPropValve_Gas4_Lam_TJ_Power_Offs4 | 3720 | Para_Gas_GasPropValve_Gas4_Lam_TJ_Power_Offs4 |  | 10000701
[8 empty] | 10000584 | Para_Gas_GasPropValve_Gas4_Lam_TJ_Speed_Offs4 | Para_Gas_GasPropValve_Gas4_Lam_TJ_Speed_Offs4 | 3721 | Para_Gas_GasPropValve_Gas4_Lam_TJ_Speed_Offs4 |  | 10000584
[8 empty] | 10003123 | Para_Gas_GasPropValve_Gas4_x1 | Para_Gas_GasPropValve_Gas4_x1 | 3722 | Para_Gas_GasPropValve_Gas4_x1 |  | 10003123
[8 empty] | 10003703 | Para_Gas_GasPropValve_Gas4_x2 | Para_Gas_GasPropValve_Gas4_x2 | 3723 | Para_Gas_GasPropValve_Gas4_x2 |  | 10003703
[8 empty] | 10003055 | Para_Gas_GasPropValve_Gas4_y1 | Para_Gas_GasPropValve_Gas4_y1 | 3724 | Para_Gas_GasPropValve_Gas4_y1 |  | 10003055
[8 empty] | 10003057 | Para_Gas_GasPropValve_Gas4_y2 | Para_Gas_GasPropValve_Gas4_y2 | 3725 | Para_Gas_GasPropValve_Gas4_y2 |  | 10003057
[8 empty] | 10001512 | Para_Gas_GasRail_Pr_GR_I_Exist | Para_Gas_GasRail_Pr_GR_I_Exist | 3726 | Para_Gas_GasRail_Pr_GR_I_Exist |  | 10001512
[8 empty] | 10001515 | Para_Gas_GasRail_Pr_GR_II_Exist | Para_Gas_GasRail_Pr_GR_II_Exist | 3727 | Para_Gas_GasRail_Pr_GR_II_Exist |  | 10001515
[8 empty] | 10002681 | Para_Gas_GasRail_Pr_GR_IScalMax | Para_Gas_GasRail_Pr_GR_IScalMax | 3728 | Para_Gas_GasRail_Pr_GR_IScalMax |  | 10002681
[8 empty] | 10002675 | Para_Gas_GasRail_Pr_GR_IScalMin | Para_Gas_GasRail_Pr_GR_IScalMin | 3729 | Para_Gas_GasRail_Pr_GR_IScalMin |  | 10002675
[8 empty] | 10001517 | Para_Gas_GasRail_T_GR_Exist | Para_Gas_GasRail_T_GR_Exist | 3730 | Para_Gas_GasRail_T_GR_Exist |  | 10001517
[8 empty] | 10001342 | Para_Gas_GasTrain_DPr_GR_BOV_Open_Hy | Para_Gas_GasTrain_DPr_GR_BOV_Open_Hy | 3731 | Para_Gas_GasTrain_DPr_GR_BOV_Open_Hy |  | 10001342
[8 empty] | 10001340 | Para_Gas_GasTrain_MGT_SetActAdjustActive | Para_Gas_GasTrain_MGT_SetActAdjustActive | 3732 | Para_Gas_GasTrain_MGT_SetActAdjustActive |  | 10001340
[8 empty] | 10001345 | Para_Gas_GasTrain_Pr_MGT_PipeLoss_Ch_P1 | Para_Gas_GasTrain_Pr_MGT_PipeLoss_Ch_P1 | 3733 | Para_Gas_GasTrain_Pr_MGT_PipeLoss_Ch_P1 |  | 10001345
[8 empty] | 10001335 | Para_Gas_GasTrain_Pr_MGT_PipeLoss_Ch_P2 | Para_Gas_GasTrain_Pr_MGT_PipeLoss_Ch_P2 | 3734 | Para_Gas_GasTrain_Pr_MGT_PipeLoss_Ch_P2 |  | 10001335
[8 empty] | 10001336 | Para_Gas_GasTrain_Pr_MGT_PipeLoss_P1 | Para_Gas_GasTrain_Pr_MGT_PipeLoss_P1 | 3735 | Para_Gas_GasTrain_Pr_MGT_PipeLoss_P1 |  | 10001336
[8 empty] | 10001338 | Para_Gas_GasTrain_Pr_MGT_PipeLoss_P2 | Para_Gas_GasTrain_Pr_MGT_PipeLoss_P2 | 3736 | Para_Gas_GasTrain_Pr_MGT_PipeLoss_P2 |  | 10001338
[8 empty] | 10001334 | Para_Gas_GasTrain_Pr_MGT_sp_offset | Para_Gas_GasTrain_Pr_MGT_sp_offset | 3737 | Para_Gas_GasTrain_Pr_MGT_sp_offset |  | 10001334
[8 empty] | 10001337 | Para_Gas_GasTrain_Pr_MGT_spScalMax | Para_Gas_GasTrain_Pr_MGT_spScalMax | 3738 | Para_Gas_GasTrain_Pr_MGT_spScalMax |  | 10001337
[8 empty] | 10001333 | Para_Gas_GasTrain_Pr_MGT_spScalMin | Para_Gas_GasTrain_Pr_MGT_spScalMin | 3739 | Para_Gas_GasTrain_Pr_MGT_spScalMin |  | 10001333
[8 empty] | 10001344 | Para_Gas_GasTrain_tiBOV_Open_Max | Para_Gas_GasTrain_tiBOV_Open_Max | 3740 | Para_Gas_GasTrain_tiBOV_Open_Max |  | 10001344
[8 empty] | 10001339 | Para_Gas_GasTrain_tiBOV_Open_Min | Para_Gas_GasTrain_tiBOV_Open_Min | 3741 | Para_Gas_GasTrain_tiBOV_Open_Min |  | 10001339
[8 empty] | 10000300 | Para_Gas_GCActive | Para_Gas_GCActive | 3742 | Para_Gas_GCActive |  | 10000300
[8 empty] | 10000125 | Para_Gas_GT_MixActive | Para_Gas_GT_MixActive | 3743 | Para_Gas_GT_MixActive |  | 10000125
[8 empty] | 10000128 | Para_Gas_GT_MixActiveEngStop | Para_Gas_GT_MixActiveEngStop | 3744 | Para_Gas_GT_MixActiveEngStop |  | 10000128
[8 empty] | 10000472 | Para_Gas_Num_GM | Para_Gas_Num_GM | 3745 | Para_Gas_Num_GM |  | 10000472
[8 empty] | 10000190 | Para_Gas_Num_GT1_Lines | Para_Gas_Num_GT1_Lines | 3746 | Para_Gas_Num_GT1_Lines |  | 10000190
[8 empty] | 10000127 | Para_Gas_P_GT_SetLim | Para_Gas_P_GT_SetLim | 3747 | Para_Gas_P_GT_SetLim |  | 10000127
[8 empty] | 10000302 | Para_Gas_Pr_GasPrAbsActive | Para_Gas_Pr_GasPrAbsActive | 3748 | Para_Gas_Pr_GasPrAbsActive |  | 10000302
[8 empty] | 10008204 | Para_Gas_PreChambDifPress_Pr_BlowOff_LimHi | Para_Gas_PreChambDifPress_Pr_BlowOff_LimHi | 3749 | Para_Gas_PreChambDifPress_Pr_BlowOff_LimHi |  | 10008204
[8 empty] | 10008367 | Para_Gas_PreChambGasTrain_PCGT_SafeDevice_Exist | Para_Gas_PreChambGasTrain_PCGT_SafeDevice_Exist | 3750 | Para_Gas_PreChambGasTrain_PCGT_SafeDevice_Exist |  | 10008367
[8 empty] | 10001341 | Para_Gas_PreChambGasTrain_PCGT_SetActAdjustActive | Para_Gas_PreChambGasTrain_PCGT_SetActAdjustActive | 3751 | Para_Gas_PreChambGasTrain_PCGT_SetActAdjustActive |  | 10001341
[8 empty] | 10001343 | Para_Gas_PreChambGasTrain_Pr_PCGT_Out_Exist | Para_Gas_PreChambGasTrain_Pr_PCGT_Out_Exist | 3752 | Para_Gas_PreChambGasTrain_Pr_PCGT_Out_Exist |  | 10001343
[8 empty] | 10001346 | Para_Gas_PreChambGasTrain_Pr_PCGT_OutScalMax | Para_Gas_PreChambGasTrain_Pr_PCGT_OutScalMax | 3753 | Para_Gas_PreChambGasTrain_Pr_PCGT_OutScalMax |  | 10001346
[8 empty] | 10001347 | Para_Gas_PreChambGasTrain_Pr_PCGT_OutScalMin | Para_Gas_PreChambGasTrain_Pr_PCGT_OutScalMin | 3754 | Para_Gas_PreChambGasTrain_Pr_PCGT_OutScalMin |  | 10001347
[8 empty] | 10000071 | Para_Gas_PreChambGasTrain_Pr_PCGT_sp_offset | Para_Gas_PreChambGasTrain_Pr_PCGT_sp_offset | 3755 | Para_Gas_PreChambGasTrain_Pr_PCGT_sp_offset |  | 10000071
[8 empty] | 10000076 | Para_Gas_PreChambGasTrain_Pr_PCGT_spScalMax | Para_Gas_PreChambGasTrain_Pr_PCGT_spScalMax | 3756 | Para_Gas_PreChambGasTrain_Pr_PCGT_spScalMax |  | 10000076
[8 empty] | 10000074 | Para_Gas_PreChambGasTrain_Pr_PCGT_spScalMin | Para_Gas_PreChambGasTrain_Pr_PCGT_spScalMin | 3757 | Para_Gas_PreChambGasTrain_Pr_PCGT_spScalMin |  | 10000074
[8 empty] | 10000116 | Para_Gas_PreChambGasTrain_T_PCGAfCo_Active | Para_Gas_PreChambGasTrain_T_PCGAfCo_Active | 3758 | Para_Gas_PreChambGasTrain_T_PCGAfCo_Active |  | 10000116
[8 empty] | 10000117 | Para_Gas_PreChambGasTrain_T_PCGAfCo_HyHi | Para_Gas_PreChambGasTrain_T_PCGAfCo_HyHi | 3759 | Para_Gas_PreChambGasTrain_T_PCGAfCo_HyHi |  | 10000117
[8 empty] | 10000118 | Para_Gas_PreChambGasTrain_T_PCGAfCo_LimHi | Para_Gas_PreChambGasTrain_T_PCGAfCo_LimHi | 3760 | Para_Gas_PreChambGasTrain_T_PCGAfCo_LimHi |  | 10000118
[8 empty] | 10008908 | Para_Gas_SpecGas_AdvGasPropValveStart_P_TJ_SG_Start_Norm | Para_Gas_SpecGas_AdvGasPropValveStart_P_TJ_SG_Start_Norm | 3761 | Para_Gas_SpecGas_AdvGasPropValveStart_P_TJ_SG_Start_Norm |  | 10008908
[8 empty] | 10008909 | Para_Gas_SpecGas_AdvGasPropValveStart_TJ_SG_Start1 | Para_Gas_SpecGas_AdvGasPropValveStart_TJ_SG_Start1 | 3762 | Para_Gas_SpecGas_AdvGasPropValveStart_TJ_SG_Start1 |  | 10008909
[8 empty] | 10008911 | Para_Gas_SpecGas_AdvGasPropValveStart_TJ_SG_Start2 | Para_Gas_SpecGas_AdvGasPropValveStart_TJ_SG_Start2 | 3763 | Para_Gas_SpecGas_AdvGasPropValveStart_TJ_SG_Start2 |  | 10008911
[8 empty] | 10008910 | Para_Gas_SpecGas_AdvGasPropValveStart_TJ_SG_Start3 | Para_Gas_SpecGas_AdvGasPropValveStart_TJ_SG_Start3 | 3764 | Para_Gas_SpecGas_AdvGasPropValveStart_TJ_SG_Start3 |  | 10008910
[8 empty] | 10008912 | Para_Gas_SpecGas_AdvGasPropValveStart_TJ_SG_Start4 | Para_Gas_SpecGas_AdvGasPropValveStart_TJ_SG_Start4 | 3765 | Para_Gas_SpecGas_AdvGasPropValveStart_TJ_SG_Start4 |  | 10008912
[8 empty] | 10008907 | Para_Gas_SpecGas_AdvGasPropValveStart_TJ_SG_Start_Ena | Para_Gas_SpecGas_AdvGasPropValveStart_TJ_SG_Start_Ena | 3766 | Para_Gas_SpecGas_AdvGasPropValveStart_TJ_SG_Start_Ena |  | 10008907
[8 empty] | 10000293 | Para_Gas_SpecGas_BioGas_BiogasActive | Para_Gas_SpecGas_BioGas_BiogasActive | 3767 | Para_Gas_SpecGas_BioGas_BiogasActive |  | 10000293
[8 empty] | 10000304 | Para_Gas_SpecGas_BioGas_Msg3327Active | Para_Gas_SpecGas_BioGas_Msg3327Active | 3768 | Para_Gas_SpecGas_BioGas_Msg3327Active |  | 10000304
[8 empty] | 10000295 | Para_Gas_SpecGas_BioGas_Msg3328Active | Para_Gas_SpecGas_BioGas_Msg3328Active | 3769 | Para_Gas_SpecGas_BioGas_Msg3328Active |  | 10000295
[8 empty] | 10000301 | Para_Gas_SpecGas_BioGas_Msg3567Active | Para_Gas_SpecGas_BioGas_Msg3567Active | 3770 | Para_Gas_SpecGas_BioGas_Msg3567Active |  | 10000301
[8 empty] | 10000289 | Para_Gas_SpecGas_BioGas_Msg3568Active | Para_Gas_SpecGas_BioGas_Msg3568Active | 3771 | Para_Gas_SpecGas_BioGas_Msg3568Active |  | 10000289
[8 empty] | 10000291 | Para_Gas_SpecGas_BioGas_Msg3569Active | Para_Gas_SpecGas_BioGas_Msg3569Active | 3772 | Para_Gas_SpecGas_BioGas_Msg3569Active |  | 10000291
[8 empty] | 10000287 | Para_Gas_SpecGas_BioGas_Msg3570Active | Para_Gas_SpecGas_BioGas_Msg3570Active | 3773 | Para_Gas_SpecGas_BioGas_Msg3570Active |  | 10000287
[8 empty] | 10008900 | Para_Gas_SpecGas_CBV34Control_CBV34_Fun | Para_Gas_SpecGas_CBV34Control_CBV34_Fun | 3774 | Para_Gas_SpecGas_CBV34Control_CBV34_Fun |  | 10008900
[8 empty] | 10008906 | Para_Gas_SpecGas_CBV34Control_CBV34_min | Para_Gas_SpecGas_CBV34Control_CBV34_min | 3775 | Para_Gas_SpecGas_CBV34Control_CBV34_min |  | 10008906
[8 empty] | 10008903 | Para_Gas_SpecGas_CBV34Control_CBV34_Set | Para_Gas_SpecGas_CBV34Control_CBV34_Set | 3776 | Para_Gas_SpecGas_CBV34Control_CBV34_Set |  | 10008903
[8 empty] | 10008905 | Para_Gas_SpecGas_CBV34Control_CBV34Ctr_ki | Para_Gas_SpecGas_CBV34Control_CBV34Ctr_ki | 3777 | Para_Gas_SpecGas_CBV34Control_CBV34Ctr_ki |  | 10008905
[8 empty] | 10008904 | Para_Gas_SpecGas_CBV34Control_CBV34Ctr_kp | Para_Gas_SpecGas_CBV34Control_CBV34Ctr_kp | 3778 | Para_Gas_SpecGas_CBV34Control_CBV34Ctr_kp |  | 10008904
[8 empty] | 10000072 | Para_Gas_SpecGas_GlowIgn_CA_SG_IP_Step | Para_Gas_SpecGas_GlowIgn_CA_SG_IP_Step | 3779 | Para_Gas_SpecGas_GlowIgn_CA_SG_IP_Step |  | 10000072
[8 empty] | 10008915 | Para_Gas_SpecGas_GlowIgn_FastPowerRed_FPRGasRed | Para_Gas_SpecGas_GlowIgn_FastPowerRed_FPRGasRed | 3780 | Para_Gas_SpecGas_GlowIgn_FastPowerRed_FPRGasRed |  | 10008915
[8 empty] | 10008913 | Para_Gas_SpecGas_GlowIgn_FastPowerRed_FPRGasRedOpt | Para_Gas_SpecGas_GlowIgn_FastPowerRed_FPRGasRedOpt | 3781 | Para_Gas_SpecGas_GlowIgn_FastPowerRed_FPRGasRedOpt |  | 10008913
[8 empty] | 10008916 | Para_Gas_SpecGas_GlowIgn_FastPowerRed_FPRGasRedTime | Para_Gas_SpecGas_GlowIgn_FastPowerRed_FPRGasRedTime | 3782 | Para_Gas_SpecGas_GlowIgn_FastPowerRed_FPRGasRedTime |  | 10008916
[8 empty] | 10008914 | Para_Gas_SpecGas_GlowIgn_FastPowerRed_Pos_SG_FPR_CBV | Para_Gas_SpecGas_GlowIgn_FastPowerRed_Pos_SG_FPR_CBV | 3783 | Para_Gas_SpecGas_GlowIgn_FastPowerRed_Pos_SG_FPR_CBV |  | 10008914
[8 empty] | 10001329 | Para_Gas_SpecGas_GlowIgn_FastPowerRed_Pos_SG_FPR_TV | Para_Gas_SpecGas_GlowIgn_FastPowerRed_Pos_SG_FPR_TV | 3784 | Para_Gas_SpecGas_GlowIgn_FastPowerRed_Pos_SG_FPR_TV |  | 10001329
[8 empty] | 10008918 | Para_Gas_SpecGas_GlowIgn_Pos_Gm_SG_Offs | Para_Gas_SpecGas_GlowIgn_Pos_Gm_SG_Offs | 3785 | Para_Gas_SpecGas_GlowIgn_Pos_Gm_SG_Offs |  | 10008918
[8 empty] | 10001359 | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_Num_SG_SCO_Max | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_Num_SG_SCO_Max | 3786 | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_Num_SG_SCO_Max |  | 10001359
[8 empty] | 10001363 | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_Num_SG_SCO_Max_DltT | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_Num_SG_SCO_Max_DltT | 3787 | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_Num_SG_SCO_Max_DltT |  | 10001363
[8 empty] | 10008917 | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_Pos_SG_SCO_CBV | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_Pos_SG_SCO_CBV | 3788 | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_Pos_SG_SCO_CBV |  | 10008917
[8 empty] | 10001355 | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_Pos_SG_SCO_TV | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_Pos_SG_SCO_TV | 3789 | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_Pos_SG_SCO_TV |  | 10001355
[8 empty] | 10001353 | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_SG_SCO_Active | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_SG_SCO_Active | 3790 | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_SG_SCO_Active |  | 10001353
[8 empty] | 10001362 | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_ti_SG_SCO_Block | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_ti_SG_SCO_Block | 3791 | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_ti_SG_SCO_Block |  | 10001362
[8 empty] | 10001357 | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_ti_SG_SCO_DurMonDis | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_ti_SG_SCO_DurMonDis | 3792 | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_ti_SG_SCO_DurMonDis |  | 10001357
[8 empty] | 10001360 | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_ti_SG_SCO_Max | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_ti_SG_SCO_Max | 3793 | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_ti_SG_SCO_Max |  | 10001360
[8 empty] | 10001358 | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_ti_SG_SCO_TV | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_ti_SG_SCO_TV | 3794 | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_ti_SG_SCO_TV |  | 10001358
[8 empty] | 10000693 | Para_Gas_SpecGas_GlowIgnPrevActive | Para_Gas_SpecGas_GlowIgnPrevActive | 3795 | Para_Gas_SpecGas_GlowIgnPrevActive |  | 10000693
[8 empty] | 10001361 | Para_Gas_SpecGas_SG_BackFirePrev | Para_Gas_SpecGas_SG_BackFirePrev | 3796 | Para_Gas_SpecGas_SG_BackFirePrev |  | 10001361
[8 empty] | 10000073 | Para_Gas_SpecGas_ti_SG_EngBlock | Para_Gas_SpecGas_ti_SG_EngBlock | 3797 | Para_Gas_SpecGas_ti_SG_EngBlock |  | 10000073
[8 empty] | 19478 | Para_GasData_Gas1_CalorificValue | Para_GasData_Gas1_CalorificValue | 3798 | Para_GasData_Gas1_CalorificValue | kWh/Nm3 | 19478
[8 empty] | 19479 | Para_GasData_Gas1_MinAirRequirement | Para_GasData_Gas1_MinAirRequirement | 3799 | Para_GasData_Gas1_MinAirRequirement | l/l | 19479
[8 empty] | 19480 | Para_GasData_Gas1_SpecificHeatRatio | Para_GasData_Gas1_SpecificHeatRatio | 3800 | Para_GasData_Gas1_SpecificHeatRatio |  | 19480
[8 empty] | 19481 | Para_GasData_Gas1_StandGasDens | Para_GasData_Gas1_StandGasDens | 3801 | Para_GasData_Gas1_StandGasDens | kg/m3 | 19481
[8 empty] | 19482 | Para_GasData_Gas2_CalorificValue | Para_GasData_Gas2_CalorificValue | 3802 | Para_GasData_Gas2_CalorificValue | kWh/Nm3 | 19482
[8 empty] | 19483 | Para_GasData_Gas2_MinAirRequirement | Para_GasData_Gas2_MinAirRequirement | 3803 | Para_GasData_Gas2_MinAirRequirement | l/l | 19483
[8 empty] | 19484 | Para_GasData_Gas2_SpecificHeatRatio | Para_GasData_Gas2_SpecificHeatRatio | 3804 | Para_GasData_Gas2_SpecificHeatRatio |  | 19484
[8 empty] | 19485 | Para_GasData_Gas2_StandGasDens | Para_GasData_Gas2_StandGasDens | 3805 | Para_GasData_Gas2_StandGasDens | kg/m3 | 19485
[8 empty] | 19486 | Para_GasData_Gas3_CalorificValue | Para_GasData_Gas3_CalorificValue | 3806 | Para_GasData_Gas3_CalorificValue | kWh/Nm3 | 19486
[8 empty] | 19487 | Para_GasData_Gas3_MinAirRequirement | Para_GasData_Gas3_MinAirRequirement | 3807 | Para_GasData_Gas3_MinAirRequirement | l/l | 19487
[8 empty] | 19488 | Para_GasData_Gas3_SpecificHeatRatio | Para_GasData_Gas3_SpecificHeatRatio | 3808 | Para_GasData_Gas3_SpecificHeatRatio |  | 19488
[8 empty] | 19489 | Para_GasData_Gas3_StandGasDens | Para_GasData_Gas3_StandGasDens | 3809 | Para_GasData_Gas3_StandGasDens | kg/m3 | 19489
[8 empty] | 19490 | Para_GasData_Gas4_CalorificValue | Para_GasData_Gas4_CalorificValue | 3810 | Para_GasData_Gas4_CalorificValue | kWh/Nm3 | 19490
[8 empty] | 19491 | Para_GasData_Gas4_MinAirRequirement | Para_GasData_Gas4_MinAirRequirement | 3811 | Para_GasData_Gas4_MinAirRequirement | l/l | 19491
[8 empty] | 19492 | Para_GasData_Gas4_SpecificHeatRatio | Para_GasData_Gas4_SpecificHeatRatio | 3812 | Para_GasData_Gas4_SpecificHeatRatio |  | 19492
[8 empty] | 19493 | Para_GasData_Gas4_StandGasDens | Para_GasData_Gas4_StandGasDens | 3813 | Para_GasData_Gas4_StandGasDens | kg/m3 | 19493
[8 empty] | 17398 | Para_Gasmixer_Gas1_AirTempPoint1 | Para_Gasmixer_Gas1_AirTempPoint1 | 3814 | Para_Gasmixer_Gas1_AirTempPoint1 |  | 17398
[8 empty] | 17399 | Para_Gasmixer_Gas1_AirTempPoint2 | Para_Gasmixer_Gas1_AirTempPoint2 | 3815 | Para_Gasmixer_Gas1_AirTempPoint2 |  | 17399
[8 empty] | 17400 | Para_Gasmixer_Gas1_GasMixPosOffsetIsland | Para_Gasmixer_Gas1_GasMixPosOffsetIsland | 3816 | Para_Gasmixer_Gas1_GasMixPosOffsetIsland | % | 17400
[8 empty] | 17401 | Para_Gasmixer_Gas1_GasMixPosOffsetNet | Para_Gasmixer_Gas1_GasMixPosOffsetNet | 3817 | Para_Gasmixer_Gas1_GasMixPosOffsetNet |  | 17401
[8 empty] | 17402 | Para_Gasmixer_Gas1_GasMixPosPoint1 | Para_Gasmixer_Gas1_GasMixPosPoint1 | 3818 | Para_Gasmixer_Gas1_GasMixPosPoint1 |  | 17402
[8 empty] | 17403 | Para_Gasmixer_Gas1_GasMixPosPoint2 | Para_Gasmixer_Gas1_GasMixPosPoint2 | 3819 | Para_Gasmixer_Gas1_GasMixPosPoint2 |  | 17403
[8 empty] | 17404 | Para_Gasmixer_Gas1_PosOffsetPoint1 | Para_Gasmixer_Gas1_PosOffsetPoint1 | 3820 | Para_Gasmixer_Gas1_PosOffsetPoint1 | % | 17404
[8 empty] | 17405 | Para_Gasmixer_Gas1_PosOffsetPoint2 | Para_Gasmixer_Gas1_PosOffsetPoint2 | 3821 | Para_Gasmixer_Gas1_PosOffsetPoint2 |  | 17405
[8 empty] | 17406 | Para_Gasmixer_Gas1_TempOilPoint1 | Para_Gasmixer_Gas1_TempOilPoint1 | 3822 | Para_Gasmixer_Gas1_TempOilPoint1 | °C | 17406
[8 empty] | 17407 | Para_Gasmixer_Gas1_TempOilPoint2 | Para_Gasmixer_Gas1_TempOilPoint2 | 3823 | Para_Gasmixer_Gas1_TempOilPoint2 | °C | 17407
[8 empty] | 17408 | Para_Gasmixer_Gas2_AirTempPoint1 | Para_Gasmixer_Gas2_AirTempPoint1 | 3824 | Para_Gasmixer_Gas2_AirTempPoint1 | °C | 17408
[8 empty] | 17409 | Para_Gasmixer_Gas2_AirTempPoint2 | Para_Gasmixer_Gas2_AirTempPoint2 | 3825 | Para_Gasmixer_Gas2_AirTempPoint2 | °C | 17409
[8 empty] | 17410 | Para_Gasmixer_Gas2_GasMixPosOffsetIsland | Para_Gasmixer_Gas2_GasMixPosOffsetIsland | 3826 | Para_Gasmixer_Gas2_GasMixPosOffsetIsland | % | 17410
[8 empty] | 17411 | Para_Gasmixer_Gas2_GasMixPosOffsetNet | Para_Gasmixer_Gas2_GasMixPosOffsetNet | 3827 | Para_Gasmixer_Gas2_GasMixPosOffsetNet | % | 17411
[8 empty] | 17412 | Para_Gasmixer_Gas2_GasMixPosPoint1 | Para_Gasmixer_Gas2_GasMixPosPoint1 | 3828 | Para_Gasmixer_Gas2_GasMixPosPoint1 |  | 17412
[8 empty] | 17413 | Para_Gasmixer_Gas2_GasMixPosPoint2 | Para_Gasmixer_Gas2_GasMixPosPoint2 | 3829 | Para_Gasmixer_Gas2_GasMixPosPoint2 |  | 17413
[8 empty] | 17414 | Para_Gasmixer_Gas2_PosOffsetPoint1 | Para_Gasmixer_Gas2_PosOffsetPoint1 | 3830 | Para_Gasmixer_Gas2_PosOffsetPoint1 | % | 17414
[8 empty] | 17415 | Para_Gasmixer_Gas2_PosOffsetPoint2 | Para_Gasmixer_Gas2_PosOffsetPoint2 | 3831 | Para_Gasmixer_Gas2_PosOffsetPoint2 | % | 17415
[8 empty] | 17416 | Para_Gasmixer_Gas2_TempOilPoint1 | Para_Gasmixer_Gas2_TempOilPoint1 | 3832 | Para_Gasmixer_Gas2_TempOilPoint1 |  | 17416
[8 empty] | 17417 | Para_Gasmixer_Gas2_TempOilPoint2 | Para_Gasmixer_Gas2_TempOilPoint2 | 3833 | Para_Gasmixer_Gas2_TempOilPoint2 |  | 17417
[8 empty] | 17418 | Para_Gasmixer_Gas3_AirTempPoint1 | Para_Gasmixer_Gas3_AirTempPoint1 | 3834 | Para_Gasmixer_Gas3_AirTempPoint1 | °C | 17418
[8 empty] | 17419 | Para_Gasmixer_Gas3_AirTempPoint2 | Para_Gasmixer_Gas3_AirTempPoint2 | 3835 | Para_Gasmixer_Gas3_AirTempPoint2 | °C | 17419
[8 empty] | 17420 | Para_Gasmixer_Gas3_GasMixPosOffsetIsland | Para_Gasmixer_Gas3_GasMixPosOffsetIsland | 3836 | Para_Gasmixer_Gas3_GasMixPosOffsetIsland |  | 17420
[8 empty] | 17421 | Para_Gasmixer_Gas3_GasMixPosOffsetNet | Para_Gasmixer_Gas3_GasMixPosOffsetNet | 3837 | Para_Gasmixer_Gas3_GasMixPosOffsetNet | % | 17421
[8 empty] | 17422 | Para_Gasmixer_Gas3_GasMixPosPoint1 | Para_Gasmixer_Gas3_GasMixPosPoint1 | 3838 | Para_Gasmixer_Gas3_GasMixPosPoint1 |  | 17422
[8 empty] | 17423 | Para_Gasmixer_Gas3_GasMixPosPoint2 | Para_Gasmixer_Gas3_GasMixPosPoint2 | 3839 | Para_Gasmixer_Gas3_GasMixPosPoint2 |  | 17423
[8 empty] | 17424 | Para_Gasmixer_Gas3_PosOffsetPoint1 | Para_Gasmixer_Gas3_PosOffsetPoint1 | 3840 | Para_Gasmixer_Gas3_PosOffsetPoint1 | % | 17424
[8 empty] | 17425 | Para_Gasmixer_Gas3_PosOffsetPoint2 | Para_Gasmixer_Gas3_PosOffsetPoint2 | 3841 | Para_Gasmixer_Gas3_PosOffsetPoint2 | % | 17425
[8 empty] | 17426 | Para_Gasmixer_Gas3_TempOilPoint1 | Para_Gasmixer_Gas3_TempOilPoint1 | 3842 | Para_Gasmixer_Gas3_TempOilPoint1 | °C | 17426
[8 empty] | 17427 | Para_Gasmixer_Gas3_TempOilPoint2 | Para_Gasmixer_Gas3_TempOilPoint2 | 3843 | Para_Gasmixer_Gas3_TempOilPoint2 | °C | 17427
[8 empty] | 17428 | Para_Gasmixer_Gas4_AirTempPoint1 | Para_Gasmixer_Gas4_AirTempPoint1 | 3844 | Para_Gasmixer_Gas4_AirTempPoint1 | °C | 17428
[8 empty] | 17429 | Para_Gasmixer_Gas4_AirTempPoint2 | Para_Gasmixer_Gas4_AirTempPoint2 | 3845 | Para_Gasmixer_Gas4_AirTempPoint2 | °C | 17429
[8 empty] | 17430 | Para_Gasmixer_Gas4_GasMixPosOffsetIsland | Para_Gasmixer_Gas4_GasMixPosOffsetIsland | 3846 | Para_Gasmixer_Gas4_GasMixPosOffsetIsland | % | 17430
[8 empty] | 17431 | Para_Gasmixer_Gas4_GasMixPosOffsetNet | Para_Gasmixer_Gas4_GasMixPosOffsetNet | 3847 | Para_Gasmixer_Gas4_GasMixPosOffsetNet | % | 17431
[8 empty] | 17432 | Para_Gasmixer_Gas4_GasMixPosPoint1 | Para_Gasmixer_Gas4_GasMixPosPoint1 | 3848 | Para_Gasmixer_Gas4_GasMixPosPoint1 | % | 17432
[8 empty] | 17433 | Para_Gasmixer_Gas4_GasMixPosPoint2 | Para_Gasmixer_Gas4_GasMixPosPoint2 | 3849 | Para_Gasmixer_Gas4_GasMixPosPoint2 | % | 17433
[8 empty] | 17434 | Para_Gasmixer_Gas4_PosOffsetPoint1 | Para_Gasmixer_Gas4_PosOffsetPoint1 | 3850 | Para_Gasmixer_Gas4_PosOffsetPoint1 |  | 17434
[8 empty] | 17435 | Para_Gasmixer_Gas4_PosOffsetPoint2 | Para_Gasmixer_Gas4_PosOffsetPoint2 | 3851 | Para_Gasmixer_Gas4_PosOffsetPoint2 | % | 17435
[8 empty] | 17436 | Para_Gasmixer_Gas4_TempOilPoint1 | Para_Gasmixer_Gas4_TempOilPoint1 | 3852 | Para_Gasmixer_Gas4_TempOilPoint1 | °C | 17436
[8 empty] | 17437 | Para_Gasmixer_Gas4_TempOilPoint2 | Para_Gasmixer_Gas4_TempOilPoint2 | 3853 | Para_Gasmixer_Gas4_TempOilPoint2 | °C | 17437
[8 empty] | 17438 | Para_Gasmixer_IdleLambdaCtr_Delay1 | Para_Gasmixer_IdleLambdaCtr_Delay1 | 3854 | Para_Gasmixer_IdleLambdaCtr_Delay1 | s | 17438
[8 empty] | 17439 | Para_Gasmixer_IdleLambdaCtr_Delay2 | Para_Gasmixer_IdleLambdaCtr_Delay2 | 3855 | Para_Gasmixer_IdleLambdaCtr_Delay2 | s | 17439
[8 empty] | 17440 | Para_Gasmixer_IdleLambdaCtr_Gas1_GasMixPosDP | Para_Gasmixer_IdleLambdaCtr_Gas1_GasMixPosDP | 3856 | Para_Gasmixer_IdleLambdaCtr_Gas1_GasMixPosDP | % | 17440
[8 empty] | 17441 | Para_Gasmixer_IdleLambdaCtr_Gas1_TrPos | Para_Gasmixer_IdleLambdaCtr_Gas1_TrPos | 3857 | Para_Gasmixer_IdleLambdaCtr_Gas1_TrPos | % | 17441
[8 empty] | 17442 | Para_Gasmixer_IdleLambdaCtr_Gas2_GasMixPosDP | Para_Gasmixer_IdleLambdaCtr_Gas2_GasMixPosDP | 3858 | Para_Gasmixer_IdleLambdaCtr_Gas2_GasMixPosDP | % | 17442
[8 empty] | 17443 | Para_Gasmixer_IdleLambdaCtr_Gas2_TrPos | Para_Gasmixer_IdleLambdaCtr_Gas2_TrPos | 3859 | Para_Gasmixer_IdleLambdaCtr_Gas2_TrPos | % | 17443
[8 empty] | 17444 | Para_Gasmixer_IdleLambdaCtr_Gas3_GasMixPosDP | Para_Gasmixer_IdleLambdaCtr_Gas3_GasMixPosDP | 3860 | Para_Gasmixer_IdleLambdaCtr_Gas3_GasMixPosDP | % | 17444
[8 empty] | 17445 | Para_Gasmixer_IdleLambdaCtr_Gas3_TrPos | Para_Gasmixer_IdleLambdaCtr_Gas3_TrPos | 3861 | Para_Gasmixer_IdleLambdaCtr_Gas3_TrPos | % | 17445
[8 empty] | 17446 | Para_Gasmixer_IdleLambdaCtr_Gas4_GasMixPosDP | Para_Gasmixer_IdleLambdaCtr_Gas4_GasMixPosDP | 3862 | Para_Gasmixer_IdleLambdaCtr_Gas4_GasMixPosDP | % | 17446
[8 empty] | 17447 | Para_Gasmixer_IdleLambdaCtr_Gas4_TrPos | Para_Gasmixer_IdleLambdaCtr_Gas4_TrPos | 3863 | Para_Gasmixer_IdleLambdaCtr_Gas4_TrPos | % | 17447
[8 empty] | 17448 | Para_Gasmixer_IdleLambdaCtr_IComp | Para_Gasmixer_IdleLambdaCtr_IComp | 3864 | Para_Gasmixer_IdleLambdaCtr_IComp |  | 17448
[8 empty] | 17449 | Para_Gasmixer_IdleLambdaCtr_PComp | Para_Gasmixer_IdleLambdaCtr_PComp | 3865 | Para_Gasmixer_IdleLambdaCtr_PComp |  | 17449
[8 empty] | 17450 | Para_Gasmixer_LimitAirTempMax | Para_Gasmixer_LimitAirTempMax | 3866 | Para_Gasmixer_LimitAirTempMax | °C | 17450
[8 empty] | 17451 | Para_Gasmixer_LimitAirTempMin | Para_Gasmixer_LimitAirTempMin | 3867 | Para_Gasmixer_LimitAirTempMin | °C | 17451
[8 empty] | 17452 | Para_Gasmixer_Special_FullStepAirThrot1 | Para_Gasmixer_Special_FullStepAirThrot1 | 3868 | Para_Gasmixer_Special_FullStepAirThrot1 |  | 17452
[8 empty] | 17453 | Para_Gasmixer_Special_FullStepAirThrot2 | Para_Gasmixer_Special_FullStepAirThrot2 | 3869 | Para_Gasmixer_Special_FullStepAirThrot2 |  | 17453
[8 empty] | 17454 | Para_Gasmixer_Special_FullStepGasThrot | Para_Gasmixer_Special_FullStepGasThrot | 3870 | Para_Gasmixer_Special_FullStepGasThrot |  | 17454
[8 empty] | 17455 | Para_Gasmixer_Special_Gas1_AirThrotFull | Para_Gasmixer_Special_Gas1_AirThrotFull | 3871 | Para_Gasmixer_Special_Gas1_AirThrotFull | mm | 17455
[8 empty] | 17456 | Para_Gasmixer_Special_Gas1_OfAirThrotIdle | Para_Gasmixer_Special_Gas1_OfAirThrotIdle | 3872 | Para_Gasmixer_Special_Gas1_OfAirThrotIdle | mm | 17456
[8 empty] | 17457 | Para_Gasmixer_Special_Gas1_OfAirThrotNetp | Para_Gasmixer_Special_Gas1_OfAirThrotNetp | 3873 | Para_Gasmixer_Special_Gas1_OfAirThrotNetp | mm | 17457
[8 empty] | 17458 | Para_Gasmixer_Special_Gas1_OfAirThrotStart | Para_Gasmixer_Special_Gas1_OfAirThrotStart | 3874 | Para_Gasmixer_Special_Gas1_OfAirThrotStart | mm | 17458
[8 empty] | 17459 | Para_Gasmixer_Special_Gas2_AirThrotFull | Para_Gasmixer_Special_Gas2_AirThrotFull | 3875 | Para_Gasmixer_Special_Gas2_AirThrotFull |  | 17459
[8 empty] | 17460 | Para_Gasmixer_Special_Gas2_OfAirThrotIdle | Para_Gasmixer_Special_Gas2_OfAirThrotIdle | 3876 | Para_Gasmixer_Special_Gas2_OfAirThrotIdle |  | 17460
[8 empty] | 17461 | Para_Gasmixer_Special_Gas2_OfAirThrotNetp | Para_Gasmixer_Special_Gas2_OfAirThrotNetp | 3877 | Para_Gasmixer_Special_Gas2_OfAirThrotNetp |  | 17461
[8 empty] | 17462 | Para_Gasmixer_Special_Gas2_OfAirThrotStart | Para_Gasmixer_Special_Gas2_OfAirThrotStart | 3878 | Para_Gasmixer_Special_Gas2_OfAirThrotStart |  | 17462
[8 empty] | 17463 | Para_Gasmixer_Special_Gas3_AirThrotFull | Para_Gasmixer_Special_Gas3_AirThrotFull | 3879 | Para_Gasmixer_Special_Gas3_AirThrotFull |  | 17463
[8 empty] | 17464 | Para_Gasmixer_Special_Gas3_OfAirThrotIdle | Para_Gasmixer_Special_Gas3_OfAirThrotIdle | 3880 | Para_Gasmixer_Special_Gas3_OfAirThrotIdle |  | 17464
[8 empty] | 17465 | Para_Gasmixer_Special_Gas3_OfAirThrotNetp | Para_Gasmixer_Special_Gas3_OfAirThrotNetp | 3881 | Para_Gasmixer_Special_Gas3_OfAirThrotNetp |  | 17465
[8 empty] | 17466 | Para_Gasmixer_Special_Gas3_OfAirThrotStart | Para_Gasmixer_Special_Gas3_OfAirThrotStart | 3882 | Para_Gasmixer_Special_Gas3_OfAirThrotStart |  | 17466
[8 empty] | 17467 | Para_Gasmixer_Special_Gas4_AirThrotFull | Para_Gasmixer_Special_Gas4_AirThrotFull | 3883 | Para_Gasmixer_Special_Gas4_AirThrotFull |  | 17467
[8 empty] | 17468 | Para_Gasmixer_Special_Gas4_OfAirThrotIdle | Para_Gasmixer_Special_Gas4_OfAirThrotIdle | 3884 | Para_Gasmixer_Special_Gas4_OfAirThrotIdle |  | 17468
[8 empty] | 17469 | Para_Gasmixer_Special_Gas4_OfAirThrotNetp | Para_Gasmixer_Special_Gas4_OfAirThrotNetp | 3885 | Para_Gasmixer_Special_Gas4_OfAirThrotNetp |  | 17469
[8 empty] | 17470 | Para_Gasmixer_Special_Gas4_OfAirThrotStart | Para_Gasmixer_Special_Gas4_OfAirThrotStart | 3886 | Para_Gasmixer_Special_Gas4_OfAirThrotStart |  | 17470
[8 empty] | 17471 | Para_Gasmixer_Special_SpeedAirThrot1 | Para_Gasmixer_Special_SpeedAirThrot1 | 3887 | Para_Gasmixer_Special_SpeedAirThrot1 |  | 17471
[8 empty] | 17472 | Para_Gasmixer_Special_SpeedAirThrot2 | Para_Gasmixer_Special_SpeedAirThrot2 | 3888 | Para_Gasmixer_Special_SpeedAirThrot2 |  | 17472
[8 empty] | 17473 | Para_Gasmixer_Special_SpeedGasThrot | Para_Gasmixer_Special_SpeedGasThrot | 3889 | Para_Gasmixer_Special_SpeedGasThrot |  | 17473
[8 empty] | 17474 | Para_Gasmixer_StepFrequency | Para_Gasmixer_StepFrequency | 3890 | Para_Gasmixer_StepFrequency | Hz | 17474
[8 empty] | 17475 | Para_Gasmixer_StepFrequency1 | Para_Gasmixer_StepFrequency1 | 3891 | Para_Gasmixer_StepFrequency1 | Hz | 17475
[8 empty] | 17476 | Para_Gasmixer_StepsGasmixPos | Para_Gasmixer_StepsGasmixPos | 3892 | Para_Gasmixer_StepsGasmixPos |  | 17476
[8 empty] | 17477 | Para_Gasmixer_StepsGasmixPos1 | Para_Gasmixer_StepsGasmixPos1 | 3893 | Para_Gasmixer_StepsGasmixPos1 |  | 17477
[8 empty] | 17478 | Para_Gasmixer_TempOilMax | Para_Gasmixer_TempOilMax | 3894 | Para_Gasmixer_TempOilMax | °C | 17478
[8 empty] | 17479 | Para_Gasmixer_TempOilMin | Para_Gasmixer_TempOilMin | 3895 | Para_Gasmixer_TempOilMin | °C | 17479
[8 empty] | 17480 | Para_GeneratCtr_ChoiceSet_ExtmAneg | Para_GeneratCtr_ChoiceSet_ExtmAneg | 3896 | Para_GeneratCtr_ChoiceSet_ExtmAneg | mA | 17480
[8 empty] | 17481 | Para_GeneratCtr_ChoiceSet_ExtmApos | Para_GeneratCtr_ChoiceSet_ExtmApos | 3897 | Para_GeneratCtr_ChoiceSet_ExtmApos | mA | 17481
[8 empty] | 17482 | Para_GeneratCtr_ChoiceSet_ExtPF1fix | Para_GeneratCtr_ChoiceSet_ExtPF1fix | 3898 | Para_GeneratCtr_ChoiceSet_ExtPF1fix |  | 17482
[8 empty] | 17483 | Para_GeneratCtr_ChoiceSet_ExtPF2fix | Para_GeneratCtr_ChoiceSet_ExtPF2fix | 3899 | Para_GeneratCtr_ChoiceSet_ExtPF2fix |  | 17483
[8 empty] | 17484 | Para_GeneratCtr_ChoiceSet_ExtPF3fix | Para_GeneratCtr_ChoiceSet_ExtPF3fix | 3900 | Para_GeneratCtr_ChoiceSet_ExtPF3fix |  | 17484
[8 empty] | 17485 | Para_GeneratCtr_ChoiceSet_ExtPF4fix | Para_GeneratCtr_ChoiceSet_ExtPF4fix | 3901 | Para_GeneratCtr_ChoiceSet_ExtPF4fix |  | 17485
[8 empty] | 17486 | Para_GeneratCtr_ChoiceSet_ExtPF5fix | Para_GeneratCtr_ChoiceSet_ExtPF5fix | 3902 | Para_GeneratCtr_ChoiceSet_ExtPF5fix |  | 17486
[8 empty] | 17487 | Para_GeneratCtr_ChoiceSet_ExtSetPF1 | Para_GeneratCtr_ChoiceSet_ExtSetPF1 | 3903 | Para_GeneratCtr_ChoiceSet_ExtSetPF1 |  | 17487
[8 empty] | 17488 | Para_GeneratCtr_ChoiceSet_ExtSetPF2 | Para_GeneratCtr_ChoiceSet_ExtSetPF2 | 3904 | Para_GeneratCtr_ChoiceSet_ExtSetPF2 |  | 17488
[8 empty] | 17489 | Para_GeneratCtr_ChoiceSet_PFIntern | Para_GeneratCtr_ChoiceSet_PFIntern | 3905 | Para_GeneratCtr_ChoiceSet_PFIntern |  | 17489
[8 empty] | 17490 | Para_GeneratCtr_ChoiceSet_Type | Para_GeneratCtr_ChoiceSet_Type | 3906 | Para_GeneratCtr_ChoiceSet_Type |  | 17490
[8 empty] | 17491 | Para_GeneratCtr_PowerDep_PFPowPoint1 | Para_GeneratCtr_PowerDep_PFPowPoint1 | 3907 | Para_GeneratCtr_PowerDep_PFPowPoint1 |  | 17491
[8 empty] | 17492 | Para_GeneratCtr_PowerDep_PFPowPoint2 | Para_GeneratCtr_PowerDep_PFPowPoint2 | 3908 | Para_GeneratCtr_PowerDep_PFPowPoint2 |  | 17492
[8 empty] | 17493 | Para_GeneratCtr_PowerDep_PowPoint1 | Para_GeneratCtr_PowerDep_PowPoint1 | 3909 | Para_GeneratCtr_PowerDep_PowPoint1 | % Pnom | 17493
[8 empty] | 17494 | Para_GeneratCtr_PowerDep_PowPoint2 | Para_GeneratCtr_PowerDep_PowPoint2 | 3910 | Para_GeneratCtr_PowerDep_PowPoint2 | % Pnom | 17494
[8 empty] | 17495 | Para_GeneratCtr_QLimit_AppPowNom | Para_GeneratCtr_QLimit_AppPowNom | 3911 | Para_GeneratCtr_QLimit_AppPowNom | kVA | 17495
[8 empty] | 17496 | Para_GeneratCtr_QLimit_PolarWheelLimit | Para_GeneratCtr_QLimit_PolarWheelLimit | 3912 | Para_GeneratCtr_QLimit_PolarWheelLimit | ° | 17496
[8 empty] | 17497 | Para_GeneratCtr_QLimit_PolarWheelTrip | Para_GeneratCtr_QLimit_PolarWheelTrip | 3913 | Para_GeneratCtr_QLimit_PolarWheelTrip | ° | 17497
[8 empty] | 17498 | Para_GeneratCtr_QLimit_SyncReakt | Para_GeneratCtr_QLimit_SyncReakt | 3914 | Para_GeneratCtr_QLimit_SyncReakt |  | 17498
[8 empty] | 17499 | Para_GeneratCtr_TimeTable_PFTimePoint1 | Para_GeneratCtr_TimeTable_PFTimePoint1 | 3915 | Para_GeneratCtr_TimeTable_PFTimePoint1 |  | 17499
[8 empty] | 17500 | Para_GeneratCtr_TimeTable_PFTimePoint2 | Para_GeneratCtr_TimeTable_PFTimePoint2 | 3916 | Para_GeneratCtr_TimeTable_PFTimePoint2 |  | 17500
[8 empty] | 17501 | Para_GeneratCtr_TimeTable_PFTimePoint3 | Para_GeneratCtr_TimeTable_PFTimePoint3 | 3917 | Para_GeneratCtr_TimeTable_PFTimePoint3 |  | 17501
[8 empty] | 17502 | Para_GeneratCtr_TimeTable_PFTimePoint4 | Para_GeneratCtr_TimeTable_PFTimePoint4 | 3918 | Para_GeneratCtr_TimeTable_PFTimePoint4 |  | 17502
[8 empty] | 17503 | Para_GeneratCtr_TimeTable_PFTimePoint5 | Para_GeneratCtr_TimeTable_PFTimePoint5 | 3919 | Para_GeneratCtr_TimeTable_PFTimePoint5 |  | 17503
[8 empty] | 17504 | Para_GeneratCtr_TimeTable_PFTimePoint6 | Para_GeneratCtr_TimeTable_PFTimePoint6 | 3920 | Para_GeneratCtr_TimeTable_PFTimePoint6 |  | 17504
[8 empty] | 17505 | Para_GeneratCtr_TimeTable_TimePoint1h | Para_GeneratCtr_TimeTable_TimePoint1h | 3921 | Para_GeneratCtr_TimeTable_TimePoint1h | h | 17505
[8 empty] | 17506 | Para_GeneratCtr_TimeTable_TimePoint1m | Para_GeneratCtr_TimeTable_TimePoint1m | 3922 | Para_GeneratCtr_TimeTable_TimePoint1m | m | 17506
[8 empty] | 17507 | Para_GeneratCtr_TimeTable_TimePoint2h | Para_GeneratCtr_TimeTable_TimePoint2h | 3923 | Para_GeneratCtr_TimeTable_TimePoint2h | h | 17507
[8 empty] | 17508 | Para_GeneratCtr_TimeTable_TimePoint2m | Para_GeneratCtr_TimeTable_TimePoint2m | 3924 | Para_GeneratCtr_TimeTable_TimePoint2m | m | 17508
[8 empty] | 17509 | Para_GeneratCtr_TimeTable_TimePoint3h | Para_GeneratCtr_TimeTable_TimePoint3h | 3925 | Para_GeneratCtr_TimeTable_TimePoint3h | h | 17509
[8 empty] | 17510 | Para_GeneratCtr_TimeTable_TimePoint3m | Para_GeneratCtr_TimeTable_TimePoint3m | 3926 | Para_GeneratCtr_TimeTable_TimePoint3m | m | 17510
[8 empty] | 17511 | Para_GeneratCtr_TimeTable_TimePoint4h | Para_GeneratCtr_TimeTable_TimePoint4h | 3927 | Para_GeneratCtr_TimeTable_TimePoint4h | h | 17511
[8 empty] | 17512 | Para_GeneratCtr_TimeTable_TimePoint4m | Para_GeneratCtr_TimeTable_TimePoint4m | 3928 | Para_GeneratCtr_TimeTable_TimePoint4m | m | 17512
[8 empty] | 17513 | Para_GeneratCtr_TimeTable_TimePoint5h | Para_GeneratCtr_TimeTable_TimePoint5h | 3929 | Para_GeneratCtr_TimeTable_TimePoint5h | h | 17513
[8 empty] | 17514 | Para_GeneratCtr_TimeTable_TimePoint5m | Para_GeneratCtr_TimeTable_TimePoint5m | 3930 | Para_GeneratCtr_TimeTable_TimePoint5m | m | 17514
[8 empty] | 17515 | Para_GeneratCtr_TimeTable_TimePoint6h | Para_GeneratCtr_TimeTable_TimePoint6h | 3931 | Para_GeneratCtr_TimeTable_TimePoint6h | h | 17515
[8 empty] | 17516 | Para_GeneratCtr_TimeTable_TimePoint6m | Para_GeneratCtr_TimeTable_TimePoint6m | 3932 | Para_GeneratCtr_TimeTable_TimePoint6m | m | 17516
[8 empty] | 17517 | Para_GeneratCtr_Type | Para_GeneratCtr_Type | 3933 | Para_GeneratCtr_Type |  | 17517
[8 empty] | 17518 | Para_GeneratCtr_Voltage_ActVoltAdjust | Para_GeneratCtr_Voltage_ActVoltAdjust | 3934 | Para_GeneratCtr_Voltage_ActVoltAdjust |  | 17518
[8 empty] | 17519 | Para_GeneratCtr_Voltage_MaxVoltAdjNeg | Para_GeneratCtr_Voltage_MaxVoltAdjNeg | 3935 | Para_GeneratCtr_Voltage_MaxVoltAdjNeg | % | 17519
[8 empty] | 17520 | Para_GeneratCtr_Voltage_MaxVoltAdjPos | Para_GeneratCtr_Voltage_MaxVoltAdjPos | 3936 | Para_GeneratCtr_Voltage_MaxVoltAdjPos | % | 17520
[8 empty] | 17521 | Para_GeneratCtr_Voltage_PFVoltPoint1 | Para_GeneratCtr_Voltage_PFVoltPoint1 | 3937 | Para_GeneratCtr_Voltage_PFVoltPoint1 |  | 17521
[8 empty] | 17522 | Para_GeneratCtr_Voltage_PFVoltPoint2 | Para_GeneratCtr_Voltage_PFVoltPoint2 | 3938 | Para_GeneratCtr_Voltage_PFVoltPoint2 |  | 17522
[8 empty] | 17523 | Para_GeneratCtr_Voltage_PFVoltPoint3 | Para_GeneratCtr_Voltage_PFVoltPoint3 | 3939 | Para_GeneratCtr_Voltage_PFVoltPoint3 |  | 17523
[8 empty] | 17524 | Para_GeneratCtr_Voltage_PFVoltPoint4 | Para_GeneratCtr_Voltage_PFVoltPoint4 | 3940 | Para_GeneratCtr_Voltage_PFVoltPoint4 |  | 17524
[8 empty] | 17525 | Para_GeneratCtr_Voltage_PFVoltPoint5 | Para_GeneratCtr_Voltage_PFVoltPoint5 | 3941 | Para_GeneratCtr_Voltage_PFVoltPoint5 |  | 17525
[8 empty] | 17526 | Para_GeneratCtr_Voltage_PFVoltPoint6 | Para_GeneratCtr_Voltage_PFVoltPoint6 | 3942 | Para_GeneratCtr_Voltage_PFVoltPoint6 |  | 17526
[8 empty] | 17527 | Para_GeneratCtr_Voltage_RampeVoltAdj | Para_GeneratCtr_Voltage_RampeVoltAdj | 3943 | Para_GeneratCtr_Voltage_RampeVoltAdj | % | 17527
[8 empty] | 17528 | Para_GeneratCtr_Voltage_VoltOffsetFullLoad | Para_GeneratCtr_Voltage_VoltOffsetFullLoad | 3944 | Para_GeneratCtr_Voltage_VoltOffsetFullLoad | % | 17528
[8 empty] | 17529 | Para_GeneratCtr_Voltage_VoltOffsetIdle | Para_GeneratCtr_Voltage_VoltOffsetIdle | 3945 | Para_GeneratCtr_Voltage_VoltOffsetIdle | % | 17529
[8 empty] | 17530 | Para_GeneratCtr_Voltage_VoltPoint1 | Para_GeneratCtr_Voltage_VoltPoint1 | 3946 | Para_GeneratCtr_Voltage_VoltPoint1 | %Unom | 17530
[8 empty] | 17531 | Para_GeneratCtr_Voltage_VoltPoint2 | Para_GeneratCtr_Voltage_VoltPoint2 | 3947 | Para_GeneratCtr_Voltage_VoltPoint2 | %Unom | 17531
[8 empty] | 17532 | Para_GeneratCtr_Voltage_VoltPoint3 | Para_GeneratCtr_Voltage_VoltPoint3 | 3948 | Para_GeneratCtr_Voltage_VoltPoint3 | %Unom | 17532
[8 empty] | 17533 | Para_GeneratCtr_Voltage_VoltPoint4 | Para_GeneratCtr_Voltage_VoltPoint4 | 3949 | Para_GeneratCtr_Voltage_VoltPoint4 |  | 17533
[8 empty] | 17534 | Para_GeneratCtr_Voltage_VoltPoint5 | Para_GeneratCtr_Voltage_VoltPoint5 | 3950 | Para_GeneratCtr_Voltage_VoltPoint5 |  | 17534
[8 empty] | 17535 | Para_GeneratCtr_Voltage_VoltPoint6 | Para_GeneratCtr_Voltage_VoltPoint6 | 3951 | Para_GeneratCtr_Voltage_VoltPoint6 |  | 17535
[8 empty] | 17536 | Para_GeneratCtr_WindTempDep_PFRedWindTemp | Para_GeneratCtr_WindTempDep_PFRedWindTemp | 3952 | Para_GeneratCtr_WindTempDep_PFRedWindTemp |  | 17536
[8 empty] | 17537 | Para_GeneratCtr_WindTempDep_TempPowRed | Para_GeneratCtr_WindTempDep_TempPowRed | 3953 | Para_GeneratCtr_WindTempDep_TempPowRed |  | 17537
[8 empty] | 17538 | Para_GeneratCtr_WindTempDep_TempStartPFred | Para_GeneratCtr_WindTempDep_TempStartPFred | 3954 | Para_GeneratCtr_WindTempDep_TempStartPFred |  | 17538
[8 empty] | 17539 | Para_Generator_ActBear1 | Para_Generator_ActBear1 | 3955 | Para_Generator_ActBear1 |  | 17539
[8 empty] | 17540 | Para_Generator_ActBear2 | Para_Generator_ActBear2 | 3956 | Para_Generator_ActBear2 |  | 17540
[8 empty] | 17541 | Para_Generator_ActDisplace | Para_Generator_ActDisplace | 3957 | Para_Generator_ActDisplace |  | 17541
[8 empty] | 17542 | Para_Generator_ActInletTemp | Para_Generator_ActInletTemp | 3958 | Para_Generator_ActInletTemp |  | 17542
[8 empty] | 17543 | Para_Generator_ActOutletTemp | Para_Generator_ActOutletTemp | 3959 | Para_Generator_ActOutletTemp |  | 17543
[8 empty] | 17544 | Para_Generator_ActPt100M1_NEx | Para_Generator_ActPt100M1_NEx | 3960 | Para_Generator_ActPt100M1_NEx |  | 17544
[8 empty] | 17545 | Para_Generator_ActPt100PTCWindTemp | Para_Generator_ActPt100PTCWindTemp | 3961 | Para_Generator_ActPt100PTCWindTemp |  | 17545
[8 empty] | 17546 | Para_Generator_ActVoltExcit | Para_Generator_ActVoltExcit | 3962 | Para_Generator_ActVoltExcit |  | 17546
[8 empty] | 17547 | Para_Generator_DeActDiffProtect | Para_Generator_DeActDiffProtect | 3963 | Para_Generator_DeActDiffProtect |  | 17547
[8 empty] | 17548 | Para_Generator_Displace20mA | Para_Generator_Displace20mA | 3964 | Para_Generator_Displace20mA | um pk-pk | 17548
[8 empty] | 17549 | Para_Generator_Displace4mA | Para_Generator_Displace4mA | 3965 | Para_Generator_Displace4mA | um pk-pk | 17549
[8 empty] | 17550 | Para_Generator_DisplaceDelay1 | Para_Generator_DisplaceDelay1 | 3966 | Para_Generator_DisplaceDelay1 | s | 17550
[8 empty] | 17551 | Para_Generator_DisplaceDelay2 | Para_Generator_DisplaceDelay2 | 3967 | Para_Generator_DisplaceDelay2 | s | 17551
[8 empty] | 17552 | Para_Generator_DisplaceLimit1 | Para_Generator_DisplaceLimit1 | 3968 | Para_Generator_DisplaceLimit1 | um pk-pk | 17552
[8 empty] | 17553 | Para_Generator_DisplaceLimit2 | Para_Generator_DisplaceLimit2 | 3969 | Para_Generator_DisplaceLimit2 | um pk-pk | 17553
[8 empty] | 17554 | Para_Generator_TempBear1Alarm | Para_Generator_TempBear1Alarm | 3970 | Para_Generator_TempBear1Alarm | °C | 17554
[8 empty] | 17555 | Para_Generator_TempBear1Trip | Para_Generator_TempBear1Trip | 3971 | Para_Generator_TempBear1Trip | °C | 17555
[8 empty] | 17556 | Para_Generator_TempBear2Alarm | Para_Generator_TempBear2Alarm | 3972 | Para_Generator_TempBear2Alarm | °C | 17556
[8 empty] | 17557 | Para_Generator_TempBear2Trip | Para_Generator_TempBear2Trip | 3973 | Para_Generator_TempBear2Trip | °C | 17557
[8 empty] | 17558 | Para_Generator_TempBearAlarmHys | Para_Generator_TempBearAlarmHys | 3974 | Para_Generator_TempBearAlarmHys | °C | 17558
[8 empty] | 17559 | Para_Generator_TempBearTripHys | Para_Generator_TempBearTripHys | 3975 | Para_Generator_TempBearTripHys | °C | 17559
[8 empty] | 17560 | Para_Generator_TempWindPh123AlarmHys | Para_Generator_TempWindPh123AlarmHys | 3976 | Para_Generator_TempWindPh123AlarmHys | °C | 17560
[8 empty] | 17561 | Para_Generator_TempWindPh123TripHys | Para_Generator_TempWindPh123TripHys | 3977 | Para_Generator_TempWindPh123TripHys | °C | 17561
[8 empty] | 17562 | Para_Generator_TempWindPh1Alarm | Para_Generator_TempWindPh1Alarm | 3978 | Para_Generator_TempWindPh1Alarm | °C | 17562
[8 empty] | 17563 | Para_Generator_TempWindPh1Trip | Para_Generator_TempWindPh1Trip | 3979 | Para_Generator_TempWindPh1Trip | °C | 17563
[8 empty] | 17564 | Para_Generator_TempWindPh2Alarm | Para_Generator_TempWindPh2Alarm | 3980 | Para_Generator_TempWindPh2Alarm | °C | 17564
[8 empty] | 17565 | Para_Generator_TempWindPh2Trip | Para_Generator_TempWindPh2Trip | 3981 | Para_Generator_TempWindPh2Trip | °C | 17565
[8 empty] | 17566 | Para_Generator_TempWindPh3Alarm | Para_Generator_TempWindPh3Alarm | 3982 | Para_Generator_TempWindPh3Alarm | °C | 17566
[8 empty] | 17567 | Para_Generator_TempWindPh3Trip | Para_Generator_TempWindPh3Trip | 3983 | Para_Generator_TempWindPh3Trip | °C | 17567
[8 empty] | 17568 | Para_Generator_TempWindPTCAlarm | Para_Generator_TempWindPTCAlarm | 3984 | Para_Generator_TempWindPTCAlarm | °C | 17568
[8 empty] | 17569 | Para_Generator_TempWindPTCAlarmHys | Para_Generator_TempWindPTCAlarmHys | 3985 | Para_Generator_TempWindPTCAlarmHys | °C | 17569
[8 empty] | 17570 | Para_Generator_TempWindPTCTrip | Para_Generator_TempWindPTCTrip | 3986 | Para_Generator_TempWindPTCTrip | °C | 17570
[8 empty] | 17571 | Para_Generator_TempWindPTCTripHys | Para_Generator_TempWindPTCTripHys | 3987 | Para_Generator_TempWindPTCTripHys | °C | 17571
[8 empty] | 17572 | Para_Generator_VoltExitLimit | Para_Generator_VoltExitLimit | 3988 | Para_Generator_VoltExitLimit | V | 17572
[8 empty] | 17573 | Para_Generator_VoltExitLimitHys | Para_Generator_VoltExitLimitHys | 3989 | Para_Generator_VoltExitLimitHys | V | 17573
[8 empty] | 17574 | Para_Generator_VoltExitMax | Para_Generator_VoltExitMax | 3990 | Para_Generator_VoltExitMax | V | 17574
[8 empty] | 17575 | Para_Generator_VoltExitMaxHys | Para_Generator_VoltExitMaxHys | 3991 | Para_Generator_VoltExitMaxHys | V | 17575
[8 empty] | 19494 | Para_Grid_DelayStabilGrid | Para_Grid_DelayStabilGrid | 3992 | Para_Grid_DelayStabilGrid | s | 19494
[8 empty] | 17576 | Para_Grid_GridCode_ActDynGridCode | Para_Grid_GridCode_ActDynGridCode | 3993 | Para_Grid_GridCode_ActDynGridCode |  | 17576
[8 empty] | 17577 | Para_Grid_GridCode_ActDynGridCodeMonOnly | Para_Grid_GridCode_ActDynGridCodeMonOnly | 3994 | Para_Grid_GridCode_ActDynGridCodeMonOnly |  | 17577
[8 empty] | 17578 | Para_Grid_GridCode_AngleSumLimit | Para_Grid_GridCode_AngleSumLimit | 3995 | Para_Grid_GridCode_AngleSumLimit | °el | 17578
[8 empty] | 17579 | Para_Grid_GridCode_CurrentChangeLimit | Para_Grid_GridCode_CurrentChangeLimit | 3996 | Para_Grid_GridCode_CurrentChangeLimit | %Inom/s | 17579
[8 empty] | 17580 | Para_Grid_GridCode_PolarWheelAngleLimit | Para_Grid_GridCode_PolarWheelAngleLimit | 3997 | Para_Grid_GridCode_PolarWheelAngleLimit | °el | 17580
[8 empty] | 17581 | Para_Grid_GridCode_PoleSlipLimit | Para_Grid_GridCode_PoleSlipLimit | 3998 | Para_Grid_GridCode_PoleSlipLimit | rpm | 17581
[8 empty] | 17582 | Para_Grid_GridCode_PowerLimit | Para_Grid_GridCode_PowerLimit | 3999 | Para_Grid_GridCode_PowerLimit | %Pnom | 17582
[8 empty] | 17583 | Para_Grid_GridCode_SpeedChangeLimit | Para_Grid_GridCode_SpeedChangeLimit | 4000 | Para_Grid_GridCode_SpeedChangeLimit | rpm/s | 17583
[8 empty] | 17584 | Para_Grid_GridCode_StopCap | Para_Grid_GridCode_StopCap | 4001 | Para_Grid_GridCode_StopCap |  | 17584
[8 empty] | 17585 | Para_Grid_GridCode_VoltageLimit | Para_Grid_GridCode_VoltageLimit | 4002 | Para_Grid_GridCode_VoltageLimit | %Unom | 17585
[8 empty] | 17586 | Para_Grid_GridCode_XqGen | Para_Grid_GridCode_XqGen | 4003 | Para_Grid_GridCode_XqGen |  | 17586
[8 empty] | 17587 | Para_Grid_GridCodeStatic_010_Ramp_ActPRampMainFailure | Para_Grid_GridCodeStatic_010_Ramp_ActPRampMainFailure | 4004 | Para_Grid_GridCodeStatic_010_Ramp_ActPRampMainFailure |  | 17587
[8 empty] | 17588 | Para_Grid_GridCodeStatic_010_Ramp_ActPRampUtility | Para_Grid_GridCodeStatic_010_Ramp_ActPRampUtility | 4005 | Para_Grid_GridCodeStatic_010_Ramp_ActPRampUtility |  | 17588
[8 empty] | 20126 | Para_Grid_GridCodeStatic_010_Ramp_ActSlowRampPFC | Para_Grid_GridCodeStatic_010_Ramp_ActSlowRampPFC | 4006 | Para_Grid_GridCodeStatic_010_Ramp_ActSlowRampPFC |  | 20126
[8 empty] | 17589 | Para_Grid_GridCodeStatic_010_Ramp_PowerFacSetpoint | Para_Grid_GridCodeStatic_010_Ramp_PowerFacSetpoint | 4007 | Para_Grid_GridCodeStatic_010_Ramp_PowerFacSetpoint | s | 17589
[8 empty] | 17590 | Para_Grid_GridCodeStatic_010_Ramp_PRampMainFailure | Para_Grid_GridCodeStatic_010_Ramp_PRampMainFailure | 4008 | Para_Grid_GridCodeStatic_010_Ramp_PRampMainFailure | %Pnom/s | 17590
[8 empty] | 17591 | Para_Grid_GridCodeStatic_010_Ramp_RampUtility | Para_Grid_GridCodeStatic_010_Ramp_RampUtility | 4009 | Para_Grid_GridCodeStatic_010_Ramp_RampUtility | %Pnom/s | 17591
[8 empty] | 17592 | Para_Grid_GridCodeStatic_010_Ramp_TimeDelMainOk | Para_Grid_GridCodeStatic_010_Ramp_TimeDelMainOk | 4010 | Para_Grid_GridCodeStatic_010_Ramp_TimeDelMainOk | min | 17592
[8 empty] | 17593 | Para_Grid_GridCodeStatic_020_PowerSet_ActPowerSetUtility | Para_Grid_GridCodeStatic_020_PowerSet_ActPowerSetUtility | 4011 | Para_Grid_GridCodeStatic_020_PowerSet_ActPowerSetUtility |  | 17593
[8 empty] | 17594 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityConst1 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityConst1 | 4012 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityConst1 | %Pnom | 17594
[8 empty] | 17595 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityConst2 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityConst2 | 4013 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityConst2 | %Pnom | 17595
[8 empty] | 17596 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityConst3 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityConst3 | 4014 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityConst3 | %Pnom | 17596
[8 empty] | 17597 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityConst4 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityConst4 | 4015 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityConst4 | %Pnom | 17597
[8 empty] | 17598 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityConst5 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityConst5 | 4016 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityConst5 | %Pnom | 17598
[8 empty] | 17599 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityCurr1 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityCurr1 | 4017 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityCurr1 | mA | 17599
[8 empty] | 17600 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityCurr2 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityCurr2 | 4018 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityCurr2 | mA | 17600
[8 empty] | 17601 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityPoint1 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityPoint1 | 4019 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityPoint1 | kW | 17601
[8 empty] | 17602 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityPoint2 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityPoint2 | 4020 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityPoint2 | kW | 17602
[8 empty] | 17603 | Para_Grid_GridCodeStatic_030_PowerLimit_ActPowerLimUtility | Para_Grid_GridCodeStatic_030_PowerLimit_ActPowerLimUtility | 4021 | Para_Grid_GridCodeStatic_030_PowerLimit_ActPowerLimUtility |  | 17603
[8 empty] | 17604 | Para_Grid_GridCodeStatic_030_PowerLimit_IntSetPoint | Para_Grid_GridCodeStatic_030_PowerLimit_IntSetPoint | 4022 | Para_Grid_GridCodeStatic_030_PowerLimit_IntSetPoint | kW | 17604
[8 empty] | 17605 | Para_Grid_GridCodeStatic_030_PowerLimit_LimitDemOff | Para_Grid_GridCodeStatic_030_PowerLimit_LimitDemOff | 4023 | Para_Grid_GridCodeStatic_030_PowerLimit_LimitDemOff | %Pnom | 17605
[8 empty] | 17606 | Para_Grid_GridCodeStatic_030_PowerLimit_LimitDemOffHys | Para_Grid_GridCodeStatic_030_PowerLimit_LimitDemOffHys | 4024 | Para_Grid_GridCodeStatic_030_PowerLimit_LimitDemOffHys | %Pnom | 17606
[8 empty] | 17607 | Para_Grid_GridCodeStatic_030_PowerLimit_LimitDemOffTimeDel | Para_Grid_GridCodeStatic_030_PowerLimit_LimitDemOffTimeDel | 4025 | Para_Grid_GridCodeStatic_030_PowerLimit_LimitDemOffTimeDel | s | 17607
[8 empty] | 17608 | Para_Grid_GridCodeStatic_030_PowerLimit_Step1 | Para_Grid_GridCodeStatic_030_PowerLimit_Step1 | 4026 | Para_Grid_GridCodeStatic_030_PowerLimit_Step1 | %Pnom | 17608
[8 empty] | 17609 | Para_Grid_GridCodeStatic_030_PowerLimit_Step2 | Para_Grid_GridCodeStatic_030_PowerLimit_Step2 | 4027 | Para_Grid_GridCodeStatic_030_PowerLimit_Step2 | %Pnom | 17609
[8 empty] | 17610 | Para_Grid_GridCodeStatic_030_PowerLimit_Step3 | Para_Grid_GridCodeStatic_030_PowerLimit_Step3 | 4028 | Para_Grid_GridCodeStatic_030_PowerLimit_Step3 | %Pnom | 17610
[8 empty] | 17611 | Para_Grid_GridCodeStatic_030_PowerLimit_Step4 | Para_Grid_GridCodeStatic_030_PowerLimit_Step4 | 4029 | Para_Grid_GridCodeStatic_030_PowerLimit_Step4 | %Pnom | 17611
[8 empty] | 17612 | Para_Grid_GridCodeStatic_030_PowerLimit_Step5 | Para_Grid_GridCodeStatic_030_PowerLimit_Step5 | 4030 | Para_Grid_GridCodeStatic_030_PowerLimit_Step5 | %Pnom | 17612
[8 empty] | 17613 | Para_Grid_GridCodeStatic_030_PowerLimit_UtilityCurr1 | Para_Grid_GridCodeStatic_030_PowerLimit_UtilityCurr1 | 4031 | Para_Grid_GridCodeStatic_030_PowerLimit_UtilityCurr1 | mA | 17613
[8 empty] | 17614 | Para_Grid_GridCodeStatic_030_PowerLimit_UtilityCurr2 | Para_Grid_GridCodeStatic_030_PowerLimit_UtilityCurr2 | 4032 | Para_Grid_GridCodeStatic_030_PowerLimit_UtilityCurr2 | mA | 17614
[8 empty] | 17615 | Para_Grid_GridCodeStatic_030_PowerLimit_UtilityPoint1 | Para_Grid_GridCodeStatic_030_PowerLimit_UtilityPoint1 | 4033 | Para_Grid_GridCodeStatic_030_PowerLimit_UtilityPoint1 | kW | 17615
[8 empty] | 17616 | Para_Grid_GridCodeStatic_030_PowerLimit_UtilityPoint2 | Para_Grid_GridCodeStatic_030_PowerLimit_UtilityPoint2 | 4034 | Para_Grid_GridCodeStatic_030_PowerLimit_UtilityPoint2 | kW | 17616
[8 empty] | 17617 | Para_Grid_GridCodeStatic_040_PFC_RMC_PFCRelative | Para_Grid_GridCodeStatic_040_PFC_RMC_PFCRelative | 4035 | Para_Grid_GridCodeStatic_040_PFC_RMC_PFCRelative |  | 17617
[8 empty] | 17618 | Para_Grid_GridCodeStatic_040_PFC_RMC_ResponseCurve | Para_Grid_GridCodeStatic_040_PFC_RMC_ResponseCurve | 4036 | Para_Grid_GridCodeStatic_040_PFC_RMC_ResponseCurve |  | 17618
[8 empty] | 17619 | Para_Grid_GridCodeStatic_040_PFC_RMC_RMCMargin | Para_Grid_GridCodeStatic_040_PFC_RMC_RMCMargin | 4037 | Para_Grid_GridCodeStatic_040_PFC_RMC_RMCMargin | %Pnom | 17619
[8 empty] | 17620 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_ActSetPointExt | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_ActSetPointExt | 4038 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_ActSetPointExt |  | 17620
[8 empty] | 17621 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_BackupSetPoint | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_BackupSetPoint | 4039 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_BackupSetPoint |  | 17621
[8 empty] | 17622 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_ChoiceFunction | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_ChoiceFunction | 4040 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_ChoiceFunction |  | 17622
[8 empty] | 17623 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtConst1 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtConst1 | 4041 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtConst1 |  | 17623
[8 empty] | 17624 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtConst2 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtConst2 | 4042 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtConst2 |  | 17624
[8 empty] | 17625 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtConst3 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtConst3 | 4043 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtConst3 |  | 17625
[8 empty] | 17626 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtConst4 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtConst4 | 4044 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtConst4 |  | 17626
[8 empty] | 17627 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtConst5 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtConst5 | 4045 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtConst5 |  | 17627
[8 empty] | 17628 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtCurr1 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtCurr1 | 4046 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtCurr1 | mA | 17628
[8 empty] | 17629 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtCurr2 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtCurr2 | 4047 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtCurr2 | mA | 17629
[8 empty] | 17630 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtPoint1 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtPoint1 | 4048 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtPoint1 |  | 17630
[8 empty] | 17631 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtPoint2 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtPoint2 | 4049 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtPoint2 |  | 17631
[8 empty] | 17632 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointInt | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointInt | 4050 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointInt |  | 17632
[8 empty] | 17633 | Para_Grid_GridCodeStatic_060_CosPhiP_ResponseCurve | Para_Grid_GridCodeStatic_060_CosPhiP_ResponseCurve | 4051 | Para_Grid_GridCodeStatic_060_CosPhiP_ResponseCurve |  | 17633
[8 empty] | 17634 | Para_Grid_GridCodeStatic_070_VoltageSet_ActSetPointExt | Para_Grid_GridCodeStatic_070_VoltageSet_ActSetPointExt | 4052 | Para_Grid_GridCodeStatic_070_VoltageSet_ActSetPointExt |  | 17634
[8 empty] | 17635 | Para_Grid_GridCodeStatic_070_VoltageSet_Backup | Para_Grid_GridCodeStatic_070_VoltageSet_Backup | 4053 | Para_Grid_GridCodeStatic_070_VoltageSet_Backup | % | 17635
[8 empty] | 17636 | Para_Grid_GridCodeStatic_070_VoltageSet_ChoiceFunction | Para_Grid_GridCodeStatic_070_VoltageSet_ChoiceFunction | 4054 | Para_Grid_GridCodeStatic_070_VoltageSet_ChoiceFunction |  | 17636
[8 empty] | 17637 | Para_Grid_GridCodeStatic_070_VoltageSet_Internal | Para_Grid_GridCodeStatic_070_VoltageSet_Internal | 4055 | Para_Grid_GridCodeStatic_070_VoltageSet_Internal | % | 17637
[8 empty] | 17638 | Para_Grid_GridCodeStatic_070_VoltageSet_SetPointExtCurr1 | Para_Grid_GridCodeStatic_070_VoltageSet_SetPointExtCurr1 | 4056 | Para_Grid_GridCodeStatic_070_VoltageSet_SetPointExtCurr1 | mA | 17638
[8 empty] | 17639 | Para_Grid_GridCodeStatic_070_VoltageSet_SetPointExtCurr2 | Para_Grid_GridCodeStatic_070_VoltageSet_SetPointExtCurr2 | 4057 | Para_Grid_GridCodeStatic_070_VoltageSet_SetPointExtCurr2 | mA | 17639
[8 empty] | 17640 | Para_Grid_GridCodeStatic_070_VoltageSet_SetPointExtPoint1 | Para_Grid_GridCodeStatic_070_VoltageSet_SetPointExtPoint1 | 4058 | Para_Grid_GridCodeStatic_070_VoltageSet_SetPointExtPoint1 | % | 17640
[8 empty] | 17641 | Para_Grid_GridCodeStatic_070_VoltageSet_SetPointExtPoint2 | Para_Grid_GridCodeStatic_070_VoltageSet_SetPointExtPoint2 | 4059 | Para_Grid_GridCodeStatic_070_VoltageSet_SetPointExtPoint2 | % | 17641
[8 empty] | 17642 | Para_Grid_GridCodeStatic_070_VoltageSet_Unom | Para_Grid_GridCodeStatic_070_VoltageSet_Unom | 4060 | Para_Grid_GridCodeStatic_070_VoltageSet_Unom | V | 17642
[8 empty] | 17643 | Para_Grid_GridCodeStatic_080_CosPhiU_ResponseCurve | Para_Grid_GridCodeStatic_080_CosPhiU_ResponseCurve | 4061 | Para_Grid_GridCodeStatic_080_CosPhiU_ResponseCurve |  | 17643
[8 empty] | 17644 | Para_Grid_GridCodeStatic_090_QVolt_ResponseCurve | Para_Grid_GridCodeStatic_090_QVolt_ResponseCurve | 4062 | Para_Grid_GridCodeStatic_090_QVolt_ResponseCurve |  | 17644
[8 empty] | 17645 | Para_Grid_GridCodeStatic_100_QSetIntExt_ActSetPointExt | Para_Grid_GridCodeStatic_100_QSetIntExt_ActSetPointExt | 4063 | Para_Grid_GridCodeStatic_100_QSetIntExt_ActSetPointExt |  | 17645
[8 empty] | 17646 | Para_Grid_GridCodeStatic_100_QSetIntExt_BackupSetPoint | Para_Grid_GridCodeStatic_100_QSetIntExt_BackupSetPoint | 4064 | Para_Grid_GridCodeStatic_100_QSetIntExt_BackupSetPoint | kvar | 17646
[8 empty] | 17647 | Para_Grid_GridCodeStatic_100_QSetIntExt_ChoiceFunction | Para_Grid_GridCodeStatic_100_QSetIntExt_ChoiceFunction | 4065 | Para_Grid_GridCodeStatic_100_QSetIntExt_ChoiceFunction |  | 17647
[8 empty] | 17648 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtConst1 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtConst1 | 4066 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtConst1 | kvar | 17648
[8 empty] | 17649 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtConst2 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtConst2 | 4067 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtConst2 | kvar | 17649
[8 empty] | 17650 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtConst3 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtConst3 | 4068 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtConst3 | kvar | 17650
[8 empty] | 17651 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtConst4 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtConst4 | 4069 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtConst4 | kvar | 17651
[8 empty] | 17652 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtConst5 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtConst5 | 4070 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtConst5 | kvar | 17652
[8 empty] | 17653 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtCurr1 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtCurr1 | 4071 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtCurr1 | mA | 17653
[8 empty] | 17654 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtCurr2 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtCurr2 | 4072 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtCurr2 | mA | 17654
[8 empty] | 17655 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtPoint1 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtPoint1 | 4073 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtPoint1 | kvar | 17655
[8 empty] | 17656 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtPoint2 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtPoint2 | 4074 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtPoint2 | kvar | 17656
[8 empty] | 17657 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointInt | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointInt | 4075 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointInt | kvar | 17657
[8 empty] | 17658 | Para_Grid_GridCodeStatic_110_QLimit_ActSetPointExt | Para_Grid_GridCodeStatic_110_QLimit_ActSetPointExt | 4076 | Para_Grid_GridCodeStatic_110_QLimit_ActSetPointExt |  | 17658
[8 empty] | 17659 | Para_Grid_GridCodeStatic_110_QLimit_SetPointExtCurr1 | Para_Grid_GridCodeStatic_110_QLimit_SetPointExtCurr1 | 4077 | Para_Grid_GridCodeStatic_110_QLimit_SetPointExtCurr1 | mA | 17659
[8 empty] | 17660 | Para_Grid_GridCodeStatic_110_QLimit_SetPointExtCurr2 | Para_Grid_GridCodeStatic_110_QLimit_SetPointExtCurr2 | 4078 | Para_Grid_GridCodeStatic_110_QLimit_SetPointExtCurr2 | mA | 17660
[8 empty] | 17661 | Para_Grid_GridCodeStatic_110_QLimit_SetPointExtPoint1 | Para_Grid_GridCodeStatic_110_QLimit_SetPointExtPoint1 | 4079 | Para_Grid_GridCodeStatic_110_QLimit_SetPointExtPoint1 | kvar | 17661
[8 empty] | 17662 | Para_Grid_GridCodeStatic_110_QLimit_SetPointExtPoint2 | Para_Grid_GridCodeStatic_110_QLimit_SetPointExtPoint2 | 4080 | Para_Grid_GridCodeStatic_110_QLimit_SetPointExtPoint2 | kvar | 17662
[8 empty] | 17663 | Para_Grid_GridCodeStatic_110_QLimit_SetPointIntLimit | Para_Grid_GridCodeStatic_110_QLimit_SetPointIntLimit | 4081 | Para_Grid_GridCodeStatic_110_QLimit_SetPointIntLimit | kvar | 17663
[8 empty] | 17664 | Para_Grid_GridCodeStatic_120_AnalogOut_ActCosPhi4mA | Para_Grid_GridCodeStatic_120_AnalogOut_ActCosPhi4mA | 4082 | Para_Grid_GridCodeStatic_120_AnalogOut_ActCosPhi4mA |  | 17664
[8 empty] | 17665 | Para_Grid_GridCodeStatic_120_AnalogOut_ActReactPower4mA | Para_Grid_GridCodeStatic_120_AnalogOut_ActReactPower4mA | 4083 | Para_Grid_GridCodeStatic_120_AnalogOut_ActReactPower4mA |  | 17665
[8 empty] | 17666 | Para_Grid_GridCodeStatic_120_AnalogOut_CosPhiOutPoint1 | Para_Grid_GridCodeStatic_120_AnalogOut_CosPhiOutPoint1 | 4084 | Para_Grid_GridCodeStatic_120_AnalogOut_CosPhiOutPoint1 |  | 17666
[8 empty] | 17667 | Para_Grid_GridCodeStatic_120_AnalogOut_CosPhiOutPoint2 | Para_Grid_GridCodeStatic_120_AnalogOut_CosPhiOutPoint2 | 4085 | Para_Grid_GridCodeStatic_120_AnalogOut_CosPhiOutPoint2 |  | 17667
[8 empty] | 17668 | Para_Grid_GridCodeStatic_120_AnalogOut_ReactPowerOutPoint1 | Para_Grid_GridCodeStatic_120_AnalogOut_ReactPowerOutPoint1 | 4086 | Para_Grid_GridCodeStatic_120_AnalogOut_ReactPowerOutPoint1 | kvar | 17668
[8 empty] | 17669 | Para_Grid_GridCodeStatic_120_AnalogOut_ReactPowerOutPoint2 | Para_Grid_GridCodeStatic_120_AnalogOut_ReactPowerOutPoint2 | 4087 | Para_Grid_GridCodeStatic_120_AnalogOut_ReactPowerOutPoint2 | kvar | 17669
[8 empty] | 10049954 | Para_halio_rpr_oxicat_in_fast_scalmax | Para_halio_rpr_oxicat_in_fast_scalmax | 4088 | Para_halio_rpr_oxicat_in_fast_scalmax |  | 10049954
[8 empty] | 10049955 | Para_halio_rpr_oxicat_in_fast_scalmin | Para_halio_rpr_oxicat_in_fast_scalmin | 4089 | Para_halio_rpr_oxicat_in_fast_scalmin |  | 10049955
[8 empty] | 10049956 | Para_halio_rpr_oxicat_in_scalmax | Para_halio_rpr_oxicat_in_scalmax | 4090 | Para_halio_rpr_oxicat_in_scalmax | mbar | 10049956
[8 empty] | 10049957 | Para_halio_rpr_oxicat_in_scalmin | Para_halio_rpr_oxicat_in_scalmin | 4091 | Para_halio_rpr_oxicat_in_scalmin | mbar | 10049957
[8 empty] | 10049958 | Para_halio_rpr_oxicat_out_scalmax | Para_halio_rpr_oxicat_out_scalmax | 4092 | Para_halio_rpr_oxicat_out_scalmax | mbar | 10049958
[8 empty] | 10049959 | Para_halio_rpr_oxicat_out_scalmin | Para_halio_rpr_oxicat_out_scalmin | 4093 | Para_halio_rpr_oxicat_out_scalmin | mbar | 10049959
[8 empty] | 10049960 | Para_halio_rt_oxicat_in_scalmax | Para_halio_rt_oxicat_in_scalmax | 4094 | Para_halio_rt_oxicat_in_scalmax | °C | 10049960
[8 empty] | 10049961 | Para_halio_rt_oxicat_in_scalmin | Para_halio_rt_oxicat_in_scalmin | 4095 | Para_halio_rt_oxicat_in_scalmin | °C | 10049961
[8 empty] | 10049962 | Para_halio_rt_oxicat_out_scalmax | Para_halio_rt_oxicat_out_scalmax | 4096 | Para_halio_rt_oxicat_out_scalmax | °C | 10049962
[8 empty] | 10049963 | Para_halio_rt_oxicat_out_scalmin | Para_halio_rt_oxicat_out_scalmin | 4097 | Para_halio_rt_oxicat_out_scalmin | °C | 10049963
[8 empty] | 10049964 | Para_halio_rt_scr_catscalmax | Para_halio_rt_scr_catscalmax | 4098 | Para_halio_rt_scr_catscalmax | °C | 10049964
[8 empty] | 10049965 | Para_halio_rt_scr_catscalmin | Para_halio_rt_scr_catscalmin | 4099 | Para_halio_rt_scr_catscalmin | °C | 10049965
[8 empty] | 17670 | Para_Hyd_CoolWat_Press_20mA | Para_Hyd_CoolWat_Press_20mA | 4100 | Para_Hyd_CoolWat_Press_20mA | bar | 17670
[8 empty] | 17671 | Para_Hyd_CoolWat_Press_Limit1 | Para_Hyd_CoolWat_Press_Limit1 | 4101 | Para_Hyd_CoolWat_Press_Limit1 | bar | 17671
[8 empty] | 17672 | Para_Hyd_CoolWat_Press_Limit1Hys | Para_Hyd_CoolWat_Press_Limit1Hys | 4102 | Para_Hyd_CoolWat_Press_Limit1Hys | bar | 17672
[8 empty] | 17673 | Para_Hyd_CoolWat_Press_Max | Para_Hyd_CoolWat_Press_Max | 4103 | Para_Hyd_CoolWat_Press_Max | bar | 17673
[8 empty] | 17674 | Para_Hyd_CoolWat_Press_MaxHys | Para_Hyd_CoolWat_Press_MaxHys | 4104 | Para_Hyd_CoolWat_Press_MaxHys | bar | 17674
[8 empty] | 17675 | Para_Hyd_CoolWat_Press_Min | Para_Hyd_CoolWat_Press_Min | 4105 | Para_Hyd_CoolWat_Press_Min | bar | 17675
[8 empty] | 17676 | Para_Hyd_CoolWat_Press_Min1 | Para_Hyd_CoolWat_Press_Min1 | 4106 | Para_Hyd_CoolWat_Press_Min1 |  | 17676
[8 empty] | 17677 | Para_Hyd_CoolWat_Press_Min1Hys | Para_Hyd_CoolWat_Press_Min1Hys | 4107 | Para_Hyd_CoolWat_Press_Min1Hys |  | 17677
[8 empty] | 17678 | Para_Hyd_CoolWat_Press_MinHys | Para_Hyd_CoolWat_Press_MinHys | 4108 | Para_Hyd_CoolWat_Press_MinHys | bar | 17678
[8 empty] | 17679 | Para_Hyd_CoolWat_Temp_Limit1 | Para_Hyd_CoolWat_Temp_Limit1 | 4109 | Para_Hyd_CoolWat_Temp_Limit1 | °C | 17679
[8 empty] | 17680 | Para_Hyd_CoolWat_Temp_Limit1Hys | Para_Hyd_CoolWat_Temp_Limit1Hys | 4110 | Para_Hyd_CoolWat_Temp_Limit1Hys | °C | 17680
[8 empty] | 17681 | Para_Hyd_CoolWat_Temp_Limit2 | Para_Hyd_CoolWat_Temp_Limit2 | 4111 | Para_Hyd_CoolWat_Temp_Limit2 | °C | 17681
[8 empty] | 17682 | Para_Hyd_CoolWat_Temp_Limit2Hys | Para_Hyd_CoolWat_Temp_Limit2Hys | 4112 | Para_Hyd_CoolWat_Temp_Limit2Hys | °C | 17682
[8 empty] | 17683 | Para_Hyd_CoolWat_Temp_LoadEnab | Para_Hyd_CoolWat_Temp_LoadEnab | 4113 | Para_Hyd_CoolWat_Temp_LoadEnab | °C | 17683
[8 empty] | 17684 | Para_Hyd_CoolWat_Temp_LoadEnabHys | Para_Hyd_CoolWat_Temp_LoadEnabHys | 4114 | Para_Hyd_CoolWat_Temp_LoadEnabHys | °C | 17684
[8 empty] | 17685 | Para_Hyd_CoolWat_Temp_Max | Para_Hyd_CoolWat_Temp_Max | 4115 | Para_Hyd_CoolWat_Temp_Max | °C | 17685
[8 empty] | 17686 | Para_Hyd_CoolWat_Temp_MaxHys | Para_Hyd_CoolWat_Temp_MaxHys | 4116 | Para_Hyd_CoolWat_Temp_MaxHys | °C | 17686
[8 empty] | 17687 | Para_Hyd_CoolWat_Temp_Min | Para_Hyd_CoolWat_Temp_Min | 4117 | Para_Hyd_CoolWat_Temp_Min | °C | 17687
[8 empty] | 17688 | Para_Hyd_CoolWat_Temp_MinHys | Para_Hyd_CoolWat_Temp_MinHys | 4118 | Para_Hyd_CoolWat_Temp_MinHys | °C | 17688
[8 empty] | 17689 | Para_Hyd_CoolWat_Temp_PreHeatOff | Para_Hyd_CoolWat_Temp_PreHeatOff | 4119 | Para_Hyd_CoolWat_Temp_PreHeatOff | °C | 17689
[8 empty] | 17690 | Para_Hyd_CoolWat_Temp_PreHeatOffHys | Para_Hyd_CoolWat_Temp_PreHeatOffHys | 4120 | Para_Hyd_CoolWat_Temp_PreHeatOffHys | °C | 17690
[8 empty] | 17691 | Para_Hyd_CrankCase_20mA | Para_Hyd_CrankCase_20mA | 4121 | Para_Hyd_CrankCase_20mA | mbar | 17691
[8 empty] | 17692 | Para_Hyd_CrankCase_4mA | Para_Hyd_CrankCase_4mA | 4122 | Para_Hyd_CrankCase_4mA | mbar | 17692
[8 empty] | 17693 | Para_Hyd_CrankCase_Act | Para_Hyd_CrankCase_Act | 4123 | Para_Hyd_CrankCase_Act |  | 17693
[8 empty] | 17694 | Para_Hyd_CrankCase_ActLimitMon | Para_Hyd_CrankCase_ActLimitMon | 4124 | Para_Hyd_CrankCase_ActLimitMon |  | 17694
[8 empty] | 17695 | Para_Hyd_CrankCase_FreqMax | Para_Hyd_CrankCase_FreqMax | 4125 | Para_Hyd_CrankCase_FreqMax | Hz | 17695
[8 empty] | 17696 | Para_Hyd_CrankCase_FreqMin | Para_Hyd_CrankCase_FreqMin | 4126 | Para_Hyd_CrankCase_FreqMin | Hz | 17696
[8 empty] | 17697 | Para_Hyd_CrankCase_Limit | Para_Hyd_CrankCase_Limit | 4127 | Para_Hyd_CrankCase_Limit |  | 17697
[8 empty] | 17698 | Para_Hyd_CrankCase_LimitHys | Para_Hyd_CrankCase_LimitHys | 4128 | Para_Hyd_CrankCase_LimitHys |  | 17698
[8 empty] | 17699 | Para_Hyd_CrankCase_LimitWarn | Para_Hyd_CrankCase_LimitWarn | 4129 | Para_Hyd_CrankCase_LimitWarn | mbar | 17699
[8 empty] | 17700 | Para_Hyd_CrankCase_LimitWarnHys | Para_Hyd_CrankCase_LimitWarnHys | 4130 | Para_Hyd_CrankCase_LimitWarnHys | mbar | 17700
[8 empty] | 17701 | Para_Hyd_Oil_Counter_OilRefillOpH | Para_Hyd_Oil_Counter_OilRefillOpH | 4131 | Para_Hyd_Oil_Counter_OilRefillOpH |  | 17701
[8 empty] | 17702 | Para_Hyd_Oil_Counter_PulseValue | Para_Hyd_Oil_Counter_PulseValue | 4132 | Para_Hyd_Oil_Counter_PulseValue |  | 17702
[8 empty] | 17703 | Para_Hyd_Oil_Level_LimitClose | Para_Hyd_Oil_Level_LimitClose | 4133 | Para_Hyd_Oil_Level_LimitClose |  | 17703
[8 empty] | 17704 | Para_Hyd_Oil_Level_LimitCloseHys | Para_Hyd_Oil_Level_LimitCloseHys | 4134 | Para_Hyd_Oil_Level_LimitCloseHys |  | 17704
[8 empty] | 17705 | Para_Hyd_Oil_Level_LimitOpen | Para_Hyd_Oil_Level_LimitOpen | 4135 | Para_Hyd_Oil_Level_LimitOpen |  | 17705
[8 empty] | 17706 | Para_Hyd_Oil_Level_LimitOpenHys | Para_Hyd_Oil_Level_LimitOpenHys | 4136 | Para_Hyd_Oil_Level_LimitOpenHys |  | 17706
[8 empty] | 17707 | Para_Hyd_Oil_Level_Max | Para_Hyd_Oil_Level_Max | 4137 | Para_Hyd_Oil_Level_Max |  | 17707
[8 empty] | 17708 | Para_Hyd_Oil_Level_MaxHys | Para_Hyd_Oil_Level_MaxHys | 4138 | Para_Hyd_Oil_Level_MaxHys |  | 17708
[8 empty] | 17709 | Para_Hyd_Oil_Level_Min | Para_Hyd_Oil_Level_Min | 4139 | Para_Hyd_Oil_Level_Min |  | 17709
[8 empty] | 17710 | Para_Hyd_Oil_Level_MinHys | Para_Hyd_Oil_Level_MinHys | 4140 | Para_Hyd_Oil_Level_MinHys |  | 17710
[8 empty] | 17711 | Para_Hyd_Oil_Press_20mA | Para_Hyd_Oil_Press_20mA | 4141 | Para_Hyd_Oil_Press_20mA |  | 17711
[8 empty] | 17712 | Para_Hyd_Oil_Press_DiffMax | Para_Hyd_Oil_Press_DiffMax | 4142 | Para_Hyd_Oil_Press_DiffMax |  | 17712
[8 empty] | 17713 | Para_Hyd_Oil_Press_DiffMaxHys | Para_Hyd_Oil_Press_DiffMaxHys | 4143 | Para_Hyd_Oil_Press_DiffMaxHys |  | 17713
[8 empty] | 17714 | Para_Hyd_Oil_Press_DiffMaxWarn | Para_Hyd_Oil_Press_DiffMaxWarn | 4144 | Para_Hyd_Oil_Press_DiffMaxWarn |  | 17714
[8 empty] | 17715 | Para_Hyd_Oil_Press_DiffMaxWarnHys | Para_Hyd_Oil_Press_DiffMaxWarnHys | 4145 | Para_Hyd_Oil_Press_DiffMaxWarnHys |  | 17715
[8 empty] | 17716 | Para_Hyd_Oil_Press_GrEqSpeed2 | Para_Hyd_Oil_Press_GrEqSpeed2 | 4146 | Para_Hyd_Oil_Press_GrEqSpeed2 |  | 17716
[8 empty] | 17717 | Para_Hyd_Oil_Press_Hys | Para_Hyd_Oil_Press_Hys | 4147 | Para_Hyd_Oil_Press_Hys |  | 17717
[8 empty] | 17718 | Para_Hyd_Oil_Press_Limit1 | Para_Hyd_Oil_Press_Limit1 | 4148 | Para_Hyd_Oil_Press_Limit1 |  | 17718
[8 empty] | 17719 | Para_Hyd_Oil_Press_Limit1Hys | Para_Hyd_Oil_Press_Limit1Hys | 4149 | Para_Hyd_Oil_Press_Limit1Hys |  | 17719
[8 empty] | 17720 | Para_Hyd_Oil_Press_Max | Para_Hyd_Oil_Press_Max | 4150 | Para_Hyd_Oil_Press_Max |  | 17720
[8 empty] | 17721 | Para_Hyd_Oil_Press_MaxDelay | Para_Hyd_Oil_Press_MaxDelay | 4151 | Para_Hyd_Oil_Press_MaxDelay |  | 17721
[8 empty] | 17722 | Para_Hyd_Oil_Press_MaxHys | Para_Hyd_Oil_Press_MaxHys | 4152 | Para_Hyd_Oil_Press_MaxHys |  | 17722
[8 empty] | 17723 | Para_Hyd_Oil_Press_PreLubrLimit1 | Para_Hyd_Oil_Press_PreLubrLimit1 | 4153 | Para_Hyd_Oil_Press_PreLubrLimit1 |  | 17723
[8 empty] | 17724 | Para_Hyd_Oil_Press_PreLubrLimit1Hys | Para_Hyd_Oil_Press_PreLubrLimit1Hys | 4154 | Para_Hyd_Oil_Press_PreLubrLimit1Hys |  | 17724
[8 empty] | 17725 | Para_Hyd_Oil_Press_PreLubrLimit2 | Para_Hyd_Oil_Press_PreLubrLimit2 | 4155 | Para_Hyd_Oil_Press_PreLubrLimit2 |  | 17725
[8 empty] | 17726 | Para_Hyd_Oil_Press_PreLubrLimit2Hys | Para_Hyd_Oil_Press_PreLubrLimit2Hys | 4156 | Para_Hyd_Oil_Press_PreLubrLimit2Hys |  | 17726
[8 empty] | 17727 | Para_Hyd_Oil_Press_SmEqSpeed1 | Para_Hyd_Oil_Press_SmEqSpeed1 | 4157 | Para_Hyd_Oil_Press_SmEqSpeed1 |  | 17727
[8 empty] | 17728 | Para_Hyd_Oil_Press_Speed1 | Para_Hyd_Oil_Press_Speed1 | 4158 | Para_Hyd_Oil_Press_Speed1 | 1/min | 17728
[8 empty] | 17729 | Para_Hyd_Oil_Press_Speed2 | Para_Hyd_Oil_Press_Speed2 | 4159 | Para_Hyd_Oil_Press_Speed2 | 1/min | 17729
[8 empty] | 17730 | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMax | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMax | 4160 | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMax |  | 17730
[8 empty] | 17731 | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMaxHys | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMaxHys | 4161 | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMaxHys |  | 17731
[8 empty] | 17732 | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMin | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMin | 4162 | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMin |  | 17732
[8 empty] | 17733 | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMinHys | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMinHys | 4163 | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMinHys |  | 17733
[8 empty] | 17734 | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMinWarn | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMinWarn | 4164 | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMinWarn |  | 17734
[8 empty] | 17735 | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMinWarnHys | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMinWarnHys | 4165 | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMinWarnHys |  | 17735
[8 empty] | 17736 | Para_Hyd_Oil_Press_TCFiltPressOutletMin1 | Para_Hyd_Oil_Press_TCFiltPressOutletMin1 | 4166 | Para_Hyd_Oil_Press_TCFiltPressOutletMin1 |  | 17736
[8 empty] | 17737 | Para_Hyd_Oil_Press_TCFiltPressOutletMin2 | Para_Hyd_Oil_Press_TCFiltPressOutletMin2 | 4167 | Para_Hyd_Oil_Press_TCFiltPressOutletMin2 |  | 17737
[8 empty] | 17738 | Para_Hyd_Oil_Press_TCFiltPressOutletMinHys | Para_Hyd_Oil_Press_TCFiltPressOutletMinHys | 4168 | Para_Hyd_Oil_Press_TCFiltPressOutletMinHys |  | 17738
[8 empty] | 17739 | Para_Hyd_Oil_Press_TCFiltSpeedMin1PressOutlet | Para_Hyd_Oil_Press_TCFiltSpeedMin1PressOutlet | 4169 | Para_Hyd_Oil_Press_TCFiltSpeedMin1PressOutlet | 1/min | 17739
[8 empty] | 17740 | Para_Hyd_Oil_Press_TCFiltSpeedMin2PressOutlet | Para_Hyd_Oil_Press_TCFiltSpeedMin2PressOutlet | 4170 | Para_Hyd_Oil_Press_TCFiltSpeedMin2PressOutlet |  | 17740
[8 empty] | 17741 | Para_Hyd_Oil_Press_TimeDelFiltDifPress | Para_Hyd_Oil_Press_TimeDelFiltDifPress | 4171 | Para_Hyd_Oil_Press_TimeDelFiltDifPress |  | 17741
[8 empty] | 17742 | Para_Hyd_Oil_PressDiffFilter_Limit1 | Para_Hyd_Oil_PressDiffFilter_Limit1 | 4172 | Para_Hyd_Oil_PressDiffFilter_Limit1 | bar | 17742
[8 empty] | 17743 | Para_Hyd_Oil_PressDiffFilter_Limit2 | Para_Hyd_Oil_PressDiffFilter_Limit2 | 4173 | Para_Hyd_Oil_PressDiffFilter_Limit2 | bar | 17743
[8 empty] | 17744 | Para_Hyd_Oil_PressDiffFilter_Limit3 | Para_Hyd_Oil_PressDiffFilter_Limit3 | 4174 | Para_Hyd_Oil_PressDiffFilter_Limit3 | bar | 17744
[8 empty] | 17745 | Para_Hyd_Oil_PressDiffFilter_LimitDelay1 | Para_Hyd_Oil_PressDiffFilter_LimitDelay1 | 4175 | Para_Hyd_Oil_PressDiffFilter_LimitDelay1 |  | 17745
[8 empty] | 17746 | Para_Hyd_Oil_PressDiffFilter_LimitDelay2 | Para_Hyd_Oil_PressDiffFilter_LimitDelay2 | 4176 | Para_Hyd_Oil_PressDiffFilter_LimitDelay2 |  | 17746
[8 empty] | 17747 | Para_Hyd_Oil_PressDiffFilter_LimitDelay3 | Para_Hyd_Oil_PressDiffFilter_LimitDelay3 | 4177 | Para_Hyd_Oil_PressDiffFilter_LimitDelay3 |  | 17747
[8 empty] | 17748 | Para_Hyd_Oil_PressDiffFilter_ReleaseTemp | Para_Hyd_Oil_PressDiffFilter_ReleaseTemp | 4178 | Para_Hyd_Oil_PressDiffFilter_ReleaseTemp | °C | 17748
[8 empty] | 17749 | Para_Hyd_Oil_PressFilterIn_20mA | Para_Hyd_Oil_PressFilterIn_20mA | 4179 | Para_Hyd_Oil_PressFilterIn_20mA |  | 17749
[8 empty] | 17750 | Para_Hyd_Oil_PressFilterIn_4mA | Para_Hyd_Oil_PressFilterIn_4mA | 4180 | Para_Hyd_Oil_PressFilterIn_4mA |  | 17750
[8 empty] | 17751 | Para_Hyd_Oil_PressFilterIn_ActMeasure | Para_Hyd_Oil_PressFilterIn_ActMeasure | 4181 | Para_Hyd_Oil_PressFilterIn_ActMeasure |  | 17751
[8 empty] | 17752 | Para_Hyd_Oil_Temp_Limit1 | Para_Hyd_Oil_Temp_Limit1 | 4182 | Para_Hyd_Oil_Temp_Limit1 |  | 17752
[8 empty] | 17753 | Para_Hyd_Oil_Temp_Limit1Hys | Para_Hyd_Oil_Temp_Limit1Hys | 4183 | Para_Hyd_Oil_Temp_Limit1Hys | d°C | 17753
[8 empty] | 17754 | Para_Hyd_Oil_Temp_Limit2 | Para_Hyd_Oil_Temp_Limit2 | 4184 | Para_Hyd_Oil_Temp_Limit2 | °C | 17754
[8 empty] | 17755 | Para_Hyd_Oil_Temp_Limit2Hys | Para_Hyd_Oil_Temp_Limit2Hys | 4185 | Para_Hyd_Oil_Temp_Limit2Hys | °C | 17755
[8 empty] | 17756 | Para_Hyd_Oil_Temp_LimitPreWarm | Para_Hyd_Oil_Temp_LimitPreWarm | 4186 | Para_Hyd_Oil_Temp_LimitPreWarm |  | 17756
[8 empty] | 17757 | Para_Hyd_Oil_Temp_LimitPreWarmHys | Para_Hyd_Oil_Temp_LimitPreWarmHys | 4187 | Para_Hyd_Oil_Temp_LimitPreWarmHys | d°C | 17757
[8 empty] | 17758 | Para_Hyd_Oil_Temp_LoadEnab | Para_Hyd_Oil_Temp_LoadEnab | 4188 | Para_Hyd_Oil_Temp_LoadEnab |  | 17758
[8 empty] | 17759 | Para_Hyd_Oil_Temp_LoadEnabHys | Para_Hyd_Oil_Temp_LoadEnabHys | 4189 | Para_Hyd_Oil_Temp_LoadEnabHys | d°C | 17759
[8 empty] | 17760 | Para_Hyd_Oil_Temp_Max | Para_Hyd_Oil_Temp_Max | 4190 | Para_Hyd_Oil_Temp_Max |  | 17760
[8 empty] | 17761 | Para_Hyd_Oil_Temp_MaxHys | Para_Hyd_Oil_Temp_MaxHys | 4191 | Para_Hyd_Oil_Temp_MaxHys | d°C | 17761
[8 empty] | 17762 | Para_Hyd_Oil_Temp_Min | Para_Hyd_Oil_Temp_Min | 4192 | Para_Hyd_Oil_Temp_Min |  | 17762
[8 empty] | 17763 | Para_Hyd_Oil_Temp_MinHys | Para_Hyd_Oil_Temp_MinHys | 4193 | Para_Hyd_Oil_Temp_MinHys | d°C | 17763
[8 empty] | 17764 | Para_Hyd_Oil_TurboCh_TCType | Para_Hyd_Oil_TurboCh_TCType | 4194 | Para_Hyd_Oil_TurboCh_TCType |  | 17764
[8 empty] | 17765 | Para_Hyd_RetWat_20mA | Para_Hyd_RetWat_20mA | 4195 | Para_Hyd_RetWat_20mA |  | 17765
[8 empty] | 17766 | Para_Hyd_RetWat_Act | Para_Hyd_RetWat_Act | 4196 | Para_Hyd_RetWat_Act |  | 17766
[8 empty] | 17767 | Para_Hyd_RetWat_ActSigTrip | Para_Hyd_RetWat_ActSigTrip | 4197 | Para_Hyd_RetWat_ActSigTrip |  | 17767
[8 empty] | 17768 | Para_Hyd_RetWat_Limit | Para_Hyd_RetWat_Limit | 4198 | Para_Hyd_RetWat_Limit |  | 17768
[8 empty] | 17769 | Para_Hyd_RetWat_Limit1 | Para_Hyd_RetWat_Limit1 | 4199 | Para_Hyd_RetWat_Limit1 |  | 17769
[8 empty] | 17770 | Para_Hyd_RetWat_Limit1Hys | Para_Hyd_RetWat_Limit1Hys | 4200 | Para_Hyd_RetWat_Limit1Hys | d°C | 17770
[8 empty] | 17771 | Para_Hyd_RetWat_LimitHys | Para_Hyd_RetWat_LimitHys | 4201 | Para_Hyd_RetWat_LimitHys | d°C | 17771
[8 empty] | 17772 | Para_Hyd_RetWatCoolOut_20mA | Para_Hyd_RetWatCoolOut_20mA | 4202 | Para_Hyd_RetWatCoolOut_20mA |  | 17772
[8 empty] | 17773 | Para_Hyd_RetWatCoolOut_Act | Para_Hyd_RetWatCoolOut_Act | 4203 | Para_Hyd_RetWatCoolOut_Act |  | 17773
[8 empty] | 17774 | Para_Hyd_RetWatCoolOut_ActSigTrip | Para_Hyd_RetWatCoolOut_ActSigTrip | 4204 | Para_Hyd_RetWatCoolOut_ActSigTrip |  | 17774
[8 empty] | 17775 | Para_Hyd_RetWatCoolOut_Limit | Para_Hyd_RetWatCoolOut_Limit | 4205 | Para_Hyd_RetWatCoolOut_Limit |  | 17775
[8 empty] | 17776 | Para_Hyd_RetWatCoolOut_Limit1 | Para_Hyd_RetWatCoolOut_Limit1 | 4206 | Para_Hyd_RetWatCoolOut_Limit1 |  | 17776
[8 empty] | 17777 | Para_Hyd_RetWatCoolOut_Limit1Hys | Para_Hyd_RetWatCoolOut_Limit1Hys | 4207 | Para_Hyd_RetWatCoolOut_Limit1Hys | d°C | 17777
[8 empty] | 17778 | Para_Hyd_RetWatCoolOut_LimitHys | Para_Hyd_RetWatCoolOut_LimitHys | 4208 | Para_Hyd_RetWatCoolOut_LimitHys | d°C | 17778
[8 empty] | 19495 | Para_Hyd_RetWatLowTemp_Act | Para_Hyd_RetWatLowTemp_Act | 4209 | Para_Hyd_RetWatLowTemp_Act |  | 19495
[8 empty] | 19496 | Para_Hyd_RetWatLowTemp_Limit | Para_Hyd_RetWatLowTemp_Limit | 4210 | Para_Hyd_RetWatLowTemp_Limit | °C | 19496
[8 empty] | 19497 | Para_Hyd_RetWatLowTemp_LimitHys | Para_Hyd_RetWatLowTemp_LimitHys | 4211 | Para_Hyd_RetWatLowTemp_LimitHys | °C | 19497
[8 empty] | 18058 | Para_Hyd_RetWatPreEng_Act | Para_Hyd_RetWatPreEng_Act | 4212 | Para_Hyd_RetWatPreEng_Act |  | 18058
[8 empty] | 18059 | Para_Hyd_RetWatPreEng_ActSigTrip | Para_Hyd_RetWatPreEng_ActSigTrip | 4213 | Para_Hyd_RetWatPreEng_ActSigTrip |  | 18059
[8 empty] | 18060 | Para_Hyd_RetWatPreEng_Limit | Para_Hyd_RetWatPreEng_Limit | 4214 | Para_Hyd_RetWatPreEng_Limit |  | 18060
[8 empty] | 18061 | Para_Hyd_RetWatPreEng_Limit1 | Para_Hyd_RetWatPreEng_Limit1 | 4215 | Para_Hyd_RetWatPreEng_Limit1 |  | 18061
[8 empty] | 18062 | Para_Hyd_RetWatPreEng_Limit1Hys | Para_Hyd_RetWatPreEng_Limit1Hys | 4216 | Para_Hyd_RetWatPreEng_Limit1Hys | d°C | 18062
[8 empty] | 18063 | Para_Hyd_RetWatPreEng_LimitHys | Para_Hyd_RetWatPreEng_LimitHys | 4217 | Para_Hyd_RetWatPreEng_LimitHys | d°C | 18063
[8 empty] | 18064 | Para_Hyd_SupWat_20mA | Para_Hyd_SupWat_20mA | 4218 | Para_Hyd_SupWat_20mA |  | 18064
[8 empty] | 18065 | Para_Hyd_SupWat_Act | Para_Hyd_SupWat_Act | 4219 | Para_Hyd_SupWat_Act |  | 18065
[8 empty] | 18066 | Para_Hyd_SupWat_ActSigTrip | Para_Hyd_SupWat_ActSigTrip | 4220 | Para_Hyd_SupWat_ActSigTrip |  | 18066
[8 empty] | 18067 | Para_Hyd_SupWat_Limit | Para_Hyd_SupWat_Limit | 4221 | Para_Hyd_SupWat_Limit |  | 18067
[8 empty] | 18068 | Para_Hyd_SupWat_Limit1 | Para_Hyd_SupWat_Limit1 | 4222 | Para_Hyd_SupWat_Limit1 |  | 18068
[8 empty] | 18069 | Para_Hyd_SupWat_Limit1Hys | Para_Hyd_SupWat_Limit1Hys | 4223 | Para_Hyd_SupWat_Limit1Hys | d°C | 18069
[8 empty] | 18070 | Para_Hyd_SupWat_LimitHys | Para_Hyd_SupWat_LimitHys | 4224 | Para_Hyd_SupWat_LimitHys | d°C | 18070
[8 empty] | 10008416 | Para_Hydraulic_Condenser_T_CD_Re_Active | Para_Hydraulic_Condenser_T_CD_Re_Active | 4225 | Para_Hydraulic_Condenser_T_CD_Re_Active |  | 10008416
[8 empty] | 10008414 | Para_Hydraulic_Condenser_T_CD_Re_HyHi | Para_Hydraulic_Condenser_T_CD_Re_HyHi | 4226 | Para_Hydraulic_Condenser_T_CD_Re_HyHi |  | 10008414
[8 empty] | 10008413 | Para_Hydraulic_Condenser_T_CD_Re_LimHi | Para_Hydraulic_Condenser_T_CD_Re_LimHi | 4227 | Para_Hydraulic_Condenser_T_CD_Re_LimHi |  | 10008413
[8 empty] | 10008412 | Para_Hydraulic_Condenser_T_CD_Su_Active | Para_Hydraulic_Condenser_T_CD_Su_Active | 4228 | Para_Hydraulic_Condenser_T_CD_Su_Active |  | 10008412
[8 empty] | 10008411 | Para_Hydraulic_Condenser_T_CD_Su_HyHi | Para_Hydraulic_Condenser_T_CD_Su_HyHi | 4229 | Para_Hydraulic_Condenser_T_CD_Su_HyHi |  | 10008411
[8 empty] | 10008410 | Para_Hydraulic_Condenser_T_CD_Su_LimHi | Para_Hydraulic_Condenser_T_CD_Su_LimHi | 4230 | Para_Hydraulic_Condenser_T_CD_Su_LimHi |  | 10008410
[8 empty] | 10000322 | Para_Hydraulic_CoolWat_ECWP_MechDriven | Para_Hydraulic_CoolWat_ECWP_MechDriven | 4231 | Para_Hydraulic_CoolWat_ECWP_MechDriven |  | 10000322
[8 empty] | 10000329 | Para_Hydraulic_CoolWat_N_ECWP_Set | Para_Hydraulic_CoolWat_N_ECWP_Set | 4232 | Para_Hydraulic_CoolWat_N_ECWP_Set |  | 10000329
[8 empty] | 10002557 | Para_Hydraulic_CoolWat_Press_Pr_ECWaEng_Active | Para_Hydraulic_CoolWat_Press_Pr_ECWaEng_Active | 4233 | Para_Hydraulic_CoolWat_Press_Pr_ECWaEng_Active |  | 10002557
[8 empty] | 10002566 | Para_Hydraulic_CoolWat_Press_Pr_ECWaEng_ScalMax | Para_Hydraulic_CoolWat_Press_Pr_ECWaEng_ScalMax | 4234 | Para_Hydraulic_CoolWat_Press_Pr_ECWaEng_ScalMax |  | 10002566
[8 empty] | 10008560 | Para_Hydraulic_CoolWat_T_ECW_bChC_HT_Active | Para_Hydraulic_CoolWat_T_ECW_bChC_HT_Active | 4235 | Para_Hydraulic_CoolWat_T_ECW_bChC_HT_Active |  | 10008560
[8 empty] | 10008564 | Para_Hydraulic_CoolWat_T_ECW_bECWC_Active | Para_Hydraulic_CoolWat_T_ECW_bECWC_Active | 4236 | Para_Hydraulic_CoolWat_T_ECW_bECWC_Active |  | 10008564
[8 empty] | 10008563 | Para_Hydraulic_CoolWat_T_ECW_bOilC_Active | Para_Hydraulic_CoolWat_T_ECW_bOilC_Active | 4237 | Para_Hydraulic_CoolWat_T_ECW_bOilC_Active |  | 10008563
[8 empty] | 10000185 | Para_Hydraulic_CoolWat_Temp_T_ECW_HyBpV | Para_Hydraulic_CoolWat_Temp_T_ECW_HyBpV | 4238 | Para_Hydraulic_CoolWat_Temp_T_ECW_HyBpV |  | 10000185
[8 empty] | 10000184 | Para_Hydraulic_CoolWat_Temp_T_ECW_LimBpV | Para_Hydraulic_CoolWat_Temp_T_ECW_LimBpV | 4239 | Para_Hydraulic_CoolWat_Temp_T_ECW_LimBpV |  | 10000184
[8 empty] | 10002564 | Para_Hydraulic_CoolWat_Temp_T_ECWbEng_Active | Para_Hydraulic_CoolWat_Temp_T_ECWbEng_Active | 4240 | Para_Hydraulic_CoolWat_Temp_T_ECWbEng_Active |  | 10002564
[8 empty] | 10008215 | Para_Hydraulic_CoolWatModule_T_ECW_Mod_In_Active | Para_Hydraulic_CoolWatModule_T_ECW_Mod_In_Active | 4241 | Para_Hydraulic_CoolWatModule_T_ECW_Mod_In_Active |  | 10008215
[8 empty] | 10008253 | Para_Hydraulic_CoolWatModule_T_ECW_Mod_Out_Active | Para_Hydraulic_CoolWatModule_T_ECW_Mod_Out_Active | 4242 | Para_Hydraulic_CoolWatModule_T_ECW_Mod_Out_Active |  | 10008253
[8 empty] | 10001486 | Para_Hydraulic_CrankCase_DPr_BbFilt_Hi_P1 | Para_Hydraulic_CrankCase_DPr_BbFilt_Hi_P1 | 4243 | Para_Hydraulic_CrankCase_DPr_BbFilt_Hi_P1 |  | 10001486
[8 empty] | 10001489 | Para_Hydraulic_CrankCase_DPr_BbFilt_Hi_P2 | Para_Hydraulic_CrankCase_DPr_BbFilt_Hi_P2 | 4244 | Para_Hydraulic_CrankCase_DPr_BbFilt_Hi_P2 |  | 10001489
[8 empty] | 10001485 | Para_Hydraulic_CrankCase_DPr_BbFilt_Lo_P1 | Para_Hydraulic_CrankCase_DPr_BbFilt_Lo_P1 | 4245 | Para_Hydraulic_CrankCase_DPr_BbFilt_Lo_P1 |  | 10001485
[8 empty] | 10001487 | Para_Hydraulic_CrankCase_DPr_BbFilt_Lo_P2 | Para_Hydraulic_CrankCase_DPr_BbFilt_Lo_P2 | 4246 | Para_Hydraulic_CrankCase_DPr_BbFilt_Lo_P2 |  | 10001487
[8 empty] | 10001490 | Para_Hydraulic_CrankCase_DPr_BbFilt_Pstart | Para_Hydraulic_CrankCase_DPr_BbFilt_Pstart | 4247 | Para_Hydraulic_CrankCase_DPr_BbFilt_Pstart |  | 10001490
[8 empty] | 10000530 | Para_Hydraulic_CrankCase_Pc_BbBlower_Hi | Para_Hydraulic_CrankCase_Pc_BbBlower_Hi | 4248 | Para_Hydraulic_CrankCase_Pc_BbBlower_Hi |  | 10000530
[8 empty] | 10008398 | Para_Hydraulic_CrankCase_Pr_a_BbFilt_A_Exist | Para_Hydraulic_CrankCase_Pr_a_BbFilt_A_Exist | 4249 | Para_Hydraulic_CrankCase_Pr_a_BbFilt_A_Exist |  | 10008398
[8 empty] | 10008399 | Para_Hydraulic_CrankCase_Pr_a_BbFilt_B_Exist | Para_Hydraulic_CrankCase_Pr_a_BbFilt_B_Exist | 4250 | Para_Hydraulic_CrankCase_Pr_a_BbFilt_B_Exist |  | 10008399
[8 empty] | 10001401 | Para_Hydraulic_CrankCase_Pr_a_BbFilt_Exist | Para_Hydraulic_CrankCase_Pr_a_BbFilt_Exist | 4251 | Para_Hydraulic_CrankCase_Pr_a_BbFilt_Exist |  | 10001401
[8 empty] | 10001396 | Para_Hydraulic_CrankCase_Pr_a_BbFiltScalMax | Para_Hydraulic_CrankCase_Pr_a_BbFiltScalMax | 4252 | Para_Hydraulic_CrankCase_Pr_a_BbFiltScalMax |  | 10001396
[8 empty] | 10001397 | Para_Hydraulic_CrankCase_Pr_a_BbFiltScalMin | Para_Hydraulic_CrankCase_Pr_a_BbFiltScalMin | 4253 | Para_Hydraulic_CrankCase_Pr_a_BbFiltScalMin |  | 10001397
[8 empty] | 10000528 | Para_Hydraulic_CrankCase_Pr_CC_Hi | Para_Hydraulic_CrankCase_Pr_CC_Hi | 4254 | Para_Hydraulic_CrankCase_Pr_CC_Hi |  | 10000528
[8 empty] | 10000527 | Para_Hydraulic_CrankCase_Pr_CC_Lo | Para_Hydraulic_CrankCase_Pr_CC_Lo | 4255 | Para_Hydraulic_CrankCase_Pr_CC_Lo |  | 10000527
[8 empty] | 10000524 | Para_Hydraulic_CrankCase_Pr_CCScalMax | Para_Hydraulic_CrankCase_Pr_CCScalMax | 4256 | Para_Hydraulic_CrankCase_Pr_CCScalMax |  | 10000524
[8 empty] | 10000526 | Para_Hydraulic_CrankCase_Pr_CCScalMin | Para_Hydraulic_CrankCase_Pr_CCScalMin | 4257 | Para_Hydraulic_CrankCase_Pr_CCScalMin |  | 10000526
[8 empty] | 10008396 | Para_Hydraulic_CrankCase_Pr_f_BbFilt_A_Exist | Para_Hydraulic_CrankCase_Pr_f_BbFilt_A_Exist | 4258 | Para_Hydraulic_CrankCase_Pr_f_BbFilt_A_Exist |  | 10008396
[8 empty] | 10008397 | Para_Hydraulic_CrankCase_Pr_f_BbFilt_B_Exist | Para_Hydraulic_CrankCase_Pr_f_BbFilt_B_Exist | 4259 | Para_Hydraulic_CrankCase_Pr_f_BbFilt_B_Exist |  | 10008397
[8 empty] | 10000529 | Para_Hydraulic_CrankCase_Pr_f_BbFilt_Exist | Para_Hydraulic_CrankCase_Pr_f_BbFilt_Exist | 4260 | Para_Hydraulic_CrankCase_Pr_f_BbFilt_Exist |  | 10000529
[8 empty] | 10001395 | Para_Hydraulic_CrankCase_Pr_f_BbFiltScalMax | Para_Hydraulic_CrankCase_Pr_f_BbFiltScalMax | 4261 | Para_Hydraulic_CrankCase_Pr_f_BbFiltScalMax |  | 10001395
[8 empty] | 10000531 | Para_Hydraulic_CrankCase_Pr_f_BbFiltScalMin | Para_Hydraulic_CrankCase_Pr_f_BbFiltScalMin | 4262 | Para_Hydraulic_CrankCase_Pr_f_BbFiltScalMin |  | 10000531
[8 empty] | 10001389 | Para_Hydraulic_CrankCase_tiPr_CC_Hi | Para_Hydraulic_CrankCase_tiPr_CC_Hi | 4263 | Para_Hydraulic_CrankCase_tiPr_CC_Hi |  | 10001389
[8 empty] | 10001393 | Para_Hydraulic_CrankCase_tiPr_CC_HiHi | Para_Hydraulic_CrankCase_tiPr_CC_HiHi | 4264 | Para_Hydraulic_CrankCase_tiPr_CC_HiHi |  | 10001393
[8 empty] | 10008458 | Para_Hydraulic_HeatCircuitRetWater_T_HW_HC_Re_Active | Para_Hydraulic_HeatCircuitRetWater_T_HW_HC_Re_Active | 4265 | Para_Hydraulic_HeatCircuitRetWater_T_HW_HC_Re_Active |  | 10008458
[8 empty] | 10008452 | Para_Hydraulic_HeatCircuitRetWater_T_HW_HC_Re_HyHi | Para_Hydraulic_HeatCircuitRetWater_T_HW_HC_Re_HyHi | 4266 | Para_Hydraulic_HeatCircuitRetWater_T_HW_HC_Re_HyHi |  | 10008452
[8 empty] | 10008451 | Para_Hydraulic_HeatCircuitRetWater_T_HW_HC_Re_LimHi | Para_Hydraulic_HeatCircuitRetWater_T_HW_HC_Re_LimHi | 4267 | Para_Hydraulic_HeatCircuitRetWater_T_HW_HC_Re_LimHi |  | 10008451
[8 empty] | 10008355 | Para_Hydraulic_HeatOutputCounter_Cnt_P_Heat | Para_Hydraulic_HeatOutputCounter_Cnt_P_Heat | 4268 | Para_Hydraulic_HeatOutputCounter_Cnt_P_Heat |  | 10008355
[8 empty] | 10008354 | Para_Hydraulic_HeatOutputCounter_ImpVal_Cnt_P_Heat | Para_Hydraulic_HeatOutputCounter_ImpVal_Cnt_P_Heat | 4269 | Para_Hydraulic_HeatOutputCounter_ImpVal_Cnt_P_Heat |  | 10008354
[8 empty] | 10008351 | Para_Hydraulic_HeatOutputCounter_P_Heat_Active | Para_Hydraulic_HeatOutputCounter_P_Heat_Active | 4270 | Para_Hydraulic_HeatOutputCounter_P_Heat_Active |  | 10008351
[8 empty] | 10008353 | Para_Hydraulic_HeatOutputCounter_P_Heat_ScalMax | Para_Hydraulic_HeatOutputCounter_P_Heat_ScalMax | 4271 | Para_Hydraulic_HeatOutputCounter_P_Heat_ScalMax |  | 10008353
[8 empty] | 10008352 | Para_Hydraulic_HeatOutputCounter_P_Heat_ScalMin | Para_Hydraulic_HeatOutputCounter_P_Heat_ScalMin | 4272 | Para_Hydraulic_HeatOutputCounter_P_Heat_ScalMin |  | 10008352
[8 empty] | 10008229 | Para_Hydraulic_HeatWaterHigh_Pr_HW_Re_HT_Active | Para_Hydraulic_HeatWaterHigh_Pr_HW_Re_HT_Active | 4273 | Para_Hydraulic_HeatWaterHigh_Pr_HW_Re_HT_Active |  | 10008229
[8 empty] | 10008231 | Para_Hydraulic_HeatWaterHigh_Pr_HW_Re_HT_ScalMax | Para_Hydraulic_HeatWaterHigh_Pr_HW_Re_HT_ScalMax | 4274 | Para_Hydraulic_HeatWaterHigh_Pr_HW_Re_HT_ScalMax |  | 10008231
[8 empty] | 10008230 | Para_Hydraulic_HeatWaterHigh_Pr_HW_Re_HT_ScalMin | Para_Hydraulic_HeatWaterHigh_Pr_HW_Re_HT_ScalMin | 4275 | Para_Hydraulic_HeatWaterHigh_Pr_HW_Re_HT_ScalMin |  | 10008230
[8 empty] | 10000729 | Para_Hydraulic_HeatWaterHigh_Pr_HW_Su_HT_Active | Para_Hydraulic_HeatWaterHigh_Pr_HW_Su_HT_Active | 4276 | Para_Hydraulic_HeatWaterHigh_Pr_HW_Su_HT_Active |  | 10000729
[8 empty] | 10000727 | Para_Hydraulic_HeatWaterHigh_Pr_HW_Su_HT_ScalMax | Para_Hydraulic_HeatWaterHigh_Pr_HW_Su_HT_ScalMax | 4277 | Para_Hydraulic_HeatWaterHigh_Pr_HW_Su_HT_ScalMax |  | 10000727
[8 empty] | 10008202 | Para_Hydraulic_HeatWaterLow_Pr_HW_Re_LT_Active | Para_Hydraulic_HeatWaterLow_Pr_HW_Re_LT_Active | 4278 | Para_Hydraulic_HeatWaterLow_Pr_HW_Re_LT_Active |  | 10008202
[8 empty] | 10008206 | Para_Hydraulic_HeatWaterLow_Pr_HW_Re_LT_ScalMax | Para_Hydraulic_HeatWaterLow_Pr_HW_Re_LT_ScalMax | 4279 | Para_Hydraulic_HeatWaterLow_Pr_HW_Re_LT_ScalMax |  | 10008206
[8 empty] | 10008205 | Para_Hydraulic_HeatWaterLow_Pr_HW_Re_LT_ScalMin | Para_Hydraulic_HeatWaterLow_Pr_HW_Re_LT_ScalMin | 4280 | Para_Hydraulic_HeatWaterLow_Pr_HW_Re_LT_ScalMin |  | 10008205
[8 empty] | 10001488 | Para_Hydraulic_HeatWaterLow_Pr_HW_Su_LT_Active | Para_Hydraulic_HeatWaterLow_Pr_HW_Su_LT_Active | 4281 | Para_Hydraulic_HeatWaterLow_Pr_HW_Su_LT_Active |  | 10001488
[8 empty] | 10001484 | Para_Hydraulic_HeatWaterLow_Pr_HW_Su_LT_ScalMax | Para_Hydraulic_HeatWaterLow_Pr_HW_Su_LT_ScalMax | 4282 | Para_Hydraulic_HeatWaterLow_Pr_HW_Su_LT_ScalMax |  | 10001484
[8 empty] | 10001507 | Para_Hydraulic_HeatWaterLow_T_HW_Su_LT_Active | Para_Hydraulic_HeatWaterLow_T_HW_Su_LT_Active | 4283 | Para_Hydraulic_HeatWaterLow_T_HW_Su_LT_Active |  | 10001507
[8 empty] | 10000151 | Para_Hydraulic_Oil_EO_Level_Active | Para_Hydraulic_Oil_EO_Level_Active | 4284 | Para_Hydraulic_Oil_EO_Level_Active |  | 10000151
[8 empty] | 10001377 | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_DE_Exist | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_DE_Exist | 4285 | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_DE_Exist |  | 10001377
[8 empty] | 10001382 | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_DE_Hi | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_DE_Hi | 4286 | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_DE_Hi |  | 10001382
[8 empty] | 10001378 | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_DE_Lo | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_DE_Lo | 4287 | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_DE_Lo |  | 10001378
[8 empty] | 10001379 | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_DEScalMax | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_DEScalMax | 4288 | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_DEScalMax |  | 10001379
[8 empty] | 10001376 | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_DEScalMin | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_DEScalMin | 4289 | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_DEScalMin |  | 10001376
[8 empty] | 10001381 | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_NDE_Exist | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_NDE_Exist | 4290 | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_NDE_Exist |  | 10001381
[8 empty] | 10001384 | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_NDE_Hi | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_NDE_Hi | 4291 | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_NDE_Hi |  | 10001384
[8 empty] | 10001386 | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_NDE_Lo | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_NDE_Lo | 4292 | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_NDE_Lo |  | 10001386
[8 empty] | 10001380 | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_NDEScalMax | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_NDEScalMax | 4293 | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_NDEScalMax |  | 10001380
[8 empty] | 10001383 | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_NDEScalMin | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_NDEScalMin | 4294 | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_NDEScalMin |  | 10001383
[8 empty] | 10001349 | Para_Hydraulic_Oil_GenOilSkid_Lev_OilSkid_Tank_Exist | Para_Hydraulic_Oil_GenOilSkid_Lev_OilSkid_Tank_Exist | 4295 | Para_Hydraulic_Oil_GenOilSkid_Lev_OilSkid_Tank_Exist |  | 10001349
[8 empty] | 10001366 | Para_Hydraulic_Oil_GenOilSkid_Lev_OilSkid_Tank_Lo | Para_Hydraulic_Oil_GenOilSkid_Lev_OilSkid_Tank_Lo | 4296 | Para_Hydraulic_Oil_GenOilSkid_Lev_OilSkid_Tank_Lo |  | 10001366
[8 empty] | 10001364 | Para_Hydraulic_Oil_GenOilSkid_Lev_OilSkid_Tank_LoLo | Para_Hydraulic_Oil_GenOilSkid_Lev_OilSkid_Tank_LoLo | 4297 | Para_Hydraulic_Oil_GenOilSkid_Lev_OilSkid_Tank_LoLo |  | 10001364
[8 empty] | 10001365 | Para_Hydraulic_Oil_GenOilSkid_Lev_OilSkid_TankScalMax | Para_Hydraulic_Oil_GenOilSkid_Lev_OilSkid_TankScalMax | 4298 | Para_Hydraulic_Oil_GenOilSkid_Lev_OilSkid_TankScalMax |  | 10001365
[8 empty] | 10001351 | Para_Hydraulic_Oil_GenOilSkid_Lev_OilSkid_TankScalMin | Para_Hydraulic_Oil_GenOilSkid_Lev_OilSkid_TankScalMin | 4299 | Para_Hydraulic_Oil_GenOilSkid_Lev_OilSkid_TankScalMin |  | 10001351
[8 empty] | 10001392 | Para_Hydraulic_Oil_GenOilSkid_Pr_OilSkid_HP_DE_Exist | Para_Hydraulic_Oil_GenOilSkid_Pr_OilSkid_HP_DE_Exist | 4300 | Para_Hydraulic_Oil_GenOilSkid_Pr_OilSkid_HP_DE_Exist |  | 10001392
[8 empty] | 10001388 | Para_Hydraulic_Oil_GenOilSkid_Pr_OilSkid_HP_Lo | Para_Hydraulic_Oil_GenOilSkid_Pr_OilSkid_HP_Lo | 4301 | Para_Hydraulic_Oil_GenOilSkid_Pr_OilSkid_HP_Lo |  | 10001388
[8 empty] | 10001391 | Para_Hydraulic_Oil_GenOilSkid_Pr_OilSkid_HP_NDE_Exist | Para_Hydraulic_Oil_GenOilSkid_Pr_OilSkid_HP_NDE_Exist | 4302 | Para_Hydraulic_Oil_GenOilSkid_Pr_OilSkid_HP_NDE_Exist |  | 10001391
[8 empty] | 10001390 | Para_Hydraulic_Oil_GenOilSkid_Pr_OilSkid_HPScalMax | Para_Hydraulic_Oil_GenOilSkid_Pr_OilSkid_HPScalMax | 4303 | Para_Hydraulic_Oil_GenOilSkid_Pr_OilSkid_HPScalMax |  | 10001390
[8 empty] | 10001385 | Para_Hydraulic_Oil_GenOilSkid_Pr_OilSkid_HPScalMin | Para_Hydraulic_Oil_GenOilSkid_Pr_OilSkid_HPScalMin | 4304 | Para_Hydraulic_Oil_GenOilSkid_Pr_OilSkid_HPScalMin |  | 10001385
[8 empty] | 10001369 | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_Supply_Exist | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_Supply_Exist | 4305 | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_Supply_Exist |  | 10001369
[8 empty] | 10001373 | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_Supply_Hi | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_Supply_Hi | 4306 | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_Supply_Hi |  | 10001373
[8 empty] | 10001374 | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_Supply_Lo | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_Supply_Lo | 4307 | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_Supply_Lo |  | 10001374
[8 empty] | 10001375 | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_SupplyScalMax | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_SupplyScalMax | 4308 | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_SupplyScalMax |  | 10001375
[8 empty] | 10001371 | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_SupplyScalMin | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_SupplyScalMin | 4309 | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_SupplyScalMin |  | 10001371
[8 empty] | 10001368 | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_Tank_Exist | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_Tank_Exist | 4310 | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_Tank_Exist |  | 10001368
[8 empty] | 10001372 | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_Tank_Set | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_Tank_Set | 4311 | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_Tank_Set |  | 10001372
[8 empty] | 10001370 | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_TankScalMax | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_TankScalMax | 4312 | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_TankScalMax |  | 10001370
[8 empty] | 10001367 | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_TankScalMin | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_TankScalMin | 4313 | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_TankScalMin |  | 10001367
[8 empty] | 10001387 | Para_Hydraulic_Oil_GenOilSkid_tiOilSkid_PumpHP_Run | Para_Hydraulic_Oil_GenOilSkid_tiOilSkid_PumpHP_Run | 4314 | Para_Hydraulic_Oil_GenOilSkid_tiOilSkid_PumpHP_Run |  | 10001387
[8 empty] | 10008559 | Para_Hydraulic_Oil_OilFilterUnit_DPr_OFU_Filt_LimHi | Para_Hydraulic_Oil_OilFilterUnit_DPr_OFU_Filt_LimHi | 4315 | Para_Hydraulic_Oil_OilFilterUnit_DPr_OFU_Filt_LimHi |  | 10008559
[8 empty] | 10008551 | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUaFilt_Active | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUaFilt_Active | 4316 | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUaFilt_Active |  | 10008551
[8 empty] | 10008557 | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUaFilt_ScalMax | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUaFilt_ScalMax | 4317 | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUaFilt_ScalMax |  | 10008557
[8 empty] | 10008554 | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUaFilt_ScalMin | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUaFilt_ScalMin | 4318 | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUaFilt_ScalMin |  | 10008554
[8 empty] | 10008533 | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbCentrifuge_Active | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbCentrifuge_Active | 4319 | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbCentrifuge_Active |  | 10008533
[8 empty] | 10008535 | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbCentrifuge_Hi | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbCentrifuge_Hi | 4320 | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbCentrifuge_Hi |  | 10008535
[8 empty] | 10008537 | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbCentrifuge_ScalMax | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbCentrifuge_ScalMax | 4321 | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbCentrifuge_ScalMax |  | 10008537
[8 empty] | 10008534 | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbCentrifuge_ScalMin | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbCentrifuge_ScalMin | 4322 | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbCentrifuge_ScalMin |  | 10008534
[8 empty] | 10008552 | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbFilt_Active | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbFilt_Active | 4323 | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbFilt_Active |  | 10008552
[8 empty] | 10008528 | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbFilt_Hi | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbFilt_Hi | 4324 | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbFilt_Hi |  | 10008528
[8 empty] | 10008556 | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbFilt_ScalMax | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbFilt_ScalMax | 4325 | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbFilt_ScalMax |  | 10008556
[8 empty] | 10008555 | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbFilt_ScalMin | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbFilt_ScalMin | 4326 | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbFilt_ScalMin |  | 10008555
[8 empty] | 10008553 | Para_Hydraulic_Oil_OilFiltUnit_Exist | Para_Hydraulic_Oil_OilFiltUnit_Exist | 4327 | Para_Hydraulic_Oil_OilFiltUnit_Exist |  | 10008553
[8 empty] | 10001348 | Para_Hydraulic_Oil_OilSkid_Exist | Para_Hydraulic_Oil_OilSkid_Exist | 4328 | Para_Hydraulic_Oil_OilSkid_Exist |  | 10001348
[8 empty] | 10000319 | Para_Hydraulic_Oil_Press_EngTyp3_Prelub_Active | Para_Hydraulic_Oil_Press_EngTyp3_Prelub_Active | 4329 | Para_Hydraulic_Oil_Press_EngTyp3_Prelub_Active |  | 10000319
[8 empty] | 10001514 | Para_Hydraulic_Oil_Press_EOP_PreHeat_Set | Para_Hydraulic_Oil_Press_EOP_PreHeat_Set | 4330 | Para_Hydraulic_Oil_Press_EOP_PreHeat_Set |  | 10001514
[8 empty] | 10001511 | Para_Hydraulic_Oil_Press_EOP_PreLube_Set | Para_Hydraulic_Oil_Press_EOP_PreLube_Set | 4331 | Para_Hydraulic_Oil_Press_EOP_PreLube_Set |  | 10001511
[8 empty] | 10008521 | Para_Hydraulic_Oil_Press_Pr_EOaP_Active | Para_Hydraulic_Oil_Press_Pr_EOaP_Active | 4332 | Para_Hydraulic_Oil_Press_Pr_EOaP_Active |  | 10008521
[8 empty] | 10008523 | Para_Hydraulic_Oil_Press_Pr_EOaP_LimHi | Para_Hydraulic_Oil_Press_Pr_EOaP_LimHi | 4333 | Para_Hydraulic_Oil_Press_Pr_EOaP_LimHi |  | 10008523
[8 empty] | 10008525 | Para_Hydraulic_Oil_Press_Pr_EOaP_LimHiHi | Para_Hydraulic_Oil_Press_Pr_EOaP_LimHiHi | 4334 | Para_Hydraulic_Oil_Press_Pr_EOaP_LimHiHi |  | 10008525
[8 empty] | 10000152 | Para_Hydraulic_Oil_Press_Pr_LimHeatRel | Para_Hydraulic_Oil_Press_Pr_LimHeatRel | 4335 | Para_Hydraulic_Oil_Press_Pr_LimHeatRel |  | 10000152
[8 empty] | 10000140 | Para_Hydraulic_Oil_PressFilterOut_Pr_EOF_After_Active | Para_Hydraulic_Oil_PressFilterOut_Pr_EOF_After_Active | 4336 | Para_Hydraulic_Oil_PressFilterOut_Pr_EOF_After_Active |  | 10000140
[8 empty] | 10001352 | Para_Hydraulic_Oil_PressFilterOut_Pr_EOF_After_ScalMax | Para_Hydraulic_Oil_PressFilterOut_Pr_EOF_After_ScalMax | 4337 | Para_Hydraulic_Oil_PressFilterOut_Pr_EOF_After_ScalMax |  | 10001352
[8 empty] | 10001350 | Para_Hydraulic_Oil_PressFilterOut_Pr_EOF_After_ScalMin | Para_Hydraulic_Oil_PressFilterOut_Pr_EOF_After_ScalMin | 4338 | Para_Hydraulic_Oil_PressFilterOut_Pr_EOF_After_ScalMin |  | 10001350
[8 empty] | 10001135 | Para_Hydraulic_Oil_Quality_OQS_Active | Para_Hydraulic_Oil_Quality_OQS_Active | 4339 | Para_Hydraulic_Oil_Quality_OQS_Active |  | 10001135
[8 empty] | 10001138 | Para_Hydraulic_Oil_Quality_OQS_Conduct_ScalMax | Para_Hydraulic_Oil_Quality_OQS_Conduct_ScalMax | 4340 | Para_Hydraulic_Oil_Quality_OQS_Conduct_ScalMax |  | 10001138
[8 empty] | 10001136 | Para_Hydraulic_Oil_Quality_OQS_Conduct_ScalMin | Para_Hydraulic_Oil_Quality_OQS_Conduct_ScalMin | 4341 | Para_Hydraulic_Oil_Quality_OQS_Conduct_ScalMin |  | 10001136
[8 empty] | 10001137 | Para_Hydraulic_Oil_Quality_OQS_Dielect_ScalMax | Para_Hydraulic_Oil_Quality_OQS_Dielect_ScalMax | 4342 | Para_Hydraulic_Oil_Quality_OQS_Dielect_ScalMax |  | 10001137
[8 empty] | 10001139 | Para_Hydraulic_Oil_Quality_OQS_Dielect_ScalMin | Para_Hydraulic_Oil_Quality_OQS_Dielect_ScalMin | 4343 | Para_Hydraulic_Oil_Quality_OQS_Dielect_ScalMin |  | 10001139
[8 empty] | 10001131 | Para_Hydraulic_Oil_Quality_OQS_Temp_ScalMax | Para_Hydraulic_Oil_Quality_OQS_Temp_ScalMax | 4344 | Para_Hydraulic_Oil_Quality_OQS_Temp_ScalMax |  | 10001131
[8 empty] | 10001132 | Para_Hydraulic_Oil_Quality_OQS_Temp_ScalMin | Para_Hydraulic_Oil_Quality_OQS_Temp_ScalMin | 4345 | Para_Hydraulic_Oil_Quality_OQS_Temp_ScalMin |  | 10001132
[8 empty] | 10001134 | Para_Hydraulic_Oil_Quality_OQS_Visco_ScalMax | Para_Hydraulic_Oil_Quality_OQS_Visco_ScalMax | 4346 | Para_Hydraulic_Oil_Quality_OQS_Visco_ScalMax |  | 10001134
[8 empty] | 10001133 | Para_Hydraulic_Oil_Quality_OQS_Visco_ScalMin | Para_Hydraulic_Oil_Quality_OQS_Visco_ScalMin | 4347 | Para_Hydraulic_Oil_Quality_OQS_Visco_ScalMin |  | 10001133
[8 empty] | 10008948 | Para_Hydraulic_Oil_ServicePrelub | Para_Hydraulic_Oil_ServicePrelub | 4348 | Para_Hydraulic_Oil_ServicePrelub |  | 10008948
[8 empty] | 10001354 | Para_Hydraulic_Oil_Temp_T_EO_Pan_Active | Para_Hydraulic_Oil_Temp_T_EO_Pan_Active | 4349 | Para_Hydraulic_Oil_Temp_T_EO_Pan_Active |  | 10001354
[8 empty] | 10000139 | Para_Hydraulic_Oil_Temp_T_EOaPump_Active | Para_Hydraulic_Oil_Temp_T_EOaPump_Active | 4350 | Para_Hydraulic_Oil_Temp_T_EOaPump_Active |  | 10000139
[8 empty] | 10000141 | Para_Hydraulic_Oil_TurboCh_Pr_Oil_LPTC_In_A | Para_Hydraulic_Oil_TurboCh_Pr_Oil_LPTC_In_A | 4351 | Para_Hydraulic_Oil_TurboCh_Pr_Oil_LPTC_In_A |  | 10000141
[8 empty] | 10000143 | Para_Hydraulic_Oil_TurboCh_Pr_Oil_LPTC_In_B | Para_Hydraulic_Oil_TurboCh_Pr_Oil_LPTC_In_B | 4352 | Para_Hydraulic_Oil_TurboCh_Pr_Oil_LPTC_In_B |  | 10000143
[8 empty] | 10000119 | Para_Hydraulic_Oil_TurboCh_Pr_TCOaF_Active | Para_Hydraulic_Oil_TurboCh_Pr_TCOaF_Active | 4353 | Para_Hydraulic_Oil_TurboCh_Pr_TCOaF_Active |  | 10000119
[8 empty] | 10002571 | Para_Hydraulic_Oil_TurboCh_Pr_TCObF_Active | Para_Hydraulic_Oil_TurboCh_Pr_TCObF_Active | 4354 | Para_Hydraulic_Oil_TurboCh_Pr_TCObF_Active |  | 10002571
[8 empty] | 10001356 | Para_Hydraulic_Oil_TurboCh_Pr_TCObF_ScalMax | Para_Hydraulic_Oil_TurboCh_Pr_TCObF_ScalMax | 4355 | Para_Hydraulic_Oil_TurboCh_Pr_TCObF_ScalMax |  | 10001356
[8 empty] | 10002569 | Para_Hydraulic_Oil_TurboCh_Pr_TCObF_ScalMin | Para_Hydraulic_Oil_TurboCh_Pr_TCObF_ScalMin | 4356 | Para_Hydraulic_Oil_TurboCh_Pr_TCObF_ScalMin |  | 10002569
[8 empty] | 10000323 | Para_Hydraulic_Oil_TurboCh_TC_PostLub_Active | Para_Hydraulic_Oil_TurboCh_TC_PostLub_Active | 4357 | Para_Hydraulic_Oil_TurboCh_TC_PostLub_Active |  | 10000323
[8 empty] | 10000326 | Para_Hydraulic_Oil_TurboCh_TC_watercooled | Para_Hydraulic_Oil_TurboCh_TC_watercooled | 4358 | Para_Hydraulic_Oil_TurboCh_TC_watercooled |  | 10000326
[8 empty] | 10002580 | Para_Hydraulic_Oil_TurboCh_tiTC_Postlub | Para_Hydraulic_Oil_TurboCh_tiTC_Postlub | 4359 | Para_Hydraulic_Oil_TurboCh_tiTC_Postlub |  | 10002580
[8 empty] | 10008211 | Para_Hydraulic_OilModule_Pr_EO_Mod_Out_Active | Para_Hydraulic_OilModule_Pr_EO_Mod_Out_Active | 4360 | Para_Hydraulic_OilModule_Pr_EO_Mod_Out_Active |  | 10008211
[8 empty] | 10008249 | Para_Hydraulic_OilModule_Pr_EO_Mod_Out_ScalMax | Para_Hydraulic_OilModule_Pr_EO_Mod_Out_ScalMax | 4361 | Para_Hydraulic_OilModule_Pr_EO_Mod_Out_ScalMax |  | 10008249
[8 empty] | 10008212 | Para_Hydraulic_OilModule_Pr_EO_Mod_Out_ScalMin | Para_Hydraulic_OilModule_Pr_EO_Mod_Out_ScalMin | 4362 | Para_Hydraulic_OilModule_Pr_EO_Mod_Out_ScalMin |  | 10008212
[8 empty] | 10008217 | Para_Hydraulic_OilModule_T_EO_Mod_In_Active | Para_Hydraulic_OilModule_T_EO_Mod_In_Active | 4363 | Para_Hydraulic_OilModule_T_EO_Mod_In_Active |  | 10008217
[8 empty] | 10008216 | Para_Hydraulic_OilModule_T_EO_Mod_Out_Active | Para_Hydraulic_OilModule_T_EO_Mod_Out_Active | 4364 | Para_Hydraulic_OilModule_T_EO_Mod_Out_Active |  | 10008216
[8 empty] | 10008208 | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_ECW_Active | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_ECW_Active | 4365 | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_ECW_Active |  | 10008208
[8 empty] | 10008193 | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_ECW_ScalMax | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_ECW_ScalMax | 4366 | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_ECW_ScalMax |  | 10008193
[8 empty] | 10008196 | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_ECW_ScalMin | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_ECW_ScalMin | 4367 | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_ECW_ScalMin |  | 10008196
[8 empty] | 10008207 | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_EO_Active | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_EO_Active | 4368 | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_EO_Active |  | 10008207
[8 empty] | 10008210 | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_EO_ScalMax | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_EO_ScalMax | 4369 | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_EO_ScalMax |  | 10008210
[8 empty] | 10008209 | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_EO_ScalMin | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_EO_ScalMin | 4370 | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_EO_ScalMin |  | 10008209
[8 empty] | 10008220 | Para_Hydraulic_PreHeat_T_HW_Re_PreH_ECW_Active | Para_Hydraulic_PreHeat_T_HW_Re_PreH_ECW_Active | 4371 | Para_Hydraulic_PreHeat_T_HW_Re_PreH_ECW_Active |  | 10008220
[8 empty] | 10008214 | Para_Hydraulic_PreHeat_T_HW_Re_PreH_EO_Active | Para_Hydraulic_PreHeat_T_HW_Re_PreH_EO_Active | 4372 | Para_Hydraulic_PreHeat_T_HW_Re_PreH_EO_Active |  | 10008214
[8 empty] | 10008218 | Para_Hydraulic_PreHeat_T_HW_Su_PreH_ECW_Active | Para_Hydraulic_PreHeat_T_HW_Su_PreH_ECW_Active | 4373 | Para_Hydraulic_PreHeat_T_HW_Su_PreH_ECW_Active |  | 10008218
[8 empty] | 10008213 | Para_Hydraulic_PreHeat_T_HW_Su_PreH_EO_Active | Para_Hydraulic_PreHeat_T_HW_Su_PreH_EO_Active | 4374 | Para_Hydraulic_PreHeat_T_HW_Su_PreH_EO_Active |  | 10008213
[8 empty] | 10000532 | Para_Hydraulic_RetWatPreEng_T_HW_ReBeEng_SF_Trip | Para_Hydraulic_RetWatPreEng_T_HW_ReBeEng_SF_Trip | 4375 | Para_Hydraulic_RetWatPreEng_T_HW_ReBeEng_SF_Trip |  | 10000532
[8 empty] | 10008360 | Para_Hydraulic_WasteHeatRec_ReturnPrim_T_Re_PriCirc_Active | Para_Hydraulic_WasteHeatRec_ReturnPrim_T_Re_PriCirc_Active | 4376 | Para_Hydraulic_WasteHeatRec_ReturnPrim_T_Re_PriCirc_Active |  | 10008360
[8 empty] | 10008361 | Para_Hydraulic_WasteHeatRec_ReturnPrim_T_Re_PriCirc_HyLimHi | Para_Hydraulic_WasteHeatRec_ReturnPrim_T_Re_PriCirc_HyLimHi | 4377 | Para_Hydraulic_WasteHeatRec_ReturnPrim_T_Re_PriCirc_HyLimHi |  | 10008361
[8 empty] | 10008363 | Para_Hydraulic_WasteHeatRec_ReturnPrim_T_Re_PriCirc_LimHi | Para_Hydraulic_WasteHeatRec_ReturnPrim_T_Re_PriCirc_LimHi | 4378 | Para_Hydraulic_WasteHeatRec_ReturnPrim_T_Re_PriCirc_LimHi |  | 10008363
[8 empty] | 10008364 | Para_Hydraulic_WasteHeatRec_ReturnSec_T_Re_SecCirc_Active | Para_Hydraulic_WasteHeatRec_ReturnSec_T_Re_SecCirc_Active | 4379 | Para_Hydraulic_WasteHeatRec_ReturnSec_T_Re_SecCirc_Active |  | 10008364
[8 empty] | 10008368 | Para_Hydraulic_WasteHeatRec_ReturnSec_T_Re_SecCirc_HyLimHi | Para_Hydraulic_WasteHeatRec_ReturnSec_T_Re_SecCirc_HyLimHi | 4380 | Para_Hydraulic_WasteHeatRec_ReturnSec_T_Re_SecCirc_HyLimHi |  | 10008368
[8 empty] | 10008366 | Para_Hydraulic_WasteHeatRec_ReturnSec_T_Re_SecCirc_LimHi | Para_Hydraulic_WasteHeatRec_ReturnSec_T_Re_SecCirc_LimHi | 4381 | Para_Hydraulic_WasteHeatRec_ReturnSec_T_Re_SecCirc_LimHi |  | 10008366
[8 empty] | 10008357 | Para_Hydraulic_WasteHeatRec_SupplyPrim_T_Su_PriCirc_Active | Para_Hydraulic_WasteHeatRec_SupplyPrim_T_Su_PriCirc_Active | 4382 | Para_Hydraulic_WasteHeatRec_SupplyPrim_T_Su_PriCirc_Active |  | 10008357
[8 empty] | 10008359 | Para_Hydraulic_WasteHeatRec_SupplyPrim_T_Su_PriCirc_HyLimHi | Para_Hydraulic_WasteHeatRec_SupplyPrim_T_Su_PriCirc_HyLimHi | 4383 | Para_Hydraulic_WasteHeatRec_SupplyPrim_T_Su_PriCirc_HyLimHi |  | 10008359
[8 empty] | 10008358 | Para_Hydraulic_WasteHeatRec_SupplyPrim_T_Su_PriCirc_LimHi | Para_Hydraulic_WasteHeatRec_SupplyPrim_T_Su_PriCirc_LimHi | 4384 | Para_Hydraulic_WasteHeatRec_SupplyPrim_T_Su_PriCirc_LimHi |  | 10008358
[8 empty] | 10008362 | Para_Hydraulic_WasteHeatRec_SupplySec_T_Su_SecCirc_Active | Para_Hydraulic_WasteHeatRec_SupplySec_T_Su_SecCirc_Active | 4385 | Para_Hydraulic_WasteHeatRec_SupplySec_T_Su_SecCirc_Active |  | 10008362
[8 empty] | 10008371 | Para_Hydraulic_WasteHeatRec_SupplySec_T_Su_SecCirc_HyLimHi | Para_Hydraulic_WasteHeatRec_SupplySec_T_Su_SecCirc_HyLimHi | 4386 | Para_Hydraulic_WasteHeatRec_SupplySec_T_Su_SecCirc_HyLimHi |  | 10008371
[8 empty] | 10008365 | Para_Hydraulic_WasteHeatRec_SupplySec_T_Su_SecCirc_LimHi | Para_Hydraulic_WasteHeatRec_SupplySec_T_Su_SecCirc_LimHi | 4387 | Para_Hydraulic_WasteHeatRec_SupplySec_T_Su_SecCirc_LimHi |  | 10008365
[8 empty] | 18071 | Para_Ignition_ActITPTbAdap | Para_Ignition_ActITPTbAdap | 4388 | Para_Ignition_ActITPTbAdap |  | 18071
[8 empty] | 18072 | Para_Ignition_EnergLev | Para_Ignition_EnergLev | 4389 | Para_Ignition_EnergLev |  | 18072
[8 empty] | 18073 | Para_Ignition_ITPEarl | Para_Ignition_ITPEarl | 4390 | Para_Ignition_ITPEarl |  | 18073
[8 empty] | 18074 | Para_Ignition_ITPGas1 | Para_Ignition_ITPGas1 | 4391 | Para_Ignition_ITPGas1 | °KW | 18074
[8 empty] | 18075 | Para_Ignition_ITPGas2 | Para_Ignition_ITPGas2 | 4392 | Para_Ignition_ITPGas2 | °KW | 18075
[8 empty] | 18076 | Para_Ignition_ITPGas3 | Para_Ignition_ITPGas3 | 4393 | Para_Ignition_ITPGas3 | °KW | 18076
[8 empty] | 18077 | Para_Ignition_ITPGas4 | Para_Ignition_ITPGas4 | 4394 | Para_Ignition_ITPGas4 | °KW | 18077
[8 empty] | 18078 | Para_Ignition_ITPIslandG1 | Para_Ignition_ITPIslandG1 | 4395 | Para_Ignition_ITPIslandG1 | °KW | 18078
[8 empty] | 18079 | Para_Ignition_ITPIslandG2 | Para_Ignition_ITPIslandG2 | 4396 | Para_Ignition_ITPIslandG2 | °KW | 18079
[8 empty] | 18080 | Para_Ignition_ITPIslandG3 | Para_Ignition_ITPIslandG3 | 4397 | Para_Ignition_ITPIslandG3 | °KW | 18080
[8 empty] | 18081 | Para_Ignition_ITPIslandG4 | Para_Ignition_ITPIslandG4 | 4398 | Para_Ignition_ITPIslandG4 | °KW | 18081
[8 empty] | 18082 | Para_Ignition_ITPKnockMonOffG1 | Para_Ignition_ITPKnockMonOffG1 | 4399 | Para_Ignition_ITPKnockMonOffG1 | °KW | 18082
[8 empty] | 18083 | Para_Ignition_ITPKnockMonOffG2 | Para_Ignition_ITPKnockMonOffG2 | 4400 | Para_Ignition_ITPKnockMonOffG2 | °KW | 18083
[8 empty] | 18084 | Para_Ignition_ITPKnockMonOffG3 | Para_Ignition_ITPKnockMonOffG3 | 4401 | Para_Ignition_ITPKnockMonOffG3 | °KW | 18084
[8 empty] | 18085 | Para_Ignition_ITPKnockMonOffG4 | Para_Ignition_ITPKnockMonOffG4 | 4402 | Para_Ignition_ITPKnockMonOffG4 | °KW | 18085
[8 empty] | 18086 | Para_Ignition_ITPLate | Para_Ignition_ITPLate | 4403 | Para_Ignition_ITPLate |  | 18086
[8 empty] | 18087 | Para_Ignition_ITPMinGas1 | Para_Ignition_ITPMinGas1 | 4404 | Para_Ignition_ITPMinGas1 |  | 18087
[8 empty] | 18088 | Para_Ignition_ITPMinGas2 | Para_Ignition_ITPMinGas2 | 4405 | Para_Ignition_ITPMinGas2 |  | 18088
[8 empty] | 18089 | Para_Ignition_ITPMinGas3 | Para_Ignition_ITPMinGas3 | 4406 | Para_Ignition_ITPMinGas3 |  | 18089
[8 empty] | 18090 | Para_Ignition_ITPMinGas4 | Para_Ignition_ITPMinGas4 | 4407 | Para_Ignition_ITPMinGas4 |  | 18090
[8 empty] | 18091 | Para_Ignition_ITPTbPosAdap | Para_Ignition_ITPTbPosAdap | 4408 | Para_Ignition_ITPTbPosAdap |  | 18091
[8 empty] | 18092 | Para_Ignition_mAOutput_Curr1 | Para_Ignition_mAOutput_Curr1 | 4409 | Para_Ignition_mAOutput_Curr1 | mA | 18092
[8 empty] | 18093 | Para_Ignition_mAOutput_Curr2 | Para_Ignition_mAOutput_Curr2 | 4410 | Para_Ignition_mAOutput_Curr2 | mA | 18093
[8 empty] | 18094 | Para_Ignition_mAOutput_Point1 | Para_Ignition_mAOutput_Point1 | 4411 | Para_Ignition_mAOutput_Point1 | °KW | 18094
[8 empty] | 18095 | Para_Ignition_mAOutput_Point2 | Para_Ignition_mAOutput_Point2 | 4412 | Para_Ignition_mAOutput_Point2 | °KW | 18095
[8 empty] | 18096 | Para_Ignition_MisfControl | Para_Ignition_MisfControl | 4413 | Para_Ignition_MisfControl |  | 18096
[8 empty] | 18097 | Para_Ignition_MORIS_CoilType | Para_Ignition_MORIS_CoilType | 4414 | Para_Ignition_MORIS_CoilType |  | 18097
[8 empty] | 18098 | Para_Ignition_MORIS_CoilType0_IonTimeEarl | Para_Ignition_MORIS_CoilType0_IonTimeEarl | 4415 | Para_Ignition_MORIS_CoilType0_IonTimeEarl |  | 18098
[8 empty] | 18099 | Para_Ignition_MORIS_CoilType0_IonTimeLate | Para_Ignition_MORIS_CoilType0_IonTimeLate | 4416 | Para_Ignition_MORIS_CoilType0_IonTimeLate |  | 18099
[8 empty] | 18100 | Para_Ignition_MORIS_CoilType0_MagLevelDec | Para_Ignition_MORIS_CoilType0_MagLevelDec | 4417 | Para_Ignition_MORIS_CoilType0_MagLevelDec |  | 18100
[8 empty] | 18101 | Para_Ignition_MORIS_CoilType0_MagLevelInc | Para_Ignition_MORIS_CoilType0_MagLevelInc | 4418 | Para_Ignition_MORIS_CoilType0_MagLevelInc |  | 18101
[8 empty] | 18102 | Para_Ignition_MORIS_CoilType0_MagLevelIon | Para_Ignition_MORIS_CoilType0_MagLevelIon | 4419 | Para_Ignition_MORIS_CoilType0_MagLevelIon |  | 18102
[8 empty] | 18103 | Para_Ignition_MORIS_CoilType0_MagLevelLim | Para_Ignition_MORIS_CoilType0_MagLevelLim | 4420 | Para_Ignition_MORIS_CoilType0_MagLevelLim |  | 18103
[8 empty] | 18104 | Para_Ignition_MORIS_CoilType0_PowerIgn | Para_Ignition_MORIS_CoilType0_PowerIgn | 4421 | Para_Ignition_MORIS_CoilType0_PowerIgn |  | 18104
[8 empty] | 18105 | Para_Ignition_MORIS_CoilType0_PowerSparkLim | Para_Ignition_MORIS_CoilType0_PowerSparkLim | 4422 | Para_Ignition_MORIS_CoilType0_PowerSparkLim |  | 18105
[8 empty] | 18106 | Para_Ignition_MORIS_CoilType0_PowerSparkRate | Para_Ignition_MORIS_CoilType0_PowerSparkRate | 4423 | Para_Ignition_MORIS_CoilType0_PowerSparkRate |  | 18106
[8 empty] | 18107 | Para_Ignition_MORIS_CoilType0_SparkCurrIonis | Para_Ignition_MORIS_CoilType0_SparkCurrIonis | 4424 | Para_Ignition_MORIS_CoilType0_SparkCurrIonis | % | 18107
[8 empty] | 18108 | Para_Ignition_MORIS_CoilType0_SparkDelayFailRate | Para_Ignition_MORIS_CoilType0_SparkDelayFailRate | 4425 | Para_Ignition_MORIS_CoilType0_SparkDelayFailRate |  | 18108
[8 empty] | 18109 | Para_Ignition_MORIS_CoilType0_SparkDelayLim | Para_Ignition_MORIS_CoilType0_SparkDelayLim | 4426 | Para_Ignition_MORIS_CoilType0_SparkDelayLim |  | 18109
[8 empty] | 18110 | Para_Ignition_MORIS_CoilType0_SparkDurIonis | Para_Ignition_MORIS_CoilType0_SparkDurIonis | 4427 | Para_Ignition_MORIS_CoilType0_SparkDurIonis | µs | 18110
[8 empty] | 18111 | Para_Ignition_MORIS_PowerSupplyOut | Para_Ignition_MORIS_PowerSupplyOut | 4428 | Para_Ignition_MORIS_PowerSupplyOut |  | 18111
[8 empty] | 18112 | Para_Ignition_MORIS_SparkChar0_SparkCurr1 | Para_Ignition_MORIS_SparkChar0_SparkCurr1 | 4429 | Para_Ignition_MORIS_SparkChar0_SparkCurr1 | % | 18112
[8 empty] | 18113 | Para_Ignition_MORIS_SparkChar0_SparkCurr2 | Para_Ignition_MORIS_SparkChar0_SparkCurr2 | 4430 | Para_Ignition_MORIS_SparkChar0_SparkCurr2 | % | 18113
[8 empty] | 18114 | Para_Ignition_MORIS_SparkChar0_SparkCurr3 | Para_Ignition_MORIS_SparkChar0_SparkCurr3 | 4431 | Para_Ignition_MORIS_SparkChar0_SparkCurr3 | % | 18114
[8 empty] | 18115 | Para_Ignition_MORIS_SparkChar0_SparkCurr4 | Para_Ignition_MORIS_SparkChar0_SparkCurr4 | 4432 | Para_Ignition_MORIS_SparkChar0_SparkCurr4 | % | 18115
[8 empty] | 18116 | Para_Ignition_MORIS_SparkChar0_SparkCurr5 | Para_Ignition_MORIS_SparkChar0_SparkCurr5 | 4433 | Para_Ignition_MORIS_SparkChar0_SparkCurr5 | % | 18116
[8 empty] | 18117 | Para_Ignition_MORIS_SparkChar0_SparkCurr6 | Para_Ignition_MORIS_SparkChar0_SparkCurr6 | 4434 | Para_Ignition_MORIS_SparkChar0_SparkCurr6 | % | 18117
[8 empty] | 18118 | Para_Ignition_MORIS_SparkChar0_SparkDur1 | Para_Ignition_MORIS_SparkChar0_SparkDur1 | 4435 | Para_Ignition_MORIS_SparkChar0_SparkDur1 | % | 18118
[8 empty] | 18119 | Para_Ignition_MORIS_SparkChar0_SparkDur2 | Para_Ignition_MORIS_SparkChar0_SparkDur2 | 4436 | Para_Ignition_MORIS_SparkChar0_SparkDur2 | % | 18119
[8 empty] | 18120 | Para_Ignition_MORIS_SparkChar0_SparkDur3 | Para_Ignition_MORIS_SparkChar0_SparkDur3 | 4437 | Para_Ignition_MORIS_SparkChar0_SparkDur3 | % | 18120
[8 empty] | 18121 | Para_Ignition_MORIS_SparkChar0_SparkDur4 | Para_Ignition_MORIS_SparkChar0_SparkDur4 | 4438 | Para_Ignition_MORIS_SparkChar0_SparkDur4 | % | 18121
[8 empty] | 18122 | Para_Ignition_MORIS_SparkChar0_SparkDur5 | Para_Ignition_MORIS_SparkChar0_SparkDur5 | 4439 | Para_Ignition_MORIS_SparkChar0_SparkDur5 | % | 18122
[8 empty] | 18123 | Para_Ignition_MORIS_SparkCurrChar | Para_Ignition_MORIS_SparkCurrChar | 4440 | Para_Ignition_MORIS_SparkCurrChar |  | 18123
[8 empty] | 18124 | Para_Ignition_MORIS_SparkCurrDur | Para_Ignition_MORIS_SparkCurrDur | 4441 | Para_Ignition_MORIS_SparkCurrDur | µs | 18124
[8 empty] | 18125 | Para_Ignition_MORIS_SparkCurrLevel | Para_Ignition_MORIS_SparkCurrLevel | 4442 | Para_Ignition_MORIS_SparkCurrLevel |  | 18125
[8 empty] | 18126 | Para_Ignition_MORIS_SparkDurTol | Para_Ignition_MORIS_SparkDurTol | 4443 | Para_Ignition_MORIS_SparkDurTol | % | 18126
[8 empty] | 18127 | Para_Ignition_MORIS_SparkDurTolFailRate | Para_Ignition_MORIS_SparkDurTolFailRate | 4444 | Para_Ignition_MORIS_SparkDurTolFailRate |  | 18127
[8 empty] | 18128 | Para_Ignition_OutputMon | Para_Ignition_OutputMon | 4445 | Para_Ignition_OutputMon |  | 18128
[8 empty] | 18129 | Para_Ignition_OverSpeed | Para_Ignition_OverSpeed | 4446 | Para_Ignition_OverSpeed |  | 18129
[8 empty] | 18130 | Para_Ignition_ResetPos | Para_Ignition_ResetPos | 4447 | Para_Ignition_ResetPos |  | 18130
[8 empty] | 18131 | Para_Ignition_SecSpeed | Para_Ignition_SecSpeed | 4448 | Para_Ignition_SecSpeed |  | 18131
[8 empty] | 18132 | Para_Ignition_Setting_EnergLev | Para_Ignition_Setting_EnergLev | 4449 | Para_Ignition_Setting_EnergLev | % | 18132
[8 empty] | 18133 | Para_Ignition_Setting_OutputMon | Para_Ignition_Setting_OutputMon | 4450 | Para_Ignition_Setting_OutputMon | 1/s | 18133
[8 empty] | 18134 | Para_Ignition_Setting_ResetPos | Para_Ignition_Setting_ResetPos | 4451 | Para_Ignition_Setting_ResetPos | °KW | 18134
[8 empty] | 18135 | Para_Ignition_Setting_SecSpeed | Para_Ignition_Setting_SecSpeed | 4452 | Para_Ignition_Setting_SecSpeed | 1/min | 18135
[8 empty] | 18136 | Para_Ignition_Setting_SpeedRelay1 | Para_Ignition_Setting_SpeedRelay1 | 4453 | Para_Ignition_Setting_SpeedRelay1 | 1/min | 18136
[8 empty] | 18137 | Para_Ignition_Setting_SpeedRelay2 | Para_Ignition_Setting_SpeedRelay2 | 4454 | Para_Ignition_Setting_SpeedRelay2 | 1/min | 18137
[8 empty] | 18138 | Para_Ignition_Setting_SpeedRelay2InvOut | Para_Ignition_Setting_SpeedRelay2InvOut | 4455 | Para_Ignition_Setting_SpeedRelay2InvOut |  | 18138
[8 empty] | 18139 | Para_Ignition_Setting_SpeedRelayHys1 | Para_Ignition_Setting_SpeedRelayHys1 | 4456 | Para_Ignition_Setting_SpeedRelayHys1 | 1/min | 18139
[8 empty] | 18140 | Para_Ignition_Setting_SpeedRelayHys2 | Para_Ignition_Setting_SpeedRelayHys2 | 4457 | Para_Ignition_Setting_SpeedRelayHys2 | 1/min | 18140
[8 empty] | 18141 | Para_Ignition_SpeedRelay1 | Para_Ignition_SpeedRelay1 | 4458 | Para_Ignition_SpeedRelay1 |  | 18141
[8 empty] | 18142 | Para_Ignition_SpeedRelay2 | Para_Ignition_SpeedRelay2 | 4459 | Para_Ignition_SpeedRelay2 |  | 18142
[8 empty] | 18143 | Para_Ignition_SpeedRelay2InvOut | Para_Ignition_SpeedRelay2InvOut | 4460 | Para_Ignition_SpeedRelay2InvOut |  | 18143
[8 empty] | 18144 | Para_Ignition_SpeedRelayHys1 | Para_Ignition_SpeedRelayHys1 | 4461 | Para_Ignition_SpeedRelayHys1 |  | 18144
[8 empty] | 18145 | Para_Ignition_SpeedRelayHys2 | Para_Ignition_SpeedRelayHys2 | 4462 | Para_Ignition_SpeedRelayHys2 |  | 18145
[8 empty] | 18146 | Para_Island_Advanced_ActMapVolEff | Para_Island_Advanced_ActMapVolEff | 4463 | Para_Island_Advanced_ActMapVolEff |  | 18146
[8 empty] | 18147 | Para_Island_Advanced_ActSpeedComp | Para_Island_Advanced_ActSpeedComp | 4464 | Para_Island_Advanced_ActSpeedComp |  | 18147
[8 empty] | 18148 | Para_Island_Advanced_CompByTimeCorr | Para_Island_Advanced_CompByTimeCorr | 4465 | Para_Island_Advanced_CompByTimeCorr |  | 18148
[8 empty] | 18149 | Para_Island_Advanced_CompByValueCorr | Para_Island_Advanced_CompByValueCorr | 4466 | Para_Island_Advanced_CompByValueCorr |  | 18149
[8 empty] | 18150 | Para_Island_Advanced_CompByValueCorrRed | Para_Island_Advanced_CompByValueCorrRed | 4467 | Para_Island_Advanced_CompByValueCorrRed |  | 18150
[8 empty] | 18151 | Para_Island_Advanced_ITPShift | Para_Island_Advanced_ITPShift | 4468 | Para_Island_Advanced_ITPShift | °KW | 18151
[8 empty] | 18152 | Para_Island_Advanced_SpeedCompCorrFact | Para_Island_Advanced_SpeedCompCorrFact | 4469 | Para_Island_Advanced_SpeedCompCorrFact |  | 18152
[8 empty] | 18153 | Para_Island_Advanced_SpeedCompFact | Para_Island_Advanced_SpeedCompFact | 4470 | Para_Island_Advanced_SpeedCompFact |  | 18153
[8 empty] | 18154 | Para_Island_Ctr_TbDComp | Para_Island_Ctr_TbDComp | 4471 | Para_Island_Ctr_TbDComp |  | 18154
[8 empty] | 18155 | Para_Island_Ctr_TbIComp | Para_Island_Ctr_TbIComp | 4472 | Para_Island_Ctr_TbIComp |  | 18155
[8 empty] | 18156 | Para_Island_Ctr_TbPComp | Para_Island_Ctr_TbPComp | 4473 | Para_Island_Ctr_TbPComp |  | 18156
[8 empty] | 18157 | Para_Island_Ctr_TbYMax | Para_Island_Ctr_TbYMax | 4474 | Para_Island_Ctr_TbYMax | % | 18157
[8 empty] | 18158 | Para_Island_Ctr_TbYMin | Para_Island_Ctr_TbYMin | 4475 | Para_Island_Ctr_TbYMin | % | 18158
[8 empty] | 18159 | Para_Island_Ctr_TrDComp | Para_Island_Ctr_TrDComp | 4476 | Para_Island_Ctr_TrDComp |  | 18159
[8 empty] | 18160 | Para_Island_Ctr_TrIComp | Para_Island_Ctr_TrIComp | 4477 | Para_Island_Ctr_TrIComp |  | 18160
[8 empty] | 18161 | Para_Island_Ctr_TrPComp | Para_Island_Ctr_TrPComp | 4478 | Para_Island_Ctr_TrPComp |  | 18161
[8 empty] | 18162 | Para_Island_Ctr_TrYMax | Para_Island_Ctr_TrYMax | 4479 | Para_Island_Ctr_TrYMax | % | 18162
[8 empty] | 18163 | Para_Island_Ctr_TrYMin | Para_Island_Ctr_TrYMin | 4480 | Para_Island_Ctr_TrYMin | % | 18163
[8 empty] | 18164 | Para_Island_LambdaAdap_FactNegPower | Para_Island_LambdaAdap_FactNegPower | 4481 | Para_Island_LambdaAdap_FactNegPower |  | 18164
[8 empty] | 18165 | Para_Island_LambdaAdap_FactNegSpeed | Para_Island_LambdaAdap_FactNegSpeed | 4482 | Para_Island_LambdaAdap_FactNegSpeed |  | 18165
[8 empty] | 18166 | Para_Island_LambdaAdap_FactPosPower | Para_Island_LambdaAdap_FactPosPower | 4483 | Para_Island_LambdaAdap_FactPosPower |  | 18166
[8 empty] | 18167 | Para_Island_LambdaAdap_FactPosSpeed | Para_Island_LambdaAdap_FactPosSpeed | 4484 | Para_Island_LambdaAdap_FactPosSpeed |  | 18167
[8 empty] | 18168 | Para_Island_LambdaAdap_TriggerLowPower | Para_Island_LambdaAdap_TriggerLowPower | 4485 | Para_Island_LambdaAdap_TriggerLowPower | % | 18168
[8 empty] | 18169 | Para_Island_LambdaAdap_TriggerLowSpeed | Para_Island_LambdaAdap_TriggerLowSpeed | 4486 | Para_Island_LambdaAdap_TriggerLowSpeed | % | 18169
[8 empty] | 18170 | Para_Island_LambdaAdap_TriggerUpPower | Para_Island_LambdaAdap_TriggerUpPower | 4487 | Para_Island_LambdaAdap_TriggerUpPower | % | 18170
[8 empty] | 18171 | Para_Island_LambdaAdap_TriggerUpSpeed | Para_Island_LambdaAdap_TriggerUpSpeed | 4488 | Para_Island_LambdaAdap_TriggerUpSpeed | % | 18171
[8 empty] | 18172 | Para_Island_Limit_LSdPowerMax | Para_Island_Limit_LSdPowerMax | 4489 | Para_Island_Limit_LSdPowerMax |  | 18172
[8 empty] | 18173 | Para_Island_Limit_LSdPowerMaxDelay | Para_Island_Limit_LSdPowerMaxDelay | 4490 | Para_Island_Limit_LSdPowerMaxDelay |  | 18173
[8 empty] | 18174 | Para_Island_Limit_LSdPowerMaxHys | Para_Island_Limit_LSdPowerMaxHys | 4491 | Para_Island_Limit_LSdPowerMaxHys |  | 18174
[8 empty] | 18175 | Para_Island_Limit_LSdPowerMinAlarm | Para_Island_Limit_LSdPowerMinAlarm | 4492 | Para_Island_Limit_LSdPowerMinAlarm |  | 18175
[8 empty] | 18176 | Para_Island_Limit_LSdPowerMinAlarmDelay | Para_Island_Limit_LSdPowerMinAlarmDelay | 4493 | Para_Island_Limit_LSdPowerMinAlarmDelay |  | 18176
[8 empty] | 18177 | Para_Island_Limit_LSdPowerMinHys | Para_Island_Limit_LSdPowerMinHys | 4494 | Para_Island_Limit_LSdPowerMinHys |  | 18177
[8 empty] | 18178 | Para_Island_Limit_LSdPowerMinTrip | Para_Island_Limit_LSdPowerMinTrip | 4495 | Para_Island_Limit_LSdPowerMinTrip |  | 18178
[8 empty] | 18179 | Para_Island_Limit_LSdPowerMinTripDelay | Para_Island_Limit_LSdPowerMinTripDelay | 4496 | Para_Island_Limit_LSdPowerMinTripDelay |  | 18179
[8 empty] | 18180 | Para_Island_Limit_LSdSpeedLimit | Para_Island_Limit_LSdSpeedLimit | 4497 | Para_Island_Limit_LSdSpeedLimit |  | 18180
[8 empty] | 18181 | Para_Island_Limit_LSdSpeedLimitDelay | Para_Island_Limit_LSdSpeedLimitDelay | 4498 | Para_Island_Limit_LSdSpeedLimitDelay |  | 18181
[8 empty] | 18182 | Para_Island_Limit_LSdSpeedLimitHys | Para_Island_Limit_LSdSpeedLimitHys | 4499 | Para_Island_Limit_LSdSpeedLimitHys |  | 18182
[8 empty] | 18183 | Para_Island_LoadSh_ActOffsetCoef | Para_Island_LoadSh_ActOffsetCoef | 4500 | Para_Island_LoadSh_ActOffsetCoef |  | 18183
[8 empty] | 18184 | Para_Island_LoadSh_LoadSh | Para_Island_LoadSh_LoadSh | 4501 | Para_Island_LoadSh_LoadSh | % | 18184
[8 empty] | 18185 | Para_Island_LoadSh_OffsetCoef | Para_Island_LoadSh_OffsetCoef | 4502 | Para_Island_LoadSh_OffsetCoef | % | 18185
[8 empty] | 18186 | Para_Island_OutPowerLimit_Curr1 | Para_Island_OutPowerLimit_Curr1 | 4503 | Para_Island_OutPowerLimit_Curr1 |  | 18186
[8 empty] | 18187 | Para_Island_OutPowerLimit_Curr2 | Para_Island_OutPowerLimit_Curr2 | 4504 | Para_Island_OutPowerLimit_Curr2 |  | 18187
[8 empty] | 18188 | Para_Island_OutPowerLimit_Point1 | Para_Island_OutPowerLimit_Point1 | 4505 | Para_Island_OutPowerLimit_Point1 |  | 18188
[8 empty] | 18189 | Para_Island_OutPowerLimit_Point2 | Para_Island_OutPowerLimit_Point2 | 4506 | Para_Island_OutPowerLimit_Point2 |  | 18189
[8 empty] | 18190 | Para_Island_Ramp_Ramp | Para_Island_Ramp_Ramp | 4507 | Para_Island_Ramp_Ramp | min-1/s | 18190
[8 empty] | 18191 | Para_Knock_ActKnockMon | Para_Knock_ActKnockMon | 4508 | Para_Knock_ActKnockMon | kW | 18191
[8 empty] | 18192 | Para_Knock_ActKnockMonHys | Para_Knock_ActKnockMonHys | 4509 | Para_Knock_ActKnockMonHys | kW | 18192
[8 empty] | 18193 | Para_Knock_CylOpt_Active | Para_Knock_CylOpt_Active | 4510 | Para_Knock_CylOpt_Active |  | 18193
[8 empty] | 18194 | Para_Knock_CylOpt_IntTimeUp | Para_Knock_CylOpt_IntTimeUp | 4511 | Para_Knock_CylOpt_IntTimeUp | s | 18194
[8 empty] | 18195 | Para_Knock_CylOpt_IPAdaptIntervall | Para_Knock_CylOpt_IPAdaptIntervall | 4512 | Para_Knock_CylOpt_IPAdaptIntervall |  | 18195
[8 empty] | 18196 | Para_Knock_CylOpt_LimitKnockInt | Para_Knock_CylOpt_LimitKnockInt | 4513 | Para_Knock_CylOpt_LimitKnockInt | % | 18196
[8 empty] | 18197 | Para_Knock_CylOpt_MonIntervall | Para_Knock_CylOpt_MonIntervall | 4514 | Para_Knock_CylOpt_MonIntervall |  | 18197
[8 empty] | 18198 | Para_Knock_CylOpt_PowAdaptIntervall | Para_Knock_CylOpt_PowAdaptIntervall | 4515 | Para_Knock_CylOpt_PowAdaptIntervall | % Pn | 18198
[8 empty] | 18199 | Para_Knock_CylOpt_ResetTimeOpt | Para_Knock_CylOpt_ResetTimeOpt | 4516 | Para_Knock_CylOpt_ResetTimeOpt |  | 18199
[8 empty] | 18200 | Para_Knock_CylOpt_ResetTimeOptPred | Para_Knock_CylOpt_ResetTimeOptPred | 4517 | Para_Knock_CylOpt_ResetTimeOptPred | min | 18200
[8 empty] | 18201 | Para_Knock_IPAdapOffsetKnockCtrGas1 | Para_Knock_IPAdapOffsetKnockCtrGas1 | 4518 | Para_Knock_IPAdapOffsetKnockCtrGas1 |  | 18201
[8 empty] | 18202 | Para_Knock_IPAdapOffsetKnockCtrGas2 | Para_Knock_IPAdapOffsetKnockCtrGas2 | 4519 | Para_Knock_IPAdapOffsetKnockCtrGas2 |  | 18202
[8 empty] | 18203 | Para_Knock_IPAdapOffsetKnockCtrGas3 | Para_Knock_IPAdapOffsetKnockCtrGas3 | 4520 | Para_Knock_IPAdapOffsetKnockCtrGas3 |  | 18203
[8 empty] | 18204 | Para_Knock_IPAdapOffsetKnockCtrGas4 | Para_Knock_IPAdapOffsetKnockCtrGas4 | 4521 | Para_Knock_IPAdapOffsetKnockCtrGas4 |  | 18204
[8 empty] | 18205 | Para_Knock_IPRedMaxKnockCtrGas1 | Para_Knock_IPRedMaxKnockCtrGas1 | 4522 | Para_Knock_IPRedMaxKnockCtrGas1 |  | 18205
[8 empty] | 18206 | Para_Knock_IPRedMaxKnockCtrGas2 | Para_Knock_IPRedMaxKnockCtrGas2 | 4523 | Para_Knock_IPRedMaxKnockCtrGas2 |  | 18206
[8 empty] | 18207 | Para_Knock_IPRedMaxKnockCtrGas3 | Para_Knock_IPRedMaxKnockCtrGas3 | 4524 | Para_Knock_IPRedMaxKnockCtrGas3 |  | 18207
[8 empty] | 18208 | Para_Knock_IPRedMaxKnockCtrGas4 | Para_Knock_IPRedMaxKnockCtrGas4 | 4525 | Para_Knock_IPRedMaxKnockCtrGas4 |  | 18208
[8 empty] | 18209 | Para_Knock_ITPMinGas1 | Para_Knock_ITPMinGas1 | 4526 | Para_Knock_ITPMinGas1 | °KW | 18209
[8 empty] | 18210 | Para_Knock_ITPMinGas2 | Para_Knock_ITPMinGas2 | 4527 | Para_Knock_ITPMinGas2 | °KW | 18210
[8 empty] | 18211 | Para_Knock_ITPMinGas3 | Para_Knock_ITPMinGas3 | 4528 | Para_Knock_ITPMinGas3 | °KW | 18211
[8 empty] | 18212 | Para_Knock_ITPMinGas4 | Para_Knock_ITPMinGas4 | 4529 | Para_Knock_ITPMinGas4 | °KW | 18212
[8 empty] | 18213 | Para_Knock_KLS90_KnockLimit1 | Para_Knock_KLS90_KnockLimit1 | 4530 | Para_Knock_KLS90_KnockLimit1 |  | 18213
[8 empty] | 18214 | Para_Knock_KLS90_KnockLimit2 | Para_Knock_KLS90_KnockLimit2 | 4531 | Para_Knock_KLS90_KnockLimit2 |  | 18214
[8 empty] | 18215 | Para_Knock_KLS98_AngleDurWindow1 | Para_Knock_KLS98_AngleDurWindow1 | 4532 | Para_Knock_KLS98_AngleDurWindow1 |  | 18215
[8 empty] | 18216 | Para_Knock_KLS98_AngleDurWindow2 | Para_Knock_KLS98_AngleDurWindow2 | 4533 | Para_Knock_KLS98_AngleDurWindow2 |  | 18216
[8 empty] | 18217 | Para_Knock_KLS98_AngleDurWindow3 | Para_Knock_KLS98_AngleDurWindow3 | 4534 | Para_Knock_KLS98_AngleDurWindow3 |  | 18217
[8 empty] | 18218 | Para_Knock_KLS98_AnglePosCam | Para_Knock_KLS98_AnglePosCam | 4535 | Para_Knock_KLS98_AnglePosCam |  | 18218
[8 empty] | 18219 | Para_Knock_KLS98_AnglePosWindow1 | Para_Knock_KLS98_AnglePosWindow1 | 4536 | Para_Knock_KLS98_AnglePosWindow1 |  | 18219
[8 empty] | 18220 | Para_Knock_KLS98_AnglePosWindow2 | Para_Knock_KLS98_AnglePosWindow2 | 4537 | Para_Knock_KLS98_AnglePosWindow2 |  | 18220
[8 empty] | 18221 | Para_Knock_KLS98_AnglePosWindow3 | Para_Knock_KLS98_AnglePosWindow3 | 4538 | Para_Knock_KLS98_AnglePosWindow3 |  | 18221
[8 empty] | 18222 | Para_Knock_KLS98_EnabCyl1 | Para_Knock_KLS98_EnabCyl1 | 4539 | Para_Knock_KLS98_EnabCyl1 |  | 18222
[8 empty] | 18223 | Para_Knock_KLS98_EnabCyl10 | Para_Knock_KLS98_EnabCyl10 | 4540 | Para_Knock_KLS98_EnabCyl10 |  | 18223
[8 empty] | 18224 | Para_Knock_KLS98_EnabCyl11 | Para_Knock_KLS98_EnabCyl11 | 4541 | Para_Knock_KLS98_EnabCyl11 |  | 18224
[8 empty] | 18225 | Para_Knock_KLS98_EnabCyl12 | Para_Knock_KLS98_EnabCyl12 | 4542 | Para_Knock_KLS98_EnabCyl12 |  | 18225
[8 empty] | 18226 | Para_Knock_KLS98_EnabCyl13 | Para_Knock_KLS98_EnabCyl13 | 4543 | Para_Knock_KLS98_EnabCyl13 |  | 18226
[8 empty] | 18227 | Para_Knock_KLS98_EnabCyl14 | Para_Knock_KLS98_EnabCyl14 | 4544 | Para_Knock_KLS98_EnabCyl14 |  | 18227
[8 empty] | 18228 | Para_Knock_KLS98_EnabCyl15 | Para_Knock_KLS98_EnabCyl15 | 4545 | Para_Knock_KLS98_EnabCyl15 |  | 18228
[8 empty] | 18229 | Para_Knock_KLS98_EnabCyl16 | Para_Knock_KLS98_EnabCyl16 | 4546 | Para_Knock_KLS98_EnabCyl16 |  | 18229
[8 empty] | 18230 | Para_Knock_KLS98_EnabCyl17 | Para_Knock_KLS98_EnabCyl17 | 4547 | Para_Knock_KLS98_EnabCyl17 |  | 18230
[8 empty] | 18231 | Para_Knock_KLS98_EnabCyl18 | Para_Knock_KLS98_EnabCyl18 | 4548 | Para_Knock_KLS98_EnabCyl18 |  | 18231
[8 empty] | 18232 | Para_Knock_KLS98_EnabCyl19 | Para_Knock_KLS98_EnabCyl19 | 4549 | Para_Knock_KLS98_EnabCyl19 |  | 18232
[8 empty] | 18233 | Para_Knock_KLS98_EnabCyl2 | Para_Knock_KLS98_EnabCyl2 | 4550 | Para_Knock_KLS98_EnabCyl2 |  | 18233
[8 empty] | 18234 | Para_Knock_KLS98_EnabCyl20 | Para_Knock_KLS98_EnabCyl20 | 4551 | Para_Knock_KLS98_EnabCyl20 |  | 18234
[8 empty] | 18235 | Para_Knock_KLS98_EnabCyl21 | Para_Knock_KLS98_EnabCyl21 | 4552 | Para_Knock_KLS98_EnabCyl21 |  | 18235
[8 empty] | 18236 | Para_Knock_KLS98_EnabCyl22 | Para_Knock_KLS98_EnabCyl22 | 4553 | Para_Knock_KLS98_EnabCyl22 |  | 18236
[8 empty] | 18237 | Para_Knock_KLS98_EnabCyl23 | Para_Knock_KLS98_EnabCyl23 | 4554 | Para_Knock_KLS98_EnabCyl23 |  | 18237
[8 empty] | 18238 | Para_Knock_KLS98_EnabCyl24 | Para_Knock_KLS98_EnabCyl24 | 4555 | Para_Knock_KLS98_EnabCyl24 |  | 18238
[8 empty] | 18239 | Para_Knock_KLS98_EnabCyl3 | Para_Knock_KLS98_EnabCyl3 | 4556 | Para_Knock_KLS98_EnabCyl3 |  | 18239
[8 empty] | 18240 | Para_Knock_KLS98_EnabCyl4 | Para_Knock_KLS98_EnabCyl4 | 4557 | Para_Knock_KLS98_EnabCyl4 |  | 18240
[8 empty] | 18241 | Para_Knock_KLS98_EnabCyl5 | Para_Knock_KLS98_EnabCyl5 | 4558 | Para_Knock_KLS98_EnabCyl5 |  | 18241
[8 empty] | 18242 | Para_Knock_KLS98_EnabCyl6 | Para_Knock_KLS98_EnabCyl6 | 4559 | Para_Knock_KLS98_EnabCyl6 |  | 18242
[8 empty] | 18243 | Para_Knock_KLS98_EnabCyl7 | Para_Knock_KLS98_EnabCyl7 | 4560 | Para_Knock_KLS98_EnabCyl7 |  | 18243
[8 empty] | 18244 | Para_Knock_KLS98_EnabCyl8 | Para_Knock_KLS98_EnabCyl8 | 4561 | Para_Knock_KLS98_EnabCyl8 |  | 18244
[8 empty] | 18245 | Para_Knock_KLS98_EnabCyl9 | Para_Knock_KLS98_EnabCyl9 | 4562 | Para_Knock_KLS98_EnabCyl9 |  | 18245
[8 empty] | 18246 | Para_Knock_KLS98_ITPAdjustGlobCylsel | Para_Knock_KLS98_ITPAdjustGlobCylsel | 4563 | Para_Knock_KLS98_ITPAdjustGlobCylsel |  | 18246
[8 empty] | 18247 | Para_Knock_KLS98_KnockFilterFunc | Para_Knock_KLS98_KnockFilterFunc | 4564 | Para_Knock_KLS98_KnockFilterFunc |  | 18247
[8 empty] | 18248 | Para_Knock_KLS98_KnockLimit | Para_Knock_KLS98_KnockLimit | 4565 | Para_Knock_KLS98_KnockLimit | mV | 18248
[8 empty] | 18249 | Para_Knock_KLS98_MeasSigDist | Para_Knock_KLS98_MeasSigDist | 4566 | Para_Knock_KLS98_MeasSigDist | mV | 18249
[8 empty] | 18250 | Para_Knock_KLS98_MechNoiseMax | Para_Knock_KLS98_MechNoiseMax | 4567 | Para_Knock_KLS98_MechNoiseMax | mV | 18250
[8 empty] | 18251 | Para_Knock_KLS98_ValveNoiseMax | Para_Knock_KLS98_ValveNoiseMax | 4568 | Para_Knock_KLS98_ValveNoiseMax | mV | 18251
[8 empty] | 18252 | Para_Knock_PBC_AngleDurGlowI | Para_Knock_PBC_AngleDurGlowI | 4569 | Para_Knock_PBC_AngleDurGlowI |  | 18252
[8 empty] | 18253 | Para_Knock_PBC_AngleDurKnock | Para_Knock_PBC_AngleDurKnock | 4570 | Para_Knock_PBC_AngleDurKnock |  | 18253
[8 empty] | 18254 | Para_Knock_PBC_AnglePosGlowI | Para_Knock_PBC_AnglePosGlowI | 4571 | Para_Knock_PBC_AnglePosGlowI | °KW | 18254
[8 empty] | 18255 | Para_Knock_PBC_AnglePosKnock | Para_Knock_PBC_AnglePosKnock | 4572 | Para_Knock_PBC_AnglePosKnock | °KW | 18255
[8 empty] | 18256 | Para_Knock_PBC_GlobalIPAdj | Para_Knock_PBC_GlobalIPAdj | 4573 | Para_Knock_PBC_GlobalIPAdj |  | 18256
[8 empty] | 18257 | Para_Knock_PBC_GlowILimit | Para_Knock_PBC_GlowILimit | 4574 | Para_Knock_PBC_GlowILimit | % | 18257
[8 empty] | 18258 | Para_Knock_PBC_KnockLimit | Para_Knock_PBC_KnockLimit | 4575 | Para_Knock_PBC_KnockLimit | mbar | 18258
[8 empty] | 18259 | Para_Knock_PBC_MeasSigLimit | Para_Knock_PBC_MeasSigLimit | 4576 | Para_Knock_PBC_MeasSigLimit | mbar | 18259
[8 empty] | 18260 | Para_Knock_RedITPEnd | Para_Knock_RedITPEnd | 4577 | Para_Knock_RedITPEnd |  | 18260
[8 empty] | 18261 | Para_Knock_RedITPEndNew | Para_Knock_RedITPEndNew | 4578 | Para_Knock_RedITPEndNew | % | 18261
[8 empty] | 18262 | Para_Knock_RedITPStart | Para_Knock_RedITPStart | 4579 | Para_Knock_RedITPStart | % | 18262
[8 empty] | 18263 | Para_Knock_RedMixTempEnd | Para_Knock_RedMixTempEnd | 4580 | Para_Knock_RedMixTempEnd |  | 18263
[8 empty] | 18264 | Para_Knock_RedMixTempEndNew | Para_Knock_RedMixTempEndNew | 4581 | Para_Knock_RedMixTempEndNew | % | 18264
[8 empty] | 18265 | Para_Knock_RedMixTempStart | Para_Knock_RedMixTempStart | 4582 | Para_Knock_RedMixTempStart | % | 18265
[8 empty] | 18266 | Para_Knock_RedPowerEnd | Para_Knock_RedPowerEnd | 4583 | Para_Knock_RedPowerEnd |  | 18266
[8 empty] | 18267 | Para_Knock_RedPowerEndNew | Para_Knock_RedPowerEndNew | 4584 | Para_Knock_RedPowerEndNew | % | 18267
[8 empty] | 18268 | Para_Knock_RedPowerStart | Para_Knock_RedPowerStart | 4585 | Para_Knock_RedPowerStart | % | 18268
[8 empty] | 18269 | Para_Knock_TempMixRedMax | Para_Knock_TempMixRedMax | 4586 | Para_Knock_TempMixRedMax | °C | 18269
[8 empty] | 18270 | Para_Knock_TimeIntDown | Para_Knock_TimeIntDown | 4587 | Para_Knock_TimeIntDown | s | 18270
[8 empty] | 18271 | Para_Knock_TimeIntUp | Para_Knock_TimeIntUp | 4588 | Para_Knock_TimeIntUp | s | 18271
[8 empty] | 18272 | Para_Leanox_ActILeanoxCtrIsland | Para_Leanox_ActILeanoxCtrIsland | 4589 | Para_Leanox_ActILeanoxCtrIsland |  | 18272
[8 empty] | 18273 | Para_Leanox_ActPRedLeanox | Para_Leanox_ActPRedLeanox | 4590 | Para_Leanox_ActPRedLeanox |  | 18273
[8 empty] | 18274 | Para_Leanox_Comp_ActITPBoostPress | Para_Leanox_Comp_ActITPBoostPress | 4591 | Para_Leanox_Comp_ActITPBoostPress |  | 18274
[8 empty] | 18275 | Para_Leanox_Comp_ActMixtTempBoostPress | Para_Leanox_Comp_ActMixtTempBoostPress | 4592 | Para_Leanox_Comp_ActMixtTempBoostPress |  | 18275
[8 empty] | 18276 | Para_Leanox_Comp_ActPowerFriction | Para_Leanox_Comp_ActPowerFriction | 4593 | Para_Leanox_Comp_ActPowerFriction | kW | 18276
[8 empty] | 18277 | Para_Leanox_Comp_ActSpeed | Para_Leanox_Comp_ActSpeed | 4594 | Para_Leanox_Comp_ActSpeed |  | 18277
[8 empty] | 18278 | Para_Leanox_Comp_ITPDeltaPress1 | Para_Leanox_Comp_ITPDeltaPress1 | 4595 | Para_Leanox_Comp_ITPDeltaPress1 | mbar/°KW | 18278
[8 empty] | 18279 | Para_Leanox_Comp_ITPDeltaPress2 | Para_Leanox_Comp_ITPDeltaPress2 | 4596 | Para_Leanox_Comp_ITPDeltaPress2 | mbar/°KW | 18279
[8 empty] | 18280 | Para_Leanox_Comp_ITPPower1 | Power SetVal | 4597 | Para_Leanox_Comp_ITPPower1 | kW | 18280
[8 empty] | 18281 | Para_Leanox_Comp_ITPPower2 | Para_Leanox_Comp_ITPPower2 | 4598 | Para_Leanox_Comp_ITPPower2 |  | 18281
[8 empty] | 18282 | Para_Leanox_Comp_ITPPowerMin | Para_Leanox_Comp_ITPPowerMin | 4599 | Para_Leanox_Comp_ITPPowerMin | % | 18282
[8 empty] | 18283 | Para_Leanox_Comp_MixTempPower1 | Para_Leanox_Comp_MixTempPower1 | 4600 | Para_Leanox_Comp_MixTempPower1 |  | 18283
[8 empty] | 18284 | Para_Leanox_Comp_MixTempPower2 | Para_Leanox_Comp_MixTempPower2 | 4601 | Para_Leanox_Comp_MixTempPower2 | kW | 18284
[8 empty] | 18285 | Para_Leanox_Comp_MixTempPowerMin | Para_Leanox_Comp_MixTempPowerMin | 4602 | Para_Leanox_Comp_MixTempPowerMin | % | 18285
[8 empty] | 18286 | Para_Leanox_Comp_MixTempPress1 | Para_Leanox_Comp_MixTempPress1 | 4603 | Para_Leanox_Comp_MixTempPress1 | mbar/°C | 18286
[8 empty] | 18287 | Para_Leanox_Comp_MixTempPress2 | Para_Leanox_Comp_MixTempPress2 | 4604 | Para_Leanox_Comp_MixTempPress2 | mbar/°C | 18287
[8 empty] | 18288 | Para_Leanox_Gas1_CtrGasmixer_DeadBand | Para_Leanox_Gas1_CtrGasmixer_DeadBand | 4605 | Para_Leanox_Gas1_CtrGasmixer_DeadBand | mbar | 18288
[8 empty] | 18289 | Para_Leanox_Gas1_CtrGasmixer_IComp | Para_Leanox_Gas1_CtrGasmixer_IComp | 4606 | Para_Leanox_Gas1_CtrGasmixer_IComp |  | 18289
[8 empty] | 18290 | Para_Leanox_Gas1_CtrGasmixer_Limit | Para_Leanox_Gas1_CtrGasmixer_Limit | 4607 | Para_Leanox_Gas1_CtrGasmixer_Limit | mbar | 18290
[8 empty] | 18291 | Para_Leanox_Gas1_CtrGasmixer_PComp | Para_Leanox_Gas1_CtrGasmixer_PComp | 4608 | Para_Leanox_Gas1_CtrGasmixer_PComp |  | 18291
[8 empty] | 18292 | Para_Leanox_Gas1_CtrGasmixer_YMax | Para_Leanox_Gas1_CtrGasmixer_YMax | 4609 | Para_Leanox_Gas1_CtrGasmixer_YMax | % | 18292
[8 empty] | 18293 | Para_Leanox_Gas1_CtrGasmixer_YMin | Para_Leanox_Gas1_CtrGasmixer_YMin | 4610 | Para_Leanox_Gas1_CtrGasmixer_YMin | % | 18293
[8 empty] | 18294 | Para_Leanox_Gas1_CtrTecjet_DeadBand | Para_Leanox_Gas1_CtrTecjet_DeadBand | 4611 | Para_Leanox_Gas1_CtrTecjet_DeadBand | mbar | 18294
[8 empty] | 18295 | Para_Leanox_Gas1_CtrTecjet_IComp | Para_Leanox_Gas1_CtrTecjet_IComp | 4612 | Para_Leanox_Gas1_CtrTecjet_IComp |  | 18295
[8 empty] | 18296 | Para_Leanox_Gas1_CtrTecjet_Limit | Para_Leanox_Gas1_CtrTecjet_Limit | 4613 | Para_Leanox_Gas1_CtrTecjet_Limit | mbar | 18296
[8 empty] | 18297 | Para_Leanox_Gas1_CtrTecjet_PComp | Para_Leanox_Gas1_CtrTecjet_PComp | 4614 | Para_Leanox_Gas1_CtrTecjet_PComp |  | 18297
[8 empty] | 18298 | Para_Leanox_Gas1_CtrTecjet_YMax | Para_Leanox_Gas1_CtrTecjet_YMax | 4615 | Para_Leanox_Gas1_CtrTecjet_YMax |  | 18298
[8 empty] | 18299 | Para_Leanox_Gas1_CtrTecjet_YMin | Para_Leanox_Gas1_CtrTecjet_YMin | 4616 | Para_Leanox_Gas1_CtrTecjet_YMin |  | 18299
[8 empty] | 18300 | Para_Leanox_Gas1_DeltaPressIsl | Para_Leanox_Gas1_DeltaPressIsl | 4617 | Para_Leanox_Gas1_DeltaPressIsl | mbar | 18300
[8 empty] | 18301 | Para_Leanox_Gas1_Para_DP | Para_Leanox_Gas1_Para_DP | 4618 | Para_Leanox_Gas1_Para_DP |  | 18301
[8 empty] | 18302 | Para_Leanox_Gas1_Para_DPIslandAdap | Para_Leanox_Gas1_Para_DPIslandAdap | 4619 | Para_Leanox_Gas1_Para_DPIslandAdap |  | 18302
[8 empty] | 18303 | Para_Leanox_Gas1_Para_P1 | Para_Leanox_Gas1_Para_P1 | 4620 | Para_Leanox_Gas1_Para_P1 |  | 18303
[8 empty] | 18304 | Para_Leanox_Gas1_Para_P2 | Para_Leanox_Gas1_Para_P2 | 4621 | Para_Leanox_Gas1_Para_P2 |  | 18304
[8 empty] | 18305 | Para_Leanox_Gas1_Para_PowerPoint1 | Para_Leanox_Gas1_Para_PowerPoint1 | 4622 | Para_Leanox_Gas1_Para_PowerPoint1 | kW | 18305
[8 empty] | 18306 | Para_Leanox_Gas1_Para_PowerPoint2 | Para_Leanox_Gas1_Para_PowerPoint2 | 4623 | Para_Leanox_Gas1_Para_PowerPoint2 | kW | 18306
[8 empty] | 18307 | Para_Leanox_Gas1_Para_PressurePoint1 | Para_Leanox_Gas1_Para_PressurePoint1 | 4624 | Para_Leanox_Gas1_Para_PressurePoint1 | mbar | 18307
[8 empty] | 18308 | Para_Leanox_Gas1_Para_PressurePoint2 | Para_Leanox_Gas1_Para_PressurePoint2 | 4625 | Para_Leanox_Gas1_Para_PressurePoint2 | mbar | 18308
[8 empty] | 18309 | Para_Leanox_Gas1_Para_SpeedPoint1 | Para_Leanox_Gas1_Para_SpeedPoint1 | 4626 | Para_Leanox_Gas1_Para_SpeedPoint1 | 1/min | 18309
[8 empty] | 18310 | Para_Leanox_Gas1_Para_SpeedPoint2 | Para_Leanox_Gas1_Para_SpeedPoint2 | 4627 | Para_Leanox_Gas1_Para_SpeedPoint2 | 1/min | 18310
[8 empty] | 18311 | Para_Leanox_Gas1_Para_T1 | Para_Leanox_Gas1_Para_T1 | 4628 | Para_Leanox_Gas1_Para_T1 |  | 18311
[8 empty] | 18312 | Para_Leanox_Gas1_Para_TempPoint1 | Para_Leanox_Gas1_Para_TempPoint1 | 4629 | Para_Leanox_Gas1_Para_TempPoint1 | °C | 18312
[8 empty] | 18313 | Para_Leanox_Gas1_Para_TempPoint2 | Para_Leanox_Gas1_Para_TempPoint2 | 4630 | Para_Leanox_Gas1_Para_TempPoint2 | °C | 18313
[8 empty] | 18314 | Para_Leanox_Gas1_Para_W1 | Para_Leanox_Gas1_Para_W1 | 4631 | Para_Leanox_Gas1_Para_W1 |  | 18314
[8 empty] | 18315 | Para_Leanox_Gas1_PowerAct | Para_Leanox_Gas1_PowerAct | 4632 | Para_Leanox_Gas1_PowerAct | kW | 18315
[8 empty] | 18316 | Para_Leanox_Gas1_PowerActHys | Para_Leanox_Gas1_PowerActHys | 4633 | Para_Leanox_Gas1_PowerActHys | kW | 18316
[8 empty] | 18317 | Para_Leanox_Gas2_CtrGasmixer_DeadBand | Para_Leanox_Gas2_CtrGasmixer_DeadBand | 4634 | Para_Leanox_Gas2_CtrGasmixer_DeadBand | mbar | 18317
[8 empty] | 18318 | Para_Leanox_Gas2_CtrGasmixer_IComp | Para_Leanox_Gas2_CtrGasmixer_IComp | 4635 | Para_Leanox_Gas2_CtrGasmixer_IComp |  | 18318
[8 empty] | 18319 | Para_Leanox_Gas2_CtrGasmixer_Limit | Para_Leanox_Gas2_CtrGasmixer_Limit | 4636 | Para_Leanox_Gas2_CtrGasmixer_Limit | mbar | 18319
[8 empty] | 18320 | Para_Leanox_Gas2_CtrGasmixer_PComp | Para_Leanox_Gas2_CtrGasmixer_PComp | 4637 | Para_Leanox_Gas2_CtrGasmixer_PComp |  | 18320
[8 empty] | 18321 | Para_Leanox_Gas2_CtrGasmixer_YMax | Para_Leanox_Gas2_CtrGasmixer_YMax | 4638 | Para_Leanox_Gas2_CtrGasmixer_YMax | % | 18321
[8 empty] | 18322 | Para_Leanox_Gas2_CtrGasmixer_YMin | Para_Leanox_Gas2_CtrGasmixer_YMin | 4639 | Para_Leanox_Gas2_CtrGasmixer_YMin | % | 18322
[8 empty] | 18323 | Para_Leanox_Gas2_CtrTecjet_DeadBand | Para_Leanox_Gas2_CtrTecjet_DeadBand | 4640 | Para_Leanox_Gas2_CtrTecjet_DeadBand | mbar | 18323
[8 empty] | 18324 | Para_Leanox_Gas2_CtrTecjet_IComp | Para_Leanox_Gas2_CtrTecjet_IComp | 4641 | Para_Leanox_Gas2_CtrTecjet_IComp |  | 18324
[8 empty] | 18325 | Para_Leanox_Gas2_CtrTecjet_Limit | Para_Leanox_Gas2_CtrTecjet_Limit | 4642 | Para_Leanox_Gas2_CtrTecjet_Limit | mbar | 18325
[8 empty] | 18326 | Para_Leanox_Gas2_CtrTecjet_PComp | Para_Leanox_Gas2_CtrTecjet_PComp | 4643 | Para_Leanox_Gas2_CtrTecjet_PComp |  | 18326
[8 empty] | 18327 | Para_Leanox_Gas2_CtrTecjet_YMax | Para_Leanox_Gas2_CtrTecjet_YMax | 4644 | Para_Leanox_Gas2_CtrTecjet_YMax |  | 18327
[8 empty] | 18328 | Para_Leanox_Gas2_CtrTecjet_YMin | Para_Leanox_Gas2_CtrTecjet_YMin | 4645 | Para_Leanox_Gas2_CtrTecjet_YMin |  | 18328
[8 empty] | 18329 | Para_Leanox_Gas2_DeltaPressIsl | Para_Leanox_Gas2_DeltaPressIsl | 4646 | Para_Leanox_Gas2_DeltaPressIsl | mbar | 18329
[8 empty] | 18330 | Para_Leanox_Gas2_Para_DP | Para_Leanox_Gas2_Para_DP | 4647 | Para_Leanox_Gas2_Para_DP |  | 18330
[8 empty] | 18331 | Para_Leanox_Gas2_Para_DPIslandAdap | Para_Leanox_Gas2_Para_DPIslandAdap | 4648 | Para_Leanox_Gas2_Para_DPIslandAdap |  | 18331
[8 empty] | 18332 | Para_Leanox_Gas2_Para_P1 | Para_Leanox_Gas2_Para_P1 | 4649 | Para_Leanox_Gas2_Para_P1 |  | 18332
[8 empty] | 18333 | Para_Leanox_Gas2_Para_P2 | Para_Leanox_Gas2_Para_P2 | 4650 | Para_Leanox_Gas2_Para_P2 |  | 18333
[8 empty] | 18334 | Para_Leanox_Gas2_Para_PowerPoint1 | Para_Leanox_Gas2_Para_PowerPoint1 | 4651 | Para_Leanox_Gas2_Para_PowerPoint1 | kW | 18334
[8 empty] | 18335 | Para_Leanox_Gas2_Para_PowerPoint2 | Para_Leanox_Gas2_Para_PowerPoint2 | 4652 | Para_Leanox_Gas2_Para_PowerPoint2 | kW | 18335
[8 empty] | 18336 | Para_Leanox_Gas2_Para_PressurePoint1 | Para_Leanox_Gas2_Para_PressurePoint1 | 4653 | Para_Leanox_Gas2_Para_PressurePoint1 | mbar | 18336
[8 empty] | 18337 | Para_Leanox_Gas2_Para_PressurePoint2 | Para_Leanox_Gas2_Para_PressurePoint2 | 4654 | Para_Leanox_Gas2_Para_PressurePoint2 | mbar | 18337
[8 empty] | 18338 | Para_Leanox_Gas2_Para_SpeedPoint1 | Para_Leanox_Gas2_Para_SpeedPoint1 | 4655 | Para_Leanox_Gas2_Para_SpeedPoint1 | 1/min | 18338
[8 empty] | 18339 | Para_Leanox_Gas2_Para_SpeedPoint2 | Para_Leanox_Gas2_Para_SpeedPoint2 | 4656 | Para_Leanox_Gas2_Para_SpeedPoint2 | 1/min | 18339
[8 empty] | 18340 | Para_Leanox_Gas2_Para_T1 | Para_Leanox_Gas2_Para_T1 | 4657 | Para_Leanox_Gas2_Para_T1 |  | 18340
[8 empty] | 18341 | Para_Leanox_Gas2_Para_TempPoint1 | Para_Leanox_Gas2_Para_TempPoint1 | 4658 | Para_Leanox_Gas2_Para_TempPoint1 | °C | 18341
[8 empty] | 18342 | Para_Leanox_Gas2_Para_TempPoint2 | Para_Leanox_Gas2_Para_TempPoint2 | 4659 | Para_Leanox_Gas2_Para_TempPoint2 | °C | 18342
[8 empty] | 18343 | Para_Leanox_Gas2_Para_W1 | Para_Leanox_Gas2_Para_W1 | 4660 | Para_Leanox_Gas2_Para_W1 |  | 18343
[8 empty] | 18344 | Para_Leanox_Gas2_PowerAct | Para_Leanox_Gas2_PowerAct | 4661 | Para_Leanox_Gas2_PowerAct | kW | 18344
[8 empty] | 18345 | Para_Leanox_Gas2_PowerActHys | Para_Leanox_Gas2_PowerActHys | 4662 | Para_Leanox_Gas2_PowerActHys | kW | 18345
[8 empty] | 18346 | Para_Leanox_Gas3_CtrGasmixer_DeadBand | Para_Leanox_Gas3_CtrGasmixer_DeadBand | 4663 | Para_Leanox_Gas3_CtrGasmixer_DeadBand | mbar | 18346
[8 empty] | 18347 | Para_Leanox_Gas3_CtrGasmixer_IComp | Para_Leanox_Gas3_CtrGasmixer_IComp | 4664 | Para_Leanox_Gas3_CtrGasmixer_IComp |  | 18347
[8 empty] | 18348 | Para_Leanox_Gas3_CtrGasmixer_Limit | Para_Leanox_Gas3_CtrGasmixer_Limit | 4665 | Para_Leanox_Gas3_CtrGasmixer_Limit | mbar | 18348
[8 empty] | 18349 | Para_Leanox_Gas3_CtrGasmixer_PComp | Para_Leanox_Gas3_CtrGasmixer_PComp | 4666 | Para_Leanox_Gas3_CtrGasmixer_PComp |  | 18349
[8 empty] | 18350 | Para_Leanox_Gas3_CtrGasmixer_YMax | Para_Leanox_Gas3_CtrGasmixer_YMax | 4667 | Para_Leanox_Gas3_CtrGasmixer_YMax | % | 18350
[8 empty] | 18351 | Para_Leanox_Gas3_CtrGasmixer_YMin | Para_Leanox_Gas3_CtrGasmixer_YMin | 4668 | Para_Leanox_Gas3_CtrGasmixer_YMin | % | 18351
[8 empty] | 18352 | Para_Leanox_Gas3_CtrTecjet_DeadBand | Para_Leanox_Gas3_CtrTecjet_DeadBand | 4669 | Para_Leanox_Gas3_CtrTecjet_DeadBand | mbar | 18352
[8 empty] | 18353 | Para_Leanox_Gas3_CtrTecjet_IComp | Para_Leanox_Gas3_CtrTecjet_IComp | 4670 | Para_Leanox_Gas3_CtrTecjet_IComp |  | 18353
[8 empty] | 18354 | Para_Leanox_Gas3_CtrTecjet_Limit | Para_Leanox_Gas3_CtrTecjet_Limit | 4671 | Para_Leanox_Gas3_CtrTecjet_Limit | mbar | 18354
[8 empty] | 18355 | Para_Leanox_Gas3_CtrTecjet_PComp | Para_Leanox_Gas3_CtrTecjet_PComp | 4672 | Para_Leanox_Gas3_CtrTecjet_PComp |  | 18355
[8 empty] | 18356 | Para_Leanox_Gas3_CtrTecjet_YMax | Para_Leanox_Gas3_CtrTecjet_YMax | 4673 | Para_Leanox_Gas3_CtrTecjet_YMax |  | 18356
[8 empty] | 18357 | Para_Leanox_Gas3_CtrTecjet_YMin | Para_Leanox_Gas3_CtrTecjet_YMin | 4674 | Para_Leanox_Gas3_CtrTecjet_YMin |  | 18357
[8 empty] | 18358 | Para_Leanox_Gas3_DeltaPressIsl | Para_Leanox_Gas3_DeltaPressIsl | 4675 | Para_Leanox_Gas3_DeltaPressIsl | mbar | 18358
[8 empty] | 18359 | Para_Leanox_Gas3_Para_DP | Para_Leanox_Gas3_Para_DP | 4676 | Para_Leanox_Gas3_Para_DP |  | 18359
[8 empty] | 18360 | Para_Leanox_Gas3_Para_DPIslandAdap | Para_Leanox_Gas3_Para_DPIslandAdap | 4677 | Para_Leanox_Gas3_Para_DPIslandAdap |  | 18360
[8 empty] | 18361 | Para_Leanox_Gas3_Para_P1 | Para_Leanox_Gas3_Para_P1 | 4678 | Para_Leanox_Gas3_Para_P1 |  | 18361
[8 empty] | 18362 | Para_Leanox_Gas3_Para_P2 | Para_Leanox_Gas3_Para_P2 | 4679 | Para_Leanox_Gas3_Para_P2 |  | 18362
[8 empty] | 18363 | Para_Leanox_Gas3_Para_PowerPoint1 | Para_Leanox_Gas3_Para_PowerPoint1 | 4680 | Para_Leanox_Gas3_Para_PowerPoint1 | kW | 18363
[8 empty] | 18364 | Para_Leanox_Gas3_Para_PowerPoint2 | Para_Leanox_Gas3_Para_PowerPoint2 | 4681 | Para_Leanox_Gas3_Para_PowerPoint2 | kW | 18364
[8 empty] | 18365 | Para_Leanox_Gas3_Para_PressurePoint1 | Para_Leanox_Gas3_Para_PressurePoint1 | 4682 | Para_Leanox_Gas3_Para_PressurePoint1 | mbar | 18365
[8 empty] | 18366 | Para_Leanox_Gas3_Para_PressurePoint2 | Para_Leanox_Gas3_Para_PressurePoint2 | 4683 | Para_Leanox_Gas3_Para_PressurePoint2 | mbar | 18366
[8 empty] | 18367 | Para_Leanox_Gas3_Para_SpeedPoint1 | Para_Leanox_Gas3_Para_SpeedPoint1 | 4684 | Para_Leanox_Gas3_Para_SpeedPoint1 | 1/min | 18367
[8 empty] | 18368 | Para_Leanox_Gas3_Para_SpeedPoint2 | Para_Leanox_Gas3_Para_SpeedPoint2 | 4685 | Para_Leanox_Gas3_Para_SpeedPoint2 | 1/min | 18368
[8 empty] | 18369 | Para_Leanox_Gas3_Para_T1 | Para_Leanox_Gas3_Para_T1 | 4686 | Para_Leanox_Gas3_Para_T1 |  | 18369
[8 empty] | 18370 | Para_Leanox_Gas3_Para_TempPoint1 | Para_Leanox_Gas3_Para_TempPoint1 | 4687 | Para_Leanox_Gas3_Para_TempPoint1 | °C | 18370
[8 empty] | 18371 | Para_Leanox_Gas3_Para_TempPoint2 | Para_Leanox_Gas3_Para_TempPoint2 | 4688 | Para_Leanox_Gas3_Para_TempPoint2 | °C | 18371
[8 empty] | 18372 | Para_Leanox_Gas3_Para_W1 | Para_Leanox_Gas3_Para_W1 | 4689 | Para_Leanox_Gas3_Para_W1 |  | 18372
[8 empty] | 18373 | Para_Leanox_Gas3_PowerAct | Para_Leanox_Gas3_PowerAct | 4690 | Para_Leanox_Gas3_PowerAct | kW | 18373
[8 empty] | 18374 | Para_Leanox_Gas3_PowerActHys | Para_Leanox_Gas3_PowerActHys | 4691 | Para_Leanox_Gas3_PowerActHys | kW | 18374
[8 empty] | 18375 | Para_Leanox_Gas4_CtrGasmixer_DeadBand | Para_Leanox_Gas4_CtrGasmixer_DeadBand | 4692 | Para_Leanox_Gas4_CtrGasmixer_DeadBand | mbar | 18375
[8 empty] | 18376 | Para_Leanox_Gas4_CtrGasmixer_IComp | Para_Leanox_Gas4_CtrGasmixer_IComp | 4693 | Para_Leanox_Gas4_CtrGasmixer_IComp |  | 18376
[8 empty] | 18377 | Para_Leanox_Gas4_CtrGasmixer_Limit | Para_Leanox_Gas4_CtrGasmixer_Limit | 4694 | Para_Leanox_Gas4_CtrGasmixer_Limit | mbar | 18377
[8 empty] | 18378 | Para_Leanox_Gas4_CtrGasmixer_PComp | Para_Leanox_Gas4_CtrGasmixer_PComp | 4695 | Para_Leanox_Gas4_CtrGasmixer_PComp |  | 18378
[8 empty] | 18379 | Para_Leanox_Gas4_CtrGasmixer_YMax | Para_Leanox_Gas4_CtrGasmixer_YMax | 4696 | Para_Leanox_Gas4_CtrGasmixer_YMax | % | 18379
[8 empty] | 18380 | Para_Leanox_Gas4_CtrGasmixer_YMin | Para_Leanox_Gas4_CtrGasmixer_YMin | 4697 | Para_Leanox_Gas4_CtrGasmixer_YMin | % | 18380
[8 empty] | 18381 | Para_Leanox_Gas4_CtrTecjet_DeadBand | Para_Leanox_Gas4_CtrTecjet_DeadBand | 4698 | Para_Leanox_Gas4_CtrTecjet_DeadBand | mbar | 18381
[8 empty] | 18382 | Para_Leanox_Gas4_CtrTecjet_IComp | Para_Leanox_Gas4_CtrTecjet_IComp | 4699 | Para_Leanox_Gas4_CtrTecjet_IComp |  | 18382
[8 empty] | 18383 | Para_Leanox_Gas4_CtrTecjet_Limit | Para_Leanox_Gas4_CtrTecjet_Limit | 4700 | Para_Leanox_Gas4_CtrTecjet_Limit | mbar | 18383
[8 empty] | 18384 | Para_Leanox_Gas4_CtrTecjet_PComp | Para_Leanox_Gas4_CtrTecjet_PComp | 4701 | Para_Leanox_Gas4_CtrTecjet_PComp |  | 18384
[8 empty] | 18385 | Para_Leanox_Gas4_CtrTecjet_YMax | Para_Leanox_Gas4_CtrTecjet_YMax | 4702 | Para_Leanox_Gas4_CtrTecjet_YMax |  | 18385
[8 empty] | 18386 | Para_Leanox_Gas4_CtrTecjet_YMin | Para_Leanox_Gas4_CtrTecjet_YMin | 4703 | Para_Leanox_Gas4_CtrTecjet_YMin |  | 18386
[8 empty] | 18387 | Para_Leanox_Gas4_DeltaPressIsl | Para_Leanox_Gas4_DeltaPressIsl | 4704 | Para_Leanox_Gas4_DeltaPressIsl | mbar | 18387
[8 empty] | 18388 | Para_Leanox_Gas4_Para_DP | Para_Leanox_Gas4_Para_DP | 4705 | Para_Leanox_Gas4_Para_DP |  | 18388
[8 empty] | 18389 | Para_Leanox_Gas4_Para_DPIslandAdap | Para_Leanox_Gas4_Para_DPIslandAdap | 4706 | Para_Leanox_Gas4_Para_DPIslandAdap |  | 18389
[8 empty] | 18390 | Para_Leanox_Gas4_Para_P1 | Para_Leanox_Gas4_Para_P1 | 4707 | Para_Leanox_Gas4_Para_P1 |  | 18390
[8 empty] | 18391 | Para_Leanox_Gas4_Para_P2 | Para_Leanox_Gas4_Para_P2 | 4708 | Para_Leanox_Gas4_Para_P2 |  | 18391
[8 empty] | 18392 | Para_Leanox_Gas4_Para_PowerPoint1 | Para_Leanox_Gas4_Para_PowerPoint1 | 4709 | Para_Leanox_Gas4_Para_PowerPoint1 | kW | 18392
[8 empty] | 18393 | Para_Leanox_Gas4_Para_PowerPoint2 | Para_Leanox_Gas4_Para_PowerPoint2 | 4710 | Para_Leanox_Gas4_Para_PowerPoint2 | kW | 18393
[8 empty] | 18394 | Para_Leanox_Gas4_Para_PressurePoint1 | Para_Leanox_Gas4_Para_PressurePoint1 | 4711 | Para_Leanox_Gas4_Para_PressurePoint1 | mbar | 18394
[8 empty] | 18395 | Para_Leanox_Gas4_Para_PressurePoint2 | Para_Leanox_Gas4_Para_PressurePoint2 | 4712 | Para_Leanox_Gas4_Para_PressurePoint2 | mbar | 18395
[8 empty] | 18396 | Para_Leanox_Gas4_Para_SpeedPoint1 | Para_Leanox_Gas4_Para_SpeedPoint1 | 4713 | Para_Leanox_Gas4_Para_SpeedPoint1 | 1/min | 18396
[8 empty] | 18397 | Para_Leanox_Gas4_Para_SpeedPoint2 | Para_Leanox_Gas4_Para_SpeedPoint2 | 4714 | Para_Leanox_Gas4_Para_SpeedPoint2 | 1/min | 18397
[8 empty] | 18398 | Para_Leanox_Gas4_Para_T1 | Para_Leanox_Gas4_Para_T1 | 4715 | Para_Leanox_Gas4_Para_T1 |  | 18398
[8 empty] | 18399 | Para_Leanox_Gas4_Para_TempPoint1 | Para_Leanox_Gas4_Para_TempPoint1 | 4716 | Para_Leanox_Gas4_Para_TempPoint1 | °C | 18399
[8 empty] | 18400 | Para_Leanox_Gas4_Para_TempPoint2 | Para_Leanox_Gas4_Para_TempPoint2 | 4717 | Para_Leanox_Gas4_Para_TempPoint2 | °C | 18400
[8 empty] | 18401 | Para_Leanox_Gas4_Para_W1 | Para_Leanox_Gas4_Para_W1 | 4718 | Para_Leanox_Gas4_Para_W1 |  | 18401
[8 empty] | 18402 | Para_Leanox_Gas4_PowerAct | Para_Leanox_Gas4_PowerAct | 4719 | Para_Leanox_Gas4_PowerAct | kW | 18402
[8 empty] | 18403 | Para_Leanox_Gas4_PowerActHys | Para_Leanox_Gas4_PowerActHys | 4720 | Para_Leanox_Gas4_PowerActHys | kW | 18403
[8 empty] | 18404 | Para_Leanox_Humidity_ActBoostTempOffset | Para_Leanox_Humidity_ActBoostTempOffset | 4721 | Para_Leanox_Humidity_ActBoostTempOffset |  | 18404
[8 empty] | 18405 | Para_Leanox_Humidity_BoostTempDevToICWT | Para_Leanox_Humidity_BoostTempDevToICWT | 4722 | Para_Leanox_Humidity_BoostTempDevToICWT | °C | 18405
[8 empty] | 18406 | Para_Leanox_Humidity_BoostTempRaiseDevTime | Para_Leanox_Humidity_BoostTempRaiseDevTime | 4723 | Para_Leanox_Humidity_BoostTempRaiseDevTime | s | 18406
[8 empty] | 18407 | Para_Leanox_Humidity_BosstTempRaiseMax | Para_Leanox_Humidity_BosstTempRaiseMax | 4724 | Para_Leanox_Humidity_BosstTempRaiseMax | °C | 18407
[8 empty] | 18408 | Para_Leanox_Humidity_CompValKnockMonStart | Para_Leanox_Humidity_CompValKnockMonStart | 4725 | Para_Leanox_Humidity_CompValKnockMonStart | mbar | 18408
[8 empty] | 18409 | Para_Leanox_Humidity_CompValPnom | Para_Leanox_Humidity_CompValPnom | 4726 | Para_Leanox_Humidity_CompValPnom | mbar | 18409
[8 empty] | 18410 | Para_Leanox_Humidity_Offset | Para_Leanox_Humidity_Offset | 4727 | Para_Leanox_Humidity_Offset | % | 18410
[8 empty] | 18411 | Para_Leanox_PressBoost_20mA | Para_Leanox_PressBoost_20mA | 4728 | Para_Leanox_PressBoost_20mA | bar | 18411
[8 empty] | 18412 | Para_Leanox_PressBoost_4mA | Para_Leanox_PressBoost_4mA | 4729 | Para_Leanox_PressBoost_4mA | bar | 18412
[8 empty] | 18413 | Para_Leanox_PressBoost_ActP2 | Para_Leanox_PressBoost_ActP2 | 4730 | Para_Leanox_PressBoost_ActP2 |  | 18413
[8 empty] | 18414 | Para_Leanox_PressBoost_P2_20mA | Para_Leanox_PressBoost_P2_20mA | 4731 | Para_Leanox_PressBoost_P2_20mA | bar | 18414
[8 empty] | 18415 | Para_Leanox_PressBoost_P2_4mA | Para_Leanox_PressBoost_P2_4mA | 4732 | Para_Leanox_PressBoost_P2_4mA | bar | 18415
[8 empty] | 18416 | Para_Leanox_RampPowerRed | Para_Leanox_RampPowerRed | 4733 | Para_Leanox_RampPowerRed |  | 18416
[8 empty] | 18417 | Para_Misfire_KLS98_Active | Para_Misfire_KLS98_Active | 4734 | Para_Misfire_KLS98_Active | % | 18417
[8 empty] | 18418 | Para_Misfire_KLS98_ActOCA | Para_Misfire_KLS98_ActOCA | 4735 | Para_Misfire_KLS98_ActOCA |  | 18418
[8 empty] | 18419 | Para_Misfire_KLS98_AngleWindowDur | Para_Misfire_KLS98_AngleWindowDur | 4736 | Para_Misfire_KLS98_AngleWindowDur | °KW | 18419
[8 empty] | 18420 | Para_Misfire_KLS98_AngleWindowLimit | Para_Misfire_KLS98_AngleWindowLimit | 4737 | Para_Misfire_KLS98_AngleWindowLimit | °KW | 18420
[8 empty] | 18421 | Para_Misfire_KLS98_Limit | Para_Misfire_KLS98_Limit | 4738 | Para_Misfire_KLS98_Limit | mV | 18421
[8 empty] | 18422 | Para_Misfire_Limit | Para_Misfire_Limit | 4739 | Para_Misfire_Limit | %Pn/s | 18422
[8 empty] | 18423 | Para_Misfire_PreWarn | Para_Misfire_PreWarn | 4740 | Para_Misfire_PreWarn | % | 18423
[8 empty] | 18424 | Para_Misfire_TimeIntDown | Para_Misfire_TimeIntDown | 4741 | Para_Misfire_TimeIntDown | s | 18424
[8 empty] | 18425 | Para_Misfire_TimeIntUp | Para_Misfire_TimeIntUp | 4742 | Para_Misfire_TimeIntUp | s | 18425
[8 empty] | 18426 | Para_MixCharge_AirFilterDiffPress_20mA | Para_MixCharge_AirFilterDiffPress_20mA | 4743 | Para_MixCharge_AirFilterDiffPress_20mA | mbar | 18426
[8 empty] | 18427 | Para_MixCharge_AirFilterDiffPress_4mA | Para_MixCharge_AirFilterDiffPress_4mA | 4744 | Para_MixCharge_AirFilterDiffPress_4mA | mbar | 18427
[8 empty] | 18428 | Para_MixCharge_AirFilterDiffPress_ActPressA | Para_MixCharge_AirFilterDiffPress_ActPressA | 4745 | Para_MixCharge_AirFilterDiffPress_ActPressA |  | 18428
[8 empty] | 18429 | Para_MixCharge_AirFilterDiffPress_ActPressB | Para_MixCharge_AirFilterDiffPress_ActPressB | 4746 | Para_MixCharge_AirFilterDiffPress_ActPressB |  | 18429
[8 empty] | 18430 | Para_MixCharge_AirFilterDiffPress_Limit | Para_MixCharge_AirFilterDiffPress_Limit | 4747 | Para_MixCharge_AirFilterDiffPress_Limit | mbar | 18430
[8 empty] | 18431 | Para_MixCharge_AirFilterDiffPress_LimitHys | Para_MixCharge_AirFilterDiffPress_LimitHys | 4748 | Para_MixCharge_AirFilterDiffPress_LimitHys | mbar | 18431
[8 empty] | 20108 | Para_MixCharge_Press_Act_Pr_Ch_P1HP | Para_MixCharge_Press_Act_Pr_Ch_P1HP | 4749 | Para_MixCharge_Press_Act_Pr_Ch_P1HP |  | 20108
[8 empty] | 20106 | Para_MixCharge_Press_Act_Pr_Ch_P1HP_A | Para_MixCharge_Press_Act_Pr_Ch_P1HP_A | 4750 | Para_MixCharge_Press_Act_Pr_Ch_P1HP_A |  | 20106
[8 empty] | 20107 | Para_MixCharge_Press_Act_Pr_Ch_P1HP_B | Para_MixCharge_Press_Act_Pr_Ch_P1HP_B | 4751 | Para_MixCharge_Press_Act_Pr_Ch_P1HP_B |  | 20107
[8 empty] | 20109 | Para_MixCharge_Press_Act_Pr_Ch_P2_A | Para_MixCharge_Press_Act_Pr_Ch_P2_A | 4752 | Para_MixCharge_Press_Act_Pr_Ch_P2_A |  | 20109
[8 empty] | 20110 | Para_MixCharge_Press_Act_Pr_Ch_P2_B | Para_MixCharge_Press_Act_Pr_Ch_P2_B | 4753 | Para_MixCharge_Press_Act_Pr_Ch_P2_B |  | 20110
[8 empty] | 20113 | Para_MixCharge_Press_Act_Pr_Ch_P2s | Para_MixCharge_Press_Act_Pr_Ch_P2s | 4754 | Para_MixCharge_Press_Act_Pr_Ch_P2s |  | 20113
[8 empty] | 20111 | Para_MixCharge_Press_Act_Pr_Ch_P2s_A | Para_MixCharge_Press_Act_Pr_Ch_P2s_A | 4755 | Para_MixCharge_Press_Act_Pr_Ch_P2s_A |  | 20111
[8 empty] | 20112 | Para_MixCharge_Press_Act_Pr_Ch_P2s_B | Para_MixCharge_Press_Act_Pr_Ch_P2s_B | 4756 | Para_MixCharge_Press_Act_Pr_Ch_P2s_B |  | 20112
[8 empty] | 20119 | Para_MixCharge_Press_Pr_Ch_P1HPScalMax | Para_MixCharge_Press_Pr_Ch_P1HPScalMax | 4757 | Para_MixCharge_Press_Pr_Ch_P1HPScalMax | bar | 20119
[8 empty] | 20120 | Para_MixCharge_Press_Pr_Ch_P1HPScalMin | Para_MixCharge_Press_Pr_Ch_P1HPScalMin | 4758 | Para_MixCharge_Press_Pr_Ch_P1HPScalMin | bar | 20120
[8 empty] | 20125 | Para_MixCharge_Press_Pr_Ch_P2s_Diff_HiHi | Para_MixCharge_Press_Pr_Ch_P2s_Diff_HiHi | 4759 | Para_MixCharge_Press_Pr_Ch_P2s_Diff_HiHi | bar | 20125
[8 empty] | 20104 | Para_MixCharge_Speed_Act_N_TCHP | Para_MixCharge_Speed_Act_N_TCHP | 4760 | Para_MixCharge_Speed_Act_N_TCHP |  | 20104
[8 empty] | 20105 | Para_MixCharge_Speed_Act_N_TCLP | Para_MixCharge_Speed_Act_N_TCLP | 4761 | Para_MixCharge_Speed_Act_N_TCLP |  | 20105
[8 empty] | 20115 | Para_MixCharge_Speed_TCHPScalMax | Para_MixCharge_Speed_TCHPScalMax | 4762 | Para_MixCharge_Speed_TCHPScalMax | 1/min | 20115
[8 empty] | 20116 | Para_MixCharge_Speed_TCHPScalMin | Para_MixCharge_Speed_TCHPScalMin | 4763 | Para_MixCharge_Speed_TCHPScalMin | 1/min | 20116
[8 empty] | 20117 | Para_MixCharge_Speed_TCLPScalMax | Para_MixCharge_Speed_TCLPScalMax | 4764 | Para_MixCharge_Speed_TCLPScalMax | 1/min | 20117
[8 empty] | 20118 | Para_MixCharge_Speed_TCLPScalMin | Para_MixCharge_Speed_TCLPScalMin | 4765 | Para_MixCharge_Speed_TCLPScalMin | 1/min | 20118
[8 empty] | 18432 | Para_MixCharge_SpreadChargePress | Para_MixCharge_SpreadChargePress | 4766 | Para_MixCharge_SpreadChargePress | bar | 18432
[8 empty] | 18433 | Para_MixCharge_SpreadChargeTemp | Para_MixCharge_SpreadChargeTemp | 4767 | Para_MixCharge_SpreadChargeTemp | °C | 18433
[8 empty] | 20114 | Para_MixCharge_Temp_Act_T_Ch_T1HP_Exist | Para_MixCharge_Temp_Act_T_Ch_T1HP_Exist | 4768 | Para_MixCharge_Temp_Act_T_Ch_T1HP_Exist |  | 20114
[8 empty] | 18434 | Para_MixCharge_Temp_ActTempInletHighpressA | Para_MixCharge_Temp_ActTempInletHighpressA | 4769 | Para_MixCharge_Temp_ActTempInletHighpressA |  | 18434
[8 empty] | 18435 | Para_MixCharge_Temp_ActTempInletHighPressB | Para_MixCharge_Temp_ActTempInletHighPressB | 4770 | Para_MixCharge_Temp_ActTempInletHighPressB |  | 18435
[8 empty] | 18436 | Para_MixCharge_Temp_MaxDtInletHighPress | Para_MixCharge_Temp_MaxDtInletHighPress | 4771 | Para_MixCharge_Temp_MaxDtInletHighPress | °C | 18436
[8 empty] | 18437 | Para_MixCharge_Temp_MaxHysDtInletHighPress | Para_MixCharge_Temp_MaxHysDtInletHighPress | 4772 | Para_MixCharge_Temp_MaxHysDtInletHighPress | °C | 18437
[8 empty] | 18438 | Para_MixCharge_Temp_MaxHysInletHighPress | Para_MixCharge_Temp_MaxHysInletHighPress | 4773 | Para_MixCharge_Temp_MaxHysInletHighPress | °C | 18438
[8 empty] | 18439 | Para_MixCharge_Temp_MaxInletHighPress | Para_MixCharge_Temp_MaxInletHighPress | 4774 | Para_MixCharge_Temp_MaxInletHighPress | °C | 18439
[8 empty] | 18440 | Para_MixCharge_Temp_MinHysInletHighPress | Para_MixCharge_Temp_MinHysInletHighPress | 4775 | Para_MixCharge_Temp_MinHysInletHighPress | °C | 18440
[8 empty] | 18441 | Para_MixCharge_Temp_MinInletHighPress | Para_MixCharge_Temp_MinInletHighPress | 4776 | Para_MixCharge_Temp_MinInletHighPress | °C | 18441
[8 empty] | 18442 | Para_MixTemp_Ctr_CycleTime | Para_MixTemp_Ctr_CycleTime | 4777 | Para_MixTemp_Ctr_CycleTime | ms | 18442
[8 empty] | 18443 | Para_MixTemp_Ctr_DComp | Para_MixTemp_Ctr_DComp | 4778 | Para_MixTemp_Ctr_DComp | TV/TA | 18443
[8 empty] | 18444 | Para_MixTemp_Ctr_DCompTune | Para_MixTemp_Ctr_DCompTune | 4779 | Para_MixTemp_Ctr_DCompTune |  | 18444
[8 empty] | 18445 | Para_MixTemp_Ctr_DeadBand | Para_MixTemp_Ctr_DeadBand | 4780 | Para_MixTemp_Ctr_DeadBand | °C | 18445
[8 empty] | 18446 | Para_MixTemp_Ctr_IComp | Para_MixTemp_Ctr_IComp | 4781 | Para_MixTemp_Ctr_IComp | TA/TN | 18446
[8 empty] | 18447 | Para_MixTemp_Ctr_ICompTune | Para_MixTemp_Ctr_ICompTune | 4782 | Para_MixTemp_Ctr_ICompTune |  | 18447
[8 empty] | 18448 | Para_MixTemp_Ctr_InvertCtrTune | Para_MixTemp_Ctr_InvertCtrTune | 4783 | Para_MixTemp_Ctr_InvertCtrTune |  | 18448
[8 empty] | 18449 | Para_MixTemp_Ctr_PComp | Para_MixTemp_Ctr_PComp | 4784 | Para_MixTemp_Ctr_PComp |  | 18449
[8 empty] | 18450 | Para_MixTemp_Ctr_PCompTune | Para_MixTemp_Ctr_PCompTune | 4785 | Para_MixTemp_Ctr_PCompTune |  | 18450
[8 empty] | 18451 | Para_MixTemp_Ctr_RangeEnd | Para_MixTemp_Ctr_RangeEnd | 4786 | Para_MixTemp_Ctr_RangeEnd | °C | 18451
[8 empty] | 18452 | Para_MixTemp_Ctr_UserLevelIntExt | Para_MixTemp_Ctr_UserLevelIntExt | 4787 | Para_MixTemp_Ctr_UserLevelIntExt |  | 18452
[8 empty] | 18453 | Para_MixTemp_Ctr_UserLevelManAut | Para_MixTemp_Ctr_UserLevelManAut | 4788 | Para_MixTemp_Ctr_UserLevelManAut |  | 18453
[8 empty] | 18454 | Para_MixTemp_Ctr_UserLevelSet | Para_MixTemp_Ctr_UserLevelSet | 4789 | Para_MixTemp_Ctr_UserLevelSet |  | 18454
[8 empty] | 18455 | Para_MixTemp_Ctr_UserLevelTune | Para_MixTemp_Ctr_UserLevelTune | 4790 | Para_MixTemp_Ctr_UserLevelTune |  | 18455
[8 empty] | 18456 | Para_MixTemp_Ctr_WGas1 | Para_MixTemp_Ctr_WGas1 | 4791 | Para_MixTemp_Ctr_WGas1 | °C | 18456
[8 empty] | 18457 | Para_MixTemp_Ctr_WGas2 | Para_MixTemp_Ctr_WGas2 | 4792 | Para_MixTemp_Ctr_WGas2 | °C | 18457
[8 empty] | 18458 | Para_MixTemp_Ctr_WGas3 | Para_MixTemp_Ctr_WGas3 | 4793 | Para_MixTemp_Ctr_WGas3 | °C | 18458
[8 empty] | 18459 | Para_MixTemp_Ctr_WGas4 | Para_MixTemp_Ctr_WGas4 | 4794 | Para_MixTemp_Ctr_WGas4 | °C | 18459
[8 empty] | 18460 | Para_MixTemp_Ctr_WMax | Para_MixTemp_Ctr_WMax | 4795 | Para_MixTemp_Ctr_WMax | °C | 18460
[8 empty] | 18461 | Para_MixTemp_Ctr_WMin | Para_MixTemp_Ctr_WMin | 4796 | Para_MixTemp_Ctr_WMin | °C | 18461
[8 empty] | 18462 | Para_MixTemp_Ctr_WRampNeg | Para_MixTemp_Ctr_WRampNeg | 4797 | Para_MixTemp_Ctr_WRampNeg | °C/s | 18462
[8 empty] | 18463 | Para_MixTemp_Ctr_WRampPos | Para_MixTemp_Ctr_WRampPos | 4798 | Para_MixTemp_Ctr_WRampPos | °C/s | 18463
[8 empty] | 18464 | Para_MixTemp_Ctr_YBlock | Para_MixTemp_Ctr_YBlock | 4799 | Para_MixTemp_Ctr_YBlock | % | 18464
[8 empty] | 18465 | Para_MixTemp_Ctr_YMax | Para_MixTemp_Ctr_YMax | 4800 | Para_MixTemp_Ctr_YMax | % | 18465
[8 empty] | 18466 | Para_MixTemp_Ctr_YMin | Para_MixTemp_Ctr_YMin | 4801 | Para_MixTemp_Ctr_YMin | % | 18466
[8 empty] | 18467 | Para_MixTemp_Ctr_YRampNeg | Para_MixTemp_Ctr_YRampNeg | 4802 | Para_MixTemp_Ctr_YRampNeg | %/TA | 18467
[8 empty] | 18468 | Para_MixTemp_Ctr_YRampPos | Para_MixTemp_Ctr_YRampPos | 4803 | Para_MixTemp_Ctr_YRampPos | %/TA | 18468
[8 empty] | 18469 | Para_MixTemp_Ctr_YRampTune | Para_MixTemp_Ctr_YRampTune | 4804 | Para_MixTemp_Ctr_YRampTune |  | 18469
[8 empty] | 20122 | Para_MixTemp_Limit_Act_T_Ch_T2s_A_Exist | Para_MixTemp_Limit_Act_T_Ch_T2s_A_Exist | 4805 | Para_MixTemp_Limit_Act_T_Ch_T2s_A_Exist |  | 20122
[8 empty] | 20123 | Para_MixTemp_Limit_Act_T_Ch_T2s_B_Exist | Para_MixTemp_Limit_Act_T_Ch_T2s_B_Exist | 4806 | Para_MixTemp_Limit_Act_T_Ch_T2s_B_Exist |  | 20123
[8 empty] | 20124 | Para_MixTemp_Limit_Act_T_Ch_T2s_Exist | Para_MixTemp_Limit_Act_T_Ch_T2s_Exist | 4807 | Para_MixTemp_Limit_Act_T_Ch_T2s_Exist |  | 20124
[8 empty] | 18470 | Para_MixTemp_Limit_TempdTMax | Para_MixTemp_Limit_TempdTMax | 4808 | Para_MixTemp_Limit_TempdTMax | °C/s | 18470
[8 empty] | 18471 | Para_MixTemp_Limit_TempLimit1 | Para_MixTemp_Limit_TempLimit1 | 4809 | Para_MixTemp_Limit_TempLimit1 | °C | 18471
[8 empty] | 18472 | Para_MixTemp_Limit_TempLimit2 | Para_MixTemp_Limit_TempLimit2 | 4810 | Para_MixTemp_Limit_TempLimit2 | °C | 18472
[8 empty] | 18473 | Para_MixTemp_Limit_TempLimitHys1 | Para_MixTemp_Limit_TempLimitHys1 | 4811 | Para_MixTemp_Limit_TempLimitHys1 | °C | 18473
[8 empty] | 18474 | Para_MixTemp_Limit_TempLimitHys2 | Para_MixTemp_Limit_TempLimitHys2 | 4812 | Para_MixTemp_Limit_TempLimitHys2 | °C | 18474
[8 empty] | 18475 | Para_MixTemp_Limit_TempMax | Para_MixTemp_Limit_TempMax | 4813 | Para_MixTemp_Limit_TempMax | °C | 18475
[8 empty] | 18476 | Para_MixTemp_Limit_TempMaxHys | Para_MixTemp_Limit_TempMaxHys | 4814 | Para_MixTemp_Limit_TempMaxHys | °C | 18476
[8 empty] | 18477 | Para_MixTemp_Limit_TempMin | Para_MixTemp_Limit_TempMin | 4815 | Para_MixTemp_Limit_TempMin |  | 18477
[8 empty] | 18478 | Para_MixTemp_Limit_TempMinHys | Para_MixTemp_Limit_TempMinHys | 4816 | Para_MixTemp_Limit_TempMinHys |  | 18478
[8 empty] | 18479 | Para_MMD_Aron | Para_MMD_Aron | 4817 | Para_MMD_Aron |  | 18479
[8 empty] | 18480 | Para_MMD_CurrAsymetry | Para_MMD_CurrAsymetry | 4818 | Para_MMD_CurrAsymetry | % | 18480
[8 empty] | 18481 | Para_MMD_CurrAsymetryDelay | Para_MMD_CurrAsymetryDelay | 4819 | Para_MMD_CurrAsymetryDelay |  | 18481
[8 empty] | 18482 | Para_MMD_CurrNeuMax | Para_MMD_CurrNeuMax | 4820 | Para_MMD_CurrNeuMax |  | 18482
[8 empty] | 18483 | Para_MMD_CurrNeuMaxDelay | Para_MMD_CurrNeuMaxDelay | 4821 | Para_MMD_CurrNeuMaxDelay |  | 18483
[8 empty] | 18484 | Para_MMD_CurrRange | Para_MMD_CurrRange | 4822 | Para_MMD_CurrRange |  | 18484
[8 empty] | 18485 | Para_MMD_CurrShortCircuit | Para_MMD_CurrShortCircuit | 4823 | Para_MMD_CurrShortCircuit | A | 18485
[8 empty] | 18486 | Para_MMD_CurrShortCircuitDelay | Para_MMD_CurrShortCircuitDelay | 4824 | Para_MMD_CurrShortCircuitDelay | s | 18486
[8 empty] | 18487 | Para_MMD_CurrThermOverloadProt | Para_MMD_CurrThermOverloadProt | 4825 | Para_MMD_CurrThermOverloadProt |  | 18487
[8 empty] | 18488 | Para_MMD_ImpulseValue | Para_MMD_ImpulseValue | 4826 | Para_MMD_ImpulseValue | kWh/I | 18488
[8 empty] | 18489 | Para_MMD_IntValue | Para_MMD_IntValue | 4827 | Para_MMD_IntValue | s | 18489
[8 empty] | 18490 | Para_MMD_MMD1_ActSynch | Para_MMD_MMD1_ActSynch | 4828 | Para_MMD_MMD1_ActSynch |  | 18490
[8 empty] | 18491 | Para_MMD_MMD1_Aron | Para_MMD_MMD1_Aron | 4829 | Para_MMD_MMD1_Aron |  | 18491
[8 empty] | 18492 | Para_MMD_MMD1_Bus3PhaseCircuit | Para_MMD_MMD1_Bus3PhaseCircuit | 4830 | Para_MMD_MMD1_Bus3PhaseCircuit |  | 18492
[8 empty] | 18493 | Para_MMD_MMD1_CurrAsymetryDelay | Para_MMD_MMD1_CurrAsymetryDelay | 4831 | Para_MMD_MMD1_CurrAsymetryDelay | s | 18493
[8 empty] | 18494 | Para_MMD_MMD1_CurrNeuMax | Para_MMD_MMD1_CurrNeuMax | 4832 | Para_MMD_MMD1_CurrNeuMax | % | 18494
[8 empty] | 18495 | Para_MMD_MMD1_CurrNeuMaxDelay | Para_MMD_MMD1_CurrNeuMaxDelay | 4833 | Para_MMD_MMD1_CurrNeuMaxDelay | s | 18495
[8 empty] | 18496 | Para_MMD_MMD1_CurrNeuNom | Para_MMD_MMD1_CurrNeuNom | 4834 | Para_MMD_MMD1_CurrNeuNom | A | 18496
[8 empty] | 18497 | Para_MMD_MMD1_CurrRange | Para_MMD_MMD1_CurrRange | 4835 | Para_MMD_MMD1_CurrRange |  | 18497
[8 empty] | 18498 | Para_MMD_MMD1_CurrShortCircuit | Para_MMD_MMD1_CurrShortCircuit | 4836 | Para_MMD_MMD1_CurrShortCircuit | % | 18498
[8 empty] | 18499 | Para_MMD_MMD1_CurrShortCircuitDelay | Para_MMD_MMD1_CurrShortCircuitDelay | 4837 | Para_MMD_MMD1_CurrShortCircuitDelay | s | 18499
[8 empty] | 18500 | Para_MMD_MMD1_CurrThermOverloadProt | Para_MMD_MMD1_CurrThermOverloadProt | 4838 | Para_MMD_MMD1_CurrThermOverloadProt | % | 18500
[8 empty] | 18501 | Para_MMD_MMD1_FreqDiffMax | Para_MMD_MMD1_FreqDiffMax | 4839 | Para_MMD_MMD1_FreqDiffMax | Hz | 18501
[8 empty] | 18502 | Para_MMD_MMD1_FreqDiffMin | Para_MMD_MMD1_FreqDiffMin | 4840 | Para_MMD_MMD1_FreqDiffMin | Hz | 18502
[8 empty] | 18503 | Para_MMD_MMD1_Gen3PhaseCircuit | Para_MMD_MMD1_Gen3PhaseCircuit | 4841 | Para_MMD_MMD1_Gen3PhaseCircuit |  | 18503
[8 empty] | 18504 | Para_MMD_MMD1_ImpulseValue | Para_MMD_MMD1_ImpulseValue | 4842 | Para_MMD_MMD1_ImpulseValue | kWh/I | 18504
[8 empty] | 18505 | Para_MMD_MMD1_IntValue | Para_MMD_MMD1_IntValue | 4843 | Para_MMD_MMD1_IntValue |  | 18505
[8 empty] | 18506 | Para_MMD_MMD1_MultiplierBusBar | Para_MMD_MMD1_MultiplierBusBar | 4844 | Para_MMD_MMD1_MultiplierBusBar |  | 18506
[8 empty] | 18507 | Para_MMD_MMD1_MultiplierIL1L3 | Para_MMD_MMD1_MultiplierIL1L3 | 4845 | Para_MMD_MMD1_MultiplierIL1L3 |  | 18507
[8 empty] | 18508 | Para_MMD_MMD1_MultiplierSynch1 | Para_MMD_MMD1_MultiplierSynch1 | 4846 | Para_MMD_MMD1_MultiplierSynch1 |  | 18508
[8 empty] | 18509 | Para_MMD_MMD1_MultiplierSynch2 | Para_MMD_MMD1_MultiplierSynch2 | 4847 | Para_MMD_MMD1_MultiplierSynch2 |  | 18509
[8 empty] | 18510 | Para_MMD_MMD1_MultiplierUL1L3 | Para_MMD_MMD1_MultiplierUL1L3 | 4848 | Para_MMD_MMD1_MultiplierUL1L3 |  | 18510
[8 empty] | 18511 | Para_MMD_MMD1_NomFreq | Para_MMD_MMD1_NomFreq | 4849 | Para_MMD_MMD1_NomFreq | Hz | 18511
[8 empty] | 18512 | Para_MMD_MMD1_NomFreqConv100 | Para_MMD_MMD1_NomFreqConv100 | 4850 | Para_MMD_MMD1_NomFreqConv100 | Hz | 18512
[8 empty] | 18513 | Para_MMD_MMD1_NomVolt | Para_MMD_MMD1_NomVolt | 4851 | Para_MMD_MMD1_NomVolt | V | 18513
[8 empty] | 18514 | Para_MMD_MMD1_OverFreq | Para_MMD_MMD1_OverFreq | 4852 | Para_MMD_MMD1_OverFreq | % | 18514
[8 empty] | 18515 | Para_MMD_MMD1_OverFreqDelay | Para_MMD_MMD1_OverFreqDelay | 4853 | Para_MMD_MMD1_OverFreqDelay | s | 18515
[8 empty] | 18516 | Para_MMD_MMD1_OverVolt | Para_MMD_MMD1_OverVolt | 4854 | Para_MMD_MMD1_OverVolt | % | 18516
[8 empty] | 18517 | Para_MMD_MMD1_OverVoltDelay | Para_MMD_MMD1_OverVoltDelay | 4855 | Para_MMD_MMD1_OverVoltDelay | s | 18517
[8 empty] | 18518 | Para_MMD_MMD1_PhaseDiffMax | Para_MMD_MMD1_PhaseDiffMax | 4856 | Para_MMD_MMD1_PhaseDiffMax | ° | 18518
[8 empty] | 18519 | Para_MMD_MMD1_Power0mA | Para_MMD_MMD1_Power0mA | 4857 | Para_MMD_MMD1_Power0mA | kW | 18519
[8 empty] | 18520 | Para_MMD_MMD1_Power20mA | Para_MMD_MMD1_Power20mA | 4858 | Para_MMD_MMD1_Power20mA | kW | 18520
[8 empty] | 18521 | Para_MMD_MMD1_PowerReactMin | Para_MMD_MMD1_PowerReactMin | 4859 | Para_MMD_MMD1_PowerReactMin |  | 18521
[8 empty] | 18522 | Para_MMD_MMD1_PowerReactMinDelay | Para_MMD_MMD1_PowerReactMinDelay | 4860 | Para_MMD_MMD1_PowerReactMinDelay | s | 18522
[8 empty] | 18523 | Para_MMD_MMD1_SwitchTimePowerCB | Para_MMD_MMD1_SwitchTimePowerCB | 4861 | Para_MMD_MMD1_SwitchTimePowerCB | ms | 18523
[8 empty] | 18524 | Para_MMD_MMD1_TimeRelImpMin | Para_MMD_MMD1_TimeRelImpMin | 4862 | Para_MMD_MMD1_TimeRelImpMin | ms | 18524
[8 empty] | 18525 | Para_MMD_MMD1_TransPhaseShift | Para_MMD_MMD1_TransPhaseShift | 4863 | Para_MMD_MMD1_TransPhaseShift | ° | 18525
[8 empty] | 18526 | Para_MMD_MMD1_UnderFreq | Para_MMD_MMD1_UnderFreq | 4864 | Para_MMD_MMD1_UnderFreq | % | 18526
[8 empty] | 18527 | Para_MMD_MMD1_UnderFreqDelay | Para_MMD_MMD1_UnderFreqDelay | 4865 | Para_MMD_MMD1_UnderFreqDelay | s | 18527
[8 empty] | 18528 | Para_MMD_MMD1_UnderVolt | Para_MMD_MMD1_UnderVolt | 4866 | Para_MMD_MMD1_UnderVolt | % | 18528
[8 empty] | 18529 | Para_MMD_MMD1_UnderVolt2 | Para_MMD_MMD1_UnderVolt2 | 4867 | Para_MMD_MMD1_UnderVolt2 | % | 18529
[8 empty] | 18530 | Para_MMD_MMD1_UnderVolt2Delay | Para_MMD_MMD1_UnderVolt2Delay | 4868 | Para_MMD_MMD1_UnderVolt2Delay | s | 18530
[8 empty] | 18531 | Para_MMD_MMD1_UnderVoltDelay | Para_MMD_MMD1_UnderVoltDelay | 4869 | Para_MMD_MMD1_UnderVoltDelay | s | 18531
[8 empty] | 18532 | Para_MMD_MMD1_VoltAsymetry | Para_MMD_MMD1_VoltAsymetry | 4870 | Para_MMD_MMD1_VoltAsymetry | % | 18532
[8 empty] | 18533 | Para_MMD_MMD1_VoltAsymetryDelay | Para_MMD_MMD1_VoltAsymetryDelay | 4871 | Para_MMD_MMD1_VoltAsymetryDelay | s | 18533
[8 empty] | 18534 | Para_MMD_MMD1_VoltBusBarMin | Para_MMD_MMD1_VoltBusBarMin | 4872 | Para_MMD_MMD1_VoltBusBarMin | % | 18534
[8 empty] | 18535 | Para_MMD_MMD1_VoltDeadBus | Para_MMD_MMD1_VoltDeadBus | 4873 | Para_MMD_MMD1_VoltDeadBus | % | 18535
[8 empty] | 18536 | Para_MMD_MMD1_VoltDiffMax | Para_MMD_MMD1_VoltDiffMax | 4874 | Para_MMD_MMD1_VoltDiffMax | % | 18536
[8 empty] | 18537 | Para_MMD_MMD1_VoltNomBusBar | Para_MMD_MMD1_VoltNomBusBar | 4875 | Para_MMD_MMD1_VoltNomBusBar | V | 18537
[8 empty] | 18538 | Para_MMD_MMD1_VoltNomSynch | Para_MMD_MMD1_VoltNomSynch | 4876 | Para_MMD_MMD1_VoltNomSynch | V | 18538
[8 empty] | 18539 | Para_MMD_MMD1_VoltRange | Para_MMD_MMD1_VoltRange | 4877 | Para_MMD_MMD1_VoltRange |  | 18539
[8 empty] | 18540 | Para_MMD_MMD1_VoltRangeBus | Para_MMD_MMD1_VoltRangeBus | 4878 | Para_MMD_MMD1_VoltRangeBus |  | 18540
[8 empty] | 18541 | Para_MMD_MMD1_VoltRangeSync1 | Para_MMD_MMD1_VoltRangeSync1 | 4879 | Para_MMD_MMD1_VoltRangeSync1 |  | 18541
[8 empty] | 18542 | Para_MMD_MMD1_VoltRangeSync2 | Para_MMD_MMD1_VoltRangeSync2 | 4880 | Para_MMD_MMD1_VoltRangeSync2 |  | 18542
[8 empty] | 18543 | Para_MMD_MMD2_ActSynch | Para_MMD_MMD2_ActSynch | 4881 | Para_MMD_MMD2_ActSynch |  | 18543
[8 empty] | 18544 | Para_MMD_MMD2_Aron | Para_MMD_MMD2_Aron | 4882 | Para_MMD_MMD2_Aron |  | 18544
[8 empty] | 18545 | Para_MMD_MMD2_Bus3PhaseCircuit | Para_MMD_MMD2_Bus3PhaseCircuit | 4883 | Para_MMD_MMD2_Bus3PhaseCircuit |  | 18545
[8 empty] | 18546 | Para_MMD_MMD2_CurrAsymetryDelay | Para_MMD_MMD2_CurrAsymetryDelay | 4884 | Para_MMD_MMD2_CurrAsymetryDelay | s | 18546
[8 empty] | 18547 | Para_MMD_MMD2_CurrNeuMax | Para_MMD_MMD2_CurrNeuMax | 4885 | Para_MMD_MMD2_CurrNeuMax | % | 18547
[8 empty] | 18548 | Para_MMD_MMD2_CurrNeuMaxDelay | Para_MMD_MMD2_CurrNeuMaxDelay | 4886 | Para_MMD_MMD2_CurrNeuMaxDelay | s | 18548
[8 empty] | 18549 | Para_MMD_MMD2_CurrNeuNom | Para_MMD_MMD2_CurrNeuNom | 4887 | Para_MMD_MMD2_CurrNeuNom | A | 18549
[8 empty] | 18550 | Para_MMD_MMD2_CurrRange | Para_MMD_MMD2_CurrRange | 4888 | Para_MMD_MMD2_CurrRange |  | 18550
[8 empty] | 18551 | Para_MMD_MMD2_CurrShortCircuit | Para_MMD_MMD2_CurrShortCircuit | 4889 | Para_MMD_MMD2_CurrShortCircuit | % | 18551
[8 empty] | 18552 | Para_MMD_MMD2_CurrShortCircuitDelay | Para_MMD_MMD2_CurrShortCircuitDelay | 4890 | Para_MMD_MMD2_CurrShortCircuitDelay | s | 18552
[8 empty] | 18553 | Para_MMD_MMD2_CurrThermOverloadProt | Para_MMD_MMD2_CurrThermOverloadProt | 4891 | Para_MMD_MMD2_CurrThermOverloadProt | % | 18553
[8 empty] | 18554 | Para_MMD_MMD2_FreqDiffMax | Para_MMD_MMD2_FreqDiffMax | 4892 | Para_MMD_MMD2_FreqDiffMax | Hz | 18554
[8 empty] | 18555 | Para_MMD_MMD2_FreqDiffMin | Para_MMD_MMD2_FreqDiffMin | 4893 | Para_MMD_MMD2_FreqDiffMin | Hz | 18555
[8 empty] | 18556 | Para_MMD_MMD2_Gen3PhaseCircuit | Para_MMD_MMD2_Gen3PhaseCircuit | 4894 | Para_MMD_MMD2_Gen3PhaseCircuit |  | 18556
[8 empty] | 18557 | Para_MMD_MMD2_ImpulseValue | Para_MMD_MMD2_ImpulseValue | 4895 | Para_MMD_MMD2_ImpulseValue | kWh/I | 18557
[8 empty] | 18558 | Para_MMD_MMD2_IntValue | Para_MMD_MMD2_IntValue | 4896 | Para_MMD_MMD2_IntValue |  | 18558
[8 empty] | 18559 | Para_MMD_MMD2_MultiplierBusBar | Para_MMD_MMD2_MultiplierBusBar | 4897 | Para_MMD_MMD2_MultiplierBusBar |  | 18559
[8 empty] | 18560 | Para_MMD_MMD2_MultiplierIL1L3 | Para_MMD_MMD2_MultiplierIL1L3 | 4898 | Para_MMD_MMD2_MultiplierIL1L3 |  | 18560
[8 empty] | 18561 | Para_MMD_MMD2_MultiplierSynch1 | Para_MMD_MMD2_MultiplierSynch1 | 4899 | Para_MMD_MMD2_MultiplierSynch1 |  | 18561
[8 empty] | 18562 | Para_MMD_MMD2_MultiplierSynch2 | Para_MMD_MMD2_MultiplierSynch2 | 4900 | Para_MMD_MMD2_MultiplierSynch2 |  | 18562
[8 empty] | 18563 | Para_MMD_MMD2_MultiplierUL1L3 | Para_MMD_MMD2_MultiplierUL1L3 | 4901 | Para_MMD_MMD2_MultiplierUL1L3 |  | 18563
[8 empty] | 18564 | Para_MMD_MMD2_NomFreq | Para_MMD_MMD2_NomFreq | 4902 | Para_MMD_MMD2_NomFreq | Hz | 18564
[8 empty] | 18565 | Para_MMD_MMD2_NomFreqConv100 | Para_MMD_MMD2_NomFreqConv100 | 4903 | Para_MMD_MMD2_NomFreqConv100 | Hz | 18565
[8 empty] | 18566 | Para_MMD_MMD2_NomVolt | Para_MMD_MMD2_NomVolt | 4904 | Para_MMD_MMD2_NomVolt | V | 18566
[8 empty] | 18567 | Para_MMD_MMD2_OverFreq | Para_MMD_MMD2_OverFreq | 4905 | Para_MMD_MMD2_OverFreq | % | 18567
[8 empty] | 18568 | Para_MMD_MMD2_OverFreqDelay | Para_MMD_MMD2_OverFreqDelay | 4906 | Para_MMD_MMD2_OverFreqDelay | s | 18568
[8 empty] | 18569 | Para_MMD_MMD2_OverVolt | Para_MMD_MMD2_OverVolt | 4907 | Para_MMD_MMD2_OverVolt | % | 18569
[8 empty] | 18570 | Para_MMD_MMD2_OverVoltDelay | Para_MMD_MMD2_OverVoltDelay | 4908 | Para_MMD_MMD2_OverVoltDelay | s | 18570
[8 empty] | 18571 | Para_MMD_MMD2_PhaseDiffMax | Para_MMD_MMD2_PhaseDiffMax | 4909 | Para_MMD_MMD2_PhaseDiffMax | ° | 18571
[8 empty] | 18572 | Para_MMD_MMD2_Power0mA | Para_MMD_MMD2_Power0mA | 4910 | Para_MMD_MMD2_Power0mA | kW | 18572
[8 empty] | 18573 | Para_MMD_MMD2_Power20mA | Para_MMD_MMD2_Power20mA | 4911 | Para_MMD_MMD2_Power20mA | kW | 18573
[8 empty] | 18574 | Para_MMD_MMD2_PowerReactMin | Para_MMD_MMD2_PowerReactMin | 4912 | Para_MMD_MMD2_PowerReactMin | kvar | 18574
[8 empty] | 18575 | Para_MMD_MMD2_PowerReactMinDelay | Para_MMD_MMD2_PowerReactMinDelay | 4913 | Para_MMD_MMD2_PowerReactMinDelay | s | 18575
[8 empty] | 18576 | Para_MMD_MMD2_SwitchTimePowerCB | Para_MMD_MMD2_SwitchTimePowerCB | 4914 | Para_MMD_MMD2_SwitchTimePowerCB | ms | 18576
[8 empty] | 18577 | Para_MMD_MMD2_TimeRelImpMin | Para_MMD_MMD2_TimeRelImpMin | 4915 | Para_MMD_MMD2_TimeRelImpMin | ms | 18577
[8 empty] | 18578 | Para_MMD_MMD2_TransPhaseShift | Para_MMD_MMD2_TransPhaseShift | 4916 | Para_MMD_MMD2_TransPhaseShift | ° | 18578
[8 empty] | 18579 | Para_MMD_MMD2_UnderFreq | Para_MMD_MMD2_UnderFreq | 4917 | Para_MMD_MMD2_UnderFreq | % | 18579
[8 empty] | 18580 | Para_MMD_MMD2_UnderFreqDelay | Para_MMD_MMD2_UnderFreqDelay | 4918 | Para_MMD_MMD2_UnderFreqDelay | s | 18580
[8 empty] | 18581 | Para_MMD_MMD2_UnderVolt | Para_MMD_MMD2_UnderVolt | 4919 | Para_MMD_MMD2_UnderVolt | % | 18581
[8 empty] | 18582 | Para_MMD_MMD2_UnderVolt2 | Para_MMD_MMD2_UnderVolt2 | 4920 | Para_MMD_MMD2_UnderVolt2 | % | 18582
[8 empty] | 18583 | Para_MMD_MMD2_UnderVolt2Delay | Para_MMD_MMD2_UnderVolt2Delay | 4921 | Para_MMD_MMD2_UnderVolt2Delay | s | 18583
[8 empty] | 18584 | Para_MMD_MMD2_UnderVoltDelay | Para_MMD_MMD2_UnderVoltDelay | 4922 | Para_MMD_MMD2_UnderVoltDelay | s | 18584
[8 empty] | 18585 | Para_MMD_MMD2_VoltAsymetry | Para_MMD_MMD2_VoltAsymetry | 4923 | Para_MMD_MMD2_VoltAsymetry | % | 18585
[8 empty] | 18586 | Para_MMD_MMD2_VoltAsymetryDelay | Para_MMD_MMD2_VoltAsymetryDelay | 4924 | Para_MMD_MMD2_VoltAsymetryDelay | s | 18586
[8 empty] | 18587 | Para_MMD_MMD2_VoltBusBarMin | Para_MMD_MMD2_VoltBusBarMin | 4925 | Para_MMD_MMD2_VoltBusBarMin | % | 18587
[8 empty] | 18588 | Para_MMD_MMD2_VoltDeadBus | Para_MMD_MMD2_VoltDeadBus | 4926 | Para_MMD_MMD2_VoltDeadBus | % | 18588
[8 empty] | 18589 | Para_MMD_MMD2_VoltDiffMax | Para_MMD_MMD2_VoltDiffMax | 4927 | Para_MMD_MMD2_VoltDiffMax | % | 18589
[8 empty] | 18590 | Para_MMD_MMD2_VoltNomBusBar | Para_MMD_MMD2_VoltNomBusBar | 4928 | Para_MMD_MMD2_VoltNomBusBar | V | 18590
[8 empty] | 18591 | Para_MMD_MMD2_VoltNomSynch | Para_MMD_MMD2_VoltNomSynch | 4929 | Para_MMD_MMD2_VoltNomSynch | V | 18591
[8 empty] | 18592 | Para_MMD_MMD2_VoltRange | Para_MMD_MMD2_VoltRange | 4930 | Para_MMD_MMD2_VoltRange |  | 18592
[8 empty] | 18593 | Para_MMD_MMD2_VoltRangeBus | Para_MMD_MMD2_VoltRangeBus | 4931 | Para_MMD_MMD2_VoltRangeBus |  | 18593
[8 empty] | 18594 | Para_MMD_MMD2_VoltRangeSync1 | Para_MMD_MMD2_VoltRangeSync1 | 4932 | Para_MMD_MMD2_VoltRangeSync1 |  | 18594
[8 empty] | 18595 | Para_MMD_MMD2_VoltRangeSync2 | Para_MMD_MMD2_VoltRangeSync2 | 4933 | Para_MMD_MMD2_VoltRangeSync2 |  | 18595
[8 empty] | 18596 | Para_MMD_MultiplierIL1L3 | Para_MMD_MultiplierIL1L3 | 4934 | Para_MMD_MultiplierIL1L3 |  | 18596
[8 empty] | 18597 | Para_MMD_MultiplierUL1L3 | Para_MMD_MultiplierUL1L3 | 4935 | Para_MMD_MultiplierUL1L3 |  | 18597
[8 empty] | 18598 | Para_MMD_OverFreq | Para_MMD_OverFreq | 4936 | Para_MMD_OverFreq | Hz | 18598
[8 empty] | 18599 | Para_MMD_OverFreqDelay | Para_MMD_OverFreqDelay | 4937 | Para_MMD_OverFreqDelay | s | 18599
[8 empty] | 18600 | Para_MMD_OverVolt | Para_MMD_OverVolt | 4938 | Para_MMD_OverVolt | V | 18600
[8 empty] | 18601 | Para_MMD_OverVoltDelay | Para_MMD_OverVoltDelay | 4939 | Para_MMD_OverVoltDelay | s | 18601
[8 empty] | 18602 | Para_MMD_Power0mA | Para_MMD_Power0mA | 4940 | Para_MMD_Power0mA |  | 18602
[8 empty] | 18603 | Para_MMD_Power20mA | Para_MMD_Power20mA | 4941 | Para_MMD_Power20mA |  | 18603
[8 empty] | 18604 | Para_MMD_PowerReactMin | Para_MMD_PowerReactMin | 4942 | Para_MMD_PowerReactMin |  | 18604
[8 empty] | 18605 | Para_MMD_PowerReactMinDelay | Para_MMD_PowerReactMinDelay | 4943 | Para_MMD_PowerReactMinDelay | s | 18605
[8 empty] | 18606 | Para_MMD_Relay1 | Para_MMD_Relay1 | 4944 | Para_MMD_Relay1 |  | 18606
[8 empty] | 18607 | Para_MMD_Relay2 | Para_MMD_Relay2 | 4945 | Para_MMD_Relay2 |  | 18607
[8 empty] | 18608 | Para_MMD_Relay3 | Para_MMD_Relay3 | 4946 | Para_MMD_Relay3 |  | 18608
[8 empty] | 18609 | Para_MMD_Relay4 | Para_MMD_Relay4 | 4947 | Para_MMD_Relay4 |  | 18609
[8 empty] | 18610 | Para_MMD_Relay5 | Para_MMD_Relay5 | 4948 | Para_MMD_Relay5 |  | 18610
[8 empty] | 18611 | Para_MMD_Relay6 | Para_MMD_Relay6 | 4949 | Para_MMD_Relay6 |  | 18611
[8 empty] | 18612 | Para_MMD_Relay7 | Para_MMD_Relay7 | 4950 | Para_MMD_Relay7 |  | 18612
[8 empty] | 18613 | Para_MMD_Relay8 | Para_MMD_Relay8 | 4951 | Para_MMD_Relay8 |  | 18613
[8 empty] | 18614 | Para_MMD_UnderFreq | Para_MMD_UnderFreq | 4952 | Para_MMD_UnderFreq | Hz | 18614
[8 empty] | 18615 | Para_MMD_UnderFreqDelay | Para_MMD_UnderFreqDelay | 4953 | Para_MMD_UnderFreqDelay | s | 18615
[8 empty] | 18616 | Para_MMD_UnderVolt | Para_MMD_UnderVolt | 4954 | Para_MMD_UnderVolt | V | 18616
[8 empty] | 18617 | Para_MMD_UnderVoltDelay | Para_MMD_UnderVoltDelay | 4955 | Para_MMD_UnderVoltDelay | s | 18617
[8 empty] | 18618 | Para_MMD_VoltAsymetry | Para_MMD_VoltAsymetry | 4956 | Para_MMD_VoltAsymetry | % | 18618
[8 empty] | 18619 | Para_MMD_VoltAsymetryDelay | Para_MMD_VoltAsymetryDelay | 4957 | Para_MMD_VoltAsymetryDelay | s | 18619
[8 empty] | 18620 | Para_MMD_VoltRange | Para_MMD_VoltRange | 4958 | Para_MMD_VoltRange |  | 18620
[8 empty] | 10000340 | Para_ModulControler_Ctr10_DComp | Para_ModulControler_Ctr10_DComp | 4959 | Para_ModulControler_Ctr10_DComp |  | 10000340
[8 empty] | 10000341 | Para_ModulControler_Ctr10_deadband | Para_ModulControler_Ctr10_deadband | 4960 | Para_ModulControler_Ctr10_deadband |  | 10000341
[8 empty] | 10000350 | Para_ModulControler_Ctr10_dW_down | Para_ModulControler_Ctr10_dW_down | 4961 | Para_ModulControler_Ctr10_dW_down |  | 10000350
[8 empty] | 10000351 | Para_ModulControler_Ctr10_dW_up | Para_ModulControler_Ctr10_dW_up | 4962 | Para_ModulControler_Ctr10_dW_up |  | 10000351
[8 empty] | 10000358 | Para_ModulControler_Ctr10_dY_max | Para_ModulControler_Ctr10_dY_max | 4963 | Para_ModulControler_Ctr10_dY_max |  | 10000358
[8 empty] | 10000344 | Para_ModulControler_Ctr10_IComp | Para_ModulControler_Ctr10_IComp | 4964 | Para_ModulControler_Ctr10_IComp |  | 10000344
[8 empty] | 10000129 | Para_ModulControler_Ctr10_Kp_manualAdjust | Para_ModulControler_Ctr10_Kp_manualAdjust | 4965 | Para_ModulControler_Ctr10_Kp_manualAdjust |  | 10000129
[8 empty] | 10000343 | Para_ModulControler_Ctr10_nvert | Para_ModulControler_Ctr10_nvert | 4966 | Para_ModulControler_Ctr10_nvert |  | 10000343
[8 empty] | 10000342 | Para_ModulControler_Ctr10_PComp | Para_ModulControler_Ctr10_PComp | 4967 | Para_ModulControler_Ctr10_PComp |  | 10000342
[8 empty] | 10008339 | Para_ModulControler_Ctr10_Pos_HW_ReValve | Para_ModulControler_Ctr10_Pos_HW_ReValve | 4968 | Para_ModulControler_Ctr10_Pos_HW_ReValve |  | 10008339
[8 empty] | 10008342 | Para_ModulControler_Ctr10_Pos_HW_ReValve_ScalMax | Para_ModulControler_Ctr10_Pos_HW_ReValve_ScalMax | 4969 | Para_ModulControler_Ctr10_Pos_HW_ReValve_ScalMax |  | 10008342
[8 empty] | 10008341 | Para_ModulControler_Ctr10_Pos_HW_ReValve_ScalMin | Para_ModulControler_Ctr10_Pos_HW_ReValve_ScalMin | 4970 | Para_ModulControler_Ctr10_Pos_HW_ReValve_ScalMin |  | 10008341
[8 empty] | 10000732 | Para_ModulControler_Ctr10_t_min_pulse_down | Para_ModulControler_Ctr10_t_min_pulse_down | 4971 | Para_ModulControler_Ctr10_t_min_pulse_down |  | 10000732
[8 empty] | 10000730 | Para_ModulControler_Ctr10_t_min_pulse_up | Para_ModulControler_Ctr10_t_min_pulse_up | 4972 | Para_ModulControler_Ctr10_t_min_pulse_up |  | 10000730
[8 empty] | 10000993 | Para_ModulControler_Ctr10_t_period_down | Para_ModulControler_Ctr10_t_period_down | 4973 | Para_ModulControler_Ctr10_t_period_down |  | 10000993
[8 empty] | 10000725 | Para_ModulControler_Ctr10_t_period_up | Para_ModulControler_Ctr10_t_period_up | 4974 | Para_ModulControler_Ctr10_t_period_up |  | 10000725
[8 empty] | 10000126 | Para_ModulControler_Ctr10_Tn_manualAdjust | Para_ModulControler_Ctr10_Tn_manualAdjust | 4975 | Para_ModulControler_Ctr10_Tn_manualAdjust |  | 10000126
[8 empty] | 10000589 | Para_ModulControler_Ctr10_Tv_manualAdjust | Para_ModulControler_Ctr10_Tv_manualAdjust | 4976 | Para_ModulControler_Ctr10_Tv_manualAdjust |  | 10000589
[8 empty] | 10000349 | Para_ModulControler_Ctr10_WMax | Para_ModulControler_Ctr10_WMax | 4977 | Para_ModulControler_Ctr10_WMax |  | 10000349
[8 empty] | 10000352 | Para_ModulControler_Ctr10_WMin | Para_ModulControler_Ctr10_WMin | 4978 | Para_ModulControler_Ctr10_WMin |  | 10000352
[8 empty] | 10000353 | Para_ModulControler_Ctr10_WStart | Para_ModulControler_Ctr10_WStart | 4979 | Para_ModulControler_Ctr10_WStart |  | 10000353
[8 empty] | 10000355 | Para_ModulControler_Ctr10_Y_block | Para_ModulControler_Ctr10_Y_block | 4980 | Para_ModulControler_Ctr10_Y_block |  | 10000355
[8 empty] | 10000357 | Para_ModulControler_Ctr10_YMax | Para_ModulControler_Ctr10_YMax | 4981 | Para_ModulControler_Ctr10_YMax |  | 10000357
[8 empty] | 10000354 | Para_ModulControler_Ctr10_YMin | Para_ModulControler_Ctr10_YMin | 4982 | Para_ModulControler_Ctr10_YMin |  | 10000354
[8 empty] | 10000362 | Para_ModulControler_Ctr11_DComp | Para_ModulControler_Ctr11_DComp | 4983 | Para_ModulControler_Ctr11_DComp |  | 10000362
[8 empty] | 10000364 | Para_ModulControler_Ctr11_deadband | Para_ModulControler_Ctr11_deadband | 4984 | Para_ModulControler_Ctr11_deadband |  | 10000364
[8 empty] | 10000373 | Para_ModulControler_Ctr11_dW_down | Para_ModulControler_Ctr11_dW_down | 4985 | Para_ModulControler_Ctr11_dW_down |  | 10000373
[8 empty] | 10000375 | Para_ModulControler_Ctr11_dW_up | Para_ModulControler_Ctr11_dW_up | 4986 | Para_ModulControler_Ctr11_dW_up |  | 10000375
[8 empty] | 10000382 | Para_ModulControler_Ctr11_dY_max | Para_ModulControler_Ctr11_dY_max | 4987 | Para_ModulControler_Ctr11_dY_max |  | 10000382
[8 empty] | 10000368 | Para_ModulControler_Ctr11_IComp | Para_ModulControler_Ctr11_IComp | 4988 | Para_ModulControler_Ctr11_IComp |  | 10000368
[8 empty] | 10000991 | Para_ModulControler_Ctr11_Kp_manualAdjust | Para_ModulControler_Ctr11_Kp_manualAdjust | 4989 | Para_ModulControler_Ctr11_Kp_manualAdjust |  | 10000991
[8 empty] | 10000366 | Para_ModulControler_Ctr11_nvert | Para_ModulControler_Ctr11_nvert | 4990 | Para_ModulControler_Ctr11_nvert |  | 10000366
[8 empty] | 10000365 | Para_ModulControler_Ctr11_PComp | Para_ModulControler_Ctr11_PComp | 4991 | Para_ModulControler_Ctr11_PComp |  | 10000365
[8 empty] | 10008343 | Para_ModulControler_Ctr11_Pos_HW_EC_ReValve | Para_ModulControler_Ctr11_Pos_HW_EC_ReValve | 4992 | Para_ModulControler_Ctr11_Pos_HW_EC_ReValve |  | 10008343
[8 empty] | 10008344 | Para_ModulControler_Ctr11_Pos_HW_EC_ReValve_ScalMax | Para_ModulControler_Ctr11_Pos_HW_EC_ReValve_ScalMax | 4993 | Para_ModulControler_Ctr11_Pos_HW_EC_ReValve_ScalMax |  | 10008344
[8 empty] | 10008347 | Para_ModulControler_Ctr11_Pos_HW_EC_ReValve_ScalMin | Para_ModulControler_Ctr11_Pos_HW_EC_ReValve_ScalMin | 4994 | Para_ModulControler_Ctr11_Pos_HW_EC_ReValve_ScalMin |  | 10008347
[8 empty] | 10001002 | Para_ModulControler_Ctr11_t_min_pulse_down | Para_ModulControler_Ctr11_t_min_pulse_down | 4995 | Para_ModulControler_Ctr11_t_min_pulse_down |  | 10001002
[8 empty] | 10001006 | Para_ModulControler_Ctr11_t_min_pulse_up | Para_ModulControler_Ctr11_t_min_pulse_up | 4996 | Para_ModulControler_Ctr11_t_min_pulse_up |  | 10001006
[8 empty] | 10001001 | Para_ModulControler_Ctr11_t_period_down | Para_ModulControler_Ctr11_t_period_down | 4997 | Para_ModulControler_Ctr11_t_period_down |  | 10001001
[8 empty] | 10001004 | Para_ModulControler_Ctr11_t_period_up | Para_ModulControler_Ctr11_t_period_up | 4998 | Para_ModulControler_Ctr11_t_period_up |  | 10001004
[8 empty] | 10001007 | Para_ModulControler_Ctr11_Tn_manualAdjust | Para_ModulControler_Ctr11_Tn_manualAdjust | 4999 | Para_ModulControler_Ctr11_Tn_manualAdjust |  | 10001007
[8 empty] | 10001005 | Para_ModulControler_Ctr11_Tv_manualAdjust | Para_ModulControler_Ctr11_Tv_manualAdjust | 5000 | Para_ModulControler_Ctr11_Tv_manualAdjust |  | 10001005
[8 empty] | 10000369 | Para_ModulControler_Ctr11_WMax | Para_ModulControler_Ctr11_WMax | 5001 | Para_ModulControler_Ctr11_WMax |  | 10000369
[8 empty] | 10000376 | Para_ModulControler_Ctr11_WMin | Para_ModulControler_Ctr11_WMin | 5002 | Para_ModulControler_Ctr11_WMin |  | 10000376
[8 empty] | 10000378 | Para_ModulControler_Ctr11_WStart | Para_ModulControler_Ctr11_WStart | 5003 | Para_ModulControler_Ctr11_WStart |  | 10000378
[8 empty] | 10000377 | Para_ModulControler_Ctr11_Y_block | Para_ModulControler_Ctr11_Y_block | 5004 | Para_ModulControler_Ctr11_Y_block |  | 10000377
[8 empty] | 10000380 | Para_ModulControler_Ctr11_YMax | Para_ModulControler_Ctr11_YMax | 5005 | Para_ModulControler_Ctr11_YMax |  | 10000380
[8 empty] | 10000381 | Para_ModulControler_Ctr11_YMin | Para_ModulControler_Ctr11_YMin | 5006 | Para_ModulControler_Ctr11_YMin |  | 10000381
[8 empty] | 10000387 | Para_ModulControler_Ctr12_DComp | Para_ModulControler_Ctr12_DComp | 5007 | Para_ModulControler_Ctr12_DComp |  | 10000387
[8 empty] | 10000384 | Para_ModulControler_Ctr12_deadband | Para_ModulControler_Ctr12_deadband | 5008 | Para_ModulControler_Ctr12_deadband |  | 10000384
[8 empty] | 10000399 | Para_ModulControler_Ctr12_dW_down | Para_ModulControler_Ctr12_dW_down | 5009 | Para_ModulControler_Ctr12_dW_down |  | 10000399
[8 empty] | 10000402 | Para_ModulControler_Ctr12_dW_up | Para_ModulControler_Ctr12_dW_up | 5010 | Para_ModulControler_Ctr12_dW_up |  | 10000402
[8 empty] | 10000403 | Para_ModulControler_Ctr12_dY_max | Para_ModulControler_Ctr12_dY_max | 5011 | Para_ModulControler_Ctr12_dY_max |  | 10000403
[8 empty] | 10000385 | Para_ModulControler_Ctr12_IComp | Para_ModulControler_Ctr12_IComp | 5012 | Para_ModulControler_Ctr12_IComp |  | 10000385
[8 empty] | 10001075 | Para_ModulControler_Ctr12_Kp_manualAdjust | Para_ModulControler_Ctr12_Kp_manualAdjust | 5013 | Para_ModulControler_Ctr12_Kp_manualAdjust |  | 10001075
[8 empty] | 10000388 | Para_ModulControler_Ctr12_nvert | Para_ModulControler_Ctr12_nvert | 5014 | Para_ModulControler_Ctr12_nvert |  | 10000388
[8 empty] | 10000389 | Para_ModulControler_Ctr12_PComp | Para_ModulControler_Ctr12_PComp | 5015 | Para_ModulControler_Ctr12_PComp |  | 10000389
[8 empty] | 10000733 | Para_ModulControler_Ctr12_t_min_pulse_down | Para_ModulControler_Ctr12_t_min_pulse_down | 5016 | Para_ModulControler_Ctr12_t_min_pulse_down |  | 10000733
[8 empty] | 10000731 | Para_ModulControler_Ctr12_t_min_pulse_up | Para_ModulControler_Ctr12_t_min_pulse_up | 5017 | Para_ModulControler_Ctr12_t_min_pulse_up |  | 10000731
[8 empty] | 10000735 | Para_ModulControler_Ctr12_t_period_down | Para_ModulControler_Ctr12_t_period_down | 5018 | Para_ModulControler_Ctr12_t_period_down |  | 10000735
[8 empty] | 10000737 | Para_ModulControler_Ctr12_t_period_up | Para_ModulControler_Ctr12_t_period_up | 5019 | Para_ModulControler_Ctr12_t_period_up |  | 10000737
[8 empty] | 10000734 | Para_ModulControler_Ctr12_Tn_manualAdjust | Para_ModulControler_Ctr12_Tn_manualAdjust | 5020 | Para_ModulControler_Ctr12_Tn_manualAdjust |  | 10000734
[8 empty] | 10000736 | Para_ModulControler_Ctr12_Tv_manualAdjust | Para_ModulControler_Ctr12_Tv_manualAdjust | 5021 | Para_ModulControler_Ctr12_Tv_manualAdjust |  | 10000736
[8 empty] | 10000397 | Para_ModulControler_Ctr12_WMax | Para_ModulControler_Ctr12_WMax | 5022 | Para_ModulControler_Ctr12_WMax |  | 10000397
[8 empty] | 10000400 | Para_ModulControler_Ctr12_WMin | Para_ModulControler_Ctr12_WMin | 5023 | Para_ModulControler_Ctr12_WMin |  | 10000400
[8 empty] | 10000398 | Para_ModulControler_Ctr12_WStart | Para_ModulControler_Ctr12_WStart | 5024 | Para_ModulControler_Ctr12_WStart |  | 10000398
[8 empty] | 10000401 | Para_ModulControler_Ctr12_Y_block | Para_ModulControler_Ctr12_Y_block | 5025 | Para_ModulControler_Ctr12_Y_block |  | 10000401
[8 empty] | 10000406 | Para_ModulControler_Ctr12_YMax | Para_ModulControler_Ctr12_YMax | 5026 | Para_ModulControler_Ctr12_YMax |  | 10000406
[8 empty] | 10000404 | Para_ModulControler_Ctr12_YMin | Para_ModulControler_Ctr12_YMin | 5027 | Para_ModulControler_Ctr12_YMin |  | 10000404
[8 empty] | 10000405 | Para_ModulControler_Ctr13_DComp | Para_ModulControler_Ctr13_DComp | 5028 | Para_ModulControler_Ctr13_DComp |  | 10000405
[8 empty] | 10000407 | Para_ModulControler_Ctr13_deadband | Para_ModulControler_Ctr13_deadband | 5029 | Para_ModulControler_Ctr13_deadband |  | 10000407
[8 empty] | 10000416 | Para_ModulControler_Ctr13_dW_down | Para_ModulControler_Ctr13_dW_down | 5030 | Para_ModulControler_Ctr13_dW_down |  | 10000416
[8 empty] | 10000414 | Para_ModulControler_Ctr13_dW_up | Para_ModulControler_Ctr13_dW_up | 5031 | Para_ModulControler_Ctr13_dW_up |  | 10000414
[8 empty] | 10000423 | Para_ModulControler_Ctr13_dY_max | Para_ModulControler_Ctr13_dY_max | 5032 | Para_ModulControler_Ctr13_dY_max |  | 10000423
[8 empty] | 10000408 | Para_ModulControler_Ctr13_IComp | Para_ModulControler_Ctr13_IComp | 5033 | Para_ModulControler_Ctr13_IComp |  | 10000408
[8 empty] | 10000738 | Para_ModulControler_Ctr13_Kp_manualAdjust | Para_ModulControler_Ctr13_Kp_manualAdjust | 5034 | Para_ModulControler_Ctr13_Kp_manualAdjust |  | 10000738
[8 empty] | 10000411 | Para_ModulControler_Ctr13_nvert | Para_ModulControler_Ctr13_nvert | 5035 | Para_ModulControler_Ctr13_nvert |  | 10000411
[8 empty] | 10000409 | Para_ModulControler_Ctr13_PComp | Para_ModulControler_Ctr13_PComp | 5036 | Para_ModulControler_Ctr13_PComp |  | 10000409
[8 empty] | 10000742 | Para_ModulControler_Ctr13_t_min_pulse_down | Para_ModulControler_Ctr13_t_min_pulse_down | 5037 | Para_ModulControler_Ctr13_t_min_pulse_down |  | 10000742
[8 empty] | 10000743 | Para_ModulControler_Ctr13_t_min_pulse_up | Para_ModulControler_Ctr13_t_min_pulse_up | 5038 | Para_ModulControler_Ctr13_t_min_pulse_up |  | 10000743
[8 empty] | 10000740 | Para_ModulControler_Ctr13_t_period_down | Para_ModulControler_Ctr13_t_period_down | 5039 | Para_ModulControler_Ctr13_t_period_down |  | 10000740
[8 empty] | 10000741 | Para_ModulControler_Ctr13_t_period_up | Para_ModulControler_Ctr13_t_period_up | 5040 | Para_ModulControler_Ctr13_t_period_up |  | 10000741
[8 empty] | 10000739 | Para_ModulControler_Ctr13_Tn_manualAdjust | Para_ModulControler_Ctr13_Tn_manualAdjust | 5041 | Para_ModulControler_Ctr13_Tn_manualAdjust |  | 10000739
[8 empty] | 10000745 | Para_ModulControler_Ctr13_Tv_manualAdjust | Para_ModulControler_Ctr13_Tv_manualAdjust | 5042 | Para_ModulControler_Ctr13_Tv_manualAdjust |  | 10000745
[8 empty] | 10000415 | Para_ModulControler_Ctr13_WMax | Para_ModulControler_Ctr13_WMax | 5043 | Para_ModulControler_Ctr13_WMax |  | 10000415
[8 empty] | 10000418 | Para_ModulControler_Ctr13_WMin | Para_ModulControler_Ctr13_WMin | 5044 | Para_ModulControler_Ctr13_WMin |  | 10000418
[8 empty] | 10000417 | Para_ModulControler_Ctr13_WStart | Para_ModulControler_Ctr13_WStart | 5045 | Para_ModulControler_Ctr13_WStart |  | 10000417
[8 empty] | 10000419 | Para_ModulControler_Ctr13_Y_block | Para_ModulControler_Ctr13_Y_block | 5046 | Para_ModulControler_Ctr13_Y_block |  | 10000419
[8 empty] | 10000422 | Para_ModulControler_Ctr13_YMax | Para_ModulControler_Ctr13_YMax | 5047 | Para_ModulControler_Ctr13_YMax |  | 10000422
[8 empty] | 10000424 | Para_ModulControler_Ctr13_YMin | Para_ModulControler_Ctr13_YMin | 5048 | Para_ModulControler_Ctr13_YMin |  | 10000424
[8 empty] | 10000425 | Para_ModulControler_Ctr14_DComp | Para_ModulControler_Ctr14_DComp | 5049 | Para_ModulControler_Ctr14_DComp |  | 10000425
[8 empty] | 10000426 | Para_ModulControler_Ctr14_deadband | Para_ModulControler_Ctr14_deadband | 5050 | Para_ModulControler_Ctr14_deadband |  | 10000426
[8 empty] | 10000432 | Para_ModulControler_Ctr14_dW_down | Para_ModulControler_Ctr14_dW_down | 5051 | Para_ModulControler_Ctr14_dW_down |  | 10000432
[8 empty] | 10000434 | Para_ModulControler_Ctr14_dW_up | Para_ModulControler_Ctr14_dW_up | 5052 | Para_ModulControler_Ctr14_dW_up |  | 10000434
[8 empty] | 10000440 | Para_ModulControler_Ctr14_dY_max | Para_ModulControler_Ctr14_dY_max | 5053 | Para_ModulControler_Ctr14_dY_max |  | 10000440
[8 empty] | 10000429 | Para_ModulControler_Ctr14_IComp | Para_ModulControler_Ctr14_IComp | 5054 | Para_ModulControler_Ctr14_IComp |  | 10000429
[8 empty] | 10000744 | Para_ModulControler_Ctr14_Kp_manualAdjust | Para_ModulControler_Ctr14_Kp_manualAdjust | 5055 | Para_ModulControler_Ctr14_Kp_manualAdjust |  | 10000744
[8 empty] | 10000428 | Para_ModulControler_Ctr14_nvert | Para_ModulControler_Ctr14_nvert | 5056 | Para_ModulControler_Ctr14_nvert |  | 10000428
[8 empty] | 10000427 | Para_ModulControler_Ctr14_PComp | Para_ModulControler_Ctr14_PComp | 5057 | Para_ModulControler_Ctr14_PComp |  | 10000427
[8 empty] | 10000746 | Para_ModulControler_Ctr14_t_min_pulse_down | Para_ModulControler_Ctr14_t_min_pulse_down | 5058 | Para_ModulControler_Ctr14_t_min_pulse_down |  | 10000746
[8 empty] | 10000747 | Para_ModulControler_Ctr14_t_min_pulse_up | Para_ModulControler_Ctr14_t_min_pulse_up | 5059 | Para_ModulControler_Ctr14_t_min_pulse_up |  | 10000747
[8 empty] | 10000749 | Para_ModulControler_Ctr14_t_period_down | Para_ModulControler_Ctr14_t_period_down | 5060 | Para_ModulControler_Ctr14_t_period_down |  | 10000749
[8 empty] | 10000753 | Para_ModulControler_Ctr14_t_period_up | Para_ModulControler_Ctr14_t_period_up | 5061 | Para_ModulControler_Ctr14_t_period_up |  | 10000753
[8 empty] | 10000748 | Para_ModulControler_Ctr14_Tn_manualAdjust | Para_ModulControler_Ctr14_Tn_manualAdjust | 5062 | Para_ModulControler_Ctr14_Tn_manualAdjust |  | 10000748
[8 empty] | 10000751 | Para_ModulControler_Ctr14_Tv_manualAdjust | Para_ModulControler_Ctr14_Tv_manualAdjust | 5063 | Para_ModulControler_Ctr14_Tv_manualAdjust |  | 10000751
[8 empty] | 10000430 | Para_ModulControler_Ctr14_WMax | Para_ModulControler_Ctr14_WMax | 5064 | Para_ModulControler_Ctr14_WMax |  | 10000430
[8 empty] | 10000431 | Para_ModulControler_Ctr14_WMin | Para_ModulControler_Ctr14_WMin | 5065 | Para_ModulControler_Ctr14_WMin |  | 10000431
[8 empty] | 10000435 | Para_ModulControler_Ctr14_WStart | Para_ModulControler_Ctr14_WStart | 5066 | Para_ModulControler_Ctr14_WStart |  | 10000435
[8 empty] | 10000433 | Para_ModulControler_Ctr14_Y_block | Para_ModulControler_Ctr14_Y_block | 5067 | Para_ModulControler_Ctr14_Y_block |  | 10000433
[8 empty] | 10000437 | Para_ModulControler_Ctr14_YMax | Para_ModulControler_Ctr14_YMax | 5068 | Para_ModulControler_Ctr14_YMax |  | 10000437
[8 empty] | 10000439 | Para_ModulControler_Ctr14_YMin | Para_ModulControler_Ctr14_YMin | 5069 | Para_ModulControler_Ctr14_YMin |  | 10000439
[8 empty] | 10000441 | Para_ModulControler_Ctr15_DComp | Para_ModulControler_Ctr15_DComp | 5070 | Para_ModulControler_Ctr15_DComp |  | 10000441
[8 empty] | 10000442 | Para_ModulControler_Ctr15_deadband | Para_ModulControler_Ctr15_deadband | 5071 | Para_ModulControler_Ctr15_deadband |  | 10000442
[8 empty] | 10000446 | Para_ModulControler_Ctr15_dW_down | Para_ModulControler_Ctr15_dW_down | 5072 | Para_ModulControler_Ctr15_dW_down |  | 10000446
[8 empty] | 10000449 | Para_ModulControler_Ctr15_dW_up | Para_ModulControler_Ctr15_dW_up | 5073 | Para_ModulControler_Ctr15_dW_up |  | 10000449
[8 empty] | 10000455 | Para_ModulControler_Ctr15_dY_max | Para_ModulControler_Ctr15_dY_max | 5074 | Para_ModulControler_Ctr15_dY_max |  | 10000455
[8 empty] | 10000443 | Para_ModulControler_Ctr15_IComp | Para_ModulControler_Ctr15_IComp | 5075 | Para_ModulControler_Ctr15_IComp |  | 10000443
[8 empty] | 10000750 | Para_ModulControler_Ctr15_Kp_manualAdjust | Para_ModulControler_Ctr15_Kp_manualAdjust | 5076 | Para_ModulControler_Ctr15_Kp_manualAdjust |  | 10000750
[8 empty] | 10000447 | Para_ModulControler_Ctr15_nvert | Para_ModulControler_Ctr15_nvert | 5077 | Para_ModulControler_Ctr15_nvert |  | 10000447
[8 empty] | 10000444 | Para_ModulControler_Ctr15_PComp | Para_ModulControler_Ctr15_PComp | 5078 | Para_ModulControler_Ctr15_PComp |  | 10000444
[8 empty] | 10000752 | Para_ModulControler_Ctr15_t_min_pulse_down | Para_ModulControler_Ctr15_t_min_pulse_down | 5079 | Para_ModulControler_Ctr15_t_min_pulse_down |  | 10000752
[8 empty] | 10000995 | Para_ModulControler_Ctr15_t_min_pulse_up | Para_ModulControler_Ctr15_t_min_pulse_up | 5080 | Para_ModulControler_Ctr15_t_min_pulse_up |  | 10000995
[8 empty] | 10000755 | Para_ModulControler_Ctr15_t_period_down | Para_ModulControler_Ctr15_t_period_down | 5081 | Para_ModulControler_Ctr15_t_period_down |  | 10000755
[8 empty] | 10000754 | Para_ModulControler_Ctr15_t_period_up | Para_ModulControler_Ctr15_t_period_up | 5082 | Para_ModulControler_Ctr15_t_period_up |  | 10000754
[8 empty] | 10000759 | Para_ModulControler_Ctr15_Tn_manualAdjust | Para_ModulControler_Ctr15_Tn_manualAdjust | 5083 | Para_ModulControler_Ctr15_Tn_manualAdjust |  | 10000759
[8 empty] | 10000756 | Para_ModulControler_Ctr15_Tv_manualAdjust | Para_ModulControler_Ctr15_Tv_manualAdjust | 5084 | Para_ModulControler_Ctr15_Tv_manualAdjust |  | 10000756
[8 empty] | 10000448 | Para_ModulControler_Ctr15_WMax | Para_ModulControler_Ctr15_WMax | 5085 | Para_ModulControler_Ctr15_WMax |  | 10000448
[8 empty] | 10000450 | Para_ModulControler_Ctr15_WMin | Para_ModulControler_Ctr15_WMin | 5086 | Para_ModulControler_Ctr15_WMin |  | 10000450
[8 empty] | 10000453 | Para_ModulControler_Ctr15_WStart | Para_ModulControler_Ctr15_WStart | 5087 | Para_ModulControler_Ctr15_WStart |  | 10000453
[8 empty] | 10000452 | Para_ModulControler_Ctr15_Y_block | Para_ModulControler_Ctr15_Y_block | 5088 | Para_ModulControler_Ctr15_Y_block |  | 10000452
[8 empty] | 10000454 | Para_ModulControler_Ctr15_YMax | Para_ModulControler_Ctr15_YMax | 5089 | Para_ModulControler_Ctr15_YMax |  | 10000454
[8 empty] | 10000451 | Para_ModulControler_Ctr15_YMin | Para_ModulControler_Ctr15_YMin | 5090 | Para_ModulControler_Ctr15_YMin |  | 10000451
[8 empty] | 10000374 | Para_ModulControler_Ctr16_DComp | Para_ModulControler_Ctr16_DComp | 5091 | Para_ModulControler_Ctr16_DComp |  | 10000374
[8 empty] | 10000356 | Para_ModulControler_Ctr16_deadband | Para_ModulControler_Ctr16_deadband | 5092 | Para_ModulControler_Ctr16_deadband |  | 10000356
[8 empty] | 10000346 | Para_ModulControler_Ctr16_dW_down | Para_ModulControler_Ctr16_dW_down | 5093 | Para_ModulControler_Ctr16_dW_down |  | 10000346
[8 empty] | 10000345 | Para_ModulControler_Ctr16_dW_up | Para_ModulControler_Ctr16_dW_up | 5094 | Para_ModulControler_Ctr16_dW_up |  | 10000345
[8 empty] | 10000361 | Para_ModulControler_Ctr16_dY_max | Para_ModulControler_Ctr16_dY_max | 5095 | Para_ModulControler_Ctr16_dY_max |  | 10000361
[8 empty] | 10000370 | Para_ModulControler_Ctr16_IComp | Para_ModulControler_Ctr16_IComp | 5096 | Para_ModulControler_Ctr16_IComp |  | 10000370
[8 empty] | 10000371 | Para_ModulControler_Ctr16_Kp_manualAdjust | Para_ModulControler_Ctr16_Kp_manualAdjust | 5097 | Para_ModulControler_Ctr16_Kp_manualAdjust |  | 10000371
[8 empty] | 10000367 | Para_ModulControler_Ctr16_nvert | Para_ModulControler_Ctr16_nvert | 5098 | Para_ModulControler_Ctr16_nvert |  | 10000367
[8 empty] | 10000372 | Para_ModulControler_Ctr16_PComp | Para_ModulControler_Ctr16_PComp | 5099 | Para_ModulControler_Ctr16_PComp |  | 10000372
[8 empty] | 10000557 | Para_ModulControler_Ctr16_t_min_pulse_down | Para_ModulControler_Ctr16_t_min_pulse_down | 5100 | Para_ModulControler_Ctr16_t_min_pulse_down |  | 10000557
[8 empty] | 10000386 | Para_ModulControler_Ctr16_t_min_pulse_up | Para_ModulControler_Ctr16_t_min_pulse_up | 5101 | Para_ModulControler_Ctr16_t_min_pulse_up |  | 10000386
[8 empty] | 10000560 | Para_ModulControler_Ctr16_t_period_down | Para_ModulControler_Ctr16_t_period_down | 5102 | Para_ModulControler_Ctr16_t_period_down |  | 10000560
[8 empty] | 10000534 | Para_ModulControler_Ctr16_t_period_up | Para_ModulControler_Ctr16_t_period_up | 5103 | Para_ModulControler_Ctr16_t_period_up |  | 10000534
[8 empty] | 10000379 | Para_ModulControler_Ctr16_Tn_manualAdjust | Para_ModulControler_Ctr16_Tn_manualAdjust | 5104 | Para_ModulControler_Ctr16_Tn_manualAdjust |  | 10000379
[8 empty] | 10000383 | Para_ModulControler_Ctr16_Tv_manualAdjust | Para_ModulControler_Ctr16_Tv_manualAdjust | 5105 | Para_ModulControler_Ctr16_Tv_manualAdjust |  | 10000383
[8 empty] | 10000348 | Para_ModulControler_Ctr16_WMax | Para_ModulControler_Ctr16_WMax | 5106 | Para_ModulControler_Ctr16_WMax |  | 10000348
[8 empty] | 10000347 | Para_ModulControler_Ctr16_WMin | Para_ModulControler_Ctr16_WMin | 5107 | Para_ModulControler_Ctr16_WMin |  | 10000347
[8 empty] | 10000142 | Para_ModulControler_Ctr16_WStart | Para_ModulControler_Ctr16_WStart | 5108 | Para_ModulControler_Ctr16_WStart |  | 10000142
[8 empty] | 10000363 | Para_ModulControler_Ctr16_Y_block | Para_ModulControler_Ctr16_Y_block | 5109 | Para_ModulControler_Ctr16_Y_block |  | 10000363
[8 empty] | 10000360 | Para_ModulControler_Ctr16_YMax | Para_ModulControler_Ctr16_YMax | 5110 | Para_ModulControler_Ctr16_YMax |  | 10000360
[8 empty] | 10000359 | Para_ModulControler_Ctr16_YMin | Para_ModulControler_Ctr16_YMin | 5111 | Para_ModulControler_Ctr16_YMin |  | 10000359
[8 empty] | 10000475 | Para_ModulControler_Ctr17_DComp | Para_ModulControler_Ctr17_DComp | 5112 | Para_ModulControler_Ctr17_DComp |  | 10000475
[8 empty] | 10000421 | Para_ModulControler_Ctr17_deadband | Para_ModulControler_Ctr17_deadband | 5113 | Para_ModulControler_Ctr17_deadband |  | 10000421
[8 empty] | 10000436 | Para_ModulControler_Ctr17_dW_down | Para_ModulControler_Ctr17_dW_down | 5114 | Para_ModulControler_Ctr17_dW_down |  | 10000436
[8 empty] | 10000438 | Para_ModulControler_Ctr17_dW_up | Para_ModulControler_Ctr17_dW_up | 5115 | Para_ModulControler_Ctr17_dW_up |  | 10000438
[8 empty] | 10000445 | Para_ModulControler_Ctr17_dY_max | Para_ModulControler_Ctr17_dY_max | 5116 | Para_ModulControler_Ctr17_dY_max |  | 10000445
[8 empty] | 10000467 | Para_ModulControler_Ctr17_IComp | Para_ModulControler_Ctr17_IComp | 5117 | Para_ModulControler_Ctr17_IComp |  | 10000467
[8 empty] | 10000798 | Para_ModulControler_Ctr17_Kp_manualAdjust | Para_ModulControler_Ctr17_Kp_manualAdjust | 5118 | Para_ModulControler_Ctr17_Kp_manualAdjust |  | 10000798
[8 empty] | 10000456 | Para_ModulControler_Ctr17_nvert | Para_ModulControler_Ctr17_nvert | 5119 | Para_ModulControler_Ctr17_nvert |  | 10000456
[8 empty] | 10000459 | Para_ModulControler_Ctr17_PComp | Para_ModulControler_Ctr17_PComp | 5120 | Para_ModulControler_Ctr17_PComp |  | 10000459
[8 empty] | 10000797 | Para_ModulControler_Ctr17_t_min_pulse_down | Para_ModulControler_Ctr17_t_min_pulse_down | 5121 | Para_ModulControler_Ctr17_t_min_pulse_down |  | 10000797
[8 empty] | 10000800 | Para_ModulControler_Ctr17_t_min_pulse_up | Para_ModulControler_Ctr17_t_min_pulse_up | 5122 | Para_ModulControler_Ctr17_t_min_pulse_up |  | 10000800
[8 empty] | 10000801 | Para_ModulControler_Ctr17_t_period_down | Para_ModulControler_Ctr17_t_period_down | 5123 | Para_ModulControler_Ctr17_t_period_down |  | 10000801
[8 empty] | 10000803 | Para_ModulControler_Ctr17_t_period_up | Para_ModulControler_Ctr17_t_period_up | 5124 | Para_ModulControler_Ctr17_t_period_up |  | 10000803
[8 empty] | 10000802 | Para_ModulControler_Ctr17_Tn_manualAdjust | Para_ModulControler_Ctr17_Tn_manualAdjust | 5125 | Para_ModulControler_Ctr17_Tn_manualAdjust |  | 10000802
[8 empty] | 10000804 | Para_ModulControler_Ctr17_Tv_manualAdjust | Para_ModulControler_Ctr17_Tv_manualAdjust | 5126 | Para_ModulControler_Ctr17_Tv_manualAdjust |  | 10000804
[8 empty] | 10000487 | Para_ModulControler_Ctr17_WMax | Para_ModulControler_Ctr17_WMax | 5127 | Para_ModulControler_Ctr17_WMax |  | 10000487
[8 empty] | 10000485 | Para_ModulControler_Ctr17_WMin | Para_ModulControler_Ctr17_WMin | 5128 | Para_ModulControler_Ctr17_WMin |  | 10000485
[8 empty] | 10000146 | Para_ModulControler_Ctr17_WStart | Para_ModulControler_Ctr17_WStart | 5129 | Para_ModulControler_Ctr17_WStart |  | 10000146
[8 empty] | 10000474 | Para_ModulControler_Ctr17_Y_block | Para_ModulControler_Ctr17_Y_block | 5130 | Para_ModulControler_Ctr17_Y_block |  | 10000474
[8 empty] | 10000476 | Para_ModulControler_Ctr17_YMax | Para_ModulControler_Ctr17_YMax | 5131 | Para_ModulControler_Ctr17_YMax |  | 10000476
[8 empty] | 10000473 | Para_ModulControler_Ctr17_YMin | Para_ModulControler_Ctr17_YMin | 5132 | Para_ModulControler_Ctr17_YMin |  | 10000473
[8 empty] | 10001466 | Para_ModulControler_Ctr18_DComp | Para_ModulControler_Ctr18_DComp | 5133 | Para_ModulControler_Ctr18_DComp |  | 10001466
[8 empty] | 10001445 | Para_ModulControler_Ctr18_deadband | Para_ModulControler_Ctr18_deadband | 5134 | Para_ModulControler_Ctr18_deadband |  | 10001445
[8 empty] | 10001448 | Para_ModulControler_Ctr18_dW_down | Para_ModulControler_Ctr18_dW_down | 5135 | Para_ModulControler_Ctr18_dW_down |  | 10001448
[8 empty] | 10001450 | Para_ModulControler_Ctr18_dW_up | Para_ModulControler_Ctr18_dW_up | 5136 | Para_ModulControler_Ctr18_dW_up |  | 10001450
[8 empty] | 10001451 | Para_ModulControler_Ctr18_dY_max | Para_ModulControler_Ctr18_dY_max | 5137 | Para_ModulControler_Ctr18_dY_max |  | 10001451
[8 empty] | 10001463 | Para_ModulControler_Ctr18_IComp | Para_ModulControler_Ctr18_IComp | 5138 | Para_ModulControler_Ctr18_IComp |  | 10001463
[8 empty] | 10001456 | Para_ModulControler_Ctr18_Kp_manualAdjust | Para_ModulControler_Ctr18_Kp_manualAdjust | 5139 | Para_ModulControler_Ctr18_Kp_manualAdjust |  | 10001456
[8 empty] | 10001452 | Para_ModulControler_Ctr18_nvert | Para_ModulControler_Ctr18_nvert | 5140 | Para_ModulControler_Ctr18_nvert |  | 10001452
[8 empty] | 10001460 | Para_ModulControler_Ctr18_PComp | Para_ModulControler_Ctr18_PComp | 5141 | Para_ModulControler_Ctr18_PComp |  | 10001460
[8 empty] | 10001455 | Para_ModulControler_Ctr18_t_min_pulse_down | Para_ModulControler_Ctr18_t_min_pulse_down | 5142 | Para_ModulControler_Ctr18_t_min_pulse_down |  | 10001455
[8 empty] | 10001454 | Para_ModulControler_Ctr18_t_min_pulse_up | Para_ModulControler_Ctr18_t_min_pulse_up | 5143 | Para_ModulControler_Ctr18_t_min_pulse_up |  | 10001454
[8 empty] | 10001453 | Para_ModulControler_Ctr18_t_period_down | Para_ModulControler_Ctr18_t_period_down | 5144 | Para_ModulControler_Ctr18_t_period_down |  | 10001453
[8 empty] | 10001458 | Para_ModulControler_Ctr18_t_period_up | Para_ModulControler_Ctr18_t_period_up | 5145 | Para_ModulControler_Ctr18_t_period_up |  | 10001458
[8 empty] | 10001461 | Para_ModulControler_Ctr18_Tn_manualAdjust | Para_ModulControler_Ctr18_Tn_manualAdjust | 5146 | Para_ModulControler_Ctr18_Tn_manualAdjust |  | 10001461
[8 empty] | 10001457 | Para_ModulControler_Ctr18_Tv_manualAdjust | Para_ModulControler_Ctr18_Tv_manualAdjust | 5147 | Para_ModulControler_Ctr18_Tv_manualAdjust |  | 10001457
[8 empty] | 10001462 | Para_ModulControler_Ctr18_WMax | Para_ModulControler_Ctr18_WMax | 5148 | Para_ModulControler_Ctr18_WMax |  | 10001462
[8 empty] | 10001505 | Para_ModulControler_Ctr18_WMin | Para_ModulControler_Ctr18_WMin | 5149 | Para_ModulControler_Ctr18_WMin |  | 10001505
[8 empty] | 10001502 | Para_ModulControler_Ctr18_WStart | Para_ModulControler_Ctr18_WStart | 5150 | Para_ModulControler_Ctr18_WStart |  | 10001502
[8 empty] | 10001459 | Para_ModulControler_Ctr18_Y_block | Para_ModulControler_Ctr18_Y_block | 5151 | Para_ModulControler_Ctr18_Y_block |  | 10001459
[8 empty] | 10001464 | Para_ModulControler_Ctr18_YMax | Para_ModulControler_Ctr18_YMax | 5152 | Para_ModulControler_Ctr18_YMax |  | 10001464
[8 empty] | 10001467 | Para_ModulControler_Ctr18_YMin | Para_ModulControler_Ctr18_YMin | 5153 | Para_ModulControler_Ctr18_YMin |  | 10001467
[8 empty] | 10001443 | Para_ModulControler_Ctr19_DComp | Para_ModulControler_Ctr19_DComp | 5154 | Para_ModulControler_Ctr19_DComp |  | 10001443
[8 empty] | 10001492 | Para_ModulControler_Ctr19_deadband | Para_ModulControler_Ctr19_deadband | 5155 | Para_ModulControler_Ctr19_deadband |  | 10001492
[8 empty] | 10001497 | Para_ModulControler_Ctr19_dW_down | Para_ModulControler_Ctr19_dW_down | 5156 | Para_ModulControler_Ctr19_dW_down |  | 10001497
[8 empty] | 10001495 | Para_ModulControler_Ctr19_dW_up | Para_ModulControler_Ctr19_dW_up | 5157 | Para_ModulControler_Ctr19_dW_up |  | 10001495
[8 empty] | 10001498 | Para_ModulControler_Ctr19_dY_max | Para_ModulControler_Ctr19_dY_max | 5158 | Para_ModulControler_Ctr19_dY_max |  | 10001498
[8 empty] | 10001444 | Para_ModulControler_Ctr19_IComp | Para_ModulControler_Ctr19_IComp | 5159 | Para_ModulControler_Ctr19_IComp |  | 10001444
[8 empty] | 10001499 | Para_ModulControler_Ctr19_Kp_manualAdjust | Para_ModulControler_Ctr19_Kp_manualAdjust | 5160 | Para_ModulControler_Ctr19_Kp_manualAdjust |  | 10001499
[8 empty] | 10001496 | Para_ModulControler_Ctr19_nvert | Para_ModulControler_Ctr19_nvert | 5161 | Para_ModulControler_Ctr19_nvert |  | 10001496
[8 empty] | 10001447 | Para_ModulControler_Ctr19_PComp | Para_ModulControler_Ctr19_PComp | 5162 | Para_ModulControler_Ctr19_PComp |  | 10001447
[8 empty] | 10001500 | Para_ModulControler_Ctr19_t_min_pulse_down | Para_ModulControler_Ctr19_t_min_pulse_down | 5163 | Para_ModulControler_Ctr19_t_min_pulse_down |  | 10001500
[8 empty] | 10001501 | Para_ModulControler_Ctr19_t_min_pulse_up | Para_ModulControler_Ctr19_t_min_pulse_up | 5164 | Para_ModulControler_Ctr19_t_min_pulse_up |  | 10001501
[8 empty] | 10001504 | Para_ModulControler_Ctr19_t_period_down | Para_ModulControler_Ctr19_t_period_down | 5165 | Para_ModulControler_Ctr19_t_period_down |  | 10001504
[8 empty] | 10001478 | Para_ModulControler_Ctr19_t_period_up | Para_ModulControler_Ctr19_t_period_up | 5166 | Para_ModulControler_Ctr19_t_period_up |  | 10001478
[8 empty] | 10001480 | Para_ModulControler_Ctr19_Tn_manualAdjust | Para_ModulControler_Ctr19_Tn_manualAdjust | 5167 | Para_ModulControler_Ctr19_Tn_manualAdjust |  | 10001480
[8 empty] | 10001479 | Para_ModulControler_Ctr19_Tv_manualAdjust | Para_ModulControler_Ctr19_Tv_manualAdjust | 5168 | Para_ModulControler_Ctr19_Tv_manualAdjust |  | 10001479
[8 empty] | 10001493 | Para_ModulControler_Ctr19_WMax | Para_ModulControler_Ctr19_WMax | 5169 | Para_ModulControler_Ctr19_WMax |  | 10001493
[8 empty] | 10001494 | Para_ModulControler_Ctr19_WMin | Para_ModulControler_Ctr19_WMin | 5170 | Para_ModulControler_Ctr19_WMin |  | 10001494
[8 empty] | 10001491 | Para_ModulControler_Ctr19_WStart | Para_ModulControler_Ctr19_WStart | 5171 | Para_ModulControler_Ctr19_WStart |  | 10001491
[8 empty] | 10001483 | Para_ModulControler_Ctr19_Y_block | Para_ModulControler_Ctr19_Y_block | 5172 | Para_ModulControler_Ctr19_Y_block |  | 10001483
[8 empty] | 10001446 | Para_ModulControler_Ctr19_YMax | Para_ModulControler_Ctr19_YMax | 5173 | Para_ModulControler_Ctr19_YMax |  | 10001446
[8 empty] | 10001449 | Para_ModulControler_Ctr19_YMin | Para_ModulControler_Ctr19_YMin | 5174 | Para_ModulControler_Ctr19_YMin |  | 10001449
[8 empty] | 10000167 | Para_ModulControler_Ctr1_DComp | Para_ModulControler_Ctr1_DComp | 5175 | Para_ModulControler_Ctr1_DComp |  | 10000167
[8 empty] | 10000169 | Para_ModulControler_Ctr1_deadband | Para_ModulControler_Ctr1_deadband | 5176 | Para_ModulControler_Ctr1_deadband |  | 10000169
[8 empty] | 10000198 | Para_ModulControler_Ctr1_dY_max | Para_ModulControler_Ctr1_dY_max | 5177 | Para_ModulControler_Ctr1_dY_max |  | 10000198
[8 empty] | 10000172 | Para_ModulControler_Ctr1_IComp | Para_ModulControler_Ctr1_IComp | 5178 | Para_ModulControler_Ctr1_IComp |  | 10000172
[8 empty] | 10000757 | Para_ModulControler_Ctr1_Kp_manualAdjust | Para_ModulControler_Ctr1_Kp_manualAdjust | 5179 | Para_ModulControler_Ctr1_Kp_manualAdjust |  | 10000757
[8 empty] | 10000178 | Para_ModulControler_Ctr1_nvert | Para_ModulControler_Ctr1_nvert | 5180 | Para_ModulControler_Ctr1_nvert |  | 10000178
[8 empty] | 10000175 | Para_ModulControler_Ctr1_PComp | Para_ModulControler_Ctr1_PComp | 5181 | Para_ModulControler_Ctr1_PComp |  | 10000175
[8 empty] | 10003031 | Para_ModulControler_Ctr1_ScaleMax | Para_ModulControler_Ctr1_ScaleMax | 5182 | Para_ModulControler_Ctr1_ScaleMax |  | 10003031
[8 empty] | 10003030 | Para_ModulControler_Ctr1_ScaleMin | Para_ModulControler_Ctr1_ScaleMin | 5183 | Para_ModulControler_Ctr1_ScaleMin |  | 10003030
[8 empty] | 10000758 | Para_ModulControler_Ctr1_t_min_pulse_down | Para_ModulControler_Ctr1_t_min_pulse_down | 5184 | Para_ModulControler_Ctr1_t_min_pulse_down |  | 10000758
[8 empty] | 10000764 | Para_ModulControler_Ctr1_t_min_pulse_up | Para_ModulControler_Ctr1_t_min_pulse_up | 5185 | Para_ModulControler_Ctr1_t_min_pulse_up |  | 10000764
[8 empty] | 10000760 | Para_ModulControler_Ctr1_t_period_down | Para_ModulControler_Ctr1_t_period_down | 5186 | Para_ModulControler_Ctr1_t_period_down |  | 10000760
[8 empty] | 10000761 | Para_ModulControler_Ctr1_t_period_up | Para_ModulControler_Ctr1_t_period_up | 5187 | Para_ModulControler_Ctr1_t_period_up |  | 10000761
[8 empty] | 10000762 | Para_ModulControler_Ctr1_Tn_manualAdjust | Para_ModulControler_Ctr1_Tn_manualAdjust | 5188 | Para_ModulControler_Ctr1_Tn_manualAdjust |  | 10000762
[8 empty] | 10000763 | Para_ModulControler_Ctr1_Tv_manualAdjust | Para_ModulControler_Ctr1_Tv_manualAdjust | 5189 | Para_ModulControler_Ctr1_Tv_manualAdjust |  | 10000763
[8 empty] | 10000186 | Para_ModulControler_Ctr1_WMax | Para_ModulControler_Ctr1_WMax | 5190 | Para_ModulControler_Ctr1_WMax |  | 10000186
[8 empty] | 10000189 | Para_ModulControler_Ctr1_WMin | Para_ModulControler_Ctr1_WMin | 5191 | Para_ModulControler_Ctr1_WMin |  | 10000189
[8 empty] | 10000193 | Para_ModulControler_Ctr1_WRampNeg | Para_ModulControler_Ctr1_WRampNeg | 5192 | Para_ModulControler_Ctr1_WRampNeg |  | 10000193
[8 empty] | 10000188 | Para_ModulControler_Ctr1_WRampPos | Para_ModulControler_Ctr1_WRampPos | 5193 | Para_ModulControler_Ctr1_WRampPos |  | 10000188
[8 empty] | 10000191 | Para_ModulControler_Ctr1_WStart | Para_ModulControler_Ctr1_WStart | 5194 | Para_ModulControler_Ctr1_WStart |  | 10000191
[8 empty] | 10000194 | Para_ModulControler_Ctr1_Y_block | Para_ModulControler_Ctr1_Y_block | 5195 | Para_ModulControler_Ctr1_Y_block |  | 10000194
[8 empty] | 10000192 | Para_ModulControler_Ctr1_YMax | Para_ModulControler_Ctr1_YMax | 5196 | Para_ModulControler_Ctr1_YMax |  | 10000192
[8 empty] | 10000195 | Para_ModulControler_Ctr1_YMin | Para_ModulControler_Ctr1_YMin | 5197 | Para_ModulControler_Ctr1_YMin |  | 10000195
[8 empty] | 10001293 | Para_ModulControler_Ctr20_DComp | Para_ModulControler_Ctr20_DComp | 5198 | Para_ModulControler_Ctr20_DComp |  | 10001293
[8 empty] | 10001303 | Para_ModulControler_Ctr20_deadband | Para_ModulControler_Ctr20_deadband | 5199 | Para_ModulControler_Ctr20_deadband |  | 10001303
[8 empty] | 10001308 | Para_ModulControler_Ctr20_dW_down | Para_ModulControler_Ctr20_dW_down | 5200 | Para_ModulControler_Ctr20_dW_down |  | 10001308
[8 empty] | 10001307 | Para_ModulControler_Ctr20_dW_up | Para_ModulControler_Ctr20_dW_up | 5201 | Para_ModulControler_Ctr20_dW_up |  | 10001307
[8 empty] | 10001306 | Para_ModulControler_Ctr20_dY_max | Para_ModulControler_Ctr20_dY_max | 5202 | Para_ModulControler_Ctr20_dY_max |  | 10001306
[8 empty] | 10001298 | Para_ModulControler_Ctr20_IComp | Para_ModulControler_Ctr20_IComp | 5203 | Para_ModulControler_Ctr20_IComp |  | 10001298
[8 empty] | 10001311 | Para_ModulControler_Ctr20_Kp_manualAdjust | Para_ModulControler_Ctr20_Kp_manualAdjust | 5204 | Para_ModulControler_Ctr20_Kp_manualAdjust |  | 10001311
[8 empty] | 10001310 | Para_ModulControler_Ctr20_nvert | Para_ModulControler_Ctr20_nvert | 5205 | Para_ModulControler_Ctr20_nvert |  | 10001310
[8 empty] | 10001296 | Para_ModulControler_Ctr20_PComp | Para_ModulControler_Ctr20_PComp | 5206 | Para_ModulControler_Ctr20_PComp |  | 10001296
[8 empty] | 10001309 | Para_ModulControler_Ctr20_t_min_pulse_down | Para_ModulControler_Ctr20_t_min_pulse_down | 5207 | Para_ModulControler_Ctr20_t_min_pulse_down |  | 10001309
[8 empty] | 10001312 | Para_ModulControler_Ctr20_t_min_pulse_up | Para_ModulControler_Ctr20_t_min_pulse_up | 5208 | Para_ModulControler_Ctr20_t_min_pulse_up |  | 10001312
[8 empty] | 10001294 | Para_ModulControler_Ctr20_t_period_down | Para_ModulControler_Ctr20_t_period_down | 5209 | Para_ModulControler_Ctr20_t_period_down |  | 10001294
[8 empty] | 10001295 | Para_ModulControler_Ctr20_t_period_up | Para_ModulControler_Ctr20_t_period_up | 5210 | Para_ModulControler_Ctr20_t_period_up |  | 10001295
[8 empty] | 10001316 | Para_ModulControler_Ctr20_Tn_manualAdjust | Para_ModulControler_Ctr20_Tn_manualAdjust | 5211 | Para_ModulControler_Ctr20_Tn_manualAdjust |  | 10001316
[8 empty] | 10001313 | Para_ModulControler_Ctr20_Tv_manualAdjust | Para_ModulControler_Ctr20_Tv_manualAdjust | 5212 | Para_ModulControler_Ctr20_Tv_manualAdjust |  | 10001313
[8 empty] | 10001301 | Para_ModulControler_Ctr20_WMax | Para_ModulControler_Ctr20_WMax | 5213 | Para_ModulControler_Ctr20_WMax |  | 10001301
[8 empty] | 10001299 | Para_ModulControler_Ctr20_WMin | Para_ModulControler_Ctr20_WMin | 5214 | Para_ModulControler_Ctr20_WMin |  | 10001299
[8 empty] | 10001304 | Para_ModulControler_Ctr20_WStart | Para_ModulControler_Ctr20_WStart | 5215 | Para_ModulControler_Ctr20_WStart |  | 10001304
[8 empty] | 10001292 | Para_ModulControler_Ctr20_Y_block | Para_ModulControler_Ctr20_Y_block | 5216 | Para_ModulControler_Ctr20_Y_block |  | 10001292
[8 empty] | 10001300 | Para_ModulControler_Ctr20_YMax | Para_ModulControler_Ctr20_YMax | 5217 | Para_ModulControler_Ctr20_YMax |  | 10001300
[8 empty] | 10001297 | Para_ModulControler_Ctr20_YMin | Para_ModulControler_Ctr20_YMin | 5218 | Para_ModulControler_Ctr20_YMin |  | 10001297
[8 empty] | 10001412 | Para_ModulControler_Ctr21_DComp | Para_ModulControler_Ctr21_DComp | 5219 | Para_ModulControler_Ctr21_DComp |  | 10001412
[8 empty] | 10001400 | Para_ModulControler_Ctr21_deadband | Para_ModulControler_Ctr21_deadband | 5220 | Para_ModulControler_Ctr21_deadband |  | 10001400
[8 empty] | 10001399 | Para_ModulControler_Ctr21_dW_down | Para_ModulControler_Ctr21_dW_down | 5221 | Para_ModulControler_Ctr21_dW_down |  | 10001399
[8 empty] | 10001398 | Para_ModulControler_Ctr21_dW_up | Para_ModulControler_Ctr21_dW_up | 5222 | Para_ModulControler_Ctr21_dW_up |  | 10001398
[8 empty] | 10001402 | Para_ModulControler_Ctr21_dY_max | Para_ModulControler_Ctr21_dY_max | 5223 | Para_ModulControler_Ctr21_dY_max |  | 10001402
[8 empty] | 10001418 | Para_ModulControler_Ctr21_IComp | Para_ModulControler_Ctr21_IComp | 5224 | Para_ModulControler_Ctr21_IComp |  | 10001418
[8 empty] | 10001404 | Para_ModulControler_Ctr21_Kp_manualAdjust | Para_ModulControler_Ctr21_Kp_manualAdjust | 5225 | Para_ModulControler_Ctr21_Kp_manualAdjust |  | 10001404
[8 empty] | 10001403 | Para_ModulControler_Ctr21_nvert | Para_ModulControler_Ctr21_nvert | 5226 | Para_ModulControler_Ctr21_nvert |  | 10001403
[8 empty] | 10001414 | Para_ModulControler_Ctr21_PComp | Para_ModulControler_Ctr21_PComp | 5227 | Para_ModulControler_Ctr21_PComp |  | 10001414
[8 empty] | 10001405 | Para_ModulControler_Ctr21_t_min_pulse_down | Para_ModulControler_Ctr21_t_min_pulse_down | 5228 | Para_ModulControler_Ctr21_t_min_pulse_down |  | 10001405
[8 empty] | 10001408 | Para_ModulControler_Ctr21_t_min_pulse_up | Para_ModulControler_Ctr21_t_min_pulse_up | 5229 | Para_ModulControler_Ctr21_t_min_pulse_up |  | 10001408
[8 empty] | 10001406 | Para_ModulControler_Ctr21_t_period_down | Para_ModulControler_Ctr21_t_period_down | 5230 | Para_ModulControler_Ctr21_t_period_down |  | 10001406
[8 empty] | 10001407 | Para_ModulControler_Ctr21_t_period_up | Para_ModulControler_Ctr21_t_period_up | 5231 | Para_ModulControler_Ctr21_t_period_up |  | 10001407
[8 empty] | 10001411 | Para_ModulControler_Ctr21_Tn_manualAdjust | Para_ModulControler_Ctr21_Tn_manualAdjust | 5232 | Para_ModulControler_Ctr21_Tn_manualAdjust |  | 10001411
[8 empty] | 10001410 | Para_ModulControler_Ctr21_Tv_manualAdjust | Para_ModulControler_Ctr21_Tv_manualAdjust | 5233 | Para_ModulControler_Ctr21_Tv_manualAdjust |  | 10001410
[8 empty] | 10001439 | Para_ModulControler_Ctr21_WMax | Para_ModulControler_Ctr21_WMax | 5234 | Para_ModulControler_Ctr21_WMax |  | 10001439
[8 empty] | 10001442 | Para_ModulControler_Ctr21_WMin | Para_ModulControler_Ctr21_WMin | 5235 | Para_ModulControler_Ctr21_WMin |  | 10001442
[8 empty] | 10001440 | Para_ModulControler_Ctr21_WStart | Para_ModulControler_Ctr21_WStart | 5236 | Para_ModulControler_Ctr21_WStart |  | 10001440
[8 empty] | 10001415 | Para_ModulControler_Ctr21_Y_block | Para_ModulControler_Ctr21_Y_block | 5237 | Para_ModulControler_Ctr21_Y_block |  | 10001415
[8 empty] | 10001416 | Para_ModulControler_Ctr21_YMax | Para_ModulControler_Ctr21_YMax | 5238 | Para_ModulControler_Ctr21_YMax |  | 10001416
[8 empty] | 10001421 | Para_ModulControler_Ctr21_YMin | Para_ModulControler_Ctr21_YMin | 5239 | Para_ModulControler_Ctr21_YMin |  | 10001421
[8 empty] | 10002530 | Para_ModulControler_Ctr22_DComp | Para_ModulControler_Ctr22_DComp | 5240 | Para_ModulControler_Ctr22_DComp |  | 10002530
[8 empty] | 10001516 | Para_ModulControler_Ctr22_deadband | Para_ModulControler_Ctr22_deadband | 5241 | Para_ModulControler_Ctr22_deadband |  | 10001516
[8 empty] | 10001520 | Para_ModulControler_Ctr22_dW_down | Para_ModulControler_Ctr22_dW_down | 5242 | Para_ModulControler_Ctr22_dW_down |  | 10001520
[8 empty] | 10001519 | Para_ModulControler_Ctr22_dW_up | Para_ModulControler_Ctr22_dW_up | 5243 | Para_ModulControler_Ctr22_dW_up |  | 10001519
[8 empty] | 10001521 | Para_ModulControler_Ctr22_dY_max | Para_ModulControler_Ctr22_dY_max | 5244 | Para_ModulControler_Ctr22_dY_max |  | 10001521
[8 empty] | 10002525 | Para_ModulControler_Ctr22_IComp | Para_ModulControler_Ctr22_IComp | 5245 | Para_ModulControler_Ctr22_IComp |  | 10002525
[8 empty] | 10002508 | Para_ModulControler_Ctr22_Kp_manualAdjust | Para_ModulControler_Ctr22_Kp_manualAdjust | 5246 | Para_ModulControler_Ctr22_Kp_manualAdjust |  | 10002508
[8 empty] | 10002514 | Para_ModulControler_Ctr22_nvert | Para_ModulControler_Ctr22_nvert | 5247 | Para_ModulControler_Ctr22_nvert |  | 10002514
[8 empty] | 10002539 | Para_ModulControler_Ctr22_PComp | Para_ModulControler_Ctr22_PComp | 5248 | Para_ModulControler_Ctr22_PComp |  | 10002539
[8 empty] | 10001518 | Para_ModulControler_Ctr22_t_min_pulse_down | Para_ModulControler_Ctr22_t_min_pulse_down | 5249 | Para_ModulControler_Ctr22_t_min_pulse_down |  | 10001518
[8 empty] | 10002522 | Para_ModulControler_Ctr22_t_min_pulse_up | Para_ModulControler_Ctr22_t_min_pulse_up | 5250 | Para_ModulControler_Ctr22_t_min_pulse_up |  | 10002522
[8 empty] | 10002515 | Para_ModulControler_Ctr22_t_period_down | Para_ModulControler_Ctr22_t_period_down | 5251 | Para_ModulControler_Ctr22_t_period_down |  | 10002515
[8 empty] | 10002516 | Para_ModulControler_Ctr22_t_period_up | Para_ModulControler_Ctr22_t_period_up | 5252 | Para_ModulControler_Ctr22_t_period_up |  | 10002516
[8 empty] | 10002524 | Para_ModulControler_Ctr22_Tn_manualAdjust | Para_ModulControler_Ctr22_Tn_manualAdjust | 5253 | Para_ModulControler_Ctr22_Tn_manualAdjust |  | 10002524
[8 empty] | 10002523 | Para_ModulControler_Ctr22_Tv_manualAdjust | Para_ModulControler_Ctr22_Tv_manualAdjust | 5254 | Para_ModulControler_Ctr22_Tv_manualAdjust |  | 10002523
[8 empty] | 10002531 | Para_ModulControler_Ctr22_WMax | Para_ModulControler_Ctr22_WMax | 5255 | Para_ModulControler_Ctr22_WMax |  | 10002531
[8 empty] | 10002548 | Para_ModulControler_Ctr22_WMin | Para_ModulControler_Ctr22_WMin | 5256 | Para_ModulControler_Ctr22_WMin |  | 10002548
[8 empty] | 10002541 | Para_ModulControler_Ctr22_WStart | Para_ModulControler_Ctr22_WStart | 5257 | Para_ModulControler_Ctr22_WStart |  | 10002541
[8 empty] | 10002526 | Para_ModulControler_Ctr22_Y_block | Para_ModulControler_Ctr22_Y_block | 5258 | Para_ModulControler_Ctr22_Y_block |  | 10002526
[8 empty] | 10002537 | Para_ModulControler_Ctr22_YMax | Para_ModulControler_Ctr22_YMax | 5259 | Para_ModulControler_Ctr22_YMax |  | 10002537
[8 empty] | 10002532 | Para_ModulControler_Ctr22_YMin | Para_ModulControler_Ctr22_YMin | 5260 | Para_ModulControler_Ctr22_YMin |  | 10002532
[8 empty] | 10008224 | Para_ModulControler_Ctr23_DComp | Para_ModulControler_Ctr23_DComp | 5261 | Para_ModulControler_Ctr23_DComp |  | 10008224
[8 empty] | 10008260 | Para_ModulControler_Ctr23_deadband | Para_ModulControler_Ctr23_deadband | 5262 | Para_ModulControler_Ctr23_deadband |  | 10008260
[8 empty] | 10008261 | Para_ModulControler_Ctr23_dW_down | Para_ModulControler_Ctr23_dW_down | 5263 | Para_ModulControler_Ctr23_dW_down |  | 10008261
[8 empty] | 10008263 | Para_ModulControler_Ctr23_dW_up | Para_ModulControler_Ctr23_dW_up | 5264 | Para_ModulControler_Ctr23_dW_up |  | 10008263
[8 empty] | 10008262 | Para_ModulControler_Ctr23_dY_max | Para_ModulControler_Ctr23_dY_max | 5265 | Para_ModulControler_Ctr23_dY_max |  | 10008262
[8 empty] | 10008225 | Para_ModulControler_Ctr23_IComp | Para_ModulControler_Ctr23_IComp | 5266 | Para_ModulControler_Ctr23_IComp |  | 10008225
[8 empty] | 10008265 | Para_ModulControler_Ctr23_Kp_manualAdjust | Para_ModulControler_Ctr23_Kp_manualAdjust | 5267 | Para_ModulControler_Ctr23_Kp_manualAdjust |  | 10008265
[8 empty] | 10008264 | Para_ModulControler_Ctr23_nvert | Para_ModulControler_Ctr23_nvert | 5268 | Para_ModulControler_Ctr23_nvert |  | 10008264
[8 empty] | 10008227 | Para_ModulControler_Ctr23_PComp | Para_ModulControler_Ctr23_PComp | 5269 | Para_ModulControler_Ctr23_PComp |  | 10008227
[8 empty] | 10008267 | Para_ModulControler_Ctr23_t_min_pulse_down | Para_ModulControler_Ctr23_t_min_pulse_down | 5270 | Para_ModulControler_Ctr23_t_min_pulse_down |  | 10008267
[8 empty] | 10008266 | Para_ModulControler_Ctr23_t_min_pulse_up | Para_ModulControler_Ctr23_t_min_pulse_up | 5271 | Para_ModulControler_Ctr23_t_min_pulse_up |  | 10008266
[8 empty] | 10008269 | Para_ModulControler_Ctr23_t_period_down | Para_ModulControler_Ctr23_t_period_down | 5272 | Para_ModulControler_Ctr23_t_period_down |  | 10008269
[8 empty] | 10008270 | Para_ModulControler_Ctr23_t_period_up | Para_ModulControler_Ctr23_t_period_up | 5273 | Para_ModulControler_Ctr23_t_period_up |  | 10008270
[8 empty] | 10008268 | Para_ModulControler_Ctr23_Tn_manualAdjust | Para_ModulControler_Ctr23_Tn_manualAdjust | 5274 | Para_ModulControler_Ctr23_Tn_manualAdjust |  | 10008268
[8 empty] | 10008271 | Para_ModulControler_Ctr23_Tv_manualAdjust | Para_ModulControler_Ctr23_Tv_manualAdjust | 5275 | Para_ModulControler_Ctr23_Tv_manualAdjust |  | 10008271
[8 empty] | 10008257 | Para_ModulControler_Ctr23_WMax | Para_ModulControler_Ctr23_WMax | 5276 | Para_ModulControler_Ctr23_WMax |  | 10008257
[8 empty] | 10008258 | Para_ModulControler_Ctr23_WMin | Para_ModulControler_Ctr23_WMin | 5277 | Para_ModulControler_Ctr23_WMin |  | 10008258
[8 empty] | 10008259 | Para_ModulControler_Ctr23_WStart | Para_ModulControler_Ctr23_WStart | 5278 | Para_ModulControler_Ctr23_WStart |  | 10008259
[8 empty] | 10008272 | Para_ModulControler_Ctr23_Y_block | Para_ModulControler_Ctr23_Y_block | 5279 | Para_ModulControler_Ctr23_Y_block |  | 10008272
[8 empty] | 10008226 | Para_ModulControler_Ctr23_YMax | Para_ModulControler_Ctr23_YMax | 5280 | Para_ModulControler_Ctr23_YMax |  | 10008226
[8 empty] | 10008228 | Para_ModulControler_Ctr23_YMin | Para_ModulControler_Ctr23_YMin | 5281 | Para_ModulControler_Ctr23_YMin |  | 10008228
[8 empty] | 10008296 | Para_ModulControler_Ctr24_DComp | Para_ModulControler_Ctr24_DComp | 5282 | Para_ModulControler_Ctr24_DComp |  | 10008296
[8 empty] | 10008304 | Para_ModulControler_Ctr24_deadband | Para_ModulControler_Ctr24_deadband | 5283 | Para_ModulControler_Ctr24_deadband |  | 10008304
[8 empty] | 10008306 | Para_ModulControler_Ctr24_dW_down | Para_ModulControler_Ctr24_dW_down | 5284 | Para_ModulControler_Ctr24_dW_down |  | 10008306
[8 empty] | 10008309 | Para_ModulControler_Ctr24_dW_up | Para_ModulControler_Ctr24_dW_up | 5285 | Para_ModulControler_Ctr24_dW_up |  | 10008309
[8 empty] | 10008311 | Para_ModulControler_Ctr24_dY_max | Para_ModulControler_Ctr24_dY_max | 5286 | Para_ModulControler_Ctr24_dY_max |  | 10008311
[8 empty] | 10008299 | Para_ModulControler_Ctr24_IComp | Para_ModulControler_Ctr24_IComp | 5287 | Para_ModulControler_Ctr24_IComp |  | 10008299
[8 empty] | 10008310 | Para_ModulControler_Ctr24_Kp_manualAdjust | Para_ModulControler_Ctr24_Kp_manualAdjust | 5288 | Para_ModulControler_Ctr24_Kp_manualAdjust |  | 10008310
[8 empty] | 10008308 | Para_ModulControler_Ctr24_nvert | Para_ModulControler_Ctr24_nvert | 5289 | Para_ModulControler_Ctr24_nvert |  | 10008308
[8 empty] | 10008300 | Para_ModulControler_Ctr24_PComp | Para_ModulControler_Ctr24_PComp | 5290 | Para_ModulControler_Ctr24_PComp |  | 10008300
[8 empty] | 10008312 | Para_ModulControler_Ctr24_t_min_pulse_down | Para_ModulControler_Ctr24_t_min_pulse_down | 5291 | Para_ModulControler_Ctr24_t_min_pulse_down |  | 10008312
[8 empty] | 10008313 | Para_ModulControler_Ctr24_t_min_pulse_up | Para_ModulControler_Ctr24_t_min_pulse_up | 5292 | Para_ModulControler_Ctr24_t_min_pulse_up |  | 10008313
[8 empty] | 10008315 | Para_ModulControler_Ctr24_t_period_down | Para_ModulControler_Ctr24_t_period_down | 5293 | Para_ModulControler_Ctr24_t_period_down |  | 10008315
[8 empty] | 10008314 | Para_ModulControler_Ctr24_t_period_up | Para_ModulControler_Ctr24_t_period_up | 5294 | Para_ModulControler_Ctr24_t_period_up |  | 10008314
[8 empty] | 10008316 | Para_ModulControler_Ctr24_Tn_manualAdjust | Para_ModulControler_Ctr24_Tn_manualAdjust | 5295 | Para_ModulControler_Ctr24_Tn_manualAdjust |  | 10008316
[8 empty] | 10008318 | Para_ModulControler_Ctr24_Tv_manualAdjust | Para_ModulControler_Ctr24_Tv_manualAdjust | 5296 | Para_ModulControler_Ctr24_Tv_manualAdjust |  | 10008318
[8 empty] | 10008303 | Para_ModulControler_Ctr24_WMax | Para_ModulControler_Ctr24_WMax | 5297 | Para_ModulControler_Ctr24_WMax |  | 10008303
[8 empty] | 10008305 | Para_ModulControler_Ctr24_WMin | Para_ModulControler_Ctr24_WMin | 5298 | Para_ModulControler_Ctr24_WMin |  | 10008305
[8 empty] | 10008307 | Para_ModulControler_Ctr24_WStart | Para_ModulControler_Ctr24_WStart | 5299 | Para_ModulControler_Ctr24_WStart |  | 10008307
[8 empty] | 10008317 | Para_ModulControler_Ctr24_Y_block | Para_ModulControler_Ctr24_Y_block | 5300 | Para_ModulControler_Ctr24_Y_block |  | 10008317
[8 empty] | 10008301 | Para_ModulControler_Ctr24_YMax | Para_ModulControler_Ctr24_YMax | 5301 | Para_ModulControler_Ctr24_YMax |  | 10008301
[8 empty] | 10008302 | Para_ModulControler_Ctr24_YMin | Para_ModulControler_Ctr24_YMin | 5302 | Para_ModulControler_Ctr24_YMin |  | 10008302
[8 empty] | 10008386 | Para_ModulControler_Ctr25_DComp | Para_ModulControler_Ctr25_DComp | 5303 | Para_ModulControler_Ctr25_DComp |  | 10008386
[8 empty] | 10008232 | Para_ModulControler_Ctr25_deadband | Para_ModulControler_Ctr25_deadband | 5304 | Para_ModulControler_Ctr25_deadband |  | 10008232
[8 empty] | 10008233 | Para_ModulControler_Ctr25_dW_down | Para_ModulControler_Ctr25_dW_down | 5305 | Para_ModulControler_Ctr25_dW_down |  | 10008233
[8 empty] | 10008234 | Para_ModulControler_Ctr25_dW_up | Para_ModulControler_Ctr25_dW_up | 5306 | Para_ModulControler_Ctr25_dW_up |  | 10008234
[8 empty] | 10008235 | Para_ModulControler_Ctr25_dY_max | Para_ModulControler_Ctr25_dY_max | 5307 | Para_ModulControler_Ctr25_dY_max |  | 10008235
[8 empty] | 10008385 | Para_ModulControler_Ctr25_IComp | Para_ModulControler_Ctr25_IComp | 5308 | Para_ModulControler_Ctr25_IComp |  | 10008385
[8 empty] | 10008237 | Para_ModulControler_Ctr25_Kp_manualAdjust | Para_ModulControler_Ctr25_Kp_manualAdjust | 5309 | Para_ModulControler_Ctr25_Kp_manualAdjust |  | 10008237
[8 empty] | 10008236 | Para_ModulControler_Ctr25_nvert | Para_ModulControler_Ctr25_nvert | 5310 | Para_ModulControler_Ctr25_nvert |  | 10008236
[8 empty] | 10008388 | Para_ModulControler_Ctr25_PComp | Para_ModulControler_Ctr25_PComp | 5311 | Para_ModulControler_Ctr25_PComp |  | 10008388
[8 empty] | 10008238 | Para_ModulControler_Ctr25_t_min_pulse_down | Para_ModulControler_Ctr25_t_min_pulse_down | 5312 | Para_ModulControler_Ctr25_t_min_pulse_down |  | 10008238
[8 empty] | 10008239 | Para_ModulControler_Ctr25_t_min_pulse_up | Para_ModulControler_Ctr25_t_min_pulse_up | 5313 | Para_ModulControler_Ctr25_t_min_pulse_up |  | 10008239
[8 empty] | 10008382 | Para_ModulControler_Ctr25_t_period_down | Para_ModulControler_Ctr25_t_period_down | 5314 | Para_ModulControler_Ctr25_t_period_down |  | 10008382
[8 empty] | 10008381 | Para_ModulControler_Ctr25_t_period_up | Para_ModulControler_Ctr25_t_period_up | 5315 | Para_ModulControler_Ctr25_t_period_up |  | 10008381
[8 empty] | 10008383 | Para_ModulControler_Ctr25_Tn_manualAdjust | Para_ModulControler_Ctr25_Tn_manualAdjust | 5316 | Para_ModulControler_Ctr25_Tn_manualAdjust |  | 10008383
[8 empty] | 10008384 | Para_ModulControler_Ctr25_Tv_manualAdjust | Para_ModulControler_Ctr25_Tv_manualAdjust | 5317 | Para_ModulControler_Ctr25_Tv_manualAdjust |  | 10008384
[8 empty] | 10008390 | Para_ModulControler_Ctr25_WMax | Para_ModulControler_Ctr25_WMax | 5318 | Para_ModulControler_Ctr25_WMax |  | 10008390
[8 empty] | 10008393 | Para_ModulControler_Ctr25_WMin | Para_ModulControler_Ctr25_WMin | 5319 | Para_ModulControler_Ctr25_WMin |  | 10008393
[8 empty] | 10008394 | Para_ModulControler_Ctr25_WStart | Para_ModulControler_Ctr25_WStart | 5320 | Para_ModulControler_Ctr25_WStart |  | 10008394
[8 empty] | 10008387 | Para_ModulControler_Ctr25_Y_block | Para_ModulControler_Ctr25_Y_block | 5321 | Para_ModulControler_Ctr25_Y_block |  | 10008387
[8 empty] | 10008392 | Para_ModulControler_Ctr25_YMax | Para_ModulControler_Ctr25_YMax | 5322 | Para_ModulControler_Ctr25_YMax |  | 10008392
[8 empty] | 10008391 | Para_ModulControler_Ctr25_YMin | Para_ModulControler_Ctr25_YMin | 5323 | Para_ModulControler_Ctr25_YMin |  | 10008391
[8 empty] | 10008283 | Para_ModulControler_Ctr26_DComp | Para_ModulControler_Ctr26_DComp | 5324 | Para_ModulControler_Ctr26_DComp |  | 10008283
[8 empty] | 10008319 | Para_ModulControler_Ctr26_deadband | Para_ModulControler_Ctr26_deadband | 5325 | Para_ModulControler_Ctr26_deadband |  | 10008319
[8 empty] | 10008321 | Para_ModulControler_Ctr26_dW_down | Para_ModulControler_Ctr26_dW_down | 5326 | Para_ModulControler_Ctr26_dW_down |  | 10008321
[8 empty] | 10008323 | Para_ModulControler_Ctr26_dW_up | Para_ModulControler_Ctr26_dW_up | 5327 | Para_ModulControler_Ctr26_dW_up |  | 10008323
[8 empty] | 10008322 | Para_ModulControler_Ctr26_dY_max | Para_ModulControler_Ctr26_dY_max | 5328 | Para_ModulControler_Ctr26_dY_max |  | 10008322
[8 empty] | 10008285 | Para_ModulControler_Ctr26_IComp | Para_ModulControler_Ctr26_IComp | 5329 | Para_ModulControler_Ctr26_IComp |  | 10008285
[8 empty] | 10008325 | Para_ModulControler_Ctr26_Kp_manualAdjust | Para_ModulControler_Ctr26_Kp_manualAdjust | 5330 | Para_ModulControler_Ctr26_Kp_manualAdjust |  | 10008325
[8 empty] | 10008324 | Para_ModulControler_Ctr26_nvert | Para_ModulControler_Ctr26_nvert | 5331 | Para_ModulControler_Ctr26_nvert |  | 10008324
[8 empty] | 10008286 | Para_ModulControler_Ctr26_PComp | Para_ModulControler_Ctr26_PComp | 5332 | Para_ModulControler_Ctr26_PComp |  | 10008286
[8 empty] | 10008326 | Para_ModulControler_Ctr26_t_min_pulse_down | Para_ModulControler_Ctr26_t_min_pulse_down | 5333 | Para_ModulControler_Ctr26_t_min_pulse_down |  | 10008326
[8 empty] | 10008327 | Para_ModulControler_Ctr26_t_min_pulse_up | Para_ModulControler_Ctr26_t_min_pulse_up | 5334 | Para_ModulControler_Ctr26_t_min_pulse_up |  | 10008327
[8 empty] | 10008328 | Para_ModulControler_Ctr26_t_period_down | Para_ModulControler_Ctr26_t_period_down | 5335 | Para_ModulControler_Ctr26_t_period_down |  | 10008328
[8 empty] | 10008329 | Para_ModulControler_Ctr26_t_period_up | Para_ModulControler_Ctr26_t_period_up | 5336 | Para_ModulControler_Ctr26_t_period_up |  | 10008329
[8 empty] | 10008330 | Para_ModulControler_Ctr26_Tn_manualAdjust | Para_ModulControler_Ctr26_Tn_manualAdjust | 5337 | Para_ModulControler_Ctr26_Tn_manualAdjust |  | 10008330
[8 empty] | 10008332 | Para_ModulControler_Ctr26_Tv_manualAdjust | Para_ModulControler_Ctr26_Tv_manualAdjust | 5338 | Para_ModulControler_Ctr26_Tv_manualAdjust |  | 10008332
[8 empty] | 10008290 | Para_ModulControler_Ctr26_WMax | Para_ModulControler_Ctr26_WMax | 5339 | Para_ModulControler_Ctr26_WMax |  | 10008290
[8 empty] | 10008288 | Para_ModulControler_Ctr26_WMin | Para_ModulControler_Ctr26_WMin | 5340 | Para_ModulControler_Ctr26_WMin |  | 10008288
[8 empty] | 10008291 | Para_ModulControler_Ctr26_WStart | Para_ModulControler_Ctr26_WStart | 5341 | Para_ModulControler_Ctr26_WStart |  | 10008291
[8 empty] | 10008333 | Para_ModulControler_Ctr26_Y_block | Para_ModulControler_Ctr26_Y_block | 5342 | Para_ModulControler_Ctr26_Y_block |  | 10008333
[8 empty] | 10008287 | Para_ModulControler_Ctr26_YMax | Para_ModulControler_Ctr26_YMax | 5343 | Para_ModulControler_Ctr26_YMax |  | 10008287
[8 empty] | 10008289 | Para_ModulControler_Ctr26_YMin | Para_ModulControler_Ctr26_YMin | 5344 | Para_ModulControler_Ctr26_YMin |  | 10008289
[8 empty] | 10008431 | Para_ModulControler_Ctr27_DComp | Para_ModulControler_Ctr27_DComp | 5345 | Para_ModulControler_Ctr27_DComp |  | 10008431
[8 empty] | 10008415 | Para_ModulControler_Ctr27_deadband | Para_ModulControler_Ctr27_deadband | 5346 | Para_ModulControler_Ctr27_deadband |  | 10008415
[8 empty] | 10008417 | Para_ModulControler_Ctr27_dW_down | Para_ModulControler_Ctr27_dW_down | 5347 | Para_ModulControler_Ctr27_dW_down |  | 10008417
[8 empty] | 10008419 | Para_ModulControler_Ctr27_dW_up | Para_ModulControler_Ctr27_dW_up | 5348 | Para_ModulControler_Ctr27_dW_up |  | 10008419
[8 empty] | 10008418 | Para_ModulControler_Ctr27_dY_max | Para_ModulControler_Ctr27_dY_max | 5349 | Para_ModulControler_Ctr27_dY_max |  | 10008418
[8 empty] | 10008429 | Para_ModulControler_Ctr27_IComp | Para_ModulControler_Ctr27_IComp | 5350 | Para_ModulControler_Ctr27_IComp |  | 10008429
[8 empty] | 10008420 | Para_ModulControler_Ctr27_Kp_manualAdjust | Para_ModulControler_Ctr27_Kp_manualAdjust | 5351 | Para_ModulControler_Ctr27_Kp_manualAdjust |  | 10008420
[8 empty] | 10008422 | Para_ModulControler_Ctr27_nvert | Para_ModulControler_Ctr27_nvert | 5352 | Para_ModulControler_Ctr27_nvert |  | 10008422
[8 empty] | 10008433 | Para_ModulControler_Ctr27_PComp | Para_ModulControler_Ctr27_PComp | 5353 | Para_ModulControler_Ctr27_PComp |  | 10008433
[8 empty] | 10008421 | Para_ModulControler_Ctr27_t_min_pulse_down | Para_ModulControler_Ctr27_t_min_pulse_down | 5354 | Para_ModulControler_Ctr27_t_min_pulse_down |  | 10008421
[8 empty] | 10008423 | Para_ModulControler_Ctr27_t_min_pulse_up | Para_ModulControler_Ctr27_t_min_pulse_up | 5355 | Para_ModulControler_Ctr27_t_min_pulse_up |  | 10008423
[8 empty] | 10008424 | Para_ModulControler_Ctr27_t_period_down | Para_ModulControler_Ctr27_t_period_down | 5356 | Para_ModulControler_Ctr27_t_period_down |  | 10008424
[8 empty] | 10008425 | Para_ModulControler_Ctr27_t_period_up | Para_ModulControler_Ctr27_t_period_up | 5357 | Para_ModulControler_Ctr27_t_period_up |  | 10008425
[8 empty] | 10008427 | Para_ModulControler_Ctr27_Tn_manualAdjust | Para_ModulControler_Ctr27_Tn_manualAdjust | 5358 | Para_ModulControler_Ctr27_Tn_manualAdjust |  | 10008427
[8 empty] | 10008428 | Para_ModulControler_Ctr27_Tv_manualAdjust | Para_ModulControler_Ctr27_Tv_manualAdjust | 5359 | Para_ModulControler_Ctr27_Tv_manualAdjust |  | 10008428
[8 empty] | 10008434 | Para_ModulControler_Ctr27_WMax | Para_ModulControler_Ctr27_WMax | 5360 | Para_ModulControler_Ctr27_WMax |  | 10008434
[8 empty] | 10008435 | Para_ModulControler_Ctr27_WMin | Para_ModulControler_Ctr27_WMin | 5361 | Para_ModulControler_Ctr27_WMin |  | 10008435
[8 empty] | 10008436 | Para_ModulControler_Ctr27_WStart | Para_ModulControler_Ctr27_WStart | 5362 | Para_ModulControler_Ctr27_WStart |  | 10008436
[8 empty] | 10008426 | Para_ModulControler_Ctr27_Y_block | Para_ModulControler_Ctr27_Y_block | 5363 | Para_ModulControler_Ctr27_Y_block |  | 10008426
[8 empty] | 10008430 | Para_ModulControler_Ctr27_YMax | Para_ModulControler_Ctr27_YMax | 5364 | Para_ModulControler_Ctr27_YMax |  | 10008430
[8 empty] | 10008432 | Para_ModulControler_Ctr27_YMin | Para_ModulControler_Ctr27_YMin | 5365 | Para_ModulControler_Ctr27_YMin |  | 10008432
[8 empty] | 10003085 | Para_ModulControler_Ctr28_DComp | Para_ModulControler_Ctr28_DComp | 5366 | Para_ModulControler_Ctr28_DComp |  | 10003085
[8 empty] | 10003072 | Para_ModulControler_Ctr28_deadband | Para_ModulControler_Ctr28_deadband | 5367 | Para_ModulControler_Ctr28_deadband |  | 10003072
[8 empty] | 10003074 | Para_ModulControler_Ctr28_dW_down | Para_ModulControler_Ctr28_dW_down | 5368 | Para_ModulControler_Ctr28_dW_down |  | 10003074
[8 empty] | 10003077 | Para_ModulControler_Ctr28_dW_up | Para_ModulControler_Ctr28_dW_up | 5369 | Para_ModulControler_Ctr28_dW_up |  | 10003077
[8 empty] | 10003076 | Para_ModulControler_Ctr28_dY_max | Para_ModulControler_Ctr28_dY_max | 5370 | Para_ModulControler_Ctr28_dY_max |  | 10003076
[8 empty] | 10003089 | Para_ModulControler_Ctr28_IComp | Para_ModulControler_Ctr28_IComp | 5371 | Para_ModulControler_Ctr28_IComp |  | 10003089
[8 empty] | 10003079 | Para_ModulControler_Ctr28_Kp_manualAdjust | Para_ModulControler_Ctr28_Kp_manualAdjust | 5372 | Para_ModulControler_Ctr28_Kp_manualAdjust |  | 10003079
[8 empty] | 10003078 | Para_ModulControler_Ctr28_nvert | Para_ModulControler_Ctr28_nvert | 5373 | Para_ModulControler_Ctr28_nvert |  | 10003078
[8 empty] | 10003088 | Para_ModulControler_Ctr28_PComp | Para_ModulControler_Ctr28_PComp | 5374 | Para_ModulControler_Ctr28_PComp |  | 10003088
[8 empty] | 10003075 | Para_ModulControler_Ctr28_t_min_pulse_down | Para_ModulControler_Ctr28_t_min_pulse_down | 5375 | Para_ModulControler_Ctr28_t_min_pulse_down |  | 10003075
[8 empty] | 10003080 | Para_ModulControler_Ctr28_t_min_pulse_up | Para_ModulControler_Ctr28_t_min_pulse_up | 5376 | Para_ModulControler_Ctr28_t_min_pulse_up |  | 10003080
[8 empty] | 10003082 | Para_ModulControler_Ctr28_t_period_down | Para_ModulControler_Ctr28_t_period_down | 5377 | Para_ModulControler_Ctr28_t_period_down |  | 10003082
[8 empty] | 10003083 | Para_ModulControler_Ctr28_t_period_up | Para_ModulControler_Ctr28_t_period_up | 5378 | Para_ModulControler_Ctr28_t_period_up |  | 10003083
[8 empty] | 10003084 | Para_ModulControler_Ctr28_Tn_manualAdjust | Para_ModulControler_Ctr28_Tn_manualAdjust | 5379 | Para_ModulControler_Ctr28_Tn_manualAdjust |  | 10003084
[8 empty] | 10003081 | Para_ModulControler_Ctr28_Tv_manualAdjust | Para_ModulControler_Ctr28_Tv_manualAdjust | 5380 | Para_ModulControler_Ctr28_Tv_manualAdjust |  | 10003081
[8 empty] | 10003092 | Para_ModulControler_Ctr28_WMax | Para_ModulControler_Ctr28_WMax | 5381 | Para_ModulControler_Ctr28_WMax |  | 10003092
[8 empty] | 10003091 | Para_ModulControler_Ctr28_WMin | Para_ModulControler_Ctr28_WMin | 5382 | Para_ModulControler_Ctr28_WMin |  | 10003091
[8 empty] | 10003093 | Para_ModulControler_Ctr28_WStart | Para_ModulControler_Ctr28_WStart | 5383 | Para_ModulControler_Ctr28_WStart |  | 10003093
[8 empty] | 10003086 | Para_ModulControler_Ctr28_Y_block | Para_ModulControler_Ctr28_Y_block | 5384 | Para_ModulControler_Ctr28_Y_block |  | 10003086
[8 empty] | 10003087 | Para_ModulControler_Ctr28_YMax | Para_ModulControler_Ctr28_YMax | 5385 | Para_ModulControler_Ctr28_YMax |  | 10003087
[8 empty] | 10003090 | Para_ModulControler_Ctr28_YMin | Para_ModulControler_Ctr28_YMin | 5386 | Para_ModulControler_Ctr28_YMin |  | 10003090
[8 empty] | 10003107 | Para_ModulControler_Ctr29_DComp | Para_ModulControler_Ctr29_DComp | 5387 | Para_ModulControler_Ctr29_DComp |  | 10003107
[8 empty] | 10003094 | Para_ModulControler_Ctr29_deadband | Para_ModulControler_Ctr29_deadband | 5388 | Para_ModulControler_Ctr29_deadband |  | 10003094
[8 empty] | 10003097 | Para_ModulControler_Ctr29_dW_down | Para_ModulControler_Ctr29_dW_down | 5389 | Para_ModulControler_Ctr29_dW_down |  | 10003097
[8 empty] | 10003096 | Para_ModulControler_Ctr29_dW_up | Para_ModulControler_Ctr29_dW_up | 5390 | Para_ModulControler_Ctr29_dW_up |  | 10003096
[8 empty] | 10003095 | Para_ModulControler_Ctr29_dY_max | Para_ModulControler_Ctr29_dY_max | 5391 | Para_ModulControler_Ctr29_dY_max |  | 10003095
[8 empty] | 10003109 | Para_ModulControler_Ctr29_IComp | Para_ModulControler_Ctr29_IComp | 5392 | Para_ModulControler_Ctr29_IComp |  | 10003109
[8 empty] | 10003099 | Para_ModulControler_Ctr29_Kp_manualAdjust | Para_ModulControler_Ctr29_Kp_manualAdjust | 5393 | Para_ModulControler_Ctr29_Kp_manualAdjust |  | 10003099
[8 empty] | 10003098 | Para_ModulControler_Ctr29_nvert | Para_ModulControler_Ctr29_nvert | 5394 | Para_ModulControler_Ctr29_nvert |  | 10003098
[8 empty] | 10003108 | Para_ModulControler_Ctr29_PComp | Para_ModulControler_Ctr29_PComp | 5395 | Para_ModulControler_Ctr29_PComp |  | 10003108
[8 empty] | 10003101 | Para_ModulControler_Ctr29_t_min_pulse_down | Para_ModulControler_Ctr29_t_min_pulse_down | 5396 | Para_ModulControler_Ctr29_t_min_pulse_down |  | 10003101
[8 empty] | 10003100 | Para_ModulControler_Ctr29_t_min_pulse_up | Para_ModulControler_Ctr29_t_min_pulse_up | 5397 | Para_ModulControler_Ctr29_t_min_pulse_up |  | 10003100
[8 empty] | 10003102 | Para_ModulControler_Ctr29_t_period_down | Para_ModulControler_Ctr29_t_period_down | 5398 | Para_ModulControler_Ctr29_t_period_down |  | 10003102
[8 empty] | 10003103 | Para_ModulControler_Ctr29_t_period_up | Para_ModulControler_Ctr29_t_period_up | 5399 | Para_ModulControler_Ctr29_t_period_up |  | 10003103
[8 empty] | 10003105 | Para_ModulControler_Ctr29_Tn_manualAdjust | Para_ModulControler_Ctr29_Tn_manualAdjust | 5400 | Para_ModulControler_Ctr29_Tn_manualAdjust |  | 10003105
[8 empty] | 10003106 | Para_ModulControler_Ctr29_Tv_manualAdjust | Para_ModulControler_Ctr29_Tv_manualAdjust | 5401 | Para_ModulControler_Ctr29_Tv_manualAdjust |  | 10003106
[8 empty] | 10003112 | Para_ModulControler_Ctr29_WMax | Para_ModulControler_Ctr29_WMax | 5402 | Para_ModulControler_Ctr29_WMax |  | 10003112
[8 empty] | 10003113 | Para_ModulControler_Ctr29_WMin | Para_ModulControler_Ctr29_WMin | 5403 | Para_ModulControler_Ctr29_WMin |  | 10003113
[8 empty] | 10003115 | Para_ModulControler_Ctr29_WStart | Para_ModulControler_Ctr29_WStart | 5404 | Para_ModulControler_Ctr29_WStart |  | 10003115
[8 empty] | 10003104 | Para_ModulControler_Ctr29_Y_block | Para_ModulControler_Ctr29_Y_block | 5405 | Para_ModulControler_Ctr29_Y_block |  | 10003104
[8 empty] | 10003111 | Para_ModulControler_Ctr29_YMax | Para_ModulControler_Ctr29_YMax | 5406 | Para_ModulControler_Ctr29_YMax |  | 10003111
[8 empty] | 10003110 | Para_ModulControler_Ctr29_YMin | Para_ModulControler_Ctr29_YMin | 5407 | Para_ModulControler_Ctr29_YMin |  | 10003110
[8 empty] | 10000197 | Para_ModulControler_Ctr2_DComp | Para_ModulControler_Ctr2_DComp | 5408 | Para_ModulControler_Ctr2_DComp |  | 10000197
[8 empty] | 10000199 | Para_ModulControler_Ctr2_deadband | Para_ModulControler_Ctr2_deadband | 5409 | Para_ModulControler_Ctr2_deadband |  | 10000199
[8 empty] | 10000227 | Para_ModulControler_Ctr2_dY_max | Para_ModulControler_Ctr2_dY_max | 5410 | Para_ModulControler_Ctr2_dY_max |  | 10000227
[8 empty] | 10000202 | Para_ModulControler_Ctr2_IComp | Para_ModulControler_Ctr2_IComp | 5411 | Para_ModulControler_Ctr2_IComp |  | 10000202
[8 empty] | 10000766 | Para_ModulControler_Ctr2_Kp_manualAdjust | Para_ModulControler_Ctr2_Kp_manualAdjust | 5412 | Para_ModulControler_Ctr2_Kp_manualAdjust |  | 10000766
[8 empty] | 10000201 | Para_ModulControler_Ctr2_nvert | Para_ModulControler_Ctr2_nvert | 5413 | Para_ModulControler_Ctr2_nvert |  | 10000201
[8 empty] | 10000212 | Para_ModulControler_Ctr2_PComp | Para_ModulControler_Ctr2_PComp | 5414 | Para_ModulControler_Ctr2_PComp |  | 10000212
[8 empty] | 10003037 | Para_ModulControler_Ctr2_ScaleMax | Para_ModulControler_Ctr2_ScaleMax | 5415 | Para_ModulControler_Ctr2_ScaleMax |  | 10003037
[8 empty] | 10003046 | Para_ModulControler_Ctr2_ScaleMin | Para_ModulControler_Ctr2_ScaleMin | 5416 | Para_ModulControler_Ctr2_ScaleMin |  | 10003046
[8 empty] | 10000767 | Para_ModulControler_Ctr2_t_min_pulse_down | Para_ModulControler_Ctr2_t_min_pulse_down | 5417 | Para_ModulControler_Ctr2_t_min_pulse_down |  | 10000767
[8 empty] | 10000765 | Para_ModulControler_Ctr2_t_min_pulse_up | Para_ModulControler_Ctr2_t_min_pulse_up | 5418 | Para_ModulControler_Ctr2_t_min_pulse_up |  | 10000765
[8 empty] | 10000768 | Para_ModulControler_Ctr2_t_period_down | Para_ModulControler_Ctr2_t_period_down | 5419 | Para_ModulControler_Ctr2_t_period_down |  | 10000768
[8 empty] | 10000769 | Para_ModulControler_Ctr2_t_period_up | Para_ModulControler_Ctr2_t_period_up | 5420 | Para_ModulControler_Ctr2_t_period_up |  | 10000769
[8 empty] | 10000770 | Para_ModulControler_Ctr2_Tn_manualAdjust | Para_ModulControler_Ctr2_Tn_manualAdjust | 5421 | Para_ModulControler_Ctr2_Tn_manualAdjust |  | 10000770
[8 empty] | 10000772 | Para_ModulControler_Ctr2_Tv_manualAdjust | Para_ModulControler_Ctr2_Tv_manualAdjust | 5422 | Para_ModulControler_Ctr2_Tv_manualAdjust |  | 10000772
[8 empty] | 10000215 | Para_ModulControler_Ctr2_WMax | Para_ModulControler_Ctr2_WMax | 5423 | Para_ModulControler_Ctr2_WMax |  | 10000215
[8 empty] | 10000218 | Para_ModulControler_Ctr2_WMin | Para_ModulControler_Ctr2_WMin | 5424 | Para_ModulControler_Ctr2_WMin |  | 10000218
[8 empty] | 10000219 | Para_ModulControler_Ctr2_WRampNeg | Para_ModulControler_Ctr2_WRampNeg | 5425 | Para_ModulControler_Ctr2_WRampNeg |  | 10000219
[8 empty] | 10000222 | Para_ModulControler_Ctr2_WRampPos | Para_ModulControler_Ctr2_WRampPos | 5426 | Para_ModulControler_Ctr2_WRampPos |  | 10000222
[8 empty] | 10000223 | Para_ModulControler_Ctr2_WStart | Para_ModulControler_Ctr2_WStart | 5427 | Para_ModulControler_Ctr2_WStart |  | 10000223
[8 empty] | 10000224 | Para_ModulControler_Ctr2_Y_block | Para_ModulControler_Ctr2_Y_block | 5428 | Para_ModulControler_Ctr2_Y_block |  | 10000224
[8 empty] | 10000225 | Para_ModulControler_Ctr2_YMax | Para_ModulControler_Ctr2_YMax | 5429 | Para_ModulControler_Ctr2_YMax |  | 10000225
[8 empty] | 10000226 | Para_ModulControler_Ctr2_YMin | Para_ModulControler_Ctr2_YMin | 5430 | Para_ModulControler_Ctr2_YMin |  | 10000226
[8 empty] | 10008812 | Para_ModulControler_Ctr30_DComp | Para_ModulControler_Ctr30_DComp | 5431 | Para_ModulControler_Ctr30_DComp |  | 10008812
[8 empty] | 10008847 | Para_ModulControler_Ctr30_deadband | Para_ModulControler_Ctr30_deadband | 5432 | Para_ModulControler_Ctr30_deadband |  | 10008847
[8 empty] | 10008848 | Para_ModulControler_Ctr30_dW_down | Para_ModulControler_Ctr30_dW_down | 5433 | Para_ModulControler_Ctr30_dW_down |  | 10008848
[8 empty] | 10008849 | Para_ModulControler_Ctr30_dW_up | Para_ModulControler_Ctr30_dW_up | 5434 | Para_ModulControler_Ctr30_dW_up |  | 10008849
[8 empty] | 10008850 | Para_ModulControler_Ctr30_dY_max | Para_ModulControler_Ctr30_dY_max | 5435 | Para_ModulControler_Ctr30_dY_max |  | 10008850
[8 empty] | 10008814 | Para_ModulControler_Ctr30_IComp | Para_ModulControler_Ctr30_IComp | 5436 | Para_ModulControler_Ctr30_IComp |  | 10008814
[8 empty] | 10008853 | Para_ModulControler_Ctr30_Kp_manualAdjust | Para_ModulControler_Ctr30_Kp_manualAdjust | 5437 | Para_ModulControler_Ctr30_Kp_manualAdjust |  | 10008853
[8 empty] | 10008851 | Para_ModulControler_Ctr30_nvert | Para_ModulControler_Ctr30_nvert | 5438 | Para_ModulControler_Ctr30_nvert |  | 10008851
[8 empty] | 10008816 | Para_ModulControler_Ctr30_PComp | Para_ModulControler_Ctr30_PComp | 5439 | Para_ModulControler_Ctr30_PComp |  | 10008816
[8 empty] | 10008852 | Para_ModulControler_Ctr30_t_min_pulse_down | Para_ModulControler_Ctr30_t_min_pulse_down | 5440 | Para_ModulControler_Ctr30_t_min_pulse_down |  | 10008852
[8 empty] | 10008856 | Para_ModulControler_Ctr30_t_min_pulse_up | Para_ModulControler_Ctr30_t_min_pulse_up | 5441 | Para_ModulControler_Ctr30_t_min_pulse_up |  | 10008856
[8 empty] | 10008854 | Para_ModulControler_Ctr30_t_period_down | Para_ModulControler_Ctr30_t_period_down | 5442 | Para_ModulControler_Ctr30_t_period_down |  | 10008854
[8 empty] | 10008855 | Para_ModulControler_Ctr30_t_period_up | Para_ModulControler_Ctr30_t_period_up | 5443 | Para_ModulControler_Ctr30_t_period_up |  | 10008855
[8 empty] | 10008857 | Para_ModulControler_Ctr30_Tn_manualAdjust | Para_ModulControler_Ctr30_Tn_manualAdjust | 5444 | Para_ModulControler_Ctr30_Tn_manualAdjust |  | 10008857
[8 empty] | 10008858 | Para_ModulControler_Ctr30_Tv_manualAdjust | Para_ModulControler_Ctr30_Tv_manualAdjust | 5445 | Para_ModulControler_Ctr30_Tv_manualAdjust |  | 10008858
[8 empty] | 10008817 | Para_ModulControler_Ctr30_WMax | Para_ModulControler_Ctr30_WMax | 5446 | Para_ModulControler_Ctr30_WMax |  | 10008817
[8 empty] | 10008819 | Para_ModulControler_Ctr30_WMin | Para_ModulControler_Ctr30_WMin | 5447 | Para_ModulControler_Ctr30_WMin |  | 10008819
[8 empty] | 10008820 | Para_ModulControler_Ctr30_WStart | Para_ModulControler_Ctr30_WStart | 5448 | Para_ModulControler_Ctr30_WStart |  | 10008820
[8 empty] | 10008860 | Para_ModulControler_Ctr30_Y_block | Para_ModulControler_Ctr30_Y_block | 5449 | Para_ModulControler_Ctr30_Y_block |  | 10008860
[8 empty] | 10008815 | Para_ModulControler_Ctr30_YMax | Para_ModulControler_Ctr30_YMax | 5450 | Para_ModulControler_Ctr30_YMax |  | 10008815
[8 empty] | 10008818 | Para_ModulControler_Ctr30_YMin | Para_ModulControler_Ctr30_YMin | 5451 | Para_ModulControler_Ctr30_YMin |  | 10008818
[8 empty] | 10008807 | Para_ModulControler_Ctr31_DComp | Para_ModulControler_Ctr31_DComp | 5452 | Para_ModulControler_Ctr31_DComp |  | 10008807
[8 empty] | 10008835 | Para_ModulControler_Ctr31_deadband | Para_ModulControler_Ctr31_deadband | 5453 | Para_ModulControler_Ctr31_deadband |  | 10008835
[8 empty] | 10008836 | Para_ModulControler_Ctr31_dW_down | Para_ModulControler_Ctr31_dW_down | 5454 | Para_ModulControler_Ctr31_dW_down |  | 10008836
[8 empty] | 10008837 | Para_ModulControler_Ctr31_dW_up | Para_ModulControler_Ctr31_dW_up | 5455 | Para_ModulControler_Ctr31_dW_up |  | 10008837
[8 empty] | 10008838 | Para_ModulControler_Ctr31_dY_max | Para_ModulControler_Ctr31_dY_max | 5456 | Para_ModulControler_Ctr31_dY_max |  | 10008838
[8 empty] | 10008808 | Para_ModulControler_Ctr31_IComp | Para_ModulControler_Ctr31_IComp | 5457 | Para_ModulControler_Ctr31_IComp |  | 10008808
[8 empty] | 10008840 | Para_ModulControler_Ctr31_Kp_manualAdjust | Para_ModulControler_Ctr31_Kp_manualAdjust | 5458 | Para_ModulControler_Ctr31_Kp_manualAdjust |  | 10008840
[8 empty] | 10008839 | Para_ModulControler_Ctr31_nvert | Para_ModulControler_Ctr31_nvert | 5459 | Para_ModulControler_Ctr31_nvert |  | 10008839
[8 empty] | 10008810 | Para_ModulControler_Ctr31_PComp | Para_ModulControler_Ctr31_PComp | 5460 | Para_ModulControler_Ctr31_PComp |  | 10008810
[8 empty] | 10008841 | Para_ModulControler_Ctr31_t_min_pulse_down | Para_ModulControler_Ctr31_t_min_pulse_down | 5461 | Para_ModulControler_Ctr31_t_min_pulse_down |  | 10008841
[8 empty] | 10008842 | Para_ModulControler_Ctr31_t_min_pulse_up | Para_ModulControler_Ctr31_t_min_pulse_up | 5462 | Para_ModulControler_Ctr31_t_min_pulse_up |  | 10008842
[8 empty] | 10008843 | Para_ModulControler_Ctr31_t_period_down | Para_ModulControler_Ctr31_t_period_down | 5463 | Para_ModulControler_Ctr31_t_period_down |  | 10008843
[8 empty] | 10008844 | Para_ModulControler_Ctr31_t_period_up | Para_ModulControler_Ctr31_t_period_up | 5464 | Para_ModulControler_Ctr31_t_period_up |  | 10008844
[8 empty] | 10008845 | Para_ModulControler_Ctr31_Tn_manualAdjust | Para_ModulControler_Ctr31_Tn_manualAdjust | 5465 | Para_ModulControler_Ctr31_Tn_manualAdjust |  | 10008845
[8 empty] | 10008846 | Para_ModulControler_Ctr31_Tv_manualAdjust | Para_ModulControler_Ctr31_Tv_manualAdjust | 5466 | Para_ModulControler_Ctr31_Tv_manualAdjust |  | 10008846
[8 empty] | 10008813 | Para_ModulControler_Ctr31_WMax | Para_ModulControler_Ctr31_WMax | 5467 | Para_ModulControler_Ctr31_WMax |  | 10008813
[8 empty] | 10008833 | Para_ModulControler_Ctr31_WMin | Para_ModulControler_Ctr31_WMin | 5468 | Para_ModulControler_Ctr31_WMin |  | 10008833
[8 empty] | 10008834 | Para_ModulControler_Ctr31_WStart | Para_ModulControler_Ctr31_WStart | 5469 | Para_ModulControler_Ctr31_WStart |  | 10008834
[8 empty] | 10008861 | Para_ModulControler_Ctr31_Y_block | Para_ModulControler_Ctr31_Y_block | 5470 | Para_ModulControler_Ctr31_Y_block |  | 10008861
[8 empty] | 10008811 | Para_ModulControler_Ctr31_YMax | Para_ModulControler_Ctr31_YMax | 5471 | Para_ModulControler_Ctr31_YMax |  | 10008811
[8 empty] | 10008809 | Para_ModulControler_Ctr31_YMin | Para_ModulControler_Ctr31_YMin | 5472 | Para_ModulControler_Ctr31_YMin |  | 10008809
[8 empty] | 10008925 | Para_ModulControler_Ctr32_Ctr_Mns_AnaIn_Setp_Enable | Para_ModulControler_Ctr32_Ctr_Mns_AnaIn_Setp_Enable | 5473 | Para_ModulControler_Ctr32_Ctr_Mns_AnaIn_Setp_Enable |  | 10008925
[8 empty] | 10008928 | Para_ModulControler_Ctr32_Ctr_Mns_Setp_ScalMax | Para_ModulControler_Ctr32_Ctr_Mns_Setp_ScalMax | 5474 | Para_ModulControler_Ctr32_Ctr_Mns_Setp_ScalMax |  | 10008928
[8 empty] | 10008964 | Para_ModulControler_Ctr32_Ctr_Mns_Setp_ScalMin | Para_ModulControler_Ctr32_Ctr_Mns_Setp_ScalMin | 5475 | Para_ModulControler_Ctr32_Ctr_Mns_Setp_ScalMin |  | 10008964
[8 empty] | 10008926 | Para_ModulControler_Ctr32_Ctr_Mns_Setp_Set4mA | Para_ModulControler_Ctr32_Ctr_Mns_Setp_Set4mA | 5476 | Para_ModulControler_Ctr32_Ctr_Mns_Setp_Set4mA |  | 10008926
[8 empty] | 10008863 | Para_ModulControler_Ctr32_DComp | Para_ModulControler_Ctr32_DComp | 5477 | Para_ModulControler_Ctr32_DComp |  | 10008863
[8 empty] | 10008824 | Para_ModulControler_Ctr32_deadband | Para_ModulControler_Ctr32_deadband | 5478 | Para_ModulControler_Ctr32_deadband |  | 10008824
[8 empty] | 10008825 | Para_ModulControler_Ctr32_dW_down | Para_ModulControler_Ctr32_dW_down | 5479 | Para_ModulControler_Ctr32_dW_down |  | 10008825
[8 empty] | 10008826 | Para_ModulControler_Ctr32_dW_up | Para_ModulControler_Ctr32_dW_up | 5480 | Para_ModulControler_Ctr32_dW_up |  | 10008826
[8 empty] | 10008828 | Para_ModulControler_Ctr32_dY_max | Para_ModulControler_Ctr32_dY_max | 5481 | Para_ModulControler_Ctr32_dY_max |  | 10008828
[8 empty] | 10008864 | Para_ModulControler_Ctr32_IComp | Para_ModulControler_Ctr32_IComp | 5482 | Para_ModulControler_Ctr32_IComp |  | 10008864
[8 empty] | 10008829 | Para_ModulControler_Ctr32_Kp_manualAdjust | Para_ModulControler_Ctr32_Kp_manualAdjust | 5483 | Para_ModulControler_Ctr32_Kp_manualAdjust |  | 10008829
[8 empty] | 10008804 | Para_ModulControler_Ctr32_Limit_DemGenerate_Lim_Off | Para_ModulControler_Ctr32_Limit_DemGenerate_Lim_Off | 5484 | Para_ModulControler_Ctr32_Limit_DemGenerate_Lim_Off |  | 10008804
[8 empty] | 10008797 | Para_ModulControler_Ctr32_Limit_DemGenerate_Lim_On | Para_ModulControler_Ctr32_Limit_DemGenerate_Lim_On | 5485 | Para_ModulControler_Ctr32_Limit_DemGenerate_Lim_On |  | 10008797
[8 empty] | 10008931 | Para_ModulControler_Ctr32_Limit_LimOnOff_aktiv | Para_ModulControler_Ctr32_Limit_LimOnOff_aktiv | 5486 | Para_ModulControler_Ctr32_Limit_LimOnOff_aktiv |  | 10008931
[8 empty] | 10008800 | Para_ModulControler_Ctr32_Limit_MainsExport_max | Para_ModulControler_Ctr32_Limit_MainsExport_max | 5487 | Para_ModulControler_Ctr32_Limit_MainsExport_max |  | 10008800
[8 empty] | 10008803 | Para_ModulControler_Ctr32_Limit_MainsExport_max_trip | Para_ModulControler_Ctr32_Limit_MainsExport_max_trip | 5488 | Para_ModulControler_Ctr32_Limit_MainsExport_max_trip |  | 10008803
[8 empty] | 10008802 | Para_ModulControler_Ctr32_Limit_MainsImport_max | Para_ModulControler_Ctr32_Limit_MainsImport_max | 5489 | Para_ModulControler_Ctr32_Limit_MainsImport_max |  | 10008802
[8 empty] | 10008801 | Para_ModulControler_Ctr32_Limit_MainsImport_max_trip | Para_ModulControler_Ctr32_Limit_MainsImport_max_trip | 5490 | Para_ModulControler_Ctr32_Limit_MainsImport_max_trip |  | 10008801
[8 empty] | 10008967 | Para_ModulControler_Ctr32_Limit_Time_Dem_Off_delay | Para_ModulControler_Ctr32_Limit_Time_Dem_Off_delay | 5491 | Para_ModulControler_Ctr32_Limit_Time_Dem_Off_delay |  | 10008967
[8 empty] | 10008965 | Para_ModulControler_Ctr32_Limit_Time_Dem_On_delay | Para_ModulControler_Ctr32_Limit_Time_Dem_On_delay | 5492 | Para_ModulControler_Ctr32_Limit_Time_Dem_On_delay |  | 10008965
[8 empty] | 10008827 | Para_ModulControler_Ctr32_nvert | Para_ModulControler_Ctr32_nvert | 5493 | Para_ModulControler_Ctr32_nvert |  | 10008827
[8 empty] | 10008963 | Para_ModulControler_Ctr32_P_Mns_AnaIn_ScalMax | Para_ModulControler_Ctr32_P_Mns_AnaIn_ScalMax | 5494 | Para_ModulControler_Ctr32_P_Mns_AnaIn_ScalMax |  | 10008963
[8 empty] | 10008927 | Para_ModulControler_Ctr32_P_Mns_AnaIn_ScalMin | Para_ModulControler_Ctr32_P_Mns_AnaIn_ScalMin | 5495 | Para_ModulControler_Ctr32_P_Mns_AnaIn_ScalMin |  | 10008927
[8 empty] | 10008929 | Para_ModulControler_Ctr32_P_Mns_AnaIn_Set4mA | Para_ModulControler_Ctr32_P_Mns_AnaIn_Set4mA | 5496 | Para_ModulControler_Ctr32_P_Mns_AnaIn_Set4mA |  | 10008929
[8 empty] | 10008930 | Para_ModulControler_Ctr32_P_Mns_MMU_Enable | Para_ModulControler_Ctr32_P_Mns_MMU_Enable | 5497 | Para_ModulControler_Ctr32_P_Mns_MMU_Enable |  | 10008930
[8 empty] | 10008866 | Para_ModulControler_Ctr32_PComp | Para_ModulControler_Ctr32_PComp | 5498 | Para_ModulControler_Ctr32_PComp |  | 10008866
[8 empty] | 10008830 | Para_ModulControler_Ctr32_t_min_pulse_down | Para_ModulControler_Ctr32_t_min_pulse_down | 5499 | Para_ModulControler_Ctr32_t_min_pulse_down |  | 10008830
[8 empty] | 10008831 | Para_ModulControler_Ctr32_t_min_pulse_up | Para_ModulControler_Ctr32_t_min_pulse_up | 5500 | Para_ModulControler_Ctr32_t_min_pulse_up |  | 10008831
[8 empty] | 10008868 | Para_ModulControler_Ctr32_t_period_down | Para_ModulControler_Ctr32_t_period_down | 5501 | Para_ModulControler_Ctr32_t_period_down |  | 10008868
[8 empty] | 10008870 | Para_ModulControler_Ctr32_t_period_up | Para_ModulControler_Ctr32_t_period_up | 5502 | Para_ModulControler_Ctr32_t_period_up |  | 10008870
[8 empty] | 10008871 | Para_ModulControler_Ctr32_Tn_manualAdjust | Para_ModulControler_Ctr32_Tn_manualAdjust | 5503 | Para_ModulControler_Ctr32_Tn_manualAdjust |  | 10008871
[8 empty] | 10008872 | Para_ModulControler_Ctr32_Tv_manualAdjust | Para_ModulControler_Ctr32_Tv_manualAdjust | 5504 | Para_ModulControler_Ctr32_Tv_manualAdjust |  | 10008872
[8 empty] | 10008821 | Para_ModulControler_Ctr32_WMax | Para_ModulControler_Ctr32_WMax | 5505 | Para_ModulControler_Ctr32_WMax |  | 10008821
[8 empty] | 10008822 | Para_ModulControler_Ctr32_WMin | Para_ModulControler_Ctr32_WMin | 5506 | Para_ModulControler_Ctr32_WMin |  | 10008822
[8 empty] | 10008823 | Para_ModulControler_Ctr32_WStart | Para_ModulControler_Ctr32_WStart | 5507 | Para_ModulControler_Ctr32_WStart |  | 10008823
[8 empty] | 10008874 | Para_ModulControler_Ctr32_Y_block | Para_ModulControler_Ctr32_Y_block | 5508 | Para_ModulControler_Ctr32_Y_block |  | 10008874
[8 empty] | 10008867 | Para_ModulControler_Ctr32_YMax | Para_ModulControler_Ctr32_YMax | 5509 | Para_ModulControler_Ctr32_YMax |  | 10008867
[8 empty] | 10008869 | Para_ModulControler_Ctr32_YMin | Para_ModulControler_Ctr32_YMin | 5510 | Para_ModulControler_Ctr32_YMin |  | 10008869
[8 empty] | 10000229 | Para_ModulControler_Ctr3_DComp | Para_ModulControler_Ctr3_DComp | 5511 | Para_ModulControler_Ctr3_DComp |  | 10000229
[8 empty] | 10000231 | Para_ModulControler_Ctr3_deadband | Para_ModulControler_Ctr3_deadband | 5512 | Para_ModulControler_Ctr3_deadband |  | 10000231
[8 empty] | 10000249 | Para_ModulControler_Ctr3_dY_max | Para_ModulControler_Ctr3_dY_max | 5513 | Para_ModulControler_Ctr3_dY_max |  | 10000249
[8 empty] | 10000234 | Para_ModulControler_Ctr3_IComp | Para_ModulControler_Ctr3_IComp | 5514 | Para_ModulControler_Ctr3_IComp |  | 10000234
[8 empty] | 10000771 | Para_ModulControler_Ctr3_Kp_manualAdjust | Para_ModulControler_Ctr3_Kp_manualAdjust | 5515 | Para_ModulControler_Ctr3_Kp_manualAdjust |  | 10000771
[8 empty] | 10000233 | Para_ModulControler_Ctr3_nvert | Para_ModulControler_Ctr3_nvert | 5516 | Para_ModulControler_Ctr3_nvert |  | 10000233
[8 empty] | 10000236 | Para_ModulControler_Ctr3_PComp | Para_ModulControler_Ctr3_PComp | 5517 | Para_ModulControler_Ctr3_PComp |  | 10000236
[8 empty] | 10003043 | Para_ModulControler_Ctr3_ScaleMax | Para_ModulControler_Ctr3_ScaleMax | 5518 | Para_ModulControler_Ctr3_ScaleMax |  | 10003043
[8 empty] | 10003047 | Para_ModulControler_Ctr3_ScaleMin | Para_ModulControler_Ctr3_ScaleMin | 5519 | Para_ModulControler_Ctr3_ScaleMin |  | 10003047
[8 empty] | 10000773 | Para_ModulControler_Ctr3_t_min_pulse_down | Para_ModulControler_Ctr3_t_min_pulse_down | 5520 | Para_ModulControler_Ctr3_t_min_pulse_down |  | 10000773
[8 empty] | 10000776 | Para_ModulControler_Ctr3_t_min_pulse_up | Para_ModulControler_Ctr3_t_min_pulse_up | 5521 | Para_ModulControler_Ctr3_t_min_pulse_up |  | 10000776
[8 empty] | 10000774 | Para_ModulControler_Ctr3_t_period_down | Para_ModulControler_Ctr3_t_period_down | 5522 | Para_ModulControler_Ctr3_t_period_down |  | 10000774
[8 empty] | 10001009 | Para_ModulControler_Ctr3_t_period_up | Para_ModulControler_Ctr3_t_period_up | 5523 | Para_ModulControler_Ctr3_t_period_up |  | 10001009
[8 empty] | 10000775 | Para_ModulControler_Ctr3_Tn_manualAdjust | Para_ModulControler_Ctr3_Tn_manualAdjust | 5524 | Para_ModulControler_Ctr3_Tn_manualAdjust |  | 10000775
[8 empty] | 10000779 | Para_ModulControler_Ctr3_Tv_manualAdjust | Para_ModulControler_Ctr3_Tv_manualAdjust | 5525 | Para_ModulControler_Ctr3_Tv_manualAdjust |  | 10000779
[8 empty] | 10000241 | Para_ModulControler_Ctr3_WMax | Para_ModulControler_Ctr3_WMax | 5526 | Para_ModulControler_Ctr3_WMax |  | 10000241
[8 empty] | 10000243 | Para_ModulControler_Ctr3_WMin | Para_ModulControler_Ctr3_WMin | 5527 | Para_ModulControler_Ctr3_WMin |  | 10000243
[8 empty] | 10000247 | Para_ModulControler_Ctr3_WRampNeg | Para_ModulControler_Ctr3_WRampNeg | 5528 | Para_ModulControler_Ctr3_WRampNeg |  | 10000247
[8 empty] | 10000244 | Para_ModulControler_Ctr3_WRampPos | Para_ModulControler_Ctr3_WRampPos | 5529 | Para_ModulControler_Ctr3_WRampPos |  | 10000244
[8 empty] | 10000246 | Para_ModulControler_Ctr3_WStart | Para_ModulControler_Ctr3_WStart | 5530 | Para_ModulControler_Ctr3_WStart |  | 10000246
[8 empty] | 10000248 | Para_ModulControler_Ctr3_Y_block | Para_ModulControler_Ctr3_Y_block | 5531 | Para_ModulControler_Ctr3_Y_block |  | 10000248
[8 empty] | 10000251 | Para_ModulControler_Ctr3_YMax | Para_ModulControler_Ctr3_YMax | 5532 | Para_ModulControler_Ctr3_YMax |  | 10000251
[8 empty] | 10000245 | Para_ModulControler_Ctr3_YMin | Para_ModulControler_Ctr3_YMin | 5533 | Para_ModulControler_Ctr3_YMin |  | 10000245
[8 empty] | 10000253 | Para_ModulControler_Ctr4_DComp | Para_ModulControler_Ctr4_DComp | 5534 | Para_ModulControler_Ctr4_DComp |  | 10000253
[8 empty] | 10000252 | Para_ModulControler_Ctr4_deadband | Para_ModulControler_Ctr4_deadband | 5535 | Para_ModulControler_Ctr4_deadband |  | 10000252
[8 empty] | 10000262 | Para_ModulControler_Ctr4_dY_max | Para_ModulControler_Ctr4_dY_max | 5536 | Para_ModulControler_Ctr4_dY_max |  | 10000262
[8 empty] | 10000254 | Para_ModulControler_Ctr4_IComp | Para_ModulControler_Ctr4_IComp | 5537 | Para_ModulControler_Ctr4_IComp |  | 10000254
[8 empty] | 10000777 | Para_ModulControler_Ctr4_Kp_manualAdjust | Para_ModulControler_Ctr4_Kp_manualAdjust | 5538 | Para_ModulControler_Ctr4_Kp_manualAdjust |  | 10000777
[8 empty] | 10000250 | Para_ModulControler_Ctr4_nvert | Para_ModulControler_Ctr4_nvert | 5539 | Para_ModulControler_Ctr4_nvert |  | 10000250
[8 empty] | 10000256 | Para_ModulControler_Ctr4_PComp | Para_ModulControler_Ctr4_PComp | 5540 | Para_ModulControler_Ctr4_PComp |  | 10000256
[8 empty] | 10003045 | Para_ModulControler_Ctr4_ScaleMax | Para_ModulControler_Ctr4_ScaleMax | 5541 | Para_ModulControler_Ctr4_ScaleMax |  | 10003045
[8 empty] | 10003048 | Para_ModulControler_Ctr4_ScaleMin | Para_ModulControler_Ctr4_ScaleMin | 5542 | Para_ModulControler_Ctr4_ScaleMin |  | 10003048
[8 empty] | 10000778 | Para_ModulControler_Ctr4_t_min_pulse_down | Para_ModulControler_Ctr4_t_min_pulse_down | 5543 | Para_ModulControler_Ctr4_t_min_pulse_down |  | 10000778
[8 empty] | 10000781 | Para_ModulControler_Ctr4_t_min_pulse_up | Para_ModulControler_Ctr4_t_min_pulse_up | 5544 | Para_ModulControler_Ctr4_t_min_pulse_up |  | 10000781
[8 empty] | 10000780 | Para_ModulControler_Ctr4_t_period_down | Para_ModulControler_Ctr4_t_period_down | 5545 | Para_ModulControler_Ctr4_t_period_down |  | 10000780
[8 empty] | 10000783 | Para_ModulControler_Ctr4_t_period_up | Para_ModulControler_Ctr4_t_period_up | 5546 | Para_ModulControler_Ctr4_t_period_up |  | 10000783
[8 empty] | 10000782 | Para_ModulControler_Ctr4_Tn_manualAdjust | Para_ModulControler_Ctr4_Tn_manualAdjust | 5547 | Para_ModulControler_Ctr4_Tn_manualAdjust |  | 10000782
[8 empty] | 10000784 | Para_ModulControler_Ctr4_Tv_manualAdjust | Para_ModulControler_Ctr4_Tv_manualAdjust | 5548 | Para_ModulControler_Ctr4_Tv_manualAdjust |  | 10000784
[8 empty] | 10000255 | Para_ModulControler_Ctr4_WMax | Para_ModulControler_Ctr4_WMax | 5549 | Para_ModulControler_Ctr4_WMax |  | 10000255
[8 empty] | 10000257 | Para_ModulControler_Ctr4_WMin | Para_ModulControler_Ctr4_WMin | 5550 | Para_ModulControler_Ctr4_WMin |  | 10000257
[8 empty] | 10000259 | Para_ModulControler_Ctr4_WRampNeg | Para_ModulControler_Ctr4_WRampNeg | 5551 | Para_ModulControler_Ctr4_WRampNeg |  | 10000259
[8 empty] | 10000258 | Para_ModulControler_Ctr4_WRampPos | Para_ModulControler_Ctr4_WRampPos | 5552 | Para_ModulControler_Ctr4_WRampPos |  | 10000258
[8 empty] | 10000260 | Para_ModulControler_Ctr4_WStart | Para_ModulControler_Ctr4_WStart | 5553 | Para_ModulControler_Ctr4_WStart |  | 10000260
[8 empty] | 10000261 | Para_ModulControler_Ctr4_Y_block | Para_ModulControler_Ctr4_Y_block | 5554 | Para_ModulControler_Ctr4_Y_block |  | 10000261
[8 empty] | 10000264 | Para_ModulControler_Ctr4_YMax | Para_ModulControler_Ctr4_YMax | 5555 | Para_ModulControler_Ctr4_YMax |  | 10000264
[8 empty] | 10000263 | Para_ModulControler_Ctr4_YMin | Para_ModulControler_Ctr4_YMin | 5556 | Para_ModulControler_Ctr4_YMin |  | 10000263
[8 empty] | 10000265 | Para_ModulControler_Ctr5_DComp | Para_ModulControler_Ctr5_DComp | 5557 | Para_ModulControler_Ctr5_DComp |  | 10000265
[8 empty] | 10000267 | Para_ModulControler_Ctr5_deadband | Para_ModulControler_Ctr5_deadband | 5558 | Para_ModulControler_Ctr5_deadband |  | 10000267
[8 empty] | 10000278 | Para_ModulControler_Ctr5_dY_max | Para_ModulControler_Ctr5_dY_max | 5559 | Para_ModulControler_Ctr5_dY_max |  | 10000278
[8 empty] | 10000266 | Para_ModulControler_Ctr5_IComp | Para_ModulControler_Ctr5_IComp | 5560 | Para_ModulControler_Ctr5_IComp |  | 10000266
[8 empty] | 10000787 | Para_ModulControler_Ctr5_Kp_manualAdjust | Para_ModulControler_Ctr5_Kp_manualAdjust | 5561 | Para_ModulControler_Ctr5_Kp_manualAdjust |  | 10000787
[8 empty] | 10000268 | Para_ModulControler_Ctr5_nvert | Para_ModulControler_Ctr5_nvert | 5562 | Para_ModulControler_Ctr5_nvert |  | 10000268
[8 empty] | 10000269 | Para_ModulControler_Ctr5_PComp | Para_ModulControler_Ctr5_PComp | 5563 | Para_ModulControler_Ctr5_PComp |  | 10000269
[8 empty] | 10003040 | Para_ModulControler_Ctr5_ScaleMax | Para_ModulControler_Ctr5_ScaleMax | 5564 | Para_ModulControler_Ctr5_ScaleMax |  | 10003040
[8 empty] | 10003049 | Para_ModulControler_Ctr5_ScaleMin | Para_ModulControler_Ctr5_ScaleMin | 5565 | Para_ModulControler_Ctr5_ScaleMin |  | 10003049
[8 empty] | 10000785 | Para_ModulControler_Ctr5_t_min_pulse_down | Para_ModulControler_Ctr5_t_min_pulse_down | 5566 | Para_ModulControler_Ctr5_t_min_pulse_down |  | 10000785
[8 empty] | 10000791 | Para_ModulControler_Ctr5_t_min_pulse_up | Para_ModulControler_Ctr5_t_min_pulse_up | 5567 | Para_ModulControler_Ctr5_t_min_pulse_up |  | 10000791
[8 empty] | 10000788 | Para_ModulControler_Ctr5_t_period_down | Para_ModulControler_Ctr5_t_period_down | 5568 | Para_ModulControler_Ctr5_t_period_down |  | 10000788
[8 empty] | 10000786 | Para_ModulControler_Ctr5_t_period_up | Para_ModulControler_Ctr5_t_period_up | 5569 | Para_ModulControler_Ctr5_t_period_up |  | 10000786
[8 empty] | 10000789 | Para_ModulControler_Ctr5_Tn_manualAdjust | Para_ModulControler_Ctr5_Tn_manualAdjust | 5570 | Para_ModulControler_Ctr5_Tn_manualAdjust |  | 10000789
[8 empty] | 10000790 | Para_ModulControler_Ctr5_Tv_manualAdjust | Para_ModulControler_Ctr5_Tv_manualAdjust | 5571 | Para_ModulControler_Ctr5_Tv_manualAdjust |  | 10000790
[8 empty] | 10000270 | Para_ModulControler_Ctr5_WMax | Para_ModulControler_Ctr5_WMax | 5572 | Para_ModulControler_Ctr5_WMax |  | 10000270
[8 empty] | 10000272 | Para_ModulControler_Ctr5_WMin | Para_ModulControler_Ctr5_WMin | 5573 | Para_ModulControler_Ctr5_WMin |  | 10000272
[8 empty] | 10000273 | Para_ModulControler_Ctr5_WRampNeg | Para_ModulControler_Ctr5_WRampNeg | 5574 | Para_ModulControler_Ctr5_WRampNeg |  | 10000273
[8 empty] | 10000271 | Para_ModulControler_Ctr5_WRampPos | Para_ModulControler_Ctr5_WRampPos | 5575 | Para_ModulControler_Ctr5_WRampPos |  | 10000271
[8 empty] | 10000274 | Para_ModulControler_Ctr5_WStart | Para_ModulControler_Ctr5_WStart | 5576 | Para_ModulControler_Ctr5_WStart |  | 10000274
[8 empty] | 10000275 | Para_ModulControler_Ctr5_Y_block | Para_ModulControler_Ctr5_Y_block | 5577 | Para_ModulControler_Ctr5_Y_block |  | 10000275
[8 empty] | 10000277 | Para_ModulControler_Ctr5_YMax | Para_ModulControler_Ctr5_YMax | 5578 | Para_ModulControler_Ctr5_YMax |  | 10000277
[8 empty] | 10000276 | Para_ModulControler_Ctr5_YMin | Para_ModulControler_Ctr5_YMin | 5579 | Para_ModulControler_Ctr5_YMin |  | 10000276
[8 empty] | 10000281 | Para_ModulControler_Ctr6_DComp | Para_ModulControler_Ctr6_DComp | 5580 | Para_ModulControler_Ctr6_DComp |  | 10000281
[8 empty] | 10000280 | Para_ModulControler_Ctr6_deadband | Para_ModulControler_Ctr6_deadband | 5581 | Para_ModulControler_Ctr6_deadband |  | 10000280
[8 empty] | 10000298 | Para_ModulControler_Ctr6_dY_max | Para_ModulControler_Ctr6_dY_max | 5582 | Para_ModulControler_Ctr6_dY_max |  | 10000298
[8 empty] | 10000282 | Para_ModulControler_Ctr6_IComp | Para_ModulControler_Ctr6_IComp | 5583 | Para_ModulControler_Ctr6_IComp |  | 10000282
[8 empty] | 10000793 | Para_ModulControler_Ctr6_Kp_manualAdjust | Para_ModulControler_Ctr6_Kp_manualAdjust | 5584 | Para_ModulControler_Ctr6_Kp_manualAdjust |  | 10000793
[8 empty] | 10000283 | Para_ModulControler_Ctr6_nvert | Para_ModulControler_Ctr6_nvert | 5585 | Para_ModulControler_Ctr6_nvert |  | 10000283
[8 empty] | 10000285 | Para_ModulControler_Ctr6_PComp | Para_ModulControler_Ctr6_PComp | 5586 | Para_ModulControler_Ctr6_PComp |  | 10000285
[8 empty] | 10003044 | Para_ModulControler_Ctr6_ScaleMax | Para_ModulControler_Ctr6_ScaleMax | 5587 | Para_ModulControler_Ctr6_ScaleMax |  | 10003044
[8 empty] | 10003053 | Para_ModulControler_Ctr6_ScaleMin | Para_ModulControler_Ctr6_ScaleMin | 5588 | Para_ModulControler_Ctr6_ScaleMin |  | 10003053
[8 empty] | 10000795 | Para_ModulControler_Ctr6_t_min_pulse_down | Para_ModulControler_Ctr6_t_min_pulse_down | 5589 | Para_ModulControler_Ctr6_t_min_pulse_down |  | 10000795
[8 empty] | 10000792 | Para_ModulControler_Ctr6_t_min_pulse_up | Para_ModulControler_Ctr6_t_min_pulse_up | 5590 | Para_ModulControler_Ctr6_t_min_pulse_up |  | 10000792
[8 empty] | 10000794 | Para_ModulControler_Ctr6_t_period_down | Para_ModulControler_Ctr6_t_period_down | 5591 | Para_ModulControler_Ctr6_t_period_down |  | 10000794
[8 empty] | 10000796 | Para_ModulControler_Ctr6_t_period_up | Para_ModulControler_Ctr6_t_period_up | 5592 | Para_ModulControler_Ctr6_t_period_up |  | 10000796
[8 empty] | 10000799 | Para_ModulControler_Ctr6_Tn_manualAdjust | Para_ModulControler_Ctr6_Tn_manualAdjust | 5593 | Para_ModulControler_Ctr6_Tn_manualAdjust |  | 10000799
[8 empty] | 10000806 | Para_ModulControler_Ctr6_Tv_manualAdjust | Para_ModulControler_Ctr6_Tv_manualAdjust | 5594 | Para_ModulControler_Ctr6_Tv_manualAdjust |  | 10000806
[8 empty] | 10000286 | Para_ModulControler_Ctr6_WMax | Para_ModulControler_Ctr6_WMax | 5595 | Para_ModulControler_Ctr6_WMax |  | 10000286
[8 empty] | 10000288 | Para_ModulControler_Ctr6_WMin | Para_ModulControler_Ctr6_WMin | 5596 | Para_ModulControler_Ctr6_WMin |  | 10000288
[8 empty] | 10000290 | Para_ModulControler_Ctr6_WRampNeg | Para_ModulControler_Ctr6_WRampNeg | 5597 | Para_ModulControler_Ctr6_WRampNeg |  | 10000290
[8 empty] | 10000292 | Para_ModulControler_Ctr6_WRampPos | Para_ModulControler_Ctr6_WRampPos | 5598 | Para_ModulControler_Ctr6_WRampPos |  | 10000292
[8 empty] | 10000294 | Para_ModulControler_Ctr6_WStart | Para_ModulControler_Ctr6_WStart | 5599 | Para_ModulControler_Ctr6_WStart |  | 10000294
[8 empty] | 10000296 | Para_ModulControler_Ctr6_Y_block | Para_ModulControler_Ctr6_Y_block | 5600 | Para_ModulControler_Ctr6_Y_block |  | 10000296
[8 empty] | 10000297 | Para_ModulControler_Ctr6_YMax | Para_ModulControler_Ctr6_YMax | 5601 | Para_ModulControler_Ctr6_YMax |  | 10000297
[8 empty] | 10000299 | Para_ModulControler_Ctr6_YMin | Para_ModulControler_Ctr6_YMin | 5602 | Para_ModulControler_Ctr6_YMin |  | 10000299
[8 empty] | 10000303 | Para_ModulControler_Ctr7_DComp | Para_ModulControler_Ctr7_DComp | 5603 | Para_ModulControler_Ctr7_DComp |  | 10000303
[8 empty] | 10000305 | Para_ModulControler_Ctr7_deadband | Para_ModulControler_Ctr7_deadband | 5604 | Para_ModulControler_Ctr7_deadband |  | 10000305
[8 empty] | 10000316 | Para_ModulControler_Ctr7_dY_max | Para_ModulControler_Ctr7_dY_max | 5605 | Para_ModulControler_Ctr7_dY_max |  | 10000316
[8 empty] | 10000308 | Para_ModulControler_Ctr7_IComp | Para_ModulControler_Ctr7_IComp | 5606 | Para_ModulControler_Ctr7_IComp |  | 10000308
[8 empty] | 10000807 | Para_ModulControler_Ctr7_Kp_manualAdjust | Para_ModulControler_Ctr7_Kp_manualAdjust | 5607 | Para_ModulControler_Ctr7_Kp_manualAdjust |  | 10000807
[8 empty] | 10000307 | Para_ModulControler_Ctr7_nvert | Para_ModulControler_Ctr7_nvert | 5608 | Para_ModulControler_Ctr7_nvert |  | 10000307
[8 empty] | 10000306 | Para_ModulControler_Ctr7_PComp | Para_ModulControler_Ctr7_PComp | 5609 | Para_ModulControler_Ctr7_PComp |  | 10000306
[8 empty] | 10003042 | Para_ModulControler_Ctr7_ScaleMax | Para_ModulControler_Ctr7_ScaleMax | 5610 | Para_ModulControler_Ctr7_ScaleMax |  | 10003042
[8 empty] | 10003052 | Para_ModulControler_Ctr7_ScaleMin | Para_ModulControler_Ctr7_ScaleMin | 5611 | Para_ModulControler_Ctr7_ScaleMin |  | 10003052
[8 empty] | 10000810 | Para_ModulControler_Ctr7_t_min_pulse_down | Para_ModulControler_Ctr7_t_min_pulse_down | 5612 | Para_ModulControler_Ctr7_t_min_pulse_down |  | 10000810
[8 empty] | 10000809 | Para_ModulControler_Ctr7_t_min_pulse_up | Para_ModulControler_Ctr7_t_min_pulse_up | 5613 | Para_ModulControler_Ctr7_t_min_pulse_up |  | 10000809
[8 empty] | 10000808 | Para_ModulControler_Ctr7_t_period_down | Para_ModulControler_Ctr7_t_period_down | 5614 | Para_ModulControler_Ctr7_t_period_down |  | 10000808
[8 empty] | 10000811 | Para_ModulControler_Ctr7_t_period_up | Para_ModulControler_Ctr7_t_period_up | 5615 | Para_ModulControler_Ctr7_t_period_up |  | 10000811
[8 empty] | 10000813 | Para_ModulControler_Ctr7_Tn_manualAdjust | Para_ModulControler_Ctr7_Tn_manualAdjust | 5616 | Para_ModulControler_Ctr7_Tn_manualAdjust |  | 10000813
[8 empty] | 10000812 | Para_ModulControler_Ctr7_Tv_manualAdjust | Para_ModulControler_Ctr7_Tv_manualAdjust | 5617 | Para_ModulControler_Ctr7_Tv_manualAdjust |  | 10000812
[8 empty] | 10000309 | Para_ModulControler_Ctr7_WMax | Para_ModulControler_Ctr7_WMax | 5618 | Para_ModulControler_Ctr7_WMax |  | 10000309
[8 empty] | 10000312 | Para_ModulControler_Ctr7_WMin | Para_ModulControler_Ctr7_WMin | 5619 | Para_ModulControler_Ctr7_WMin |  | 10000312
[8 empty] | 10000310 | Para_ModulControler_Ctr7_WRampNeg | Para_ModulControler_Ctr7_WRampNeg | 5620 | Para_ModulControler_Ctr7_WRampNeg |  | 10000310
[8 empty] | 10000311 | Para_ModulControler_Ctr7_WRampPos | Para_ModulControler_Ctr7_WRampPos | 5621 | Para_ModulControler_Ctr7_WRampPos |  | 10000311
[8 empty] | 10000314 | Para_ModulControler_Ctr7_WStart | Para_ModulControler_Ctr7_WStart | 5622 | Para_ModulControler_Ctr7_WStart |  | 10000314
[8 empty] | 10000315 | Para_ModulControler_Ctr7_Y_block | Para_ModulControler_Ctr7_Y_block | 5623 | Para_ModulControler_Ctr7_Y_block |  | 10000315
[8 empty] | 10000313 | Para_ModulControler_Ctr7_YMax | Para_ModulControler_Ctr7_YMax | 5624 | Para_ModulControler_Ctr7_YMax |  | 10000313
[8 empty] | 10000317 | Para_ModulControler_Ctr7_YMin | Para_ModulControler_Ctr7_YMin | 5625 | Para_ModulControler_Ctr7_YMin |  | 10000317
[8 empty] | 10000318 | Para_ModulControler_Ctr8_DComp | Para_ModulControler_Ctr8_DComp | 5626 | Para_ModulControler_Ctr8_DComp |  | 10000318
[8 empty] | 10000320 | Para_ModulControler_Ctr8_deadband | Para_ModulControler_Ctr8_deadband | 5627 | Para_ModulControler_Ctr8_deadband |  | 10000320
[8 empty] | 10000339 | Para_ModulControler_Ctr8_dY_max | Para_ModulControler_Ctr8_dY_max | 5628 | Para_ModulControler_Ctr8_dY_max |  | 10000339
[8 empty] | 10000321 | Para_ModulControler_Ctr8_IComp | Para_ModulControler_Ctr8_IComp | 5629 | Para_ModulControler_Ctr8_IComp |  | 10000321
[8 empty] | 10000815 | Para_ModulControler_Ctr8_Kp_manualAdjust | Para_ModulControler_Ctr8_Kp_manualAdjust | 5630 | Para_ModulControler_Ctr8_Kp_manualAdjust |  | 10000815
[8 empty] | 10000325 | Para_ModulControler_Ctr8_nvert | Para_ModulControler_Ctr8_nvert | 5631 | Para_ModulControler_Ctr8_nvert |  | 10000325
[8 empty] | 10000324 | Para_ModulControler_Ctr8_PComp | Para_ModulControler_Ctr8_PComp | 5632 | Para_ModulControler_Ctr8_PComp |  | 10000324
[8 empty] | 10003073 | Para_ModulControler_Ctr8_ScaleMax | Para_ModulControler_Ctr8_ScaleMax | 5633 | Para_ModulControler_Ctr8_ScaleMax |  | 10003073
[8 empty] | 10003051 | Para_ModulControler_Ctr8_ScaleMin | Para_ModulControler_Ctr8_ScaleMin | 5634 | Para_ModulControler_Ctr8_ScaleMin |  | 10003051
[8 empty] | 10000814 | Para_ModulControler_Ctr8_t_min_pulse_down | Para_ModulControler_Ctr8_t_min_pulse_down | 5635 | Para_ModulControler_Ctr8_t_min_pulse_down |  | 10000814
[8 empty] | 10000817 | Para_ModulControler_Ctr8_t_min_pulse_up | Para_ModulControler_Ctr8_t_min_pulse_up | 5636 | Para_ModulControler_Ctr8_t_min_pulse_up |  | 10000817
[8 empty] | 10000816 | Para_ModulControler_Ctr8_t_period_down | Para_ModulControler_Ctr8_t_period_down | 5637 | Para_ModulControler_Ctr8_t_period_down |  | 10000816
[8 empty] | 10000820 | Para_ModulControler_Ctr8_t_period_up | Para_ModulControler_Ctr8_t_period_up | 5638 | Para_ModulControler_Ctr8_t_period_up |  | 10000820
[8 empty] | 10000819 | Para_ModulControler_Ctr8_Tn_manualAdjust | Para_ModulControler_Ctr8_Tn_manualAdjust | 5639 | Para_ModulControler_Ctr8_Tn_manualAdjust |  | 10000819
[8 empty] | 10000821 | Para_ModulControler_Ctr8_Tv_manualAdjust | Para_ModulControler_Ctr8_Tv_manualAdjust | 5640 | Para_ModulControler_Ctr8_Tv_manualAdjust |  | 10000821
[8 empty] | 10000331 | Para_ModulControler_Ctr8_WMax | Para_ModulControler_Ctr8_WMax | 5641 | Para_ModulControler_Ctr8_WMax |  | 10000331
[8 empty] | 10000330 | Para_ModulControler_Ctr8_WMin | Para_ModulControler_Ctr8_WMin | 5642 | Para_ModulControler_Ctr8_WMin |  | 10000330
[8 empty] | 10000332 | Para_ModulControler_Ctr8_WRampNeg | Para_ModulControler_Ctr8_WRampNeg | 5643 | Para_ModulControler_Ctr8_WRampNeg |  | 10000332
[8 empty] | 10000333 | Para_ModulControler_Ctr8_WRampPos | Para_ModulControler_Ctr8_WRampPos | 5644 | Para_ModulControler_Ctr8_WRampPos |  | 10000333
[8 empty] | 10000335 | Para_ModulControler_Ctr8_WStart | Para_ModulControler_Ctr8_WStart | 5645 | Para_ModulControler_Ctr8_WStart |  | 10000335
[8 empty] | 10000337 | Para_ModulControler_Ctr8_Y_block | Para_ModulControler_Ctr8_Y_block | 5646 | Para_ModulControler_Ctr8_Y_block |  | 10000337
[8 empty] | 10000336 | Para_ModulControler_Ctr8_YMax | Para_ModulControler_Ctr8_YMax | 5647 | Para_ModulControler_Ctr8_YMax |  | 10000336
[8 empty] | 10000338 | Para_ModulControler_Ctr8_YMin | Para_ModulControler_Ctr8_YMin | 5648 | Para_ModulControler_Ctr8_YMin |  | 10000338
[8 empty] | 10001503 | Para_ModulControler_Ctr_CC | Para_ModulControler_Ctr_CC | 5649 | Para_ModulControler_Ctr_CC |  | 10001503
[8 empty] | 10008439 | Para_ModulControler_Ctr_CDSu | Para_ModulControler_Ctr_CDSu | 5650 | Para_ModulControler_Ctr_CDSu |  | 10008439
[8 empty] | 10000478 | Para_ModulControler_Ctr_ChCHP | Para_ModulControler_Ctr_ChCHP | 5651 | Para_ModulControler_Ctr_ChCHP |  | 10000478
[8 empty] | 10008320 | Para_ModulControler_Ctr_CircLou | Para_ModulControler_Ctr_CircLou | 5652 | Para_ModulControler_Ctr_CircLou |  | 10008320
[8 empty] | 10000463 | Para_ModulControler_Ctr_Cust1 | Para_ModulControler_Ctr_Cust1 | 5653 | Para_ModulControler_Ctr_Cust1 |  | 10000463
[8 empty] | 10000465 | Para_ModulControler_Ctr_Cust2 | Para_ModulControler_Ctr_Cust2 | 5654 | Para_ModulControler_Ctr_Cust2 |  | 10000465
[8 empty] | 10000461 | Para_ModulControler_Ctr_Cust3 | Para_ModulControler_Ctr_Cust3 | 5655 | Para_ModulControler_Ctr_Cust3 |  | 10000461
[8 empty] | 10000464 | Para_ModulControler_Ctr_Cust4 | Para_ModulControler_Ctr_Cust4 | 5656 | Para_ModulControler_Ctr_Cust4 |  | 10000464
[8 empty] | 10000466 | Para_ModulControler_Ctr_Cust5 | Para_ModulControler_Ctr_Cust5 | 5657 | Para_ModulControler_Ctr_Cust5 |  | 10000466
[8 empty] | 10000470 | Para_ModulControler_Ctr_Cust6 | Para_ModulControler_Ctr_Cust6 | 5658 | Para_ModulControler_Ctr_Cust6 |  | 10000470
[8 empty] | 10000468 | Para_ModulControler_Ctr_Cust7 | Para_ModulControler_Ctr_Cust7 | 5659 | Para_ModulControler_Ctr_Cust7 |  | 10000468
[8 empty] | 10000469 | Para_ModulControler_Ctr_Cust8 | Para_ModulControler_Ctr_Cust8 | 5660 | Para_ModulControler_Ctr_Cust8 |  | 10000469
[8 empty] | 10000091 | Para_ModulControler_Ctr_ECW | Para_ModulControler_Ctr_ECW | 5661 | Para_ModulControler_Ctr_ECW |  | 10000091
[8 empty] | 10001482 | Para_ModulControler_Ctr_EOVal_Active | Para_ModulControler_Ctr_EOVal_Active | 5662 | Para_ModulControler_Ctr_EOVal_Active |  | 10001482
[8 empty] | 10002545 | Para_ModulControler_Ctr_EOVal_LT_Active | Para_ModulControler_Ctr_EOVal_LT_Active | 5663 | Para_ModulControler_Ctr_EOVal_LT_Active |  | 10002545
[8 empty] | 10001441 | Para_ModulControler_Ctr_GC | Para_ModulControler_Ctr_GC | 5664 | Para_ModulControler_Ctr_GC |  | 10001441
[8 empty] | 10008273 | Para_ModulControler_Ctr_InlLou | Para_ModulControler_Ctr_InlLou | 5665 | Para_ModulControler_Ctr_InlLou |  | 10008273
[8 empty] | 10008865 | Para_ModulControler_Ctr_Mns_Enable | Para_ModulControler_Ctr_Mns_Enable | 5666 | Para_ModulControler_Ctr_Mns_Enable |  | 10008865
[8 empty] | 10008395 | Para_ModulControler_Ctr_OutlLou_RDP | Para_ModulControler_Ctr_OutlLou_RDP | 5667 | Para_ModulControler_Ctr_OutlLou_RDP |  | 10008395
[8 empty] | 10008241 | Para_ModulControler_Ctr_OutlLou_RT | Para_ModulControler_Ctr_OutlLou_RT | 5668 | Para_ModulControler_Ctr_OutlLou_RT |  | 10008241
[8 empty] | 10008859 | Para_ModulControler_Ctr_OutlVE_RDP | Para_ModulControler_Ctr_OutlVE_RDP | 5669 | Para_ModulControler_Ctr_OutlVE_RDP |  | 10008859
[8 empty] | 10008805 | Para_ModulControler_Ctr_OutlVE_RT | Para_ModulControler_Ctr_OutlVE_RT | 5670 | Para_ModulControler_Ctr_OutlVE_RT |  | 10008805
[8 empty] | 10003114 | Para_ModulControler_Ctr_SCR_Flow | Para_ModulControler_Ctr_SCR_Flow | 5671 | Para_ModulControler_Ctr_SCR_Flow |  | 10003114
[8 empty] | 10003116 | Para_ModulControler_Ctr_SCR_NOx | Para_ModulControler_Ctr_SCR_NOx | 5672 | Para_ModulControler_Ctr_SCR_NOx |  | 10003116
[8 empty] | 10000462 | Para_ModulControler_CtrGenPF_Active | Para_ModulControler_CtrGenPF_Active | 5673 | Para_ModulControler_CtrGenPF_Active |  | 10000462
[8 empty] | 10000104 | Para_ModulControler_CtrThR_Heater_Active | Para_ModulControler_CtrThR_Heater_Active | 5674 | Para_ModulControler_CtrThR_Heater_Active |  | 10000104
[8 empty] | 18621 | Para_Monic_ActVoltAvgMax | Para_Monic_ActVoltAvgMax | 5675 | Para_Monic_ActVoltAvgMax |  | 18621
[8 empty] | 18622 | Para_Monic_ActVoltDif | Para_Monic_ActVoltDif | 5676 | Para_Monic_ActVoltDif |  | 18622
[8 empty] | 18623 | Para_Monic_ActVoltMax | Para_Monic_ActVoltMax | 5677 | Para_Monic_ActVoltMax |  | 18623
[8 empty] | 18624 | Para_Monic_ActVoltMin | Para_Monic_ActVoltMin | 5678 | Para_Monic_ActVoltMin |  | 18624
[8 empty] | 18625 | Para_Monic_LimitActive | Para_Monic_LimitActive | 5679 | Para_Monic_LimitActive | kV | 18625
[8 empty] | 18626 | Para_Monic_LimitActiveHys | Para_Monic_LimitActiveHys | 5680 | Para_Monic_LimitActiveHys | kV | 18626
[8 empty] | 18627 | Para_Monic_TriggerVolt | Para_Monic_TriggerVolt | 5681 | Para_Monic_TriggerVolt | kV | 18627
[8 empty] | 18628 | Para_Monic_VoltAvgMax | Para_Monic_VoltAvgMax | 5682 | Para_Monic_VoltAvgMax | kV | 18628
[8 empty] | 18629 | Para_Monic_VoltAvgMaxDelay | Para_Monic_VoltAvgMaxDelay | 5683 | Para_Monic_VoltAvgMaxDelay | s | 18629
[8 empty] | 18630 | Para_Monic_VoltDif | Para_Monic_VoltDif | 5684 | Para_Monic_VoltDif | kV | 18630
[8 empty] | 18631 | Para_Monic_VoltDifDelay | Para_Monic_VoltDifDelay | 5685 | Para_Monic_VoltDifDelay | s | 18631
[8 empty] | 18632 | Para_Monic_VoltMax | Para_Monic_VoltMax | 5686 | Para_Monic_VoltMax | kV | 18632
[8 empty] | 18633 | Para_Monic_VoltMaxDelay | Para_Monic_VoltMaxDelay | 5687 | Para_Monic_VoltMaxDelay | s | 18633
[8 empty] | 18634 | Para_Monic_VoltMin | Para_Monic_VoltMin | 5688 | Para_Monic_VoltMin | kV | 18634
[8 empty] | 18635 | Para_Monic_VoltMinDelay | Para_Monic_VoltMinDelay | 5689 | Para_Monic_VoltMinDelay | s | 18635
[8 empty] | 18636 | Para_PBC_AI_NEx | Para_PBC_AI_NEx | 5690 | Para_PBC_AI_NEx |  | 18636
[8 empty] | 19498 | Para_PBC_AvgPMaxLimit | Para_PBC_AvgPMaxLimit | 5691 | Para_PBC_AvgPMaxLimit | bar | 19498
[8 empty] | 17379 | Para_PBC_LimitPressMax | Para_PBC_LimitPressMax | 5692 | Para_PBC_LimitPressMax | bar | 17379
[8 empty] | 17380 | Para_PBC_LimitPressMaxAvg | Para_PBC_LimitPressMaxAvg | 5693 | Para_PBC_LimitPressMaxAvg | bar | 17380
[8 empty] | 17381 | Para_PBC_NumbCycBelowPressMax | Para_PBC_NumbCycBelowPressMax | 5694 | Para_PBC_NumbCycBelowPressMax |  | 17381
[8 empty] | 17382 | Para_PBC_NumbCycBelowPressMean | Para_PBC_NumbCycBelowPressMean | 5695 | Para_PBC_NumbCycBelowPressMean |  | 17382
[8 empty] | 17383 | Para_PBC_NumbCycExcPressMax | Para_PBC_NumbCycExcPressMax | 5696 | Para_PBC_NumbCycExcPressMax |  | 17383
[8 empty] | 17384 | Para_PBC_NumbCycExcPressMean | Para_PBC_NumbCycExcPressMean | 5697 | Para_PBC_NumbCycExcPressMean |  | 17384
[8 empty] | 17385 | Para_PBC_NumbMisfCycMin | Para_PBC_NumbMisfCycMin | 5698 | Para_PBC_NumbMisfCycMin |  | 17385
[8 empty] | 17386 | Para_PBC_PowerRed | Para_PBC_PowerRed | 5699 | Para_PBC_PowerRed | %Pnom | 17386
[8 empty] | 17387 | Para_PBC_PressMeanDevMisf | Para_PBC_PressMeanDevMisf | 5700 | Para_PBC_PressMeanDevMisf | bar | 17387
[8 empty] | 17388 | Para_PBC_PressMeanDevNeg | Para_PBC_PressMeanDevNeg | 5701 | Para_PBC_PressMeanDevNeg | bar | 17388
[8 empty] | 17389 | Para_PBC_PressMeanDevPos | Para_PBC_PressMeanDevPos | 5702 | Para_PBC_PressMeanDevPos | bar | 17389
[8 empty] | 17390 | Para_PBC_Sensitivity | Para_PBC_Sensitivity | 5703 | Para_PBC_Sensitivity | mV/bar | 17390
[8 empty] | 17391 | Para_PI_20mA | Para_PI_20mA | 5704 | Para_PI_20mA | bar | 17391
[8 empty] | 17392 | Para_PI_4mA | Para_PI_4mA | 5705 | Para_PI_4mA | bar | 17392
[8 empty] | 17393 | Para_PI_ActCloseDetection | Para_PI_ActCloseDetection | 5706 | Para_PI_ActCloseDetection |  | 17393
[8 empty] | 17394 | Para_PI_FailRateValveOpen | Para_PI_FailRateValveOpen | 5707 | Para_PI_FailRateValveOpen |  | 17394
[8 empty] | 17395 | Para_PI_FailRateValveOpenTP | Para_PI_FailRateValveOpenTP | 5708 | Para_PI_FailRateValveOpenTP |  | 17395
[8 empty] | 19499 | Para_PI_LambdaFeedFwdCtr_Gas1_OffsetStartLambda | Para_PI_LambdaFeedFwdCtr_Gas1_OffsetStartLambda | 5709 | Para_PI_LambdaFeedFwdCtr_Gas1_OffsetStartLambda |  | 19499
[8 empty] | 19500 | Para_PI_LambdaFeedFwdCtr_Gas2_OffsetStartLambda | Para_PI_LambdaFeedFwdCtr_Gas2_OffsetStartLambda | 5710 | Para_PI_LambdaFeedFwdCtr_Gas2_OffsetStartLambda |  | 19500
[8 empty] | 19501 | Para_PI_LambdaFeedFwdCtr_Gas3_OffsetStartLambda | Para_PI_LambdaFeedFwdCtr_Gas3_OffsetStartLambda | 5711 | Para_PI_LambdaFeedFwdCtr_Gas3_OffsetStartLambda |  | 19501
[8 empty] | 19502 | Para_PI_LambdaFeedFwdCtr_Gas4_OffsetStartLambda | Para_PI_LambdaFeedFwdCtr_Gas4_OffsetStartLambda | 5712 | Para_PI_LambdaFeedFwdCtr_Gas4_OffsetStartLambda |  | 19502
[8 empty] | 17779 | Para_PI_Limit_GasRailPressDiffMax | Para_PI_Limit_GasRailPressDiffMax | 5713 | Para_PI_Limit_GasRailPressDiffMax | bar | 17779
[8 empty] | 17780 | Para_PI_Limit_GasRailPressDiffMin | Para_PI_Limit_GasRailPressDiffMin | 5714 | Para_PI_Limit_GasRailPressDiffMin | bar | 17780
[8 empty] | 17781 | Para_PI_Limit_GasRailPressMax | Para_PI_Limit_GasRailPressMax | 5715 | Para_PI_Limit_GasRailPressMax | bar | 17781
[8 empty] | 17782 | Para_PI_Limit_GasRailPressMin | Para_PI_Limit_GasRailPressMin | 5716 | Para_PI_Limit_GasRailPressMin | bar | 17782
[8 empty] | 17783 | Para_PI_Limit_GasRailTempMax | Para_PI_Limit_GasRailTempMax | 5717 | Para_PI_Limit_GasRailTempMax | °C | 17783
[8 empty] | 17784 | Para_PI_Limit_GasRailTempMin | Para_PI_Limit_GasRailTempMin | 5718 | Para_PI_Limit_GasRailTempMin | °C | 17784
[8 empty] | 17785 | Para_PI_ReleaseBal | Para_PI_ReleaseBal | 5719 | Para_PI_ReleaseBal |  | 17785
[8 empty] | 17786 | Para_PI_ValveType | Para_PI_ValveType | 5720 | Para_PI_ValveType |  | 17786
[8 empty] | 17787 | Para_Power_Actual_Curr1 | Para_Power_Actual_Curr1 | 5721 | Para_Power_Actual_Curr1 | mA | 17787
[8 empty] | 17788 | Para_Power_Actual_Curr2 | Para_Power_Actual_Curr2 | 5722 | Para_Power_Actual_Curr2 | mA | 17788
[8 empty] | 17789 | Para_Power_Actual_Point1 | Para_Power_Actual_Point1 | 5723 | Para_Power_Actual_Point1 | kW | 17789
[8 empty] | 17790 | Para_Power_Actual_Point2 | Para_Power_Actual_Point2 | 5724 | Para_Power_Actual_Point2 | kW | 17790
[8 empty] | 17791 | Para_Power_Ctr_TbDComp | Para_Power_Ctr_TbDComp | 5725 | Para_Power_Ctr_TbDComp |  | 17791
[8 empty] | 17792 | Para_Power_Ctr_TbIComp | Para_Power_Ctr_TbIComp | 5726 | Para_Power_Ctr_TbIComp |  | 17792
[8 empty] | 17793 | Para_Power_Ctr_TbPComp | Para_Power_Ctr_TbPComp | 5727 | Para_Power_Ctr_TbPComp |  | 17793
[8 empty] | 17794 | Para_Power_Ctr_TbYMax | Para_Power_Ctr_TbYMax | 5728 | Para_Power_Ctr_TbYMax | % | 17794
[8 empty] | 17795 | Para_Power_Ctr_TbYMin | Para_Power_Ctr_TbYMin | 5729 | Para_Power_Ctr_TbYMin | % | 17795
[8 empty] | 17796 | Para_Power_Ctr_TrDComp | Para_Power_Ctr_TrDComp | 5730 | Para_Power_Ctr_TrDComp |  | 17796
[8 empty] | 17797 | Para_Power_Ctr_TrIComp | Para_Power_Ctr_TrIComp | 5731 | Para_Power_Ctr_TrIComp |  | 17797
[8 empty] | 17798 | Para_Power_Ctr_TrPComp | Para_Power_Ctr_TrPComp | 5732 | Para_Power_Ctr_TrPComp |  | 17798
[8 empty] | 17799 | Para_Power_Ctr_TrYMax | Para_Power_Ctr_TrYMax | 5733 | Para_Power_Ctr_TrYMax | % | 17799
[8 empty] | 17800 | Para_Power_Ctr_TrYMin | Para_Power_Ctr_TrYMin | 5734 | Para_Power_Ctr_TrYMin | % | 17800
[8 empty] | 17801 | Para_Power_ExtRed_Curr1 | Para_Power_ExtRed_Curr1 | 5735 | Para_Power_ExtRed_Curr1 | mA | 17801
[8 empty] | 17802 | Para_Power_ExtRed_Curr2 | Para_Power_ExtRed_Curr2 | 5736 | Para_Power_ExtRed_Curr2 | mA | 17802
[8 empty] | 17803 | Para_Power_ExtRed_Point1 | Para_Power_ExtRed_Point1 | 5737 | Para_Power_ExtRed_Point1 | kW | 17803
[8 empty] | 17804 | Para_Power_ExtRed_Point2 | Para_Power_ExtRed_Point2 | 5738 | Para_Power_ExtRed_Point2 | kW | 17804
[8 empty] | 17805 | Para_Power_ExtSet_ConstSetPoint1 | Para_Power_ExtSet_ConstSetPoint1 | 5739 | Para_Power_ExtSet_ConstSetPoint1 | % | 17805
[8 empty] | 17806 | Para_Power_ExtSet_ConstSetPoint2 | Para_Power_ExtSet_ConstSetPoint2 | 5740 | Para_Power_ExtSet_ConstSetPoint2 |  | 17806
[8 empty] | 17807 | Para_Power_ExtSet_ConstSetPoint3 | Para_Power_ExtSet_ConstSetPoint3 | 5741 | Para_Power_ExtSet_ConstSetPoint3 |  | 17807
[8 empty] | 17808 | Para_Power_ExtSet_ConstSetPoint4 | Para_Power_ExtSet_ConstSetPoint4 | 5742 | Para_Power_ExtSet_ConstSetPoint4 |  | 17808
[8 empty] | 17809 | Para_Power_ExtSet_ConstSetPoint5 | Para_Power_ExtSet_ConstSetPoint5 | 5743 | Para_Power_ExtSet_ConstSetPoint5 | % | 17809
[8 empty] | 17810 | Para_Power_ExtSet_Curr1 | Para_Power_ExtSet_Curr1 | 5744 | Para_Power_ExtSet_Curr1 | mA | 17810
[8 empty] | 17811 | Para_Power_ExtSet_Curr2 | Para_Power_ExtSet_Curr2 | 5745 | Para_Power_ExtSet_Curr2 | mA | 17811
[8 empty] | 17812 | Para_Power_ExtSet_Point1 | Para_Power_ExtSet_Point1 | 5746 | Para_Power_ExtSet_Point1 | kW | 17812
[8 empty] | 17813 | Para_Power_ExtSet_Point2 | Para_Power_ExtSet_Point2 | 5747 | Para_Power_ExtSet_Point2 | kW | 17813
[8 empty] | 17814 | Para_Power_IntakeAirRed_RedFac | Para_Power_IntakeAirRed_RedFac | 5748 | Para_Power_IntakeAirRed_RedFac | %Pn/°C | 17814
[8 empty] | 19503 | Para_Power_IntakeAirRed_RedFac2 | Para_Power_IntakeAirRed_RedFac2 | 5749 | Para_Power_IntakeAirRed_RedFac2 | %Pn/°C | 19503
[8 empty] | 17396 | Para_Power_IntakeAirRed_Start | Para_Power_IntakeAirRed_Start | 5750 | Para_Power_IntakeAirRed_Start | °C | 17396
[8 empty] | 19504 | Para_Power_IntakeAirRed_Start2 | Para_Power_IntakeAirRed_Start2 | 5751 | Para_Power_IntakeAirRed_Start2 | °C | 19504
[8 empty] | 18637 | Para_Power_IPAdap_ActITPTbAdap | Para_Power_IPAdap_ActITPTbAdap | 5752 | Para_Power_IPAdap_ActITPTbAdap |  | 18637
[8 empty] | 18638 | Para_Power_IPAdap_IPRedTBGas1 | Para_Power_IPAdap_IPRedTBGas1 | 5753 | Para_Power_IPAdap_IPRedTBGas1 | °KW | 18638
[8 empty] | 18639 | Para_Power_IPAdap_IPRedTBGas2 | Para_Power_IPAdap_IPRedTBGas2 | 5754 | Para_Power_IPAdap_IPRedTBGas2 | °KW | 18639
[8 empty] | 18640 | Para_Power_IPAdap_IPRedTBGas3 | Para_Power_IPAdap_IPRedTBGas3 | 5755 | Para_Power_IPAdap_IPRedTBGas3 | °KW | 18640
[8 empty] | 18641 | Para_Power_IPAdap_IPRedTBGas4 | Para_Power_IPAdap_IPRedTBGas4 | 5756 | Para_Power_IPAdap_IPRedTBGas4 | °KW | 18641
[8 empty] | 18642 | Para_Power_IPAdap_ITPTbPosAdap | Para_Power_IPAdap_ITPTbPosAdap | 5757 | Para_Power_IPAdap_ITPTbPosAdap | % | 18642
[8 empty] | 18643 | Para_Power_Limit_Backfire | Para_Power_Limit_Backfire | 5758 | Para_Power_Limit_Backfire | % | 18643
[8 empty] | 18644 | Para_Power_Limit_BackfireHys | Para_Power_Limit_BackfireHys | 5759 | Para_Power_Limit_BackfireHys | kW | 18644
[8 empty] | 18645 | Para_Power_Limit_GasChange | Para_Power_Limit_GasChange | 5760 | Para_Power_Limit_GasChange | % | 18645
[8 empty] | 18646 | Para_Power_Limit_GasChangeHys | Para_Power_Limit_GasChangeHys | 5761 | Para_Power_Limit_GasChangeHys | kW | 18646
[8 empty] | 18647 | Para_Power_Limit_Perc40Pnom | Para_Power_Limit_Perc40Pnom | 5762 | Para_Power_Limit_Perc40Pnom | % | 18647
[8 empty] | 18648 | Para_Power_Limit_Perc40PnomHys | Para_Power_Limit_Perc40PnomHys | 5763 | Para_Power_Limit_Perc40PnomHys | kW | 18648
[8 empty] | 18649 | Para_Power_Limit_PowerDiff | Para_Power_Limit_PowerDiff | 5764 | Para_Power_Limit_PowerDiff | % | 18649
[8 empty] | 18650 | Para_Power_Limit_PowerDiffDelay | Para_Power_Limit_PowerDiffDelay | 5765 | Para_Power_Limit_PowerDiffDelay | s | 18650
[8 empty] | 18651 | Para_Power_Limit_PowerDiffRated | Para_Power_Limit_PowerDiffRated | 5766 | Para_Power_Limit_PowerDiffRated |  | 18651
[8 empty] | 18652 | Para_Power_Limit_PowerDiffRatedDelay | Para_Power_Limit_PowerDiffRatedDelay | 5767 | Para_Power_Limit_PowerDiffRatedDelay |  | 18652
[8 empty] | 18653 | Para_Power_Limit_PowerLimit1 | Para_Power_Limit_PowerLimit1 | 5768 | Para_Power_Limit_PowerLimit1 | % | 18653
[8 empty] | 18654 | Para_Power_Limit_PowerLimit1Hys | Para_Power_Limit_PowerLimit1Hys | 5769 | Para_Power_Limit_PowerLimit1Hys | kW | 18654
[8 empty] | 18655 | Para_Power_Limit_PowerRetLimit | Para_Power_Limit_PowerRetLimit | 5770 | Para_Power_Limit_PowerRetLimit | kW | 18655
[8 empty] | 18656 | Para_Power_Limit_PowerRetLimitHys | Para_Power_Limit_PowerRetLimitHys | 5771 | Para_Power_Limit_PowerRetLimitHys | kW | 18656
[8 empty] | 18657 | Para_Power_Limit_SigLoss | Para_Power_Limit_SigLoss | 5772 | Para_Power_Limit_SigLoss | % | 18657
[8 empty] | 18658 | Para_Power_Limit_SigLossHys | Para_Power_Limit_SigLossHys | 5773 | Para_Power_Limit_SigLossHys | kW | 18658
[8 empty] | 18659 | Para_Power_Limit_SigOverload | Para_Power_Limit_SigOverload | 5774 | Para_Power_Limit_SigOverload | % | 18659
[8 empty] | 18660 | Para_Power_Limit_SigOverloadHys | Para_Power_Limit_SigOverloadHys | 5775 | Para_Power_Limit_SigOverloadHys | kW | 18660
[8 empty] | 18661 | Para_Power_Limit_SigTrip | Para_Power_Limit_SigTrip | 5776 | Para_Power_Limit_SigTrip | mA | 18661
[8 empty] | 18662 | Para_Power_Limit_SwitchCosPhi | Para_Power_Limit_SwitchCosPhi | 5777 | Para_Power_Limit_SwitchCosPhi | % | 18662
[8 empty] | 18663 | Para_Power_Limit_SwitchCosPhiHys | Para_Power_Limit_SwitchCosPhiHys | 5778 | Para_Power_Limit_SwitchCosPhiHys | kW | 18663
[8 empty] | 18664 | Para_Power_Nominal_Power1 | Para_Power_Nominal_Power1 | 5779 | Para_Power_Nominal_Power1 | kW | 18664
[8 empty] | 18665 | Para_Power_Nominal_Power2 | Para_Power_Nominal_Power2 | 5780 | Para_Power_Nominal_Power2 | kW | 18665
[8 empty] | 18666 | Para_Power_Nominal_Power3 | Para_Power_Nominal_Power3 | 5781 | Para_Power_Nominal_Power3 | kW | 18666
[8 empty] | 18667 | Para_Power_Nominal_Power4 | Para_Power_Nominal_Power4 | 5782 | Para_Power_Nominal_Power4 | kW | 18667
[8 empty] | 18668 | Para_Power_Nominal_PowerMin | Para_Power_Nominal_PowerMin | 5783 | Para_Power_Nominal_PowerMin | % | 18668
[8 empty] | 18669 | Para_Power_Ramp_DownG1 | Para_Power_Ramp_DownG1 | 5784 | Para_Power_Ramp_DownG1 | kW/s | 18669
[8 empty] | 18670 | Para_Power_Ramp_DownG2 | Para_Power_Ramp_DownG2 | 5785 | Para_Power_Ramp_DownG2 | kW/s | 18670
[8 empty] | 18671 | Para_Power_Ramp_DownG3 | Para_Power_Ramp_DownG3 | 5786 | Para_Power_Ramp_DownG3 | kW/s | 18671
[8 empty] | 18672 | Para_Power_Ramp_DownG4 | Para_Power_Ramp_DownG4 | 5787 | Para_Power_Ramp_DownG4 | kW/s | 18672
[8 empty] | 18673 | Para_Power_Ramp_UpG1 | Para_Power_Ramp_UpG1 | 5788 | Para_Power_Ramp_UpG1 | kW/s | 18673
[8 empty] | 18674 | Para_Power_Ramp_UpG2 | Para_Power_Ramp_UpG2 | 5789 | Para_Power_Ramp_UpG2 | kW/s | 18674
[8 empty] | 18675 | Para_Power_Ramp_UpG3 | Para_Power_Ramp_UpG3 | 5790 | Para_Power_Ramp_UpG3 | kW/s | 18675
[8 empty] | 18676 | Para_Power_Ramp_UpG4 | Para_Power_Ramp_UpG4 | 5791 | Para_Power_Ramp_UpG4 | kW/s | 18676
[8 empty] | 18677 | Para_Power_RedChargeTemp_Active | Para_Power_RedChargeTemp_Active | 5792 | Para_Power_RedChargeTemp_Active |  | 18677
[8 empty] | 18678 | Para_Power_RedChargeTemp_Fix | Para_Power_RedChargeTemp_Fix | 5793 | Para_Power_RedChargeTemp_Fix |  | 18678
[8 empty] | 18679 | Para_Power_RedCoolWatTemp_Rate | Para_Power_RedCoolWatTemp_Rate | 5794 | Para_Power_RedCoolWatTemp_Rate |  | 18679
[8 empty] | 18680 | Para_Power_RedCoolWatTemp_Start | Para_Power_RedCoolWatTemp_Start | 5795 | Para_Power_RedCoolWatTemp_Start |  | 18680
[8 empty] | 18681 | Para_Power_RedGenerator_ActPowRedFreq | Para_Power_RedGenerator_ActPowRedFreq | 5796 | Para_Power_RedGenerator_ActPowRedFreq |  | 18681
[8 empty] | 18682 | Para_Power_RedGenerator_ActPowRedVolt | Para_Power_RedGenerator_ActPowRedVolt | 5797 | Para_Power_RedGenerator_ActPowRedVolt |  | 18682
[8 empty] | 18683 | Para_Power_RedGenerator_FreqHighStart | Para_Power_RedGenerator_FreqHighStart | 5798 | Para_Power_RedGenerator_FreqHighStart |  | 18683
[8 empty] | 18684 | Para_Power_RedGenerator_FreqHighStop | Para_Power_RedGenerator_FreqHighStop | 5799 | Para_Power_RedGenerator_FreqHighStop |  | 18684
[8 empty] | 18685 | Para_Power_RedGenerator_FreqLowStart | Para_Power_RedGenerator_FreqLowStart | 5800 | Para_Power_RedGenerator_FreqLowStart |  | 18685
[8 empty] | 18686 | Para_Power_RedGenerator_FreqLowStop | Para_Power_RedGenerator_FreqLowStop | 5801 | Para_Power_RedGenerator_FreqLowStop |  | 18686
[8 empty] | 18687 | Para_Power_RedGenerator_FreqReturn | Para_Power_RedGenerator_FreqReturn | 5802 | Para_Power_RedGenerator_FreqReturn |  | 18687
[8 empty] | 18688 | Para_Power_RedGenerator_PowerMinFreqHigh | Para_Power_RedGenerator_PowerMinFreqHigh | 5803 | Para_Power_RedGenerator_PowerMinFreqHigh |  | 18688
[8 empty] | 18689 | Para_Power_RedGenerator_PowerMinFreqLow | Para_Power_RedGenerator_PowerMinFreqLow | 5804 | Para_Power_RedGenerator_PowerMinFreqLow |  | 18689
[8 empty] | 18690 | Para_Power_RedGenerator_PowerMinVoltHigh | Para_Power_RedGenerator_PowerMinVoltHigh | 5805 | Para_Power_RedGenerator_PowerMinVoltHigh |  | 18690
[8 empty] | 18691 | Para_Power_RedGenerator_PowerMinVoltLow | Para_Power_RedGenerator_PowerMinVoltLow | 5806 | Para_Power_RedGenerator_PowerMinVoltLow |  | 18691
[8 empty] | 18692 | Para_Power_RedGenerator_TempPowRed | Para_Power_RedGenerator_TempPowRed | 5807 | Para_Power_RedGenerator_TempPowRed |  | 18692
[8 empty] | 18693 | Para_Power_RedGenerator_VoltHighStart | Para_Power_RedGenerator_VoltHighStart | 5808 | Para_Power_RedGenerator_VoltHighStart |  | 18693
[8 empty] | 18694 | Para_Power_RedGenerator_VoltHighStop | Para_Power_RedGenerator_VoltHighStop | 5809 | Para_Power_RedGenerator_VoltHighStop |  | 18694
[8 empty] | 18695 | Para_Power_RedGenerator_VoltLowStart | Para_Power_RedGenerator_VoltLowStart | 5810 | Para_Power_RedGenerator_VoltLowStart |  | 18695
[8 empty] | 18696 | Para_Power_RedGenerator_VoltLowStop | Para_Power_RedGenerator_VoltLowStop | 5811 | Para_Power_RedGenerator_VoltLowStop |  | 18696
[8 empty] | 18697 | Para_Power_RedGenerator_WindTempHighStart | Para_Power_RedGenerator_WindTempHighStart | 5812 | Para_Power_RedGenerator_WindTempHighStart |  | 18697
[8 empty] | 18698 | Para_Power_RedHumidity_ActPred | Para_Power_RedHumidity_ActPred | 5813 | Para_Power_RedHumidity_ActPred |  | 18698
[8 empty] | 18699 | Para_Power_RedHumidity_PRedLimit | Para_Power_RedHumidity_PRedLimit | 5814 | Para_Power_RedHumidity_PRedLimit | % | 18699
[8 empty] | 18700 | Para_Power_RedOilTemp_Rate | Para_Power_RedOilTemp_Rate | 5815 | Para_Power_RedOilTemp_Rate |  | 18700
[8 empty] | 18701 | Para_Power_RedOilTemp_Start | Para_Power_RedOilTemp_Start | 5816 | Para_Power_RedOilTemp_Start |  | 18701
[8 empty] | 18702 | Para_Power_RedPreChambGasTrain_ActPowerRed | Para_Power_RedPreChambGasTrain_ActPowerRed | 5817 | Para_Power_RedPreChambGasTrain_ActPowerRed |  | 18702
[8 empty] | 18703 | Para_Power_RedPreChambGasTrain_Rate | Para_Power_RedPreChambGasTrain_Rate | 5818 | Para_Power_RedPreChambGasTrain_Rate |  | 18703
[8 empty] | 18704 | Para_Power_RedPreChambGasTrain_Start | Para_Power_RedPreChambGasTrain_Start | 5819 | Para_Power_RedPreChambGasTrain_Start |  | 18704
[8 empty] | 18705 | Para_Power_RedRetWat_PowRedActive | Para_Power_RedRetWat_PowRedActive | 5820 | Para_Power_RedRetWat_PowRedActive |  | 18705
[8 empty] | 18706 | Para_Power_RedRetWat_Rate | Para_Power_RedRetWat_Rate | 5821 | Para_Power_RedRetWat_Rate |  | 18706
[8 empty] | 18707 | Para_Power_RedRetWat_Start | Para_Power_RedRetWat_Start | 5822 | Para_Power_RedRetWat_Start |  | 18707
[8 empty] | 18708 | Para_Power_RedUtility_Step1 | Para_Power_RedUtility_Step1 | 5823 | Para_Power_RedUtility_Step1 |  | 18708
[8 empty] | 18709 | Para_Power_RedUtility_Step2 | Para_Power_RedUtility_Step2 | 5824 | Para_Power_RedUtility_Step2 |  | 18709
[8 empty] | 18710 | Para_Power_TCSpeedRed_RedValue | Para_Power_TCSpeedRed_RedValue | 5825 | Para_Power_TCSpeedRed_RedValue | kW | 18710
[8 empty] | 18711 | Para_Power_TMixRed_DeltaPG1 | Para_Power_TMixRed_DeltaPG1 | 5826 | Para_Power_TMixRed_DeltaPG1 | %Pnom/°C | 18711
[8 empty] | 18712 | Para_Power_TMixRed_DeltaPG2 | Para_Power_TMixRed_DeltaPG2 | 5827 | Para_Power_TMixRed_DeltaPG2 | %Pnom/°C | 18712
[8 empty] | 18713 | Para_Power_TMixRed_DeltaPG3 | Para_Power_TMixRed_DeltaPG3 | 5828 | Para_Power_TMixRed_DeltaPG3 | %Pnom/°C | 18713
[8 empty] | 18714 | Para_Power_TMixRed_DeltaPG4 | Para_Power_TMixRed_DeltaPG4 | 5829 | Para_Power_TMixRed_DeltaPG4 | %Pnom/°C | 18714
[8 empty] | 18715 | Para_Power_TMixRed_TempRedG1 | Para_Power_TMixRed_TempRedG1 | 5830 | Para_Power_TMixRed_TempRedG1 | °C | 18715
[8 empty] | 18716 | Para_Power_TMixRed_TempRedG2 | Para_Power_TMixRed_TempRedG2 | 5831 | Para_Power_TMixRed_TempRedG2 | °C | 18716
[8 empty] | 18717 | Para_Power_TMixRed_TempRedG3 | Para_Power_TMixRed_TempRedG3 | 5832 | Para_Power_TMixRed_TempRedG3 | °C | 18717
[8 empty] | 18718 | Para_Power_TMixRed_TempRedG4 | Para_Power_TMixRed_TempRedG4 | 5833 | Para_Power_TMixRed_TempRedG4 | °C | 18718
[8 empty] | 18719 | Para_Reserve_Analog_Active1 | Para_Reserve_Analog_Active1 | 5834 | Para_Reserve_Analog_Active1 |  | 18719
[8 empty] | 18720 | Para_Reserve_Analog_Active10 | Para_Reserve_Analog_Active10 | 5835 | Para_Reserve_Analog_Active10 |  | 18720
[8 empty] | 18721 | Para_Reserve_Analog_Active11 | Para_Reserve_Analog_Active11 | 5836 | Para_Reserve_Analog_Active11 |  | 18721
[8 empty] | 18722 | Para_Reserve_Analog_Active12 | Para_Reserve_Analog_Active12 | 5837 | Para_Reserve_Analog_Active12 |  | 18722
[8 empty] | 18723 | Para_Reserve_Analog_Active13 | Para_Reserve_Analog_Active13 | 5838 | Para_Reserve_Analog_Active13 |  | 18723
[8 empty] | 18724 | Para_Reserve_Analog_Active14 | Para_Reserve_Analog_Active14 | 5839 | Para_Reserve_Analog_Active14 |  | 18724
[8 empty] | 18725 | Para_Reserve_Analog_Active15 | Para_Reserve_Analog_Active15 | 5840 | Para_Reserve_Analog_Active15 |  | 18725
[8 empty] | 18726 | Para_Reserve_Analog_Active16 | Para_Reserve_Analog_Active16 | 5841 | Para_Reserve_Analog_Active16 |  | 18726
[8 empty] | 18727 | Para_Reserve_Analog_Active2 | Para_Reserve_Analog_Active2 | 5842 | Para_Reserve_Analog_Active2 |  | 18727
[8 empty] | 18728 | Para_Reserve_Analog_Active3 | Para_Reserve_Analog_Active3 | 5843 | Para_Reserve_Analog_Active3 |  | 18728
[8 empty] | 18729 | Para_Reserve_Analog_Active4 | Para_Reserve_Analog_Active4 | 5844 | Para_Reserve_Analog_Active4 |  | 18729
[8 empty] | 18730 | Para_Reserve_Analog_Active5 | Para_Reserve_Analog_Active5 | 5845 | Para_Reserve_Analog_Active5 |  | 18730
[8 empty] | 18731 | Para_Reserve_Analog_Active6 | Para_Reserve_Analog_Active6 | 5846 | Para_Reserve_Analog_Active6 |  | 18731
[8 empty] | 18732 | Para_Reserve_Analog_Active7 | Para_Reserve_Analog_Active7 | 5847 | Para_Reserve_Analog_Active7 |  | 18732
[8 empty] | 18733 | Para_Reserve_Analog_Active8 | Para_Reserve_Analog_Active8 | 5848 | Para_Reserve_Analog_Active8 |  | 18733
[8 empty] | 18734 | Para_Reserve_Analog_Active9 | Para_Reserve_Analog_Active9 | 5849 | Para_Reserve_Analog_Active9 |  | 18734
[8 empty] | 18735 | Para_Reserve_Analog_LiveZero1 | Para_Reserve_Analog_LiveZero1 | 5850 | Para_Reserve_Analog_LiveZero1 |  | 18735
[8 empty] | 18736 | Para_Reserve_Analog_LiveZero10 | Para_Reserve_Analog_LiveZero10 | 5851 | Para_Reserve_Analog_LiveZero10 |  | 18736
[8 empty] | 18737 | Para_Reserve_Analog_LiveZero11 | Para_Reserve_Analog_LiveZero11 | 5852 | Para_Reserve_Analog_LiveZero11 |  | 18737
[8 empty] | 18738 | Para_Reserve_Analog_LiveZero12 | Para_Reserve_Analog_LiveZero12 | 5853 | Para_Reserve_Analog_LiveZero12 |  | 18738
[8 empty] | 18739 | Para_Reserve_Analog_LiveZero13 | Para_Reserve_Analog_LiveZero13 | 5854 | Para_Reserve_Analog_LiveZero13 |  | 18739
[8 empty] | 18740 | Para_Reserve_Analog_LiveZero14 | Para_Reserve_Analog_LiveZero14 | 5855 | Para_Reserve_Analog_LiveZero14 |  | 18740
[8 empty] | 18741 | Para_Reserve_Analog_LiveZero15 | Para_Reserve_Analog_LiveZero15 | 5856 | Para_Reserve_Analog_LiveZero15 |  | 18741
[8 empty] | 18742 | Para_Reserve_Analog_LiveZero16 | Para_Reserve_Analog_LiveZero16 | 5857 | Para_Reserve_Analog_LiveZero16 |  | 18742
[8 empty] | 18743 | Para_Reserve_Analog_LiveZero2 | Para_Reserve_Analog_LiveZero2 | 5858 | Para_Reserve_Analog_LiveZero2 |  | 18743
[8 empty] | 18744 | Para_Reserve_Analog_LiveZero3 | Para_Reserve_Analog_LiveZero3 | 5859 | Para_Reserve_Analog_LiveZero3 |  | 18744
[8 empty] | 18745 | Para_Reserve_Analog_LiveZero4 | Para_Reserve_Analog_LiveZero4 | 5860 | Para_Reserve_Analog_LiveZero4 |  | 18745
[8 empty] | 18746 | Para_Reserve_Analog_LiveZero5 | Para_Reserve_Analog_LiveZero5 | 5861 | Para_Reserve_Analog_LiveZero5 |  | 18746
[8 empty] | 18747 | Para_Reserve_Analog_LiveZero6 | Para_Reserve_Analog_LiveZero6 | 5862 | Para_Reserve_Analog_LiveZero6 |  | 18747
[8 empty] | 18748 | Para_Reserve_Analog_LiveZero7 | Para_Reserve_Analog_LiveZero7 | 5863 | Para_Reserve_Analog_LiveZero7 |  | 18748
[8 empty] | 18749 | Para_Reserve_Analog_LiveZero8 | Para_Reserve_Analog_LiveZero8 | 5864 | Para_Reserve_Analog_LiveZero8 |  | 18749
[8 empty] | 18750 | Para_Reserve_Analog_LiveZero9 | Para_Reserve_Analog_LiveZero9 | 5865 | Para_Reserve_Analog_LiveZero9 |  | 18750
[8 empty] | 18751 | Para_Reserve_Analog_ScaleBegin1 | Para_Reserve_Analog_ScaleBegin1 | 5866 | Para_Reserve_Analog_ScaleBegin1 |  | 18751
[8 empty] | 18752 | Para_Reserve_Analog_ScaleBegin10 | Para_Reserve_Analog_ScaleBegin10 | 5867 | Para_Reserve_Analog_ScaleBegin10 |  | 18752
[8 empty] | 18753 | Para_Reserve_Analog_ScaleBegin11 | Para_Reserve_Analog_ScaleBegin11 | 5868 | Para_Reserve_Analog_ScaleBegin11 |  | 18753
[8 empty] | 18754 | Para_Reserve_Analog_ScaleBegin12 | Para_Reserve_Analog_ScaleBegin12 | 5869 | Para_Reserve_Analog_ScaleBegin12 |  | 18754
[8 empty] | 18755 | Para_Reserve_Analog_ScaleBegin13 | Para_Reserve_Analog_ScaleBegin13 | 5870 | Para_Reserve_Analog_ScaleBegin13 |  | 18755
[8 empty] | 18756 | Para_Reserve_Analog_ScaleBegin14 | Para_Reserve_Analog_ScaleBegin14 | 5871 | Para_Reserve_Analog_ScaleBegin14 |  | 18756
[8 empty] | 18757 | Para_Reserve_Analog_ScaleBegin15 | Para_Reserve_Analog_ScaleBegin15 | 5872 | Para_Reserve_Analog_ScaleBegin15 |  | 18757
[8 empty] | 18758 | Para_Reserve_Analog_ScaleBegin16 | Para_Reserve_Analog_ScaleBegin16 | 5873 | Para_Reserve_Analog_ScaleBegin16 |  | 18758
[8 empty] | 18759 | Para_Reserve_Analog_ScaleBegin2 | Para_Reserve_Analog_ScaleBegin2 | 5874 | Para_Reserve_Analog_ScaleBegin2 |  | 18759
[8 empty] | 18760 | Para_Reserve_Analog_ScaleBegin3 | Para_Reserve_Analog_ScaleBegin3 | 5875 | Para_Reserve_Analog_ScaleBegin3 |  | 18760
[8 empty] | 18761 | Para_Reserve_Analog_ScaleBegin4 | Para_Reserve_Analog_ScaleBegin4 | 5876 | Para_Reserve_Analog_ScaleBegin4 |  | 18761
[8 empty] | 18762 | Para_Reserve_Analog_ScaleBegin5 | Para_Reserve_Analog_ScaleBegin5 | 5877 | Para_Reserve_Analog_ScaleBegin5 |  | 18762
[8 empty] | 18763 | Para_Reserve_Analog_ScaleBegin6 | Para_Reserve_Analog_ScaleBegin6 | 5878 | Para_Reserve_Analog_ScaleBegin6 |  | 18763
[8 empty] | 18764 | Para_Reserve_Analog_ScaleBegin7 | Para_Reserve_Analog_ScaleBegin7 | 5879 | Para_Reserve_Analog_ScaleBegin7 |  | 18764
[8 empty] | 18765 | Para_Reserve_Analog_ScaleBegin8 | Para_Reserve_Analog_ScaleBegin8 | 5880 | Para_Reserve_Analog_ScaleBegin8 |  | 18765
[8 empty] | 18766 | Para_Reserve_Analog_ScaleBegin9 | Para_Reserve_Analog_ScaleBegin9 | 5881 | Para_Reserve_Analog_ScaleBegin9 |  | 18766
[8 empty] | 18767 | Para_Reserve_Analog_ScaleEnd1 | Para_Reserve_Analog_ScaleEnd1 | 5882 | Para_Reserve_Analog_ScaleEnd1 |  | 18767
[8 empty] | 18768 | Para_Reserve_Analog_ScaleEnd10 | Para_Reserve_Analog_ScaleEnd10 | 5883 | Para_Reserve_Analog_ScaleEnd10 |  | 18768
[8 empty] | 18769 | Para_Reserve_Analog_ScaleEnd11 | Para_Reserve_Analog_ScaleEnd11 | 5884 | Para_Reserve_Analog_ScaleEnd11 |  | 18769
[8 empty] | 18770 | Para_Reserve_Analog_ScaleEnd12 | Para_Reserve_Analog_ScaleEnd12 | 5885 | Para_Reserve_Analog_ScaleEnd12 |  | 18770
[8 empty] | 18771 | Para_Reserve_Analog_ScaleEnd13 | Para_Reserve_Analog_ScaleEnd13 | 5886 | Para_Reserve_Analog_ScaleEnd13 |  | 18771
[8 empty] | 18772 | Para_Reserve_Analog_ScaleEnd14 | Para_Reserve_Analog_ScaleEnd14 | 5887 | Para_Reserve_Analog_ScaleEnd14 |  | 18772
[8 empty] | 18773 | Para_Reserve_Analog_ScaleEnd15 | Para_Reserve_Analog_ScaleEnd15 | 5888 | Para_Reserve_Analog_ScaleEnd15 |  | 18773
[8 empty] | 18774 | Para_Reserve_Analog_ScaleEnd16 | Para_Reserve_Analog_ScaleEnd16 | 5889 | Para_Reserve_Analog_ScaleEnd16 |  | 18774
[8 empty] | 18775 | Para_Reserve_Analog_ScaleEnd2 | Para_Reserve_Analog_ScaleEnd2 | 5890 | Para_Reserve_Analog_ScaleEnd2 |  | 18775
[8 empty] | 18776 | Para_Reserve_Analog_ScaleEnd3 | Para_Reserve_Analog_ScaleEnd3 | 5891 | Para_Reserve_Analog_ScaleEnd3 |  | 18776
[8 empty] | 18777 | Para_Reserve_Analog_ScaleEnd4 | Para_Reserve_Analog_ScaleEnd4 | 5892 | Para_Reserve_Analog_ScaleEnd4 |  | 18777
[8 empty] | 18778 | Para_Reserve_Analog_ScaleEnd5 | Para_Reserve_Analog_ScaleEnd5 | 5893 | Para_Reserve_Analog_ScaleEnd5 |  | 18778
[8 empty] | 18779 | Para_Reserve_Analog_ScaleEnd6 | Para_Reserve_Analog_ScaleEnd6 | 5894 | Para_Reserve_Analog_ScaleEnd6 |  | 18779
[8 empty] | 18780 | Para_Reserve_Analog_ScaleEnd7 | Para_Reserve_Analog_ScaleEnd7 | 5895 | Para_Reserve_Analog_ScaleEnd7 |  | 18780
[8 empty] | 18781 | Para_Reserve_Analog_ScaleEnd8 | Para_Reserve_Analog_ScaleEnd8 | 5896 | Para_Reserve_Analog_ScaleEnd8 |  | 18781
[8 empty] | 18782 | Para_Reserve_Analog_ScaleEnd9 | Para_Reserve_Analog_ScaleEnd9 | 5897 | Para_Reserve_Analog_ScaleEnd9 |  | 18782
[8 empty] | 18783 | Para_Reserve_Para2_Par031 | Para_Reserve_Para2_Par031 | 5898 | Para_Reserve_Para2_Par031 |  | 18783
[8 empty] | 18784 | Para_Reserve_Para2_Par032 | Para_Reserve_Para2_Par032 | 5899 | Para_Reserve_Para2_Par032 |  | 18784
[8 empty] | 18785 | Para_Reserve_Para2_Par033 | Para_Reserve_Para2_Par033 | 5900 | Para_Reserve_Para2_Par033 |  | 18785
[8 empty] | 18786 | Para_Reserve_Para2_Par034 | Para_Reserve_Para2_Par034 | 5901 | Para_Reserve_Para2_Par034 |  | 18786
[8 empty] | 18787 | Para_Reserve_Para2_Par035 | Para_Reserve_Para2_Par035 | 5902 | Para_Reserve_Para2_Par035 |  | 18787
[8 empty] | 18788 | Para_Reserve_Para2_Par036 | Para_Reserve_Para2_Par036 | 5903 | Para_Reserve_Para2_Par036 |  | 18788
[8 empty] | 18789 | Para_Reserve_Para2_Par037 | Para_Reserve_Para2_Par037 | 5904 | Para_Reserve_Para2_Par037 |  | 18789
[8 empty] | 18790 | Para_Reserve_Para2_Par038 | Para_Reserve_Para2_Par038 | 5905 | Para_Reserve_Para2_Par038 |  | 18790
[8 empty] | 18791 | Para_Reserve_Para2_Par039 | Para_Reserve_Para2_Par039 | 5906 | Para_Reserve_Para2_Par039 |  | 18791
[8 empty] | 18792 | Para_Reserve_Para2_Par040 | Para_Reserve_Para2_Par040 | 5907 | Para_Reserve_Para2_Par040 |  | 18792
[8 empty] | 18793 | Para_Reserve_Para2_Par041 | Para_Reserve_Para2_Par041 | 5908 | Para_Reserve_Para2_Par041 |  | 18793
[8 empty] | 18794 | Para_Reserve_Para2_Par042 | Para_Reserve_Para2_Par042 | 5909 | Para_Reserve_Para2_Par042 |  | 18794
[8 empty] | 18795 | Para_Reserve_Para2_Par043 | Para_Reserve_Para2_Par043 | 5910 | Para_Reserve_Para2_Par043 |  | 18795
[8 empty] | 18796 | Para_Reserve_Para2_Par044 | Para_Reserve_Para2_Par044 | 5911 | Para_Reserve_Para2_Par044 |  | 18796
[8 empty] | 18797 | Para_Reserve_Para2_Par045 | Para_Reserve_Para2_Par045 | 5912 | Para_Reserve_Para2_Par045 |  | 18797
[8 empty] | 18798 | Para_Reserve_Para2_Par046 | Para_Reserve_Para2_Par046 | 5913 | Para_Reserve_Para2_Par046 |  | 18798
[8 empty] | 18799 | Para_Reserve_Para2_Par047 | Para_Reserve_Para2_Par047 | 5914 | Para_Reserve_Para2_Par047 |  | 18799
[8 empty] | 18800 | Para_Reserve_Para2_Par048 | Para_Reserve_Para2_Par048 | 5915 | Para_Reserve_Para2_Par048 |  | 18800
[8 empty] | 18801 | Para_Reserve_Para2_Par049 | Para_Reserve_Para2_Par049 | 5916 | Para_Reserve_Para2_Par049 |  | 18801
[8 empty] | 18802 | Para_Reserve_Para2_Par050 | Para_Reserve_Para2_Par050 | 5917 | Para_Reserve_Para2_Par050 |  | 18802
[8 empty] | 18803 | Para_Reserve_Para2_Par051 | Para_Reserve_Para2_Par051 | 5918 | Para_Reserve_Para2_Par051 |  | 18803
[8 empty] | 18804 | Para_Reserve_Para2_Par052 | Para_Reserve_Para2_Par052 | 5919 | Para_Reserve_Para2_Par052 |  | 18804
[8 empty] | 18805 | Para_Reserve_Para2_Par053 | Para_Reserve_Para2_Par053 | 5920 | Para_Reserve_Para2_Par053 |  | 18805
[8 empty] | 18806 | Para_Reserve_Para2_Par054 | Para_Reserve_Para2_Par054 | 5921 | Para_Reserve_Para2_Par054 |  | 18806
[8 empty] | 18807 | Para_Reserve_Para2_Par055 | Para_Reserve_Para2_Par055 | 5922 | Para_Reserve_Para2_Par055 |  | 18807
[8 empty] | 18808 | Para_Reserve_Para2_Par056 | Para_Reserve_Para2_Par056 | 5923 | Para_Reserve_Para2_Par056 |  | 18808
[8 empty] | 18809 | Para_Reserve_Para2_Par057 | Para_Reserve_Para2_Par057 | 5924 | Para_Reserve_Para2_Par057 |  | 18809
[8 empty] | 18810 | Para_Reserve_Para2_Par058 | Para_Reserve_Para2_Par058 | 5925 | Para_Reserve_Para2_Par058 |  | 18810
[8 empty] | 18811 | Para_Reserve_Para2_Par059 | Para_Reserve_Para2_Par059 | 5926 | Para_Reserve_Para2_Par059 |  | 18811
[8 empty] | 18812 | Para_Reserve_Para2_Par060 | Para_Reserve_Para2_Par060 | 5927 | Para_Reserve_Para2_Par060 |  | 18812
[8 empty] | 18813 | Para_Reserve_Para2_ParaName031 | Para_Reserve_Para2_ParaName031 | 5928 | Para_Reserve_Para2_ParaName031 |  | 18813
[8 empty] | 18814 | Para_Reserve_Para2_ParaName032 | Para_Reserve_Para2_ParaName032 | 5929 | Para_Reserve_Para2_ParaName032 |  | 18814
[8 empty] | 18815 | Para_Reserve_Para2_ParaName033 | Para_Reserve_Para2_ParaName033 | 5930 | Para_Reserve_Para2_ParaName033 |  | 18815
[8 empty] | 18816 | Para_Reserve_Para2_ParaName034 | Para_Reserve_Para2_ParaName034 | 5931 | Para_Reserve_Para2_ParaName034 |  | 18816
[8 empty] | 18817 | Para_Reserve_Para2_ParaName035 | Para_Reserve_Para2_ParaName035 | 5932 | Para_Reserve_Para2_ParaName035 |  | 18817
[8 empty] | 18818 | Para_Reserve_Para2_ParaName036 | Para_Reserve_Para2_ParaName036 | 5933 | Para_Reserve_Para2_ParaName036 |  | 18818
[8 empty] | 18819 | Para_Reserve_Para2_ParaName037 | Para_Reserve_Para2_ParaName037 | 5934 | Para_Reserve_Para2_ParaName037 |  | 18819
[8 empty] | 18820 | Para_Reserve_Para2_ParaName038 | Para_Reserve_Para2_ParaName038 | 5935 | Para_Reserve_Para2_ParaName038 |  | 18820
[8 empty] | 18821 | Para_Reserve_Para2_ParaName039 | Para_Reserve_Para2_ParaName039 | 5936 | Para_Reserve_Para2_ParaName039 |  | 18821
[8 empty] | 18822 | Para_Reserve_Para2_ParaName040 | Para_Reserve_Para2_ParaName040 | 5937 | Para_Reserve_Para2_ParaName040 |  | 18822
[8 empty] | 18823 | Para_Reserve_Para2_ParaName041 | Para_Reserve_Para2_ParaName041 | 5938 | Para_Reserve_Para2_ParaName041 |  | 18823
[8 empty] | 18824 | Para_Reserve_Para2_ParaName042 | Para_Reserve_Para2_ParaName042 | 5939 | Para_Reserve_Para2_ParaName042 |  | 18824
[8 empty] | 18825 | Para_Reserve_Para2_ParaName043 | Para_Reserve_Para2_ParaName043 | 5940 | Para_Reserve_Para2_ParaName043 |  | 18825
[8 empty] | 18826 | Para_Reserve_Para2_ParaName044 | Para_Reserve_Para2_ParaName044 | 5941 | Para_Reserve_Para2_ParaName044 |  | 18826
[8 empty] | 18827 | Para_Reserve_Para2_ParaName045 | Para_Reserve_Para2_ParaName045 | 5942 | Para_Reserve_Para2_ParaName045 |  | 18827
[8 empty] | 18828 | Para_Reserve_Para2_ParaName046 | Para_Reserve_Para2_ParaName046 | 5943 | Para_Reserve_Para2_ParaName046 |  | 18828
[8 empty] | 18829 | Para_Reserve_Para2_ParaName047 | Para_Reserve_Para2_ParaName047 | 5944 | Para_Reserve_Para2_ParaName047 |  | 18829
[8 empty] | 18830 | Para_Reserve_Para2_ParaName048 | Para_Reserve_Para2_ParaName048 | 5945 | Para_Reserve_Para2_ParaName048 |  | 18830
[8 empty] | 18831 | Para_Reserve_Para2_ParaName049 | Para_Reserve_Para2_ParaName049 | 5946 | Para_Reserve_Para2_ParaName049 |  | 18831
[8 empty] | 18832 | Para_Reserve_Para2_ParaName050 | Para_Reserve_Para2_ParaName050 | 5947 | Para_Reserve_Para2_ParaName050 |  | 18832
[8 empty] | 18833 | Para_Reserve_Para2_ParaName051 | Para_Reserve_Para2_ParaName051 | 5948 | Para_Reserve_Para2_ParaName051 |  | 18833
[8 empty] | 18834 | Para_Reserve_Para2_ParaName052 | Para_Reserve_Para2_ParaName052 | 5949 | Para_Reserve_Para2_ParaName052 |  | 18834
[8 empty] | 18835 | Para_Reserve_Para2_ParaName053 | Para_Reserve_Para2_ParaName053 | 5950 | Para_Reserve_Para2_ParaName053 |  | 18835
[8 empty] | 18836 | Para_Reserve_Para2_ParaName054 | Para_Reserve_Para2_ParaName054 | 5951 | Para_Reserve_Para2_ParaName054 |  | 18836
[8 empty] | 18837 | Para_Reserve_Para2_ParaName055 | Para_Reserve_Para2_ParaName055 | 5952 | Para_Reserve_Para2_ParaName055 |  | 18837
[8 empty] | 18838 | Para_Reserve_Para2_ParaName056 | Para_Reserve_Para2_ParaName056 | 5953 | Para_Reserve_Para2_ParaName056 |  | 18838
[8 empty] | 18839 | Para_Reserve_Para2_ParaName057 | Para_Reserve_Para2_ParaName057 | 5954 | Para_Reserve_Para2_ParaName057 |  | 18839
[8 empty] | 18840 | Para_Reserve_Para2_ParaName058 | Para_Reserve_Para2_ParaName058 | 5955 | Para_Reserve_Para2_ParaName058 |  | 18840
[8 empty] | 18841 | Para_Reserve_Para2_ParaName059 | Para_Reserve_Para2_ParaName059 | 5956 | Para_Reserve_Para2_ParaName059 |  | 18841
[8 empty] | 18842 | Para_Reserve_Para2_ParaName060 | Para_Reserve_Para2_ParaName060 | 5957 | Para_Reserve_Para2_ParaName060 |  | 18842
[8 empty] | 18843 | Para_Reserve_Para2_ParaNameF031 | Para_Reserve_Para2_ParaNameF031 | 5958 | Para_Reserve_Para2_ParaNameF031 |  | 18843
[8 empty] | 18844 | Para_Reserve_Para2_ParaNameF032 | Para_Reserve_Para2_ParaNameF032 | 5959 | Para_Reserve_Para2_ParaNameF032 |  | 18844
[8 empty] | 18845 | Para_Reserve_Para2_ParaNameF033 | Para_Reserve_Para2_ParaNameF033 | 5960 | Para_Reserve_Para2_ParaNameF033 |  | 18845
[8 empty] | 18846 | Para_Reserve_Para2_ParaNameF034 | Para_Reserve_Para2_ParaNameF034 | 5961 | Para_Reserve_Para2_ParaNameF034 |  | 18846
[8 empty] | 18847 | Para_Reserve_Para2_ParaNameF035 | Para_Reserve_Para2_ParaNameF035 | 5962 | Para_Reserve_Para2_ParaNameF035 |  | 18847
[8 empty] | 18848 | Para_Reserve_Para2_ParaNameF036 | Para_Reserve_Para2_ParaNameF036 | 5963 | Para_Reserve_Para2_ParaNameF036 |  | 18848
[8 empty] | 18849 | Para_Reserve_Para2_ParaNameF037 | Para_Reserve_Para2_ParaNameF037 | 5964 | Para_Reserve_Para2_ParaNameF037 |  | 18849
[8 empty] | 18850 | Para_Reserve_Para2_ParaNameF038 | Para_Reserve_Para2_ParaNameF038 | 5965 | Para_Reserve_Para2_ParaNameF038 |  | 18850
[8 empty] | 18851 | Para_Reserve_Para2_ParaNameF039 | Para_Reserve_Para2_ParaNameF039 | 5966 | Para_Reserve_Para2_ParaNameF039 |  | 18851
[8 empty] | 18852 | Para_Reserve_Para2_ParaNameF040 | Para_Reserve_Para2_ParaNameF040 | 5967 | Para_Reserve_Para2_ParaNameF040 |  | 18852
[8 empty] | 18853 | Para_Reserve_Para2_ParaNameF041 | Para_Reserve_Para2_ParaNameF041 | 5968 | Para_Reserve_Para2_ParaNameF041 |  | 18853
[8 empty] | 18854 | Para_Reserve_Para2_ParaNameF042 | Para_Reserve_Para2_ParaNameF042 | 5969 | Para_Reserve_Para2_ParaNameF042 |  | 18854
[8 empty] | 18855 | Para_Reserve_Para2_ParaNameF043 | Para_Reserve_Para2_ParaNameF043 | 5970 | Para_Reserve_Para2_ParaNameF043 |  | 18855
[8 empty] | 18856 | Para_Reserve_Para2_ParaNameF044 | Para_Reserve_Para2_ParaNameF044 | 5971 | Para_Reserve_Para2_ParaNameF044 |  | 18856
[8 empty] | 18857 | Para_Reserve_Para2_ParaNameF045 | Para_Reserve_Para2_ParaNameF045 | 5972 | Para_Reserve_Para2_ParaNameF045 |  | 18857
[8 empty] | 18858 | Para_Reserve_Para2_ParaNameF046 | Para_Reserve_Para2_ParaNameF046 | 5973 | Para_Reserve_Para2_ParaNameF046 |  | 18858
[8 empty] | 18859 | Para_Reserve_Para2_ParaNameF047 | Para_Reserve_Para2_ParaNameF047 | 5974 | Para_Reserve_Para2_ParaNameF047 |  | 18859
[8 empty] | 18860 | Para_Reserve_Para2_ParaNameF048 | Para_Reserve_Para2_ParaNameF048 | 5975 | Para_Reserve_Para2_ParaNameF048 |  | 18860
[8 empty] | 18861 | Para_Reserve_Para2_ParaNameF049 | Para_Reserve_Para2_ParaNameF049 | 5976 | Para_Reserve_Para2_ParaNameF049 |  | 18861
[8 empty] | 18862 | Para_Reserve_Para2_ParaNameF050 | Para_Reserve_Para2_ParaNameF050 | 5977 | Para_Reserve_Para2_ParaNameF050 |  | 18862
[8 empty] | 18863 | Para_Reserve_Para2_ParaNameF051 | Para_Reserve_Para2_ParaNameF051 | 5978 | Para_Reserve_Para2_ParaNameF051 |  | 18863
[8 empty] | 18864 | Para_Reserve_Para2_ParaNameF052 | Para_Reserve_Para2_ParaNameF052 | 5979 | Para_Reserve_Para2_ParaNameF052 |  | 18864
[8 empty] | 18865 | Para_Reserve_Para2_ParaNameF053 | Para_Reserve_Para2_ParaNameF053 | 5980 | Para_Reserve_Para2_ParaNameF053 |  | 18865
[8 empty] | 18866 | Para_Reserve_Para2_ParaNameF054 | Para_Reserve_Para2_ParaNameF054 | 5981 | Para_Reserve_Para2_ParaNameF054 |  | 18866
[8 empty] | 18867 | Para_Reserve_Para2_ParaNameF055 | Para_Reserve_Para2_ParaNameF055 | 5982 | Para_Reserve_Para2_ParaNameF055 |  | 18867
[8 empty] | 18868 | Para_Reserve_Para2_ParaNameF056 | Para_Reserve_Para2_ParaNameF056 | 5983 | Para_Reserve_Para2_ParaNameF056 |  | 18868
[8 empty] | 18869 | Para_Reserve_Para2_ParaNameF057 | Para_Reserve_Para2_ParaNameF057 | 5984 | Para_Reserve_Para2_ParaNameF057 |  | 18869
[8 empty] | 18870 | Para_Reserve_Para2_ParaNameF058 | Para_Reserve_Para2_ParaNameF058 | 5985 | Para_Reserve_Para2_ParaNameF058 |  | 18870
[8 empty] | 18871 | Para_Reserve_Para2_ParaNameF059 | Para_Reserve_Para2_ParaNameF059 | 5986 | Para_Reserve_Para2_ParaNameF059 |  | 18871
[8 empty] | 18872 | Para_Reserve_Para2_ParaNameF060 | Para_Reserve_Para2_ParaNameF060 | 5987 | Para_Reserve_Para2_ParaNameF060 |  | 18872
[8 empty] | 18873 | Para_Reserve_Para2_ParaUnit031 | Para_Reserve_Para2_ParaUnit031 | 5988 | Para_Reserve_Para2_ParaUnit031 |  | 18873
[8 empty] | 18874 | Para_Reserve_Para2_ParaUnit032 | Para_Reserve_Para2_ParaUnit032 | 5989 | Para_Reserve_Para2_ParaUnit032 |  | 18874
[8 empty] | 18875 | Para_Reserve_Para2_ParaUnit033 | Para_Reserve_Para2_ParaUnit033 | 5990 | Para_Reserve_Para2_ParaUnit033 |  | 18875
[8 empty] | 18876 | Para_Reserve_Para2_ParaUnit034 | Para_Reserve_Para2_ParaUnit034 | 5991 | Para_Reserve_Para2_ParaUnit034 |  | 18876
[8 empty] | 18877 | Para_Reserve_Para2_ParaUnit035 | Para_Reserve_Para2_ParaUnit035 | 5992 | Para_Reserve_Para2_ParaUnit035 |  | 18877
[8 empty] | 18878 | Para_Reserve_Para2_ParaUnit036 | Para_Reserve_Para2_ParaUnit036 | 5993 | Para_Reserve_Para2_ParaUnit036 |  | 18878
[8 empty] | 18879 | Para_Reserve_Para2_ParaUnit037 | Para_Reserve_Para2_ParaUnit037 | 5994 | Para_Reserve_Para2_ParaUnit037 |  | 18879
[8 empty] | 18880 | Para_Reserve_Para2_ParaUnit038 | Para_Reserve_Para2_ParaUnit038 | 5995 | Para_Reserve_Para2_ParaUnit038 |  | 18880
[8 empty] | 18881 | Para_Reserve_Para2_ParaUnit039 | Para_Reserve_Para2_ParaUnit039 | 5996 | Para_Reserve_Para2_ParaUnit039 |  | 18881
[8 empty] | 18882 | Para_Reserve_Para2_ParaUnit040 | Para_Reserve_Para2_ParaUnit040 | 5997 | Para_Reserve_Para2_ParaUnit040 |  | 18882
[8 empty] | 18883 | Para_Reserve_Para2_ParaUnit041 | Para_Reserve_Para2_ParaUnit041 | 5998 | Para_Reserve_Para2_ParaUnit041 |  | 18883
[8 empty] | 18884 | Para_Reserve_Para2_ParaUnit042 | Para_Reserve_Para2_ParaUnit042 | 5999 | Para_Reserve_Para2_ParaUnit042 |  | 18884
[8 empty] | 18885 | Para_Reserve_Para2_ParaUnit043 | Para_Reserve_Para2_ParaUnit043 | 6000 | Para_Reserve_Para2_ParaUnit043 |  | 18885
[8 empty] | 18886 | Para_Reserve_Para2_ParaUnit044 | Para_Reserve_Para2_ParaUnit044 | 6001 | Para_Reserve_Para2_ParaUnit044 |  | 18886
[8 empty] | 18887 | Para_Reserve_Para2_ParaUnit045 | Para_Reserve_Para2_ParaUnit045 | 6002 | Para_Reserve_Para2_ParaUnit045 |  | 18887
[8 empty] | 18888 | Para_Reserve_Para2_ParaUnit046 | Para_Reserve_Para2_ParaUnit046 | 6003 | Para_Reserve_Para2_ParaUnit046 |  | 18888
[8 empty] | 18889 | Para_Reserve_Para2_ParaUnit047 | Para_Reserve_Para2_ParaUnit047 | 6004 | Para_Reserve_Para2_ParaUnit047 |  | 18889
[8 empty] | 18890 | Para_Reserve_Para2_ParaUnit048 | Para_Reserve_Para2_ParaUnit048 | 6005 | Para_Reserve_Para2_ParaUnit048 |  | 18890
[8 empty] | 18891 | Para_Reserve_Para2_ParaUnit049 | Para_Reserve_Para2_ParaUnit049 | 6006 | Para_Reserve_Para2_ParaUnit049 |  | 18891
[8 empty] | 18892 | Para_Reserve_Para2_ParaUnit050 | Para_Reserve_Para2_ParaUnit050 | 6007 | Para_Reserve_Para2_ParaUnit050 |  | 18892
[8 empty] | 18893 | Para_Reserve_Para2_ParaUnit051 | Para_Reserve_Para2_ParaUnit051 | 6008 | Para_Reserve_Para2_ParaUnit051 |  | 18893
[8 empty] | 18894 | Para_Reserve_Para2_ParaUnit052 | Para_Reserve_Para2_ParaUnit052 | 6009 | Para_Reserve_Para2_ParaUnit052 |  | 18894
[8 empty] | 18895 | Para_Reserve_Para2_ParaUnit053 | Para_Reserve_Para2_ParaUnit053 | 6010 | Para_Reserve_Para2_ParaUnit053 |  | 18895
[8 empty] | 18896 | Para_Reserve_Para2_ParaUnit054 | Para_Reserve_Para2_ParaUnit054 | 6011 | Para_Reserve_Para2_ParaUnit054 |  | 18896
[8 empty] | 18897 | Para_Reserve_Para2_ParaUnit055 | Para_Reserve_Para2_ParaUnit055 | 6012 | Para_Reserve_Para2_ParaUnit055 |  | 18897
[8 empty] | 18898 | Para_Reserve_Para2_ParaUnit056 | Para_Reserve_Para2_ParaUnit056 | 6013 | Para_Reserve_Para2_ParaUnit056 |  | 18898
[8 empty] | 18899 | Para_Reserve_Para2_ParaUnit057 | Para_Reserve_Para2_ParaUnit057 | 6014 | Para_Reserve_Para2_ParaUnit057 |  | 18899
[8 empty] | 18900 | Para_Reserve_Para2_ParaUnit058 | Para_Reserve_Para2_ParaUnit058 | 6015 | Para_Reserve_Para2_ParaUnit058 |  | 18900
[8 empty] | 18901 | Para_Reserve_Para2_ParaUnit059 | Para_Reserve_Para2_ParaUnit059 | 6016 | Para_Reserve_Para2_ParaUnit059 |  | 18901
[8 empty] | 18902 | Para_Reserve_Para2_ParaUnit060 | Para_Reserve_Para2_ParaUnit060 | 6017 | Para_Reserve_Para2_ParaUnit060 |  | 18902
[8 empty] | 18903 | Para_Reserve_Para3_Par061 | Para_Reserve_Para3_Par061 | 6018 | Para_Reserve_Para3_Par061 |  | 18903
[8 empty] | 18904 | Para_Reserve_Para3_Par062 | Para_Reserve_Para3_Par062 | 6019 | Para_Reserve_Para3_Par062 |  | 18904
[8 empty] | 18905 | Para_Reserve_Para3_Par063 | Para_Reserve_Para3_Par063 | 6020 | Para_Reserve_Para3_Par063 |  | 18905
[8 empty] | 18906 | Para_Reserve_Para3_Par064 | Para_Reserve_Para3_Par064 | 6021 | Para_Reserve_Para3_Par064 |  | 18906
[8 empty] | 18907 | Para_Reserve_Para3_Par065 | Para_Reserve_Para3_Par065 | 6022 | Para_Reserve_Para3_Par065 |  | 18907
[8 empty] | 18908 | Para_Reserve_Para3_Par066 | Para_Reserve_Para3_Par066 | 6023 | Para_Reserve_Para3_Par066 |  | 18908
[8 empty] | 18909 | Para_Reserve_Para3_Par067 | Para_Reserve_Para3_Par067 | 6024 | Para_Reserve_Para3_Par067 |  | 18909
[8 empty] | 18910 | Para_Reserve_Para3_Par068 | Para_Reserve_Para3_Par068 | 6025 | Para_Reserve_Para3_Par068 |  | 18910
[8 empty] | 18911 | Para_Reserve_Para3_Par069 | Para_Reserve_Para3_Par069 | 6026 | Para_Reserve_Para3_Par069 |  | 18911
[8 empty] | 18912 | Para_Reserve_Para3_Par070 | Para_Reserve_Para3_Par070 | 6027 | Para_Reserve_Para3_Par070 |  | 18912
[8 empty] | 18913 | Para_Reserve_Para3_ParaName061 | Para_Reserve_Para3_ParaName061 | 6028 | Para_Reserve_Para3_ParaName061 |  | 18913
[8 empty] | 18914 | Para_Reserve_Para3_ParaName062 | Para_Reserve_Para3_ParaName062 | 6029 | Para_Reserve_Para3_ParaName062 |  | 18914
[8 empty] | 18915 | Para_Reserve_Para3_ParaName063 | Para_Reserve_Para3_ParaName063 | 6030 | Para_Reserve_Para3_ParaName063 |  | 18915
[8 empty] | 18916 | Para_Reserve_Para3_ParaName064 | Para_Reserve_Para3_ParaName064 | 6031 | Para_Reserve_Para3_ParaName064 |  | 18916
[8 empty] | 18917 | Para_Reserve_Para3_ParaName065 | Para_Reserve_Para3_ParaName065 | 6032 | Para_Reserve_Para3_ParaName065 |  | 18917
[8 empty] | 18918 | Para_Reserve_Para3_ParaName066 | Para_Reserve_Para3_ParaName066 | 6033 | Para_Reserve_Para3_ParaName066 |  | 18918
[8 empty] | 18919 | Para_Reserve_Para3_ParaName067 | Para_Reserve_Para3_ParaName067 | 6034 | Para_Reserve_Para3_ParaName067 |  | 18919
[8 empty] | 18920 | Para_Reserve_Para3_ParaName068 | Para_Reserve_Para3_ParaName068 | 6035 | Para_Reserve_Para3_ParaName068 |  | 18920
[8 empty] | 18921 | Para_Reserve_Para3_ParaName069 | Para_Reserve_Para3_ParaName069 | 6036 | Para_Reserve_Para3_ParaName069 |  | 18921
[8 empty] | 18922 | Para_Reserve_Para3_ParaName070 | Para_Reserve_Para3_ParaName070 | 6037 | Para_Reserve_Para3_ParaName070 |  | 18922
[8 empty] | 18923 | Para_Reserve_Para3_ParaNameF061 | Para_Reserve_Para3_ParaNameF061 | 6038 | Para_Reserve_Para3_ParaNameF061 |  | 18923
[8 empty] | 18924 | Para_Reserve_Para3_ParaNameF062 | Para_Reserve_Para3_ParaNameF062 | 6039 | Para_Reserve_Para3_ParaNameF062 |  | 18924
[8 empty] | 18925 | Para_Reserve_Para3_ParaNameF063 | Para_Reserve_Para3_ParaNameF063 | 6040 | Para_Reserve_Para3_ParaNameF063 |  | 18925
[8 empty] | 18926 | Para_Reserve_Para3_ParaNameF064 | Para_Reserve_Para3_ParaNameF064 | 6041 | Para_Reserve_Para3_ParaNameF064 |  | 18926
[8 empty] | 18927 | Para_Reserve_Para3_ParaNameF065 | Para_Reserve_Para3_ParaNameF065 | 6042 | Para_Reserve_Para3_ParaNameF065 |  | 18927
[8 empty] | 18928 | Para_Reserve_Para3_ParaNameF066 | Para_Reserve_Para3_ParaNameF066 | 6043 | Para_Reserve_Para3_ParaNameF066 |  | 18928
[8 empty] | 18929 | Para_Reserve_Para3_ParaNameF067 | Para_Reserve_Para3_ParaNameF067 | 6044 | Para_Reserve_Para3_ParaNameF067 |  | 18929
[8 empty] | 18930 | Para_Reserve_Para3_ParaNameF068 | Para_Reserve_Para3_ParaNameF068 | 6045 | Para_Reserve_Para3_ParaNameF068 |  | 18930
[8 empty] | 18931 | Para_Reserve_Para3_ParaNameF069 | Para_Reserve_Para3_ParaNameF069 | 6046 | Para_Reserve_Para3_ParaNameF069 |  | 18931
[8 empty] | 18932 | Para_Reserve_Para3_ParaNameF070 | Para_Reserve_Para3_ParaNameF070 | 6047 | Para_Reserve_Para3_ParaNameF070 |  | 18932
[8 empty] | 18933 | Para_Reserve_Para3_ParaUnit061 | Para_Reserve_Para3_ParaUnit061 | 6048 | Para_Reserve_Para3_ParaUnit061 |  | 18933
[8 empty] | 18934 | Para_Reserve_Para3_ParaUnit062 | Para_Reserve_Para3_ParaUnit062 | 6049 | Para_Reserve_Para3_ParaUnit062 |  | 18934
[8 empty] | 18935 | Para_Reserve_Para3_ParaUnit063 | Para_Reserve_Para3_ParaUnit063 | 6050 | Para_Reserve_Para3_ParaUnit063 |  | 18935
[8 empty] | 18936 | Para_Reserve_Para3_ParaUnit064 | Para_Reserve_Para3_ParaUnit064 | 6051 | Para_Reserve_Para3_ParaUnit064 |  | 18936
[8 empty] | 18937 | Para_Reserve_Para3_ParaUnit065 | Para_Reserve_Para3_ParaUnit065 | 6052 | Para_Reserve_Para3_ParaUnit065 |  | 18937
[8 empty] | 18938 | Para_Reserve_Para3_ParaUnit066 | Para_Reserve_Para3_ParaUnit066 | 6053 | Para_Reserve_Para3_ParaUnit066 |  | 18938
[8 empty] | 18939 | Para_Reserve_Para3_ParaUnit067 | Para_Reserve_Para3_ParaUnit067 | 6054 | Para_Reserve_Para3_ParaUnit067 |  | 18939
[8 empty] | 18940 | Para_Reserve_Para3_ParaUnit068 | Para_Reserve_Para3_ParaUnit068 | 6055 | Para_Reserve_Para3_ParaUnit068 |  | 18940
[8 empty] | 18941 | Para_Reserve_Para3_ParaUnit069 | Para_Reserve_Para3_ParaUnit069 | 6056 | Para_Reserve_Para3_ParaUnit069 |  | 18941
[8 empty] | 18942 | Para_Reserve_Para3_ParaUnit070 | Para_Reserve_Para3_ParaUnit070 | 6057 | Para_Reserve_Para3_ParaUnit070 |  | 18942
[8 empty] | 18943 | Para_Reserve_Para_Par001 | Para_Reserve_Para_Par001 | 6058 | Para_Reserve_Para_Par001 |  | 18943
[8 empty] | 18944 | Para_Reserve_Para_Par002 | Para_Reserve_Para_Par002 | 6059 | Para_Reserve_Para_Par002 |  | 18944
[8 empty] | 18945 | Para_Reserve_Para_Par003 | Para_Reserve_Para_Par003 | 6060 | Para_Reserve_Para_Par003 |  | 18945
[8 empty] | 18946 | Para_Reserve_Para_Par004 | Para_Reserve_Para_Par004 | 6061 | Para_Reserve_Para_Par004 |  | 18946
[8 empty] | 18947 | Para_Reserve_Para_Par005 | Para_Reserve_Para_Par005 | 6062 | Para_Reserve_Para_Par005 |  | 18947
[8 empty] | 18948 | Para_Reserve_Para_Par006 | Para_Reserve_Para_Par006 | 6063 | Para_Reserve_Para_Par006 |  | 18948
[8 empty] | 18949 | Para_Reserve_Para_Par007 | Para_Reserve_Para_Par007 | 6064 | Para_Reserve_Para_Par007 |  | 18949
[8 empty] | 18950 | Para_Reserve_Para_Par008 | Para_Reserve_Para_Par008 | 6065 | Para_Reserve_Para_Par008 |  | 18950
[8 empty] | 18951 | Para_Reserve_Para_Par009 | Para_Reserve_Para_Par009 | 6066 | Para_Reserve_Para_Par009 |  | 18951
[8 empty] | 18952 | Para_Reserve_Para_Par010 | Para_Reserve_Para_Par010 | 6067 | Para_Reserve_Para_Par010 |  | 18952
[8 empty] | 18953 | Para_Reserve_Para_Par011 | Para_Reserve_Para_Par011 | 6068 | Para_Reserve_Para_Par011 |  | 18953
[8 empty] | 18954 | Para_Reserve_Para_Par012 | Para_Reserve_Para_Par012 | 6069 | Para_Reserve_Para_Par012 |  | 18954
[8 empty] | 18955 | Para_Reserve_Para_Par013 | Para_Reserve_Para_Par013 | 6070 | Para_Reserve_Para_Par013 |  | 18955
[8 empty] | 18956 | Para_Reserve_Para_Par014 | Para_Reserve_Para_Par014 | 6071 | Para_Reserve_Para_Par014 |  | 18956
[8 empty] | 18957 | Para_Reserve_Para_Par015 | Para_Reserve_Para_Par015 | 6072 | Para_Reserve_Para_Par015 |  | 18957
[8 empty] | 18958 | Para_Reserve_Para_Par016 | Para_Reserve_Para_Par016 | 6073 | Para_Reserve_Para_Par016 |  | 18958
[8 empty] | 18959 | Para_Reserve_Para_Par017 | Para_Reserve_Para_Par017 | 6074 | Para_Reserve_Para_Par017 |  | 18959
[8 empty] | 18960 | Para_Reserve_Para_Par018 | Para_Reserve_Para_Par018 | 6075 | Para_Reserve_Para_Par018 |  | 18960
[8 empty] | 18961 | Para_Reserve_Para_Par019 | Para_Reserve_Para_Par019 | 6076 | Para_Reserve_Para_Par019 |  | 18961
[8 empty] | 18962 | Para_Reserve_Para_Par020 | Para_Reserve_Para_Par020 | 6077 | Para_Reserve_Para_Par020 |  | 18962
[8 empty] | 18963 | Para_Reserve_Para_Par021 | Para_Reserve_Para_Par021 | 6078 | Para_Reserve_Para_Par021 |  | 18963
[8 empty] | 18964 | Para_Reserve_Para_Par022 | Para_Reserve_Para_Par022 | 6079 | Para_Reserve_Para_Par022 |  | 18964
[8 empty] | 18965 | Para_Reserve_Para_Par023 | Para_Reserve_Para_Par023 | 6080 | Para_Reserve_Para_Par023 |  | 18965
[8 empty] | 18966 | Para_Reserve_Para_Par024 | Para_Reserve_Para_Par024 | 6081 | Para_Reserve_Para_Par024 |  | 18966
[8 empty] | 18967 | Para_Reserve_Para_Par025 | Para_Reserve_Para_Par025 | 6082 | Para_Reserve_Para_Par025 |  | 18967
[8 empty] | 18968 | Para_Reserve_Para_Par026 | Para_Reserve_Para_Par026 | 6083 | Para_Reserve_Para_Par026 |  | 18968
[8 empty] | 18969 | Para_Reserve_Para_Par027 | Para_Reserve_Para_Par027 | 6084 | Para_Reserve_Para_Par027 |  | 18969
[8 empty] | 18970 | Para_Reserve_Para_Par028 | Para_Reserve_Para_Par028 | 6085 | Para_Reserve_Para_Par028 |  | 18970
[8 empty] | 18971 | Para_Reserve_Para_Par029 | Para_Reserve_Para_Par029 | 6086 | Para_Reserve_Para_Par029 |  | 18971
[8 empty] | 18972 | Para_Reserve_Para_Par030 | Para_Reserve_Para_Par030 | 6087 | Para_Reserve_Para_Par030 |  | 18972
[8 empty] | 18973 | Para_Reserve_Para_ParaName001 | Para_Reserve_Para_ParaName001 | 6088 | Para_Reserve_Para_ParaName001 |  | 18973
[8 empty] | 18974 | Para_Reserve_Para_ParaName002 | Para_Reserve_Para_ParaName002 | 6089 | Para_Reserve_Para_ParaName002 |  | 18974
[8 empty] | 18975 | Para_Reserve_Para_ParaName003 | Para_Reserve_Para_ParaName003 | 6090 | Para_Reserve_Para_ParaName003 |  | 18975
[8 empty] | 18976 | Para_Reserve_Para_ParaName004 | Para_Reserve_Para_ParaName004 | 6091 | Para_Reserve_Para_ParaName004 |  | 18976
[8 empty] | 18977 | Para_Reserve_Para_ParaName005 | Para_Reserve_Para_ParaName005 | 6092 | Para_Reserve_Para_ParaName005 |  | 18977
[8 empty] | 18978 | Para_Reserve_Para_ParaName006 | Para_Reserve_Para_ParaName006 | 6093 | Para_Reserve_Para_ParaName006 |  | 18978
[8 empty] | 18979 | Para_Reserve_Para_ParaName007 | Para_Reserve_Para_ParaName007 | 6094 | Para_Reserve_Para_ParaName007 |  | 18979
[8 empty] | 18980 | Para_Reserve_Para_ParaName008 | Para_Reserve_Para_ParaName008 | 6095 | Para_Reserve_Para_ParaName008 |  | 18980
[8 empty] | 18981 | Para_Reserve_Para_ParaName009 | Para_Reserve_Para_ParaName009 | 6096 | Para_Reserve_Para_ParaName009 |  | 18981
[8 empty] | 18982 | Para_Reserve_Para_ParaName010 | Para_Reserve_Para_ParaName010 | 6097 | Para_Reserve_Para_ParaName010 |  | 18982
[8 empty] | 18983 | Para_Reserve_Para_ParaName011 | Para_Reserve_Para_ParaName011 | 6098 | Para_Reserve_Para_ParaName011 |  | 18983
[8 empty] | 18984 | Para_Reserve_Para_ParaName012 | Para_Reserve_Para_ParaName012 | 6099 | Para_Reserve_Para_ParaName012 |  | 18984
[8 empty] | 18985 | Para_Reserve_Para_ParaName013 | Para_Reserve_Para_ParaName013 | 6100 | Para_Reserve_Para_ParaName013 |  | 18985
[8 empty] | 18986 | Para_Reserve_Para_ParaName014 | Para_Reserve_Para_ParaName014 | 6101 | Para_Reserve_Para_ParaName014 |  | 18986
[8 empty] | 18987 | Para_Reserve_Para_ParaName015 | Para_Reserve_Para_ParaName015 | 6102 | Para_Reserve_Para_ParaName015 |  | 18987
[8 empty] | 18988 | Para_Reserve_Para_ParaName016 | Para_Reserve_Para_ParaName016 | 6103 | Para_Reserve_Para_ParaName016 |  | 18988
[8 empty] | 18989 | Para_Reserve_Para_ParaName017 | Para_Reserve_Para_ParaName017 | 6104 | Para_Reserve_Para_ParaName017 |  | 18989
[8 empty] | 18990 | Para_Reserve_Para_ParaName018 | Para_Reserve_Para_ParaName018 | 6105 | Para_Reserve_Para_ParaName018 |  | 18990
[8 empty] | 18991 | Para_Reserve_Para_ParaName019 | Para_Reserve_Para_ParaName019 | 6106 | Para_Reserve_Para_ParaName019 |  | 18991
[8 empty] | 18992 | Para_Reserve_Para_ParaName020 | Para_Reserve_Para_ParaName020 | 6107 | Para_Reserve_Para_ParaName020 |  | 18992
[8 empty] | 18993 | Para_Reserve_Para_ParaName021 | Para_Reserve_Para_ParaName021 | 6108 | Para_Reserve_Para_ParaName021 |  | 18993
[8 empty] | 18994 | Para_Reserve_Para_ParaName022 | Para_Reserve_Para_ParaName022 | 6109 | Para_Reserve_Para_ParaName022 |  | 18994
[8 empty] | 18995 | Para_Reserve_Para_ParaName023 | Para_Reserve_Para_ParaName023 | 6110 | Para_Reserve_Para_ParaName023 |  | 18995
[8 empty] | 18996 | Para_Reserve_Para_ParaName024 | Para_Reserve_Para_ParaName024 | 6111 | Para_Reserve_Para_ParaName024 |  | 18996
[8 empty] | 18997 | Para_Reserve_Para_ParaName025 | Para_Reserve_Para_ParaName025 | 6112 | Para_Reserve_Para_ParaName025 |  | 18997
[8 empty] | 18998 | Para_Reserve_Para_ParaName026 | Para_Reserve_Para_ParaName026 | 6113 | Para_Reserve_Para_ParaName026 |  | 18998
[8 empty] | 18999 | Para_Reserve_Para_ParaName027 | Para_Reserve_Para_ParaName027 | 6114 | Para_Reserve_Para_ParaName027 |  | 18999
[8 empty] | 19000 | Para_Reserve_Para_ParaName028 | Para_Reserve_Para_ParaName028 | 6115 | Para_Reserve_Para_ParaName028 |  | 19000
[8 empty] | 19001 | Para_Reserve_Para_ParaName029 | Para_Reserve_Para_ParaName029 | 6116 | Para_Reserve_Para_ParaName029 |  | 19001
[8 empty] | 19002 | Para_Reserve_Para_ParaName030 | Para_Reserve_Para_ParaName030 | 6117 | Para_Reserve_Para_ParaName030 |  | 19002
[8 empty] | 19003 | Para_Reserve_Para_ParaNameF001 | Para_Reserve_Para_ParaNameF001 | 6118 | Para_Reserve_Para_ParaNameF001 |  | 19003
[8 empty] | 19004 | Para_Reserve_Para_ParaNameF002 | Para_Reserve_Para_ParaNameF002 | 6119 | Para_Reserve_Para_ParaNameF002 |  | 19004
[8 empty] | 19005 | Para_Reserve_Para_ParaNameF003 | Para_Reserve_Para_ParaNameF003 | 6120 | Para_Reserve_Para_ParaNameF003 |  | 19005
[8 empty] | 19006 | Para_Reserve_Para_ParaNameF004 | Para_Reserve_Para_ParaNameF004 | 6121 | Para_Reserve_Para_ParaNameF004 |  | 19006
[8 empty] | 19007 | Para_Reserve_Para_ParaNameF005 | Para_Reserve_Para_ParaNameF005 | 6122 | Para_Reserve_Para_ParaNameF005 |  | 19007
[8 empty] | 19008 | Para_Reserve_Para_ParaNameF006 | Para_Reserve_Para_ParaNameF006 | 6123 | Para_Reserve_Para_ParaNameF006 |  | 19008
[8 empty] | 19009 | Para_Reserve_Para_ParaNameF007 | Para_Reserve_Para_ParaNameF007 | 6124 | Para_Reserve_Para_ParaNameF007 |  | 19009
[8 empty] | 19010 | Para_Reserve_Para_ParaNameF008 | Para_Reserve_Para_ParaNameF008 | 6125 | Para_Reserve_Para_ParaNameF008 |  | 19010
[8 empty] | 19011 | Para_Reserve_Para_ParaNameF009 | Para_Reserve_Para_ParaNameF009 | 6126 | Para_Reserve_Para_ParaNameF009 |  | 19011
[8 empty] | 19012 | Para_Reserve_Para_ParaNameF010 | Para_Reserve_Para_ParaNameF010 | 6127 | Para_Reserve_Para_ParaNameF010 |  | 19012
[8 empty] | 19013 | Para_Reserve_Para_ParaNameF011 | Para_Reserve_Para_ParaNameF011 | 6128 | Para_Reserve_Para_ParaNameF011 |  | 19013
[8 empty] | 19014 | Para_Reserve_Para_ParaNameF012 | Para_Reserve_Para_ParaNameF012 | 6129 | Para_Reserve_Para_ParaNameF012 |  | 19014
[8 empty] | 19015 | Para_Reserve_Para_ParaNameF013 | Para_Reserve_Para_ParaNameF013 | 6130 | Para_Reserve_Para_ParaNameF013 |  | 19015
[8 empty] | 19016 | Para_Reserve_Para_ParaNameF014 | Para_Reserve_Para_ParaNameF014 | 6131 | Para_Reserve_Para_ParaNameF014 |  | 19016
[8 empty] | 19017 | Para_Reserve_Para_ParaNameF015 | Para_Reserve_Para_ParaNameF015 | 6132 | Para_Reserve_Para_ParaNameF015 |  | 19017
[8 empty] | 19018 | Para_Reserve_Para_ParaNameF016 | Para_Reserve_Para_ParaNameF016 | 6133 | Para_Reserve_Para_ParaNameF016 |  | 19018
[8 empty] | 19019 | Para_Reserve_Para_ParaNameF017 | Para_Reserve_Para_ParaNameF017 | 6134 | Para_Reserve_Para_ParaNameF017 |  | 19019
[8 empty] | 19020 | Para_Reserve_Para_ParaNameF018 | Para_Reserve_Para_ParaNameF018 | 6135 | Para_Reserve_Para_ParaNameF018 |  | 19020
[8 empty] | 19021 | Para_Reserve_Para_ParaNameF019 | Para_Reserve_Para_ParaNameF019 | 6136 | Para_Reserve_Para_ParaNameF019 |  | 19021
[8 empty] | 19022 | Para_Reserve_Para_ParaNameF020 | Para_Reserve_Para_ParaNameF020 | 6137 | Para_Reserve_Para_ParaNameF020 |  | 19022
[8 empty] | 19023 | Para_Reserve_Para_ParaNameF021 | Para_Reserve_Para_ParaNameF021 | 6138 | Para_Reserve_Para_ParaNameF021 |  | 19023
[8 empty] | 19024 | Para_Reserve_Para_ParaNameF022 | Para_Reserve_Para_ParaNameF022 | 6139 | Para_Reserve_Para_ParaNameF022 |  | 19024
[8 empty] | 19025 | Para_Reserve_Para_ParaNameF023 | Para_Reserve_Para_ParaNameF023 | 6140 | Para_Reserve_Para_ParaNameF023 |  | 19025
[8 empty] | 19026 | Para_Reserve_Para_ParaNameF024 | Para_Reserve_Para_ParaNameF024 | 6141 | Para_Reserve_Para_ParaNameF024 |  | 19026
[8 empty] | 19027 | Para_Reserve_Para_ParaNameF025 | Para_Reserve_Para_ParaNameF025 | 6142 | Para_Reserve_Para_ParaNameF025 |  | 19027
[8 empty] | 19028 | Para_Reserve_Para_ParaNameF026 | Para_Reserve_Para_ParaNameF026 | 6143 | Para_Reserve_Para_ParaNameF026 |  | 19028
[8 empty] | 19029 | Para_Reserve_Para_ParaNameF027 | Para_Reserve_Para_ParaNameF027 | 6144 | Para_Reserve_Para_ParaNameF027 |  | 19029
[8 empty] | 19030 | Para_Reserve_Para_ParaNameF028 | Para_Reserve_Para_ParaNameF028 | 6145 | Para_Reserve_Para_ParaNameF028 |  | 19030
[8 empty] | 19031 | Para_Reserve_Para_ParaNameF029 | Para_Reserve_Para_ParaNameF029 | 6146 | Para_Reserve_Para_ParaNameF029 |  | 19031
[8 empty] | 19032 | Para_Reserve_Para_ParaNameF030 | Para_Reserve_Para_ParaNameF030 | 6147 | Para_Reserve_Para_ParaNameF030 |  | 19032
[8 empty] | 19033 | Para_Reserve_Para_ParaUnit001 | Para_Reserve_Para_ParaUnit001 | 6148 | Para_Reserve_Para_ParaUnit001 |  | 19033
[8 empty] | 19034 | Para_Reserve_Para_ParaUnit002 | Para_Reserve_Para_ParaUnit002 | 6149 | Para_Reserve_Para_ParaUnit002 |  | 19034
[8 empty] | 19035 | Para_Reserve_Para_ParaUnit003 | Para_Reserve_Para_ParaUnit003 | 6150 | Para_Reserve_Para_ParaUnit003 |  | 19035
[8 empty] | 19036 | Para_Reserve_Para_ParaUnit004 | Para_Reserve_Para_ParaUnit004 | 6151 | Para_Reserve_Para_ParaUnit004 |  | 19036
[8 empty] | 19037 | Para_Reserve_Para_ParaUnit005 | Para_Reserve_Para_ParaUnit005 | 6152 | Para_Reserve_Para_ParaUnit005 |  | 19037
[8 empty] | 19038 | Para_Reserve_Para_ParaUnit006 | Para_Reserve_Para_ParaUnit006 | 6153 | Para_Reserve_Para_ParaUnit006 |  | 19038
[8 empty] | 19039 | Para_Reserve_Para_ParaUnit007 | Para_Reserve_Para_ParaUnit007 | 6154 | Para_Reserve_Para_ParaUnit007 |  | 19039
[8 empty] | 19040 | Para_Reserve_Para_ParaUnit008 | Para_Reserve_Para_ParaUnit008 | 6155 | Para_Reserve_Para_ParaUnit008 |  | 19040
[8 empty] | 19041 | Para_Reserve_Para_ParaUnit009 | Para_Reserve_Para_ParaUnit009 | 6156 | Para_Reserve_Para_ParaUnit009 |  | 19041
[8 empty] | 19042 | Para_Reserve_Para_ParaUnit010 | Para_Reserve_Para_ParaUnit010 | 6157 | Para_Reserve_Para_ParaUnit010 |  | 19042
[8 empty] | 19043 | Para_Reserve_Para_ParaUnit011 | Para_Reserve_Para_ParaUnit011 | 6158 | Para_Reserve_Para_ParaUnit011 |  | 19043
[8 empty] | 19044 | Para_Reserve_Para_ParaUnit012 | Para_Reserve_Para_ParaUnit012 | 6159 | Para_Reserve_Para_ParaUnit012 |  | 19044
[8 empty] | 19045 | Para_Reserve_Para_ParaUnit013 | Para_Reserve_Para_ParaUnit013 | 6160 | Para_Reserve_Para_ParaUnit013 |  | 19045
[8 empty] | 19046 | Para_Reserve_Para_ParaUnit014 | Para_Reserve_Para_ParaUnit014 | 6161 | Para_Reserve_Para_ParaUnit014 |  | 19046
[8 empty] | 19047 | Para_Reserve_Para_ParaUnit015 | Para_Reserve_Para_ParaUnit015 | 6162 | Para_Reserve_Para_ParaUnit015 |  | 19047
[8 empty] | 19048 | Para_Reserve_Para_ParaUnit016 | Para_Reserve_Para_ParaUnit016 | 6163 | Para_Reserve_Para_ParaUnit016 |  | 19048
[8 empty] | 19049 | Para_Reserve_Para_ParaUnit017 | Para_Reserve_Para_ParaUnit017 | 6164 | Para_Reserve_Para_ParaUnit017 |  | 19049
[8 empty] | 19050 | Para_Reserve_Para_ParaUnit018 | Para_Reserve_Para_ParaUnit018 | 6165 | Para_Reserve_Para_ParaUnit018 |  | 19050
[8 empty] | 19051 | Para_Reserve_Para_ParaUnit019 | Para_Reserve_Para_ParaUnit019 | 6166 | Para_Reserve_Para_ParaUnit019 |  | 19051
[8 empty] | 19052 | Para_Reserve_Para_ParaUnit020 | Para_Reserve_Para_ParaUnit020 | 6167 | Para_Reserve_Para_ParaUnit020 |  | 19052
[8 empty] | 19053 | Para_Reserve_Para_ParaUnit021 | Para_Reserve_Para_ParaUnit021 | 6168 | Para_Reserve_Para_ParaUnit021 |  | 19053
[8 empty] | 19054 | Para_Reserve_Para_ParaUnit022 | Para_Reserve_Para_ParaUnit022 | 6169 | Para_Reserve_Para_ParaUnit022 |  | 19054
[8 empty] | 19055 | Para_Reserve_Para_ParaUnit023 | Para_Reserve_Para_ParaUnit023 | 6170 | Para_Reserve_Para_ParaUnit023 |  | 19055
[8 empty] | 19056 | Para_Reserve_Para_ParaUnit024 | Para_Reserve_Para_ParaUnit024 | 6171 | Para_Reserve_Para_ParaUnit024 |  | 19056
[8 empty] | 19057 | Para_Reserve_Para_ParaUnit025 | Para_Reserve_Para_ParaUnit025 | 6172 | Para_Reserve_Para_ParaUnit025 |  | 19057
[8 empty] | 19058 | Para_Reserve_Para_ParaUnit026 | Para_Reserve_Para_ParaUnit026 | 6173 | Para_Reserve_Para_ParaUnit026 |  | 19058
[8 empty] | 19059 | Para_Reserve_Para_ParaUnit027 | Para_Reserve_Para_ParaUnit027 | 6174 | Para_Reserve_Para_ParaUnit027 |  | 19059
[8 empty] | 19060 | Para_Reserve_Para_ParaUnit028 | Para_Reserve_Para_ParaUnit028 | 6175 | Para_Reserve_Para_ParaUnit028 |  | 19060
[8 empty] | 19061 | Para_Reserve_Para_ParaUnit029 | Para_Reserve_Para_ParaUnit029 | 6176 | Para_Reserve_Para_ParaUnit029 |  | 19061
[8 empty] | 19062 | Para_Reserve_Para_ParaUnit030 | Para_Reserve_Para_ParaUnit030 | 6177 | Para_Reserve_Para_ParaUnit030 |  | 19062
[8 empty] | 19063 | Para_SAFI_ActExhTemp | Para_SAFI_ActExhTemp | 6178 | Para_SAFI_ActExhTemp |  | 19063
[8 empty] | 19064 | Para_SAFI_ActHighVolt | Para_SAFI_ActHighVolt | 6179 | Para_SAFI_ActHighVolt |  | 19064
[8 empty] | 19065 | Para_SAFI_ActIgn | Para_SAFI_ActIgn | 6180 | Para_SAFI_ActIgn |  | 19065
[8 empty] | 19066 | Para_SAFI_ActITPTolCheck | Para_SAFI_ActITPTolCheck | 6181 | Para_SAFI_ActITPTolCheck |  | 19066
[8 empty] | 19067 | Para_SAFI_ActKnock | Para_SAFI_ActKnock | 6182 | Para_SAFI_ActKnock |  | 19067
[8 empty] | 19068 | Para_SAFI_ActOCA | Para_SAFI_ActOCA | 6183 | Para_SAFI_ActOCA |  | 19068
[8 empty] | 19069 | Para_SAFI_ActPBC | Para_SAFI_ActPBC | 6184 | Para_SAFI_ActPBC |  | 19069
[8 empty] | 19070 | Para_SAFI_ActPI | Para_SAFI_ActPI | 6185 | Para_SAFI_ActPI |  | 19070
[8 empty] | 19071 | Para_SAFI_ITPTol | Para_SAFI_ITPTol | 6186 | Para_SAFI_ITPTol | °KW | 19071
[8 empty] | 19072 | Para_SAFI_ResetPos | Para_SAFI_ResetPos | 6187 | Para_SAFI_ResetPos | °KW | 19072
[8 empty] | 19505 | Para_SpecGas_ActBackfireIMEP_P | Para_SpecGas_ActBackfireIMEP_P | 6188 | Para_SpecGas_ActBackfireIMEP_P |  | 19505
[8 empty] | 17397 | Para_SpecGas_ActScavN2 | Para_SpecGas_ActScavN2 | 6189 | Para_SpecGas_ActScavN2 |  | 17397
[8 empty] | 19506 | Para_SpecGas_BlockEngineRun | Para_SpecGas_BlockEngineRun | 6190 | Para_SpecGas_BlockEngineRun | min | 19506
[8 empty] | 17815 | Para_SpecGas_CalValue_ActGas1_2 | Para_SpecGas_CalValue_ActGas1_2 | 6191 | Para_SpecGas_CalValue_ActGas1_2 |  | 17815
[8 empty] | 17816 | Para_SpecGas_CalValue_ActMeasure | Para_SpecGas_CalValue_ActMeasure | 6192 | Para_SpecGas_CalValue_ActMeasure |  | 17816
[8 empty] | 17817 | Para_SpecGas_CalValue_ActMinAlarm | Para_SpecGas_CalValue_ActMinAlarm | 6193 | Para_SpecGas_CalValue_ActMinAlarm |  | 17817
[8 empty] | 17818 | Para_SpecGas_CalValue_ActMinSd | Para_SpecGas_CalValue_ActMinSd | 6194 | Para_SpecGas_CalValue_ActMinSd |  | 17818
[8 empty] | 17819 | Para_SpecGas_CalValue_ActPowerRed | Para_SpecGas_CalValue_ActPowerRed | 6195 | Para_SpecGas_CalValue_ActPowerRed |  | 17819
[8 empty] | 17820 | Para_SpecGas_CalValue_ContentGas1 | Para_SpecGas_CalValue_ContentGas1 | 6196 | Para_SpecGas_CalValue_ContentGas1 | kWh/Nm3 | 17820
[8 empty] | 17821 | Para_SpecGas_CalValue_ContentGas2 | Para_SpecGas_CalValue_ContentGas2 | 6197 | Para_SpecGas_CalValue_ContentGas2 | kWh/Nm3 | 17821
[8 empty] | 17822 | Para_SpecGas_CalValue_DefaultValGas1_2 | Para_SpecGas_CalValue_DefaultValGas1_2 | 6198 | Para_SpecGas_CalValue_DefaultValGas1_2 | % | 17822
[8 empty] | 17823 | Para_SpecGas_CalValue_HalfLoad | Para_SpecGas_CalValue_HalfLoad | 6199 | Para_SpecGas_CalValue_HalfLoad | kWh/Nm3 | 17823
[8 empty] | 17824 | Para_SpecGas_CalValue_HysMinAlarm | Para_SpecGas_CalValue_HysMinAlarm | 6200 | Para_SpecGas_CalValue_HysMinAlarm | kWh/Nm3 | 17824
[8 empty] | 17825 | Para_SpecGas_CalValue_HysMinSD | Para_SpecGas_CalValue_HysMinSD | 6201 | Para_SpecGas_CalValue_HysMinSD | kWh/Nm3 | 17825
[8 empty] | 17826 | Para_SpecGas_CalValue_LimitMinSd | Para_SpecGas_CalValue_LimitMinSd | 6202 | Para_SpecGas_CalValue_LimitMinSd | kWh/Nm3 | 17826
[8 empty] | 17827 | Para_SpecGas_CalValue_Range20mA | Para_SpecGas_CalValue_Range20mA | 6203 | Para_SpecGas_CalValue_Range20mA | kWh/Nm3 | 17827
[8 empty] | 17828 | Para_SpecGas_CalValue_Range4mA | Para_SpecGas_CalValue_Range4mA | 6204 | Para_SpecGas_CalValue_Range4mA | kWh/Nm3 | 17828
[8 empty] | 17829 | Para_SpecGas_CalValue_StartPRed | Para_SpecGas_CalValue_StartPRed | 6205 | Para_SpecGas_CalValue_StartPRed | kWh/Nm3 | 17829
[8 empty] | 17830 | Para_SpecGas_CalValue_SwitchPointMinAlarm | Para_SpecGas_CalValue_SwitchPointMinAlarm | 6206 | Para_SpecGas_CalValue_SwitchPointMinAlarm | kWh/Nm3 | 17830
[8 empty] | 17831 | Para_SpecGas_CH4_ActGas1_2 | Para_SpecGas_CH4_ActGas1_2 | 6207 | Para_SpecGas_CH4_ActGas1_2 |  | 17831
[8 empty] | 17832 | Para_SpecGas_CH4_ActMeasure | Para_SpecGas_CH4_ActMeasure | 6208 | Para_SpecGas_CH4_ActMeasure |  | 17832
[8 empty] | 17833 | Para_SpecGas_CH4_ActMinAlarm | Para_SpecGas_CH4_ActMinAlarm | 6209 | Para_SpecGas_CH4_ActMinAlarm |  | 17833
[8 empty] | 17834 | Para_SpecGas_CH4_ActMinSd | Para_SpecGas_CH4_ActMinSd | 6210 | Para_SpecGas_CH4_ActMinSd |  | 17834
[8 empty] | 17835 | Para_SpecGas_CH4_ActPowerRed | Para_SpecGas_CH4_ActPowerRed | 6211 | Para_SpecGas_CH4_ActPowerRed |  | 17835
[8 empty] | 17836 | Para_SpecGas_CH4_ContentGas1 | Para_SpecGas_CH4_ContentGas1 | 6212 | Para_SpecGas_CH4_ContentGas1 | % | 17836
[8 empty] | 17837 | Para_SpecGas_CH4_ContentGas2 | Para_SpecGas_CH4_ContentGas2 | 6213 | Para_SpecGas_CH4_ContentGas2 | % | 17837
[8 empty] | 17838 | Para_SpecGas_CH4_DefaultValGas1_2 | Para_SpecGas_CH4_DefaultValGas1_2 | 6214 | Para_SpecGas_CH4_DefaultValGas1_2 | % | 17838
[8 empty] | 17839 | Para_SpecGas_CH4_HalfLoad | Para_SpecGas_CH4_HalfLoad | 6215 | Para_SpecGas_CH4_HalfLoad | % | 17839
[8 empty] | 17840 | Para_SpecGas_CH4_HysMinAlarm | Para_SpecGas_CH4_HysMinAlarm | 6216 | Para_SpecGas_CH4_HysMinAlarm | % | 17840
[8 empty] | 17841 | Para_SpecGas_CH4_HysMinSD | Para_SpecGas_CH4_HysMinSD | 6217 | Para_SpecGas_CH4_HysMinSD | % | 17841
[8 empty] | 17842 | Para_SpecGas_CH4_LimitMinSd | Para_SpecGas_CH4_LimitMinSd | 6218 | Para_SpecGas_CH4_LimitMinSd | % | 17842
[8 empty] | 17843 | Para_SpecGas_CH4_Range20mA | Para_SpecGas_CH4_Range20mA | 6219 | Para_SpecGas_CH4_Range20mA | % | 17843
[8 empty] | 17844 | Para_SpecGas_CH4_Range4mA | Para_SpecGas_CH4_Range4mA | 6220 | Para_SpecGas_CH4_Range4mA | % | 17844
[8 empty] | 17845 | Para_SpecGas_CH4_StartPRed | Para_SpecGas_CH4_StartPRed | 6221 | Para_SpecGas_CH4_StartPRed | % | 17845
[8 empty] | 17846 | Para_SpecGas_CH4_SwitchPointMinAlarm | Para_SpecGas_CH4_SwitchPointMinAlarm | 6222 | Para_SpecGas_CH4_SwitchPointMinAlarm | % | 17846
[8 empty] | 17847 | Para_SpecGas_GasPress_ActMaxAlarm | Para_SpecGas_GasPress_ActMaxAlarm | 6223 | Para_SpecGas_GasPress_ActMaxAlarm |  | 17847
[8 empty] | 17848 | Para_SpecGas_GasPress_ActMeasure | Para_SpecGas_GasPress_ActMeasure | 6224 | Para_SpecGas_GasPress_ActMeasure |  | 17848
[8 empty] | 17849 | Para_SpecGas_GasPress_ActMinAlarm | Para_SpecGas_GasPress_ActMinAlarm | 6225 | Para_SpecGas_GasPress_ActMinAlarm |  | 17849
[8 empty] | 17850 | Para_SpecGas_GasPress_ActPowerRed | Para_SpecGas_GasPress_ActPowerRed | 6226 | Para_SpecGas_GasPress_ActPowerRed |  | 17850
[8 empty] | 17851 | Para_SpecGas_GasPress_EndPRed | Para_SpecGas_GasPress_EndPRed | 6227 | Para_SpecGas_GasPress_EndPRed | mbar | 17851
[8 empty] | 17852 | Para_SpecGas_GasPress_HysMaxAlarm | Para_SpecGas_GasPress_HysMaxAlarm | 6228 | Para_SpecGas_GasPress_HysMaxAlarm | mbar | 17852
[8 empty] | 17853 | Para_SpecGas_GasPress_HysMinAlarm | Para_SpecGas_GasPress_HysMinAlarm | 6229 | Para_SpecGas_GasPress_HysMinAlarm | mbar | 17853
[8 empty] | 17854 | Para_SpecGas_GasPress_LimitMaxAlarm | Para_SpecGas_GasPress_LimitMaxAlarm | 6230 | Para_SpecGas_GasPress_LimitMaxAlarm | mbar | 17854
[8 empty] | 17855 | Para_SpecGas_GasPress_LimitMinAlarm | Para_SpecGas_GasPress_LimitMinAlarm | 6231 | Para_SpecGas_GasPress_LimitMinAlarm | mbar | 17855
[8 empty] | 17856 | Para_SpecGas_GasPress_LimitMinAlarmDelay | Para_SpecGas_GasPress_LimitMinAlarmDelay | 6232 | Para_SpecGas_GasPress_LimitMinAlarmDelay | s | 17856
[8 empty] | 17857 | Para_SpecGas_GasPress_Range20mA | Para_SpecGas_GasPress_Range20mA | 6233 | Para_SpecGas_GasPress_Range20mA | mbar | 17857
[8 empty] | 17858 | Para_SpecGas_GasPress_Range4mA | Para_SpecGas_GasPress_Range4mA | 6234 | Para_SpecGas_GasPress_Range4mA | mbar | 17858
[8 empty] | 17859 | Para_SpecGas_GasPress_StartPRed | Para_SpecGas_GasPress_StartPRed | 6235 | Para_SpecGas_GasPress_StartPRed | mbar | 17859
[8 empty] | 17860 | Para_SpecGas_GasTemp_ActMeasure | Para_SpecGas_GasTemp_ActMeasure | 6236 | Para_SpecGas_GasTemp_ActMeasure |  | 17860
[8 empty] | 17861 | Para_SpecGas_GasTemp_HysMax | Para_SpecGas_GasTemp_HysMax | 6237 | Para_SpecGas_GasTemp_HysMax | °C | 17861
[8 empty] | 17862 | Para_SpecGas_GasTemp_HysMin | Para_SpecGas_GasTemp_HysMin | 6238 | Para_SpecGas_GasTemp_HysMin | °C | 17862
[8 empty] | 17863 | Para_SpecGas_GasTemp_LimitMax | Para_SpecGas_GasTemp_LimitMax | 6239 | Para_SpecGas_GasTemp_LimitMax | °C | 17863
[8 empty] | 17864 | Para_SpecGas_GasTemp_LimitMin | Para_SpecGas_GasTemp_LimitMin | 6240 | Para_SpecGas_GasTemp_LimitMin | °C | 17864
[8 empty] | 17865 | Para_SpecGas_GasTemp_Range20mA | Para_SpecGas_GasTemp_Range20mA | 6241 | Para_SpecGas_GasTemp_Range20mA | °C | 17865
[8 empty] | 17866 | Para_SpecGas_GasTemp_Range4mA | Para_SpecGas_GasTemp_Range4mA | 6242 | Para_SpecGas_GasTemp_Range4mA | °C | 17866
[8 empty] | 17867 | Para_SpecGas_GasVol_ActMeasure | Para_SpecGas_GasVol_ActMeasure | 6243 | Para_SpecGas_GasVol_ActMeasure |  | 17867
[8 empty] | 17868 | Para_SpecGas_GasVol_Range20mA | Para_SpecGas_GasVol_Range20mA | 6244 | Para_SpecGas_GasVol_Range20mA | m3/h | 17868
[8 empty] | 17869 | Para_SpecGas_GasVol_Range4mA | Para_SpecGas_GasVol_Range4mA | 6245 | Para_SpecGas_GasVol_Range4mA | m3/h | 17869
[8 empty] | 19507 | Para_SpecGas_GlowIgn_ActPredIPRedPBC | Para_SpecGas_GlowIgn_ActPredIPRedPBC | 6246 | Para_SpecGas_GlowIgn_ActPredIPRedPBC |  | 19507
[8 empty] | 17870 | Para_SpecGas_GlowIgn_EmergShut_ActEmergShut | Para_SpecGas_GlowIgn_EmergShut_ActEmergShut | 6247 | Para_SpecGas_GlowIgn_EmergShut_ActEmergShut |  | 17870
[8 empty] | 17871 | Para_SpecGas_GlowIgn_EmergShut_ActEmergShutPBC | Para_SpecGas_GlowIgn_EmergShut_ActEmergShutPBC | 6248 | Para_SpecGas_GlowIgn_EmergShut_ActEmergShutPBC |  | 17871
[8 empty] | 17872 | Para_SpecGas_GlowIgn_EmergShut_BlockTimeNumbMax | Para_SpecGas_GlowIgn_EmergShut_BlockTimeNumbMax | 6249 | Para_SpecGas_GlowIgn_EmergShut_BlockTimeNumbMax | min | 17872
[8 empty] | 17873 | Para_SpecGas_GlowIgn_EmergShut_CloseTimeGasValve | Para_SpecGas_GlowIgn_EmergShut_CloseTimeGasValve | 6250 | Para_SpecGas_GlowIgn_EmergShut_CloseTimeGasValve | s | 17873
[8 empty] | 17874 | Para_SpecGas_GlowIgn_EmergShut_LimitContent | Para_SpecGas_GlowIgn_EmergShut_LimitContent | 6251 | Para_SpecGas_GlowIgn_EmergShut_LimitContent | % | 17874
[8 empty] | 17875 | Para_SpecGas_GlowIgn_EmergShut_LimitDeltaCylTemp | Para_SpecGas_GlowIgn_EmergShut_LimitDeltaCylTemp | 6252 | Para_SpecGas_GlowIgn_EmergShut_LimitDeltaCylTemp | °C/s | 17875
[8 empty] | 17876 | Para_SpecGas_GlowIgn_EmergShut_LimitDevCylTempAvg | Para_SpecGas_GlowIgn_EmergShut_LimitDevCylTempAvg | 6253 | Para_SpecGas_GlowIgn_EmergShut_LimitDevCylTempAvg | °C | 17876
[8 empty] | 17877 | Para_SpecGas_GlowIgn_EmergShut_NumbMax | Para_SpecGas_GlowIgn_EmergShut_NumbMax | 6254 | Para_SpecGas_GlowIgn_EmergShut_NumbMax |  | 17877
[8 empty] | 17878 | Para_SpecGas_GlowIgn_EmergShut_NumbMax30s | Para_SpecGas_GlowIgn_EmergShut_NumbMax30s | 6255 | Para_SpecGas_GlowIgn_EmergShut_NumbMax30s |  | 17878
[8 empty] | 17879 | Para_SpecGas_GlowIgn_EmergShut_PowerActTempMon | Para_SpecGas_GlowIgn_EmergShut_PowerActTempMon | 6256 | Para_SpecGas_GlowIgn_EmergShut_PowerActTempMon | kW | 17879
[8 empty] | 17880 | Para_SpecGas_GlowIgn_EmergShut_SelfReset | Para_SpecGas_GlowIgn_EmergShut_SelfReset | 6257 | Para_SpecGas_GlowIgn_EmergShut_SelfReset |  | 17880
[8 empty] | 17881 | Para_SpecGas_GlowIgn_EmergShut_TimeDurMonDeact | Para_SpecGas_GlowIgn_EmergShut_TimeDurMonDeact | 6258 | Para_SpecGas_GlowIgn_EmergShut_TimeDurMonDeact | s | 17881
[8 empty] | 17882 | Para_SpecGas_GlowIgn_EmergShut_TimeNumbMax | Para_SpecGas_GlowIgn_EmergShut_TimeNumbMax | 6259 | Para_SpecGas_GlowIgn_EmergShut_TimeNumbMax | min | 17882
[8 empty] | 17883 | Para_SpecGas_GlowIgn_EmergShut_TrPos | Para_SpecGas_GlowIgn_EmergShut_TrPos | 6260 | Para_SpecGas_GlowIgn_EmergShut_TrPos | % | 17883
[8 empty] | 17884 | Para_SpecGas_GlowIgn_EmergShut_TrPosTimeDur | Para_SpecGas_GlowIgn_EmergShut_TrPosTimeDur | 6261 | Para_SpecGas_GlowIgn_EmergShut_TrPosTimeDur | s | 17884
[8 empty] | 17885 | Para_SpecGas_GlowIgn_FastPowerRed_ActFastPowerRed | Para_SpecGas_GlowIgn_FastPowerRed_ActFastPowerRed | 6262 | Para_SpecGas_GlowIgn_FastPowerRed_ActFastPowerRed |  | 17885
[8 empty] | 17886 | Para_SpecGas_GlowIgn_FastPowerRed_ActFastPowerRedPBC | Para_SpecGas_GlowIgn_FastPowerRed_ActFastPowerRedPBC | 6263 | Para_SpecGas_GlowIgn_FastPowerRed_ActFastPowerRedPBC |  | 17886
[8 empty] | 17887 | Para_SpecGas_GlowIgn_FastPowerRed_Limitp2s | Para_SpecGas_GlowIgn_FastPowerRed_Limitp2s | 6264 | Para_SpecGas_GlowIgn_FastPowerRed_Limitp2s | mbar/s | 17887
[8 empty] | 17888 | Para_SpecGas_GlowIgn_FastPowerRed_MaxNumb | Para_SpecGas_GlowIgn_FastPowerRed_MaxNumb | 6265 | Para_SpecGas_GlowIgn_FastPowerRed_MaxNumb |  | 17888
[8 empty] | 17889 | Para_SpecGas_GlowIgn_FastPowerRed_PowerActive | Para_SpecGas_GlowIgn_FastPowerRed_PowerActive | 6266 | Para_SpecGas_GlowIgn_FastPowerRed_PowerActive | kW | 17889
[8 empty] | 17890 | Para_SpecGas_GlowIgn_FastPowerRed_PowerDiff | Para_SpecGas_GlowIgn_FastPowerRed_PowerDiff | 6267 | Para_SpecGas_GlowIgn_FastPowerRed_PowerDiff | %Pnom | 17890
[8 empty] | 17891 | Para_SpecGas_GlowIgn_FastPowerRed_PowerSave | Para_SpecGas_GlowIgn_FastPowerRed_PowerSave | 6268 | Para_SpecGas_GlowIgn_FastPowerRed_PowerSave | %Pnom | 17891
[8 empty] | 17892 | Para_SpecGas_GlowIgn_FastPowerRed_PowerSaveDur | Para_SpecGas_GlowIgn_FastPowerRed_PowerSaveDur | 6269 | Para_SpecGas_GlowIgn_FastPowerRed_PowerSaveDur | min | 17892
[8 empty] | 17893 | Para_SpecGas_GlowIgn_FastPowerRed_TimeDiff | Para_SpecGas_GlowIgn_FastPowerRed_TimeDiff | 6270 | Para_SpecGas_GlowIgn_FastPowerRed_TimeDiff | s | 17893
[8 empty] | 17894 | Para_SpecGas_GlowIgn_FastPowerRed_TimeDur | Para_SpecGas_GlowIgn_FastPowerRed_TimeDur | 6271 | Para_SpecGas_GlowIgn_FastPowerRed_TimeDur | s | 17894
[8 empty] | 17895 | Para_SpecGas_GlowIgn_FastPowerRed_TrPos | Para_SpecGas_GlowIgn_FastPowerRed_TrPos | 6272 | Para_SpecGas_GlowIgn_FastPowerRed_TrPos | % | 17895
[8 empty] | 17896 | Para_SpecGas_GlowIgn_ITPstep | Para_SpecGas_GlowIgn_ITPstep | 6273 | Para_SpecGas_GlowIgn_ITPstep | °KW | 17896
[8 empty] | 17897 | Para_SpecGas_GlowIgn_LambdaOffset | Para_SpecGas_GlowIgn_LambdaOffset | 6274 | Para_SpecGas_GlowIgn_LambdaOffset |  | 17897
[8 empty] | 17898 | Para_SpecGas_GlowIgnPrevent | Para_SpecGas_GlowIgnPrevent | 6275 | Para_SpecGas_GlowIgnPrevent |  | 17898
[8 empty] | 17899 | Para_SpecGas_O2_ActMeasure | Para_SpecGas_O2_ActMeasure | 6276 | Para_SpecGas_O2_ActMeasure |  | 17899
[8 empty] | 17900 | Para_SpecGas_O2_ActShutdownMax | Para_SpecGas_O2_ActShutdownMax | 6277 | Para_SpecGas_O2_ActShutdownMax |  | 17900
[8 empty] | 17901 | Para_SpecGas_O2_HysMaxSd | Para_SpecGas_O2_HysMaxSd | 6278 | Para_SpecGas_O2_HysMaxSd | % | 17901
[8 empty] | 17902 | Para_SpecGas_O2_LimitMaxSd | Para_SpecGas_O2_LimitMaxSd | 6279 | Para_SpecGas_O2_LimitMaxSd | % | 17902
[8 empty] | 17903 | Para_SpecGas_O2_Range20mA | Para_SpecGas_O2_Range20mA | 6280 | Para_SpecGas_O2_Range20mA | % | 17903
[8 empty] | 17904 | Para_SpecGas_O2_Range4mA | Para_SpecGas_O2_Range4mA | 6281 | Para_SpecGas_O2_Range4mA | % | 17904
[8 empty] | 17905 | Para_SpecGas_SucPress_ActMeasure | Para_SpecGas_SucPress_ActMeasure | 6282 | Para_SpecGas_SucPress_ActMeasure |  | 17905
[8 empty] | 17906 | Para_SpecGas_SucPress_ActPowerRed | Para_SpecGas_SucPress_ActPowerRed | 6283 | Para_SpecGas_SucPress_ActPowerRed |  | 17906
[8 empty] | 17907 | Para_SpecGas_SucPress_EndPRed | Para_SpecGas_SucPress_EndPRed | 6284 | Para_SpecGas_SucPress_EndPRed | mbar | 17907
[8 empty] | 17908 | Para_SpecGas_SucPress_HysMaxAlarm | Para_SpecGas_SucPress_HysMaxAlarm | 6285 | Para_SpecGas_SucPress_HysMaxAlarm | mbar | 17908
[8 empty] | 17909 | Para_SpecGas_SucPress_HysMinAlarm | Para_SpecGas_SucPress_HysMinAlarm | 6286 | Para_SpecGas_SucPress_HysMinAlarm | mbar | 17909
[8 empty] | 17910 | Para_SpecGas_SucPress_LimitMaxAlarm | Para_SpecGas_SucPress_LimitMaxAlarm | 6287 | Para_SpecGas_SucPress_LimitMaxAlarm | mbar | 17910
[8 empty] | 17911 | Para_SpecGas_SucPress_LimitMinAlarm | Para_SpecGas_SucPress_LimitMinAlarm | 6288 | Para_SpecGas_SucPress_LimitMinAlarm | mbar | 17911
[8 empty] | 17912 | Para_SpecGas_SucPress_Range20mA | Para_SpecGas_SucPress_Range20mA | 6289 | Para_SpecGas_SucPress_Range20mA | mbar | 17912
[8 empty] | 17913 | Para_SpecGas_SucPress_Range4mA | Para_SpecGas_SucPress_Range4mA | 6290 | Para_SpecGas_SucPress_Range4mA | mbar | 17913
[8 empty] | 17914 | Para_SpecGas_SucPress_StartPRed | Para_SpecGas_SucPress_StartPRed | 6291 | Para_SpecGas_SucPress_StartPRed | mbar | 17914
[8 empty] | 17915 | Para_SpecGas_TwoIgnition | Para_SpecGas_TwoIgnition | 6292 | Para_SpecGas_TwoIgnition |  | 17915
[8 empty] | 17916 | Para_SpecGas_TwoN2Valves | Para_SpecGas_TwoN2Valves | 6293 | Para_SpecGas_TwoN2Valves |  | 17916
[8 empty] | 17917 | Para_Speed_Ctr_Active | Para_Speed_Ctr_Active | 6294 | Para_Speed_Ctr_Active | 1/min | 17917
[8 empty] | 17918 | Para_Speed_Ctr_ActStartCompBypassOpen | Para_Speed_Ctr_ActStartCompBypassOpen | 6295 | Para_Speed_Ctr_ActStartCompBypassOpen |  | 17918
[8 empty] | 17919 | Para_Speed_Ctr_TrDComp | Para_Speed_Ctr_TrDComp | 6296 | Para_Speed_Ctr_TrDComp |  | 17919
[8 empty] | 17920 | Para_Speed_Ctr_TrIComp | Para_Speed_Ctr_TrIComp | 6297 | Para_Speed_Ctr_TrIComp |  | 17920
[8 empty] | 17921 | Para_Speed_Ctr_TrPComp | Para_Speed_Ctr_TrPComp | 6298 | Para_Speed_Ctr_TrPComp |  | 17921
[8 empty] | 17922 | Para_Speed_Ctr_TrYMax | Para_Speed_Ctr_TrYMax | 6299 | Para_Speed_Ctr_TrYMax | % | 17922
[8 empty] | 17923 | Para_Speed_Ctr_TrYMin | Para_Speed_Ctr_TrYMin | 6300 | Para_Speed_Ctr_TrYMin | % | 17923
[8 empty] | 17924 | Para_Speed_ExtSet_Curr1 | Para_Speed_ExtSet_Curr1 | 6301 | Para_Speed_ExtSet_Curr1 | mA | 17924
[8 empty] | 17925 | Para_Speed_ExtSet_Curr2 | Para_Speed_ExtSet_Curr2 | 6302 | Para_Speed_ExtSet_Curr2 | mA | 17925
[8 empty] | 17926 | Para_Speed_ExtSet_Point1 | Para_Speed_ExtSet_Point1 | 6303 | Para_Speed_ExtSet_Point1 | 1/min | 17926
[8 empty] | 17927 | Para_Speed_ExtSet_Point2 | Para_Speed_ExtSet_Point2 | 6304 | Para_Speed_ExtSet_Point2 | 1/min | 17927
[8 empty] | 17928 | Para_Speed_Limit_Gr1495 | Para_Speed_Limit_Gr1495 | 6305 | Para_Speed_Limit_Gr1495 | 1/min | 17928
[8 empty] | 17929 | Para_Speed_Limit_Gr1495Hys | Para_Speed_Limit_Gr1495Hys | 6306 | Para_Speed_Limit_Gr1495Hys | 1/min | 17929
[8 empty] | 17930 | Para_Speed_Limit_Limit1 | Para_Speed_Limit_Limit1 | 6307 | Para_Speed_Limit_Limit1 | 1/min | 17930
[8 empty] | 17931 | Para_Speed_Limit_Limit1Hys | Para_Speed_Limit_Limit1Hys | 6308 | Para_Speed_Limit_Limit1Hys | 1/min | 17931
[8 empty] | 17932 | Para_Speed_Limit_OverSpeed | Para_Speed_Limit_OverSpeed | 6309 | Para_Speed_Limit_OverSpeed | 1/min | 17932
[8 empty] | 17933 | Para_Speed_Limit_OverSpeedHys | Para_Speed_Limit_OverSpeedHys | 6310 | Para_Speed_Limit_OverSpeedHys | 1/min | 17933
[8 empty] | 17934 | Para_Speed_Limit_RunUp | Para_Speed_Limit_RunUp | 6311 | Para_Speed_Limit_RunUp | 1/min | 17934
[8 empty] | 17935 | Para_Speed_Limit_RunUpHys | Para_Speed_Limit_RunUpHys | 6312 | Para_Speed_Limit_RunUpHys | 1/min | 17935
[8 empty] | 17936 | Para_Speed_Limit_Sm1505 | Para_Speed_Limit_Sm1505 | 6313 | Para_Speed_Limit_Sm1505 | 1/min | 17936
[8 empty] | 17937 | Para_Speed_Limit_Sm1505Hys | Para_Speed_Limit_Sm1505Hys | 6314 | Para_Speed_Limit_Sm1505Hys | 1/min | 17937
[8 empty] | 17938 | Para_Speed_Limit_Start | Para_Speed_Limit_Start | 6315 | Para_Speed_Limit_Start | 1/min | 17938
[8 empty] | 17939 | Para_Speed_Limit_StartHys | Para_Speed_Limit_StartHys | 6316 | Para_Speed_Limit_StartHys | 1/min | 17939
[8 empty] | 17940 | Para_Speed_Limit_StartSpeedMon | Para_Speed_Limit_StartSpeedMon | 6317 | Para_Speed_Limit_StartSpeedMon | 1/min | 17940
[8 empty] | 17941 | Para_Speed_Limit_StartSpeedMonHys | Para_Speed_Limit_StartSpeedMonHys | 6318 | Para_Speed_Limit_StartSpeedMonHys | 1/min | 17941
[8 empty] | 17942 | Para_Speed_Nominal | N nom | 6319 | Para_Speed_Nominal | 1/min | 17942
[8 empty] | 17943 | Para_Speed_Ramp_Ramp | Para_Speed_Ramp_Ramp | 6320 | Para_Speed_Ramp_Ramp | min-1/s | 17943
[8 empty] | 10008502 | Para_System_HA_Pt100InputFilter | Para_System_HA_Pt100InputFilter | 6321 | Para_System_HA_Pt100InputFilter |  | 10008502
[8 empty] | 10008795 | Para_System_IPC_T_IPC_Board_LimHi | Para_System_IPC_T_IPC_Board_LimHi | 6322 | Para_System_IPC_T_IPC_Board_LimHi |  | 10008795
[8 empty] | 10008794 | Para_System_IPC_T_IPC_CFast_LimHi | Para_System_IPC_T_IPC_CFast_LimHi | 6323 | Para_System_IPC_T_IPC_CFast_LimHi |  | 10008794
[8 empty] | 10008796 | Para_System_IPC_T_IPC_Chipset_LimHi | Para_System_IPC_T_IPC_Chipset_LimHi | 6324 | Para_System_IPC_T_IPC_Chipset_LimHi |  | 10008796
[8 empty] | 10008798 | Para_System_IPC_T_IPC_CPU_LimHi | Para_System_IPC_T_IPC_CPU_LimHi | 6325 | Para_System_IPC_T_IPC_CPU_LimHi |  | 10008798
[8 empty] | 10008799 | Para_System_IPC_T_IPC_PS_LimHi | Para_System_IPC_T_IPC_PS_LimHi | 6326 | Para_System_IPC_T_IPC_PS_LimHi |  | 10008799
[8 empty] | 17944 | Para_Tecjet_Gas1_AirDemandMin | Para_Tecjet_Gas1_AirDemandMin | 6327 | Para_Tecjet_Gas1_AirDemandMin | l/l | 17944
[8 empty] | 17945 | Para_Tecjet_Gas1_CalorificValue | Para_Tecjet_Gas1_CalorificValue | 6328 | Para_Tecjet_Gas1_CalorificValue | kWh/Nm3 | 17945
[8 empty] | 17946 | Para_Tecjet_Gas1_StandGasDens | Para_Tecjet_Gas1_StandGasDens | 6329 | Para_Tecjet_Gas1_StandGasDens | g/m3 | 17946
[8 empty] | 17947 | Para_Tecjet_Gas1_TecJetOffsetIsland | Para_Tecjet_Gas1_TecJetOffsetIsland | 6330 | Para_Tecjet_Gas1_TecJetOffsetIsland |  | 17947
[8 empty] | 17948 | Para_Tecjet_Gas1_TecJetOffsetNet | Para_Tecjet_Gas1_TecJetOffsetNet | 6331 | Para_Tecjet_Gas1_TecJetOffsetNet |  | 17948
[8 empty] | 17949 | Para_Tecjet_Gas1_TecJetPoint1 | Para_Tecjet_Gas1_TecJetPoint1 | 6332 | Para_Tecjet_Gas1_TecJetPoint1 |  | 17949
[8 empty] | 17950 | Para_Tecjet_Gas1_TecJetPoint2 | Para_Tecjet_Gas1_TecJetPoint2 | 6333 | Para_Tecjet_Gas1_TecJetPoint2 |  | 17950
[8 empty] | 17951 | Para_Tecjet_Gas1_TempOilPoint1 | Para_Tecjet_Gas1_TempOilPoint1 | 6334 | Para_Tecjet_Gas1_TempOilPoint1 | °C | 17951
[8 empty] | 17952 | Para_Tecjet_Gas1_TempOilPoint2 | Para_Tecjet_Gas1_TempOilPoint2 | 6335 | Para_Tecjet_Gas1_TempOilPoint2 | °C | 17952
[8 empty] | 17953 | Para_Tecjet_Gas2_AirDemandMin | Para_Tecjet_Gas2_AirDemandMin | 6336 | Para_Tecjet_Gas2_AirDemandMin | l/l | 17953
[8 empty] | 17954 | Para_Tecjet_Gas2_CalorificValue | Para_Tecjet_Gas2_CalorificValue | 6337 | Para_Tecjet_Gas2_CalorificValue | kWh/Nm3 | 17954
[8 empty] | 17955 | Para_Tecjet_Gas2_StandGasDens | Para_Tecjet_Gas2_StandGasDens | 6338 | Para_Tecjet_Gas2_StandGasDens | g/m3 | 17955
[8 empty] | 17956 | Para_Tecjet_Gas2_TecJetOffsetIsland | Para_Tecjet_Gas2_TecJetOffsetIsland | 6339 | Para_Tecjet_Gas2_TecJetOffsetIsland |  | 17956
[8 empty] | 17957 | Para_Tecjet_Gas2_TecJetOffsetNet | Para_Tecjet_Gas2_TecJetOffsetNet | 6340 | Para_Tecjet_Gas2_TecJetOffsetNet |  | 17957
[8 empty] | 17958 | Para_Tecjet_Gas2_TecJetPoint1 | Para_Tecjet_Gas2_TecJetPoint1 | 6341 | Para_Tecjet_Gas2_TecJetPoint1 |  | 17958
[8 empty] | 17959 | Para_Tecjet_Gas2_TecJetPoint2 | Para_Tecjet_Gas2_TecJetPoint2 | 6342 | Para_Tecjet_Gas2_TecJetPoint2 |  | 17959
[8 empty] | 17960 | Para_Tecjet_Gas2_TempOilPoint1 | Para_Tecjet_Gas2_TempOilPoint1 | 6343 | Para_Tecjet_Gas2_TempOilPoint1 | °C | 17960
[8 empty] | 17961 | Para_Tecjet_Gas2_TempOilPoint2 | Para_Tecjet_Gas2_TempOilPoint2 | 6344 | Para_Tecjet_Gas2_TempOilPoint2 | °C | 17961
[8 empty] | 17962 | Para_Tecjet_Gas3_AirDemandMin | Para_Tecjet_Gas3_AirDemandMin | 6345 | Para_Tecjet_Gas3_AirDemandMin | l/l | 17962
[8 empty] | 17963 | Para_Tecjet_Gas3_CalorificValue | Para_Tecjet_Gas3_CalorificValue | 6346 | Para_Tecjet_Gas3_CalorificValue | kWh/Nm3 | 17963
[8 empty] | 17964 | Para_Tecjet_Gas3_StandGasDens | Para_Tecjet_Gas3_StandGasDens | 6347 | Para_Tecjet_Gas3_StandGasDens | g/m3 | 17964
[8 empty] | 17965 | Para_Tecjet_Gas3_TecJetOffsetIsland | Para_Tecjet_Gas3_TecJetOffsetIsland | 6348 | Para_Tecjet_Gas3_TecJetOffsetIsland |  | 17965
[8 empty] | 17966 | Para_Tecjet_Gas3_TecJetOffsetNet | Para_Tecjet_Gas3_TecJetOffsetNet | 6349 | Para_Tecjet_Gas3_TecJetOffsetNet |  | 17966
[8 empty] | 17967 | Para_Tecjet_Gas3_TecJetPoint1 | Para_Tecjet_Gas3_TecJetPoint1 | 6350 | Para_Tecjet_Gas3_TecJetPoint1 |  | 17967
[8 empty] | 17968 | Para_Tecjet_Gas3_TecJetPoint2 | Para_Tecjet_Gas3_TecJetPoint2 | 6351 | Para_Tecjet_Gas3_TecJetPoint2 |  | 17968
[8 empty] | 17969 | Para_Tecjet_Gas3_TempOilPoint1 | Para_Tecjet_Gas3_TempOilPoint1 | 6352 | Para_Tecjet_Gas3_TempOilPoint1 | °C | 17969
[8 empty] | 17970 | Para_Tecjet_Gas3_TempOilPoint2 | Para_Tecjet_Gas3_TempOilPoint2 | 6353 | Para_Tecjet_Gas3_TempOilPoint2 | °C | 17970
[8 empty] | 17971 | Para_Tecjet_Gas4_AirDemandMin | Para_Tecjet_Gas4_AirDemandMin | 6354 | Para_Tecjet_Gas4_AirDemandMin | l/l | 17971
[8 empty] | 17972 | Para_Tecjet_Gas4_CalorificValue | Para_Tecjet_Gas4_CalorificValue | 6355 | Para_Tecjet_Gas4_CalorificValue | kWh/Nm3 | 17972
[8 empty] | 17973 | Para_Tecjet_Gas4_StandGasDens | Para_Tecjet_Gas4_StandGasDens | 6356 | Para_Tecjet_Gas4_StandGasDens | g/m3 | 17973
[8 empty] | 17974 | Para_Tecjet_Gas4_TecJetOffsetIsland | Para_Tecjet_Gas4_TecJetOffsetIsland | 6357 | Para_Tecjet_Gas4_TecJetOffsetIsland |  | 17974
[8 empty] | 17975 | Para_Tecjet_Gas4_TecJetOffsetNet | Para_Tecjet_Gas4_TecJetOffsetNet | 6358 | Para_Tecjet_Gas4_TecJetOffsetNet |  | 17975
[8 empty] | 17976 | Para_Tecjet_Gas4_TecJetPoint1 | Para_Tecjet_Gas4_TecJetPoint1 | 6359 | Para_Tecjet_Gas4_TecJetPoint1 |  | 17976
[8 empty] | 17977 | Para_Tecjet_Gas4_TecJetPoint2 | Para_Tecjet_Gas4_TecJetPoint2 | 6360 | Para_Tecjet_Gas4_TecJetPoint2 |  | 17977
[8 empty] | 17978 | Para_Tecjet_Gas4_TempOilPoint1 | Para_Tecjet_Gas4_TempOilPoint1 | 6361 | Para_Tecjet_Gas4_TempOilPoint1 | °C | 17978
[8 empty] | 17979 | Para_Tecjet_Gas4_TempOilPoint2 | Para_Tecjet_Gas4_TempOilPoint2 | 6362 | Para_Tecjet_Gas4_TempOilPoint2 | °C | 17979
[8 empty] | 17980 | Para_Tecjet_IdleLambdaCtr_Delay1 | Para_Tecjet_IdleLambdaCtr_Delay1 | 6363 | Para_Tecjet_IdleLambdaCtr_Delay1 | s | 17980
[8 empty] | 17981 | Para_Tecjet_IdleLambdaCtr_Delay2 | Para_Tecjet_IdleLambdaCtr_Delay2 | 6364 | Para_Tecjet_IdleLambdaCtr_Delay2 | s | 17981
[8 empty] | 17982 | Para_Tecjet_IdleLambdaCtr_Gas1_TecJetDP | Para_Tecjet_IdleLambdaCtr_Gas1_TecJetDP | 6365 | Para_Tecjet_IdleLambdaCtr_Gas1_TecJetDP |  | 17982
[8 empty] | 17983 | Para_Tecjet_IdleLambdaCtr_Gas1_TrPos | Para_Tecjet_IdleLambdaCtr_Gas1_TrPos | 6366 | Para_Tecjet_IdleLambdaCtr_Gas1_TrPos | % | 17983
[8 empty] | 17984 | Para_Tecjet_IdleLambdaCtr_Gas2_TecJetDP | Para_Tecjet_IdleLambdaCtr_Gas2_TecJetDP | 6367 | Para_Tecjet_IdleLambdaCtr_Gas2_TecJetDP |  | 17984
[8 empty] | 17985 | Para_Tecjet_IdleLambdaCtr_Gas2_TrPos | Para_Tecjet_IdleLambdaCtr_Gas2_TrPos | 6368 | Para_Tecjet_IdleLambdaCtr_Gas2_TrPos | % | 17985
[8 empty] | 17986 | Para_Tecjet_IdleLambdaCtr_Gas3_TecJetDP | Para_Tecjet_IdleLambdaCtr_Gas3_TecJetDP | 6369 | Para_Tecjet_IdleLambdaCtr_Gas3_TecJetDP |  | 17986
[8 empty] | 17987 | Para_Tecjet_IdleLambdaCtr_Gas3_TrPos | Para_Tecjet_IdleLambdaCtr_Gas3_TrPos | 6370 | Para_Tecjet_IdleLambdaCtr_Gas3_TrPos | % | 17987
[8 empty] | 17988 | Para_Tecjet_IdleLambdaCtr_Gas4_TecJetDP | Para_Tecjet_IdleLambdaCtr_Gas4_TecJetDP | 6371 | Para_Tecjet_IdleLambdaCtr_Gas4_TecJetDP |  | 17988
[8 empty] | 17989 | Para_Tecjet_IdleLambdaCtr_Gas4_TrPos | Para_Tecjet_IdleLambdaCtr_Gas4_TrPos | 6372 | Para_Tecjet_IdleLambdaCtr_Gas4_TrPos | % | 17989
[8 empty] | 17990 | Para_Tecjet_IdleLambdaCtr_IComp | Para_Tecjet_IdleLambdaCtr_IComp | 6373 | Para_Tecjet_IdleLambdaCtr_IComp |  | 17990
[8 empty] | 17991 | Para_Tecjet_IdleLambdaCtr_PComp | Para_Tecjet_IdleLambdaCtr_PComp | 6374 | Para_Tecjet_IdleLambdaCtr_PComp |  | 17991
[8 empty] | 17992 | Para_Tecjet_LambdaAdapStartup_LambdaOffsetX2 | Para_Tecjet_LambdaAdapStartup_LambdaOffsetX2 | 6375 | Para_Tecjet_LambdaAdapStartup_LambdaOffsetX2 | rpm | 17992
[8 empty] | 17993 | Para_Tecjet_LambdaAdapStartup_LambdaOffsetX3 | Para_Tecjet_LambdaAdapStartup_LambdaOffsetX3 | 6376 | Para_Tecjet_LambdaAdapStartup_LambdaOffsetX3 | rpm | 17993
[8 empty] | 17994 | Para_Tecjet_LambdaAdapStartup_LambdaOffsetY1 | Para_Tecjet_LambdaAdapStartup_LambdaOffsetY1 | 6377 | Para_Tecjet_LambdaAdapStartup_LambdaOffsetY1 |  | 17994
[8 empty] | 17995 | Para_Tecjet_LambdaAdapStartup_LambdaOffsetY2 | Para_Tecjet_LambdaAdapStartup_LambdaOffsetY2 | 6378 | Para_Tecjet_LambdaAdapStartup_LambdaOffsetY2 |  | 17995
[8 empty] | 17996 | Para_Tecjet_LambdaAdapStartup_LambdaStartMin | Para_Tecjet_LambdaAdapStartup_LambdaStartMin | 6379 | Para_Tecjet_LambdaAdapStartup_LambdaStartMin |  | 17996
[8 empty] | 17997 | Para_Tecjet_TempOilMax | Para_Tecjet_TempOilMax | 6380 | Para_Tecjet_TempOilMax | °C | 17997
[8 empty] | 17998 | Para_Tecjet_TempOilMin | Para_Tecjet_TempOilMin | 6381 | Para_Tecjet_TempOilMin | °C | 17998
[8 empty] | 17999 | Para_Tecjet_VolumEffic | TJ Vol Eff | 6382 | Para_Tecjet_VolumEffic |  | 17999
[8 empty] | 19380 | Para_UniversalIO_Ana_InFirst | Para_UniversalIO_Ana_InFirst | 6383 | Para_UniversalIO_Ana_InFirst |  | 19380
[8 empty] | 19381 | Para_UniversalIO_Ana_InLast | Para_UniversalIO_Ana_InLast | 6384 | Para_UniversalIO_Ana_InLast |  | 19381
[8 empty] | 19382 | Para_UniversalIO_Ana_OutFirst | Para_UniversalIO_Ana_OutFirst | 6385 | Para_UniversalIO_Ana_OutFirst |  | 19382
[8 empty] | 19383 | Para_UniversalIO_Ana_OutLast | Para_UniversalIO_Ana_OutLast | 6386 | Para_UniversalIO_Ana_OutLast |  | 19383
[8 empty] | 19384 | Para_UniversalIO_Dig_CntFirst | Para_UniversalIO_Dig_CntFirst | 6387 | Para_UniversalIO_Dig_CntFirst |  | 19384
[8 empty] | 19385 | Para_UniversalIO_Dig_CntLast | Para_UniversalIO_Dig_CntLast | 6388 | Para_UniversalIO_Dig_CntLast |  | 19385
[8 empty] | 19386 | Para_UniversalIO_Dig_FlagFirst | Para_UniversalIO_Dig_FlagFirst | 6389 | Para_UniversalIO_Dig_FlagFirst |  | 19386
[8 empty] | 19387 | Para_UniversalIO_Dig_FlagLast | Para_UniversalIO_Dig_FlagLast | 6390 | Para_UniversalIO_Dig_FlagLast |  | 19387
[8 empty] | 19388 | Para_UniversalIO_Dig_InFirst | Para_UniversalIO_Dig_InFirst | 6391 | Para_UniversalIO_Dig_InFirst |  | 19388
[8 empty] | 19389 | Para_UniversalIO_Dig_InLast | Para_UniversalIO_Dig_InLast | 6392 | Para_UniversalIO_Dig_InLast |  | 19389
[8 empty] | 19390 | Para_UniversalIO_Dig_OutFirst | Para_UniversalIO_Dig_OutFirst | 6393 | Para_UniversalIO_Dig_OutFirst |  | 19390
[8 empty] | 19391 | Para_UniversalIO_Dig_OutLast | Para_UniversalIO_Dig_OutLast | 6394 | Para_UniversalIO_Dig_OutLast |  | 19391
[8 empty] | 18000 | Para_Visu_ActRemoteRequest | Para_Visu_ActRemoteRequest | 6395 | Para_Visu_ActRemoteRequest |  | 18000
[8 empty] | 18001 | Para_Visu_Aux_ActAirInLou1 | Para_Visu_Aux_ActAirInLou1 | 6396 | Para_Visu_Aux_ActAirInLou1 |  | 18001
[8 empty] | 18002 | Para_Visu_Aux_ActAirInLou2 | Para_Visu_Aux_ActAirInLou2 | 6397 | Para_Visu_Aux_ActAirInLou2 |  | 18002
[8 empty] | 18003 | Para_Visu_Aux_ActAirInVent1 | Para_Visu_Aux_ActAirInVent1 | 6398 | Para_Visu_Aux_ActAirInVent1 |  | 18003
[8 empty] | 18004 | Para_Visu_Aux_ActAirInVent2 | Para_Visu_Aux_ActAirInVent2 | 6399 | Para_Visu_Aux_ActAirInVent2 |  | 18004
[8 empty] | 18005 | Para_Visu_Aux_ActAirInVentF | Para_Visu_Aux_ActAirInVentF | 6400 | Para_Visu_Aux_ActAirInVentF |  | 18005
[8 empty] | 18006 | Para_Visu_Aux_ActAirOutLou | Para_Visu_Aux_ActAirOutLou | 6401 | Para_Visu_Aux_ActAirOutLou |  | 18006
[8 empty] | 18007 | Para_Visu_Aux_ActCoolRadStage1 | Para_Visu_Aux_ActCoolRadStage1 | 6402 | Para_Visu_Aux_ActCoolRadStage1 |  | 18007
[8 empty] | 18008 | Para_Visu_Aux_ActCoolRadStage2 | Para_Visu_Aux_ActCoolRadStage2 | 6403 | Para_Visu_Aux_ActCoolRadStage2 |  | 18008
[8 empty] | 18009 | Para_Visu_Aux_ActCoolRadStageX | Para_Visu_Aux_ActCoolRadStageX | 6404 | Para_Visu_Aux_ActCoolRadStageX |  | 18009
[8 empty] | 18010 | Para_Visu_Aux_ActExhGasValveBypass | Para_Visu_Aux_ActExhGasValveBypass | 6405 | Para_Visu_Aux_ActExhGasValveBypass |  | 18010
[8 empty] | 18011 | Para_Visu_Aux_ActExhGasValveHeatEx | Para_Visu_Aux_ActExhGasValveHeatEx | 6406 | Para_Visu_Aux_ActExhGasValveHeatEx |  | 18011
[8 empty] | 18012 | Para_Visu_Aux_ActMixCoolRadStageX | Para_Visu_Aux_ActMixCoolRadStageX | 6407 | Para_Visu_Aux_ActMixCoolRadStageX |  | 18012
[8 empty] | 18013 | Para_Visu_Aux_ActPreHeat | Para_Visu_Aux_ActPreHeat | 6408 | Para_Visu_Aux_ActPreHeat |  | 18013
[8 empty] | 18014 | Para_Visu_Aux_ActPreHeatWatPump | Para_Visu_Aux_ActPreHeatWatPump | 6409 | Para_Visu_Aux_ActPreHeatWatPump |  | 18014
[8 empty] | 18015 | Para_Visu_Counter_MaintCountName1 | Para_Visu_Counter_MaintCountName1 | 6410 | Para_Visu_Counter_MaintCountName1 |  | 18015
[8 empty] | 18016 | Para_Visu_Counter_MaintCountName1_uc_NEx | Para_Visu_Counter_MaintCountName1_uc_NEx | 6411 | Para_Visu_Counter_MaintCountName1_uc_NEx |  | 18016
[8 empty] | 18017 | Para_Visu_Counter_MaintCountName2 | Para_Visu_Counter_MaintCountName2 | 6412 | Para_Visu_Counter_MaintCountName2 |  | 18017
[8 empty] | 18018 | Para_Visu_Counter_MaintCountName2_uc_NEx | Para_Visu_Counter_MaintCountName2_uc_NEx | 6413 | Para_Visu_Counter_MaintCountName2_uc_NEx |  | 18018
[8 empty] | 18019 | Para_Visu_Counter_MaintCountName3 | Para_Visu_Counter_MaintCountName3 | 6414 | Para_Visu_Counter_MaintCountName3 |  | 18019
[8 empty] | 18020 | Para_Visu_Counter_MaintCountName3_uc_NEx | Para_Visu_Counter_MaintCountName3_uc_NEx | 6415 | Para_Visu_Counter_MaintCountName3_uc_NEx |  | 18020
[8 empty] | 18021 | Para_Visu_Counter_MaintCountName4 | Para_Visu_Counter_MaintCountName4 | 6416 | Para_Visu_Counter_MaintCountName4 |  | 18021
[8 empty] | 18022 | Para_Visu_Counter_MaintCountName4_uc_NEx | Para_Visu_Counter_MaintCountName4_uc_NEx | 6417 | Para_Visu_Counter_MaintCountName4_uc_NEx |  | 18022
[8 empty] | 18023 | Para_Visu_Counter_MaintCountNameF1 | Para_Visu_Counter_MaintCountNameF1 | 6418 | Para_Visu_Counter_MaintCountNameF1 |  | 18023
[8 empty] | 18024 | Para_Visu_Counter_MaintCountNameF1_uc_NEx | Para_Visu_Counter_MaintCountNameF1_uc_NEx | 6419 | Para_Visu_Counter_MaintCountNameF1_uc_NEx |  | 18024
[8 empty] | 18025 | Para_Visu_Counter_MaintCountNameF2 | Para_Visu_Counter_MaintCountNameF2 | 6420 | Para_Visu_Counter_MaintCountNameF2 |  | 18025
[8 empty] | 18026 | Para_Visu_Counter_MaintCountNameF2_uc_NEx | Para_Visu_Counter_MaintCountNameF2_uc_NEx | 6421 | Para_Visu_Counter_MaintCountNameF2_uc_NEx |  | 18026
[8 empty] | 18027 | Para_Visu_Counter_MaintCountNameF3 | Para_Visu_Counter_MaintCountNameF3 | 6422 | Para_Visu_Counter_MaintCountNameF3 |  | 18027
[8 empty] | 18028 | Para_Visu_Counter_MaintCountNameF3_uc_NEx | Para_Visu_Counter_MaintCountNameF3_uc_NEx | 6423 | Para_Visu_Counter_MaintCountNameF3_uc_NEx |  | 18028
[8 empty] | 18029 | Para_Visu_Counter_MaintCountNameF4 | Para_Visu_Counter_MaintCountNameF4 | 6424 | Para_Visu_Counter_MaintCountNameF4 |  | 18029
[8 empty] | 18030 | Para_Visu_Counter_MaintCountNameF4_uc_NEx | Para_Visu_Counter_MaintCountNameF4_uc_NEx | 6425 | Para_Visu_Counter_MaintCountNameF4_uc_NEx |  | 18030
[8 empty] | 18031 | Para_Visu_Counter_ResCountName1 | Para_Visu_Counter_ResCountName1 | 6426 | Para_Visu_Counter_ResCountName1 |  | 18031
[8 empty] | 18032 | Para_Visu_Counter_ResCountName2 | Para_Visu_Counter_ResCountName2 | 6427 | Para_Visu_Counter_ResCountName2 |  | 18032
[8 empty] | 18033 | Para_Visu_Counter_ResCountName3 | Para_Visu_Counter_ResCountName3 | 6428 | Para_Visu_Counter_ResCountName3 |  | 18033
[8 empty] | 18034 | Para_Visu_Counter_ResCountName4 | Para_Visu_Counter_ResCountName4 | 6429 | Para_Visu_Counter_ResCountName4 |  | 18034
[8 empty] | 18035 | Para_Visu_Counter_ResCountNameF1 | Para_Visu_Counter_ResCountNameF1 | 6430 | Para_Visu_Counter_ResCountNameF1 |  | 18035
[8 empty] | 18036 | Para_Visu_Counter_ResCountNameF2 | Para_Visu_Counter_ResCountNameF2 | 6431 | Para_Visu_Counter_ResCountNameF2 |  | 18036
[8 empty] | 18037 | Para_Visu_Counter_ResCountNameF3 | Para_Visu_Counter_ResCountNameF3 | 6432 | Para_Visu_Counter_ResCountNameF3 |  | 18037
[8 empty] | 18038 | Para_Visu_Counter_ResCountNameF4 | Para_Visu_Counter_ResCountNameF4 | 6433 | Para_Visu_Counter_ResCountNameF4 |  | 18038
[8 empty] | 18039 | Para_Visu_Counter_ResCountUnit1 | Para_Visu_Counter_ResCountUnit1 | 6434 | Para_Visu_Counter_ResCountUnit1 |  | 18039
[8 empty] | 18040 | Para_Visu_Counter_ResCountUnit2 | Para_Visu_Counter_ResCountUnit2 | 6435 | Para_Visu_Counter_ResCountUnit2 |  | 18040
[8 empty] | 18041 | Para_Visu_Counter_ResCountUnit3 | Para_Visu_Counter_ResCountUnit3 | 6436 | Para_Visu_Counter_ResCountUnit3 |  | 18041
[8 empty] | 18042 | Para_Visu_Counter_ResCountUnit4 | Para_Visu_Counter_ResCountUnit4 | 6437 | Para_Visu_Counter_ResCountUnit4 |  | 18042
[8 empty] | 18043 | Para_Visu_Ele_ActGenNetPath | Para_Visu_Ele_ActGenNetPath | 6438 | Para_Visu_Ele_ActGenNetPath |  | 18043
[8 empty] | 18044 | Para_Visu_Ele_ActNetOK_NEx | Para_Visu_Ele_ActNetOK_NEx | 6439 | Para_Visu_Ele_ActNetOK_NEx |  | 18044
[8 empty] | 18045 | Para_Visu_Ele_ActTrGenDown | Para_Visu_Ele_ActTrGenDown | 6440 | Para_Visu_Ele_ActTrGenDown |  | 18045
[8 empty] | 18046 | Para_Visu_Ele_ActTrGenUp | Para_Visu_Ele_ActTrGenUp | 6441 | Para_Visu_Ele_ActTrGenUp |  | 18046
[8 empty] | 18047 | Para_Visu_Ele_ActTrNetDown | Para_Visu_Ele_ActTrNetDown | 6442 | Para_Visu_Ele_ActTrNetDown |  | 18047
[8 empty] | 18048 | Para_Visu_Ele_ActTrNetUp | Para_Visu_Ele_ActTrNetUp | 6443 | Para_Visu_Ele_ActTrNetUp |  | 18048
[8 empty] | 18049 | Para_Visu_Hyd_ActCoolWaterCircuit | Para_Visu_Hyd_ActCoolWaterCircuit | 6444 | Para_Visu_Hyd_ActCoolWaterCircuit |  | 18049
[8 empty] | 18050 | Para_Visu_Hyd_ActDeskCooler | Para_Visu_Hyd_ActDeskCooler | 6445 | Para_Visu_Hyd_ActDeskCooler |  | 18050
[8 empty] | 18051 | Para_Visu_Hyd_ActExtHeating | Para_Visu_Hyd_ActExtHeating | 6446 | Para_Visu_Hyd_ActExtHeating |  | 18051
[8 empty] | 18052 | Para_Visu_Hyd_ActIntHeating | Para_Visu_Hyd_ActIntHeating | 6447 | Para_Visu_Hyd_ActIntHeating |  | 18052
[8 empty] | 18053 | Para_Visu_Hyd_ActOil2Stage | Para_Visu_Hyd_ActOil2Stage | 6448 | Para_Visu_Hyd_ActOil2Stage |  | 18053
[8 empty] | 18054 | Para_Visu_Hyd_ActOilPreLubPumpAC | Para_Visu_Hyd_ActOilPreLubPumpAC | 6449 | Para_Visu_Hyd_ActOilPreLubPumpAC |  | 18054
[8 empty] | 18055 | Para_Visu_Hyd_ActOilPreLubPumpDC | Para_Visu_Hyd_ActOilPreLubPumpDC | 6450 | Para_Visu_Hyd_ActOilPreLubPumpDC |  | 18055
[8 empty] | 18056 | Para_Visu_Hyd_ActTC | Para_Visu_Hyd_ActTC | 6451 | Para_Visu_Hyd_ActTC |  | 18056
[8 empty] | 18057 | Para_Visu_UserLevelAck | Para_Visu_UserLevelAck | 6452 | Para_Visu_UserLevelAck |  | 18057
[8 empty] | 20444 | PBC_HeatChar10_Cyl01 | PBC_HeatChar10_Cyl01 | 6453 | PBC_HeatChar10_Cyl01 |  | 20444
[8 empty] | 20445 | PBC_HeatChar10_Cyl02 | PBC_HeatChar10_Cyl02 | 6454 | PBC_HeatChar10_Cyl02 |  | 20445
[8 empty] | 20446 | PBC_HeatChar10_Cyl03 | PBC_HeatChar10_Cyl03 | 6455 | PBC_HeatChar10_Cyl03 |  | 20446
[8 empty] | 20447 | PBC_HeatChar10_Cyl04 | PBC_HeatChar10_Cyl04 | 6456 | PBC_HeatChar10_Cyl04 |  | 20447
[8 empty] | 20448 | PBC_HeatChar10_Cyl05 | PBC_HeatChar10_Cyl05 | 6457 | PBC_HeatChar10_Cyl05 |  | 20448
[8 empty] | 20449 | PBC_HeatChar10_Cyl06 | PBC_HeatChar10_Cyl06 | 6458 | PBC_HeatChar10_Cyl06 |  | 20449
[8 empty] | 20450 | PBC_HeatChar10_Cyl07 | PBC_HeatChar10_Cyl07 | 6459 | PBC_HeatChar10_Cyl07 |  | 20450
[8 empty] | 20451 | PBC_HeatChar10_Cyl08 | PBC_HeatChar10_Cyl08 | 6460 | PBC_HeatChar10_Cyl08 |  | 20451
[8 empty] | 20452 | PBC_HeatChar10_Cyl09 | PBC_HeatChar10_Cyl09 | 6461 | PBC_HeatChar10_Cyl09 |  | 20452
[8 empty] | 20453 | PBC_HeatChar10_Cyl10 | PBC_HeatChar10_Cyl10 | 6462 | PBC_HeatChar10_Cyl10 |  | 20453
[8 empty] | 20454 | PBC_HeatChar10_Cyl11 | PBC_HeatChar10_Cyl11 | 6463 | PBC_HeatChar10_Cyl11 |  | 20454
[8 empty] | 20455 | PBC_HeatChar10_Cyl12 | PBC_HeatChar10_Cyl12 | 6464 | PBC_HeatChar10_Cyl12 |  | 20455
[8 empty] | 20456 | PBC_HeatChar10_Cyl13 | PBC_HeatChar10_Cyl13 | 6465 | PBC_HeatChar10_Cyl13 |  | 20456
[8 empty] | 20457 | PBC_HeatChar10_Cyl14 | PBC_HeatChar10_Cyl14 | 6466 | PBC_HeatChar10_Cyl14 |  | 20457
[8 empty] | 20458 | PBC_HeatChar10_Cyl15 | PBC_HeatChar10_Cyl15 | 6467 | PBC_HeatChar10_Cyl15 |  | 20458
[8 empty] | 20459 | PBC_HeatChar10_Cyl16 | PBC_HeatChar10_Cyl16 | 6468 | PBC_HeatChar10_Cyl16 |  | 20459
[8 empty] | 20460 | PBC_HeatChar10_Cyl17 | PBC_HeatChar10_Cyl17 | 6469 | PBC_HeatChar10_Cyl17 |  | 20460
[8 empty] | 20461 | PBC_HeatChar10_Cyl18 | PBC_HeatChar10_Cyl18 | 6470 | PBC_HeatChar10_Cyl18 |  | 20461
[8 empty] | 20462 | PBC_HeatChar10_Cyl19 | PBC_HeatChar10_Cyl19 | 6471 | PBC_HeatChar10_Cyl19 |  | 20462
[8 empty] | 20463 | PBC_HeatChar10_Cyl20 | PBC_HeatChar10_Cyl20 | 6472 | PBC_HeatChar10_Cyl20 |  | 20463
[8 empty] | 20464 | PBC_HeatChar10_Cyl21 | PBC_HeatChar10_Cyl21 | 6473 | PBC_HeatChar10_Cyl21 |  | 20464
[8 empty] | 20465 | PBC_HeatChar10_Cyl22 | PBC_HeatChar10_Cyl22 | 6474 | PBC_HeatChar10_Cyl22 |  | 20465
[8 empty] | 20466 | PBC_HeatChar10_Cyl23 | PBC_HeatChar10_Cyl23 | 6475 | PBC_HeatChar10_Cyl23 |  | 20466
[8 empty] | 20467 | PBC_HeatChar10_Cyl24 | PBC_HeatChar10_Cyl24 | 6476 | PBC_HeatChar10_Cyl24 |  | 20467
[8 empty] | 20468 | PBC_HeatChar90_Cyl01 | PBC_HeatChar90_Cyl01 | 6477 | PBC_HeatChar90_Cyl01 |  | 20468
[8 empty] | 20469 | PBC_HeatChar90_Cyl02 | PBC_HeatChar90_Cyl02 | 6478 | PBC_HeatChar90_Cyl02 |  | 20469
[8 empty] | 20470 | PBC_HeatChar90_Cyl03 | PBC_HeatChar90_Cyl03 | 6479 | PBC_HeatChar90_Cyl03 |  | 20470
[8 empty] | 20471 | PBC_HeatChar90_Cyl04 | PBC_HeatChar90_Cyl04 | 6480 | PBC_HeatChar90_Cyl04 |  | 20471
[8 empty] | 20472 | PBC_HeatChar90_Cyl05 | PBC_HeatChar90_Cyl05 | 6481 | PBC_HeatChar90_Cyl05 |  | 20472
[8 empty] | 20473 | PBC_HeatChar90_Cyl06 | PBC_HeatChar90_Cyl06 | 6482 | PBC_HeatChar90_Cyl06 |  | 20473
[8 empty] | 20474 | PBC_HeatChar90_Cyl07 | PBC_HeatChar90_Cyl07 | 6483 | PBC_HeatChar90_Cyl07 |  | 20474
[8 empty] | 20475 | PBC_HeatChar90_Cyl08 | PBC_HeatChar90_Cyl08 | 6484 | PBC_HeatChar90_Cyl08 |  | 20475
[8 empty] | 20476 | PBC_HeatChar90_Cyl09 | PBC_HeatChar90_Cyl09 | 6485 | PBC_HeatChar90_Cyl09 |  | 20476
[8 empty] | 20477 | PBC_HeatChar90_Cyl10 | PBC_HeatChar90_Cyl10 | 6486 | PBC_HeatChar90_Cyl10 |  | 20477
[8 empty] | 20478 | PBC_HeatChar90_Cyl11 | PBC_HeatChar90_Cyl11 | 6487 | PBC_HeatChar90_Cyl11 |  | 20478
[8 empty] | 20479 | PBC_HeatChar90_Cyl12 | PBC_HeatChar90_Cyl12 | 6488 | PBC_HeatChar90_Cyl12 |  | 20479
[8 empty] | 20480 | PBC_HeatChar90_Cyl13 | PBC_HeatChar90_Cyl13 | 6489 | PBC_HeatChar90_Cyl13 |  | 20480
[8 empty] | 20481 | PBC_HeatChar90_Cyl14 | PBC_HeatChar90_Cyl14 | 6490 | PBC_HeatChar90_Cyl14 |  | 20481
[8 empty] | 20482 | PBC_HeatChar90_Cyl15 | PBC_HeatChar90_Cyl15 | 6491 | PBC_HeatChar90_Cyl15 |  | 20482
[8 empty] | 20483 | PBC_HeatChar90_Cyl16 | PBC_HeatChar90_Cyl16 | 6492 | PBC_HeatChar90_Cyl16 |  | 20483
[8 empty] | 20484 | PBC_HeatChar90_Cyl17 | PBC_HeatChar90_Cyl17 | 6493 | PBC_HeatChar90_Cyl17 |  | 20484
[8 empty] | 20485 | PBC_HeatChar90_Cyl18 | PBC_HeatChar90_Cyl18 | 6494 | PBC_HeatChar90_Cyl18 |  | 20485
[8 empty] | 20486 | PBC_HeatChar90_Cyl19 | PBC_HeatChar90_Cyl19 | 6495 | PBC_HeatChar90_Cyl19 |  | 20486
[8 empty] | 20487 | PBC_HeatChar90_Cyl20 | PBC_HeatChar90_Cyl20 | 6496 | PBC_HeatChar90_Cyl20 |  | 20487
[8 empty] | 20488 | PBC_HeatChar90_Cyl21 | PBC_HeatChar90_Cyl21 | 6497 | PBC_HeatChar90_Cyl21 |  | 20488
[8 empty] | 20489 | PBC_HeatChar90_Cyl22 | PBC_HeatChar90_Cyl22 | 6498 | PBC_HeatChar90_Cyl22 |  | 20489
[8 empty] | 20490 | PBC_HeatChar90_Cyl23 | PBC_HeatChar90_Cyl23 | 6499 | PBC_HeatChar90_Cyl23 |  | 20490
[8 empty] | 20491 | PBC_HeatChar90_Cyl24 | PBC_HeatChar90_Cyl24 | 6500 | PBC_HeatChar90_Cyl24 |  | 20491
[8 empty] | 20304 | PBC_HeatCharVar_Avg | PBC_HeatCharVar_Avg | 6501 | PBC_HeatCharVar_Avg | °CA | 20304
[8 empty] | 19194 | PBC_HeatCharVar_Cyl01 | PBC_HeatCharVar_Cyl01 | 6502 | PBC_HeatCharVar_Cyl01 | °CA | 19194
[8 empty] | 19195 | PBC_HeatCharVar_Cyl02 | PBC_HeatCharVar_Cyl02 | 6503 | PBC_HeatCharVar_Cyl02 | °CA | 19195
[8 empty] | 19196 | PBC_HeatCharVar_Cyl03 | PBC_HeatCharVar_Cyl03 | 6504 | PBC_HeatCharVar_Cyl03 | °CA | 19196
[8 empty] | 19197 | PBC_HeatCharVar_Cyl04 | PBC_HeatCharVar_Cyl04 | 6505 | PBC_HeatCharVar_Cyl04 | °CA | 19197
[8 empty] | 19198 | PBC_HeatCharVar_Cyl05 | PBC_HeatCharVar_Cyl05 | 6506 | PBC_HeatCharVar_Cyl05 | °CA | 19198
[8 empty] | 19199 | PBC_HeatCharVar_Cyl06 | PBC_HeatCharVar_Cyl06 | 6507 | PBC_HeatCharVar_Cyl06 | °CA | 19199
[8 empty] | 19200 | PBC_HeatCharVar_Cyl07 | PBC_HeatCharVar_Cyl07 | 6508 | PBC_HeatCharVar_Cyl07 | °CA | 19200
[8 empty] | 19201 | PBC_HeatCharVar_Cyl08 | PBC_HeatCharVar_Cyl08 | 6509 | PBC_HeatCharVar_Cyl08 | °CA | 19201
[8 empty] | 19202 | PBC_HeatCharVar_Cyl09 | PBC_HeatCharVar_Cyl09 | 6510 | PBC_HeatCharVar_Cyl09 | °CA | 19202
[8 empty] | 19203 | PBC_HeatCharVar_Cyl10 | PBC_HeatCharVar_Cyl10 | 6511 | PBC_HeatCharVar_Cyl10 | °CA | 19203
[8 empty] | 19204 | PBC_HeatCharVar_Cyl11 | PBC_HeatCharVar_Cyl11 | 6512 | PBC_HeatCharVar_Cyl11 | °CA | 19204
[8 empty] | 19205 | PBC_HeatCharVar_Cyl12 | PBC_HeatCharVar_Cyl12 | 6513 | PBC_HeatCharVar_Cyl12 | °CA | 19205
[8 empty] | 19206 | PBC_HeatCharVar_Cyl13 | PBC_HeatCharVar_Cyl13 | 6514 | PBC_HeatCharVar_Cyl13 | °CA | 19206
[8 empty] | 19207 | PBC_HeatCharVar_Cyl14 | PBC_HeatCharVar_Cyl14 | 6515 | PBC_HeatCharVar_Cyl14 | °CA | 19207
[8 empty] | 19208 | PBC_HeatCharVar_Cyl15 | PBC_HeatCharVar_Cyl15 | 6516 | PBC_HeatCharVar_Cyl15 | °CA | 19208
[8 empty] | 19209 | PBC_HeatCharVar_Cyl16 | PBC_HeatCharVar_Cyl16 | 6517 | PBC_HeatCharVar_Cyl16 | °CA | 19209
[8 empty] | 19210 | PBC_HeatCharVar_Cyl17 | PBC_HeatCharVar_Cyl17 | 6518 | PBC_HeatCharVar_Cyl17 | °CA | 19210
[8 empty] | 19211 | PBC_HeatCharVar_Cyl18 | PBC_HeatCharVar_Cyl18 | 6519 | PBC_HeatCharVar_Cyl18 | °CA | 19211
[8 empty] | 19212 | PBC_HeatCharVar_Cyl19 | PBC_HeatCharVar_Cyl19 | 6520 | PBC_HeatCharVar_Cyl19 | °CA | 19212
[8 empty] | 19213 | PBC_HeatCharVar_Cyl20 | PBC_HeatCharVar_Cyl20 | 6521 | PBC_HeatCharVar_Cyl20 | °CA | 19213
[8 empty] | 19214 | PBC_HeatCharVar_Cyl21 | PBC_HeatCharVar_Cyl21 | 6522 | PBC_HeatCharVar_Cyl21 | °CA | 19214
[8 empty] | 19215 | PBC_HeatCharVar_Cyl22 | PBC_HeatCharVar_Cyl22 | 6523 | PBC_HeatCharVar_Cyl22 | °CA | 19215
[8 empty] | 19216 | PBC_HeatCharVar_Cyl23 | PBC_HeatCharVar_Cyl23 | 6524 | PBC_HeatCharVar_Cyl23 | °CA | 19216
[8 empty] | 19217 | PBC_HeatCharVar_Cyl24 | PBC_HeatCharVar_Cyl24 | 6525 | PBC_HeatCharVar_Cyl24 | °CA | 19217
[8 empty] | 20305 | PBC_HeatCharVar_Max | PBC_HeatCharVar_Max | 6526 | PBC_HeatCharVar_Max | °CA | 20305
[8 empty] | 20306 | PBC_HeatCharVar_Min | PBC_HeatCharVar_Min | 6527 | PBC_HeatCharVar_Min | °CA | 20306
[8 empty] | 20348 | PBC_Press49bfTDC_Avg | PBC_Press49bfTDC_Avg | 6528 | PBC_Press49bfTDC_Avg | mbar | 20348
[8 empty] | 20351 | PBC_Press49bfTDC_Cyl01 | PBC_Press49bfTDC_Cyl01 | 6529 | PBC_Press49bfTDC_Cyl01 | mbar | 20351
[8 empty] | 20352 | PBC_Press49bfTDC_Cyl02 | PBC_Press49bfTDC_Cyl02 | 6530 | PBC_Press49bfTDC_Cyl02 | mbar | 20352
[8 empty] | 20353 | PBC_Press49bfTDC_Cyl03 | PBC_Press49bfTDC_Cyl03 | 6531 | PBC_Press49bfTDC_Cyl03 | mbar | 20353
[8 empty] | 20354 | PBC_Press49bfTDC_Cyl04 | PBC_Press49bfTDC_Cyl04 | 6532 | PBC_Press49bfTDC_Cyl04 | mbar | 20354
[8 empty] | 20355 | PBC_Press49bfTDC_Cyl05 | PBC_Press49bfTDC_Cyl05 | 6533 | PBC_Press49bfTDC_Cyl05 | mbar | 20355
[8 empty] | 20356 | PBC_Press49bfTDC_Cyl06 | PBC_Press49bfTDC_Cyl06 | 6534 | PBC_Press49bfTDC_Cyl06 | mbar | 20356
[8 empty] | 20357 | PBC_Press49bfTDC_Cyl07 | PBC_Press49bfTDC_Cyl07 | 6535 | PBC_Press49bfTDC_Cyl07 | mbar | 20357
[8 empty] | 20358 | PBC_Press49bfTDC_Cyl08 | PBC_Press49bfTDC_Cyl08 | 6536 | PBC_Press49bfTDC_Cyl08 | mbar | 20358
[8 empty] | 20359 | PBC_Press49bfTDC_Cyl09 | PBC_Press49bfTDC_Cyl09 | 6537 | PBC_Press49bfTDC_Cyl09 | mbar | 20359
[8 empty] | 20360 | PBC_Press49bfTDC_Cyl10 | PBC_Press49bfTDC_Cyl10 | 6538 | PBC_Press49bfTDC_Cyl10 | mbar | 20360
[8 empty] | 20361 | PBC_Press49bfTDC_Cyl11 | PBC_Press49bfTDC_Cyl11 | 6539 | PBC_Press49bfTDC_Cyl11 | mbar | 20361
[8 empty] | 20362 | PBC_Press49bfTDC_Cyl12 | PBC_Press49bfTDC_Cyl12 | 6540 | PBC_Press49bfTDC_Cyl12 | mbar | 20362
[8 empty] | 20363 | PBC_Press49bfTDC_Cyl13 | PBC_Press49bfTDC_Cyl13 | 6541 | PBC_Press49bfTDC_Cyl13 | mbar | 20363
[8 empty] | 20364 | PBC_Press49bfTDC_Cyl14 | PBC_Press49bfTDC_Cyl14 | 6542 | PBC_Press49bfTDC_Cyl14 | mbar | 20364
[8 empty] | 20365 | PBC_Press49bfTDC_Cyl15 | PBC_Press49bfTDC_Cyl15 | 6543 | PBC_Press49bfTDC_Cyl15 | mbar | 20365
[8 empty] | 20366 | PBC_Press49bfTDC_Cyl16 | PBC_Press49bfTDC_Cyl16 | 6544 | PBC_Press49bfTDC_Cyl16 | mbar | 20366
[8 empty] | 20367 | PBC_Press49bfTDC_Cyl17 | PBC_Press49bfTDC_Cyl17 | 6545 | PBC_Press49bfTDC_Cyl17 | mbar | 20367
[8 empty] | 20368 | PBC_Press49bfTDC_Cyl18 | PBC_Press49bfTDC_Cyl18 | 6546 | PBC_Press49bfTDC_Cyl18 | mbar | 20368
[8 empty] | 20369 | PBC_Press49bfTDC_Cyl19 | PBC_Press49bfTDC_Cyl19 | 6547 | PBC_Press49bfTDC_Cyl19 | mbar | 20369
[8 empty] | 20370 | PBC_Press49bfTDC_Cyl20 | PBC_Press49bfTDC_Cyl20 | 6548 | PBC_Press49bfTDC_Cyl20 | mbar | 20370
[8 empty] | 20371 | PBC_Press49bfTDC_Cyl21 | PBC_Press49bfTDC_Cyl21 | 6549 | PBC_Press49bfTDC_Cyl21 | mbar | 20371
[8 empty] | 20372 | PBC_Press49bfTDC_Cyl22 | PBC_Press49bfTDC_Cyl22 | 6550 | PBC_Press49bfTDC_Cyl22 | mbar | 20372
[8 empty] | 20373 | PBC_Press49bfTDC_Cyl23 | PBC_Press49bfTDC_Cyl23 | 6551 | PBC_Press49bfTDC_Cyl23 | mbar | 20373
[8 empty] | 20374 | PBC_Press49bfTDC_Cyl24 | PBC_Press49bfTDC_Cyl24 | 6552 | PBC_Press49bfTDC_Cyl24 | mbar | 20374
[8 empty] | 20350 | PBC_Press49bfTDC_Max | PBC_Press49bfTDC_Max | 6553 | PBC_Press49bfTDC_Max | mbar | 20350
[8 empty] | 20349 | PBC_Press49bfTDC_Min | PBC_Press49bfTDC_Min | 6554 | PBC_Press49bfTDC_Min | mbar | 20349
[8 empty] | 19218 | PBC_PressMean_Avg | PBC_PressMean_Avg | 6555 | PBC_PressMean_Avg | bar | 19218
[8 empty] | 19219 | PBC_PressMean_Cyl01 | PBC_PressMean_Cyl01 | 6556 | PBC_PressMean_Cyl01 | bar | 19219
[8 empty] | 19220 | PBC_PressMean_Cyl02 | PBC_PressMean_Cyl02 | 6557 | PBC_PressMean_Cyl02 | bar | 19220
[8 empty] | 19221 | PBC_PressMean_Cyl03 | PBC_PressMean_Cyl03 | 6558 | PBC_PressMean_Cyl03 | bar | 19221
[8 empty] | 19222 | PBC_PressMean_Cyl04 | PBC_PressMean_Cyl04 | 6559 | PBC_PressMean_Cyl04 | bar | 19222
[8 empty] | 19223 | PBC_PressMean_Cyl05 | PBC_PressMean_Cyl05 | 6560 | PBC_PressMean_Cyl05 | bar | 19223
[8 empty] | 19224 | PBC_PressMean_Cyl06 | PBC_PressMean_Cyl06 | 6561 | PBC_PressMean_Cyl06 | bar | 19224
[8 empty] | 19225 | PBC_PressMean_Cyl07 | PBC_PressMean_Cyl07 | 6562 | PBC_PressMean_Cyl07 | bar | 19225
[8 empty] | 19226 | PBC_PressMean_Cyl08 | PBC_PressMean_Cyl08 | 6563 | PBC_PressMean_Cyl08 | bar | 19226
[8 empty] | 19227 | PBC_PressMean_Cyl09 | PBC_PressMean_Cyl09 | 6564 | PBC_PressMean_Cyl09 | bar | 19227
[8 empty] | 19228 | PBC_PressMean_Cyl10 | PBC_PressMean_Cyl10 | 6565 | PBC_PressMean_Cyl10 | bar | 19228
[8 empty] | 19229 | PBC_PressMean_Cyl11 | PBC_PressMean_Cyl11 | 6566 | PBC_PressMean_Cyl11 | bar | 19229
[8 empty] | 19230 | PBC_PressMean_Cyl12 | PBC_PressMean_Cyl12 | 6567 | PBC_PressMean_Cyl12 | bar | 19230
[8 empty] | 19231 | PBC_PressMean_Cyl13 | PBC_PressMean_Cyl13 | 6568 | PBC_PressMean_Cyl13 | bar | 19231
[8 empty] | 19232 | PBC_PressMean_Cyl14 | PBC_PressMean_Cyl14 | 6569 | PBC_PressMean_Cyl14 | bar | 19232
[8 empty] | 19233 | PBC_PressMean_Cyl15 | PBC_PressMean_Cyl15 | 6570 | PBC_PressMean_Cyl15 | bar | 19233
[8 empty] | 19234 | PBC_PressMean_Cyl16 | PBC_PressMean_Cyl16 | 6571 | PBC_PressMean_Cyl16 | bar | 19234
[8 empty] | 19235 | PBC_PressMean_Cyl17 | PBC_PressMean_Cyl17 | 6572 | PBC_PressMean_Cyl17 | bar | 19235
[8 empty] | 19236 | PBC_PressMean_Cyl18 | PBC_PressMean_Cyl18 | 6573 | PBC_PressMean_Cyl18 | bar | 19236
[8 empty] | 19237 | PBC_PressMean_Cyl19 | PBC_PressMean_Cyl19 | 6574 | PBC_PressMean_Cyl19 | bar | 19237
[8 empty] | 19238 | PBC_PressMean_Cyl20 | PBC_PressMean_Cyl20 | 6575 | PBC_PressMean_Cyl20 | bar | 19238
[8 empty] | 19239 | PBC_PressMean_Cyl21 | PBC_PressMean_Cyl21 | 6576 | PBC_PressMean_Cyl21 | bar | 19239
[8 empty] | 19240 | PBC_PressMean_Cyl22 | PBC_PressMean_Cyl22 | 6577 | PBC_PressMean_Cyl22 | bar | 19240
[8 empty] | 19241 | PBC_PressMean_Cyl23 | PBC_PressMean_Cyl23 | 6578 | PBC_PressMean_Cyl23 | bar | 19241
[8 empty] | 19242 | PBC_PressMean_Cyl24 | PBC_PressMean_Cyl24 | 6579 | PBC_PressMean_Cyl24 | bar | 19242
[8 empty] | 19243 | PBC_PressMean_Max | PBC_PressMean_Max | 6580 | PBC_PressMean_Max | bar | 19243
[8 empty] | 19244 | PBC_PressMean_Min | PBC_PressMean_Min | 6581 | PBC_PressMean_Min | bar | 19244
[8 empty] | 10009054 | PI_Commissioning | PI_Commissioning | 6582 | PI_Commissioning |  | 10009054
[8 empty] | 20307 | PI_Duration_Avg | PI_Duration_Avg | 6583 | PI_Duration_Avg | °CA | 20307
[8 empty] | 20310 | PI_Duration_Cyl01 | PI_Duration_Cyl01 | 6584 | PI_Duration_Cyl01 | °CA | 20310
[8 empty] | 20311 | PI_Duration_Cyl02 | PI_Duration_Cyl02 | 6585 | PI_Duration_Cyl02 | °CA | 20311
[8 empty] | 20312 | PI_Duration_Cyl03 | PI_Duration_Cyl03 | 6586 | PI_Duration_Cyl03 | °CA | 20312
[8 empty] | 20313 | PI_Duration_Cyl04 | PI_Duration_Cyl04 | 6587 | PI_Duration_Cyl04 | °CA | 20313
[8 empty] | 20314 | PI_Duration_Cyl05 | PI_Duration_Cyl05 | 6588 | PI_Duration_Cyl05 | °CA | 20314
[8 empty] | 20315 | PI_Duration_Cyl06 | PI_Duration_Cyl06 | 6589 | PI_Duration_Cyl06 | °CA | 20315
[8 empty] | 20316 | PI_Duration_Cyl07 | PI_Duration_Cyl07 | 6590 | PI_Duration_Cyl07 | °CA | 20316
[8 empty] | 20317 | PI_Duration_Cyl08 | PI_Duration_Cyl08 | 6591 | PI_Duration_Cyl08 | °CA | 20317
[8 empty] | 20318 | PI_Duration_Cyl09 | PI_Duration_Cyl09 | 6592 | PI_Duration_Cyl09 | °CA | 20318
[8 empty] | 20319 | PI_Duration_Cyl10 | PI_Duration_Cyl10 | 6593 | PI_Duration_Cyl10 | °CA | 20319
[8 empty] | 20320 | PI_Duration_Cyl11 | PI_Duration_Cyl11 | 6594 | PI_Duration_Cyl11 | °CA | 20320
[8 empty] | 20321 | PI_Duration_Cyl12 | PI_Duration_Cyl12 | 6595 | PI_Duration_Cyl12 | °CA | 20321
[8 empty] | 20322 | PI_Duration_Cyl13 | PI_Duration_Cyl13 | 6596 | PI_Duration_Cyl13 | °CA | 20322
[8 empty] | 20323 | PI_Duration_Cyl14 | PI_Duration_Cyl14 | 6597 | PI_Duration_Cyl14 | °CA | 20323
[8 empty] | 20324 | PI_Duration_Cyl15 | PI_Duration_Cyl15 | 6598 | PI_Duration_Cyl15 | °CA | 20324
[8 empty] | 20325 | PI_Duration_Cyl16 | PI_Duration_Cyl16 | 6599 | PI_Duration_Cyl16 | °CA | 20325
[8 empty] | 20326 | PI_Duration_Cyl17 | PI_Duration_Cyl17 | 6600 | PI_Duration_Cyl17 | °CA | 20326
[8 empty] | 20327 | PI_Duration_Cyl18 | PI_Duration_Cyl18 | 6601 | PI_Duration_Cyl18 | °CA | 20327
[8 empty] | 20328 | PI_Duration_Cyl19 | PI_Duration_Cyl19 | 6602 | PI_Duration_Cyl19 | °CA | 20328
[8 empty] | 20329 | PI_Duration_Cyl20 | PI_Duration_Cyl20 | 6603 | PI_Duration_Cyl20 | °CA | 20329
[8 empty] | 20344 | PI_Duration_Cyl21 | PI_Duration_Cyl21 | 6604 | PI_Duration_Cyl21 | °CA | 20344
[8 empty] | 20345 | PI_Duration_Cyl22 | PI_Duration_Cyl22 | 6605 | PI_Duration_Cyl22 | °CA | 20345
[8 empty] | 20346 | PI_Duration_Cyl23 | PI_Duration_Cyl23 | 6606 | PI_Duration_Cyl23 | °CA | 20346
[8 empty] | 20347 | PI_Duration_Cyl24 | PI_Duration_Cyl24 | 6607 | PI_Duration_Cyl24 | °CA | 20347
[8 empty] | 20309 | PI_Duration_Max | PI_Duration_Max | 6608 | PI_Duration_Max | °CA | 20309
[8 empty] | 20308 | PI_Duration_Min | PI_Duration_Min | 6609 | PI_Duration_Min | °CA | 20308
[8 empty] | 10009053 | PI_Man_Req | PI_Man_Req | 6610 | PI_Man_Req |  | 10009053
[8 empty] | 20424 | PI_Numb_SkipCyl_Act | PI_Numb_SkipCyl_Act | 6611 | PI_Numb_SkipCyl_Act |  | 20424
[8 empty] | 10009052 | PI_Required | PI_Required | 6612 | PI_Required |  | 10009052
[8 empty] | 10008974 | PI_ResetMap | PI_ResetMap | 6613 | PI_ResetMap |  | 10008974
[8 empty] | 10008970 | PI_SteadyState | PI_SteadyState | 6614 | PI_SteadyState |  | 10008970
[8 empty] | 1040177 | pole_slipping_counter | pole_slipping_counter | 6615 | pole_slipping_counter | count | 1040177
[8 empty] | 102 | Power_PowerAct | P Act | 6616 | Power_PowerAct | kW | 102
[8 empty] | 75 | Power_PowerActUnfilt | Power_PowerActUnfilt | 6617 | Power_PowerActUnfilt | kW | 75
[8 empty] | 19926 | Power_PowerMax | Power_PowerMax | 6618 | Power_PowerMax | kW | 19926
[8 empty] | 19643 | Power_PowerNominal | P nom | 6619 | Power_PowerNominal | kW | 19643
[8 empty] | 220 | Power_RedExt | Pred ext | 6620 | Power_RedExt | % | 220
[8 empty] | 233 | Power_RedExtBus | Pred Bus | 6621 | Power_RedExtBus | % | 233
[8 empty] | 196 | Power_RedKnock | Pred knock | 6622 | Power_RedKnock | % | 196
[8 empty] | 216 | Power_RedMisfire | Pred misfire | 6623 | Power_RedMisfire | % | 216
[8 empty] | 77 | Power_RedMixTemp | Pred mixtemp | 6624 | Power_RedMixTemp | % | 77
[8 empty] | 124 | Power_RedPowerAct | P red Act | 6625 | Power_RedPowerAct | kW | 124
[8 empty] | 143 | Power_SetPower | Power_SetPower | 6626 | Power_SetPower | kW | 143
[8 empty] | 178 | Power_SetPowerExtInt | Power_SetPowerExtInt | 6627 | Power_SetPowerExtInt |  | 178
[8 empty] | 125 | Power_SetPowerUnred | Power_SetPowerUnred | 6628 | Power_SetPowerUnred | kW | 125
[8 empty] | 10049283 | pr_ch_p1hp_a | P11 A | 6629 | pr_ch_p1hp_a | bar | 10049283
[8 empty] | 10049284 | pr_ch_p1hp_b | P11 B | 6630 | pr_ch_p1hp_b | bar | 10049284
[8 empty] | 10049285 | pr_egahptc_a | pr_egahptc_a | 6631 | pr_egahptc_a | bar | 10049285
[8 empty] | 10049286 | pr_egahptc_b | pr_egahptc_b | 6632 | pr_egahptc_b | bar | 10049286
[8 empty] | 10049287 | pr_egalptc_a | pr_egalptc_a | 6633 | pr_egalptc_a | bar | 10049287
[8 empty] | 10049288 | pr_egalptc_b | pr_egalptc_b | 6634 | pr_egalptc_b | bar | 10049288
[8 empty] | 10049289 | pr_egbhptc_a | pr_egbhptc_a | 6635 | pr_egbhptc_a | bar | 10049289
[8 empty] | 10049290 | pr_egbhptc_b | pr_egbhptc_b | 6636 | pr_egbhptc_b | bar | 10049290
[8 empty] | 10009006 | rE_SinceStart | E since Start | 6637 | rE_SinceStart |  | 10009006
[8 empty] | 10009023 | rHours_SinceStart | h since Start | 6638 | rHours_SinceStart |  | 10009023
[8 empty] | 1001100 | RMD_ListAvgCCP_CCPSensor | Crankcase Pressure | 6639 | RMD_ListAvgCCP_CCPSensor | mbar | 1001100
[8 empty] | 1001103 | RMD_ListAvgOilPress_OilPressureLimit | Oil P limit | 6640 | RMD_ListAvgOilPress_OilPressureLimit | bar | 1001103
[8 empty] | 1001101 | RMD_ListBuffMAvgOilConsume_OilConsumption | LOC Avg | 6641 | RMD_ListBuffMAvgOilConsume_OilConsumption | g/kWh | 1001101
[8 empty] | 1001102 | RMD_ListBuffMAvgOilDiffPress_OilDiffPress | DP Oilfilter | 6642 | RMD_ListBuffMAvgOilDiffPress_OilDiffPress | bar | 1001102
[8 empty] | 10009050 | rP_Ramp_Act | rP_Ramp_Act | 6643 | rP_Ramp_Act |  | 10009050
[8 empty] | 10009049 | rP_Ramp_Set | LoadRamp | 6644 | rP_Ramp_Set |  | 10009049
[8 empty] | 10009051 | rP_Targ_LastStart | rP_Targ_LastStart | 6645 | rP_Targ_LastStart |  | 10009051
[8 empty] | 10049329 | rpr_oil_lptc_in_a | rpr_oil_lptc_in_a | 6646 | rpr_oil_lptc_in_a | bar | 10049329
[8 empty] | 10049330 | rpr_oil_lptc_in_b | rpr_oil_lptc_in_b | 6647 | rpr_oil_lptc_in_b | bar | 10049330
[8 empty] | 10049328 | rpr_tc_eof_after | rpr_tc_eof_after | 6648 | rpr_tc_eof_after | bar | 10049328
[8 empty] | 10009045 | rT_ECW_FS_Perm | rT_ECW_FS_Perm | 6649 | rT_ECW_FS_Perm |  | 10009045
[8 empty] | 10009027 | rT_EGaHPTC | rT_EGaHPTC | 6650 | rT_EGaHPTC |  | 10009027
[8 empty] | 10009047 | rT_EO_FS_Perm | rT_EO_FS_Perm | 6651 | rT_EO_FS_Perm |  | 10009047
[8 empty] | 10049331 | rt_eo_pan | rt_eo_pan | 6652 | rt_eo_pan |  | 10049331
[8 empty] | 10009008 | rTi_Load_0 | rTi_Load_0 | 6653 | rTi_Load_0 |  | 10009008
[8 empty] | 10009007 | rTi_Load_2 | rTi_Load_2 | 6654 | rTi_Load_2 |  | 10009007
[8 empty] | 10009010 | rTi_Prep_0 | rTi_Prep_0 | 6655 | rTi_Prep_0 |  | 10009010
[8 empty] | 10009009 | rTi_Prep_1 | rTi_Prep_1 | 6656 | rTi_Prep_1 |  | 10009009
[8 empty] | 10009011 | rTi_Prep_2 | rTi_Prep_2 | 6657 | rTi_Prep_2 |  | 10009011
[8 empty] | 10009012 | rTi_Speedup_0 | rTi_Speedup_0 | 6658 | rTi_Speedup_0 |  | 10009012
[8 empty] | 10009013 | rTi_Speedup_1 | rTi_Speedup_1 | 6659 | rTi_Speedup_1 |  | 10009013
[8 empty] | 10009016 | rTi_Speedup_2 | rTi_Speedup_2 | 6660 | rTi_Speedup_2 |  | 10009016
[8 empty] | 10009014 | rTi_Start_0 | rTi_Start_0 | 6661 | rTi_Start_0 |  | 10009014
[8 empty] | 10009015 | rTi_Start_1 | rTi_Start_1 | 6662 | rTi_Start_1 |  | 10009015
[8 empty] | 10009017 | rTi_Start_2 | rTi_Start_2 | 6663 | rTi_Start_2 |  | 10009017
[8 empty] | 10009018 | rTi_SumLoad | rTi_SumLoad | 6664 | rTi_SumLoad |  | 10009018
[8 empty] | 10009019 | rTi_SumSync | rTi_SumSync | 6665 | rTi_SumSync |  | 10009019
[8 empty] | 10009020 | rTi_Sync_0 | rTi_Sync_0 | 6666 | rTi_Sync_0 |  | 10009020
[8 empty] | 10009021 | rTi_Sync_1 | rTi_Sync_1 | 6667 | rTi_Sync_1 |  | 10009021
[8 empty] | 10009022 | rTi_Sync_2 | rTi_Sync_2 | 6668 | rTi_Sync_2 |  | 10009022
[8 empty] | 10009030 | rTi_Targ | rTi_Targ | 6669 | rTi_Targ |  | 10009030
[8 empty] | 1000647 | SAFI_Electronic_Temp_Average | Safi Temp | 6670 | SAFI_Electronic_Temp_Average | C | 1000647
[8 empty] | 10049259 | safi_valvelashset_1 | safi_valvelashset_1 | 6671 | safi_valvelashset_1 |  | 10049259
[8 empty] | 10049268 | safi_valvelashset_10 | safi_valvelashset_10 | 6672 | safi_valvelashset_10 |  | 10049268
[8 empty] | 10049269 | safi_valvelashset_11 | safi_valvelashset_11 | 6673 | safi_valvelashset_11 |  | 10049269
[8 empty] | 10049270 | safi_valvelashset_12 | safi_valvelashset_12 | 6674 | safi_valvelashset_12 |  | 10049270
[8 empty] | 10049271 | safi_valvelashset_13 | safi_valvelashset_13 | 6675 | safi_valvelashset_13 |  | 10049271
[8 empty] | 10049272 | safi_valvelashset_14 | safi_valvelashset_14 | 6676 | safi_valvelashset_14 |  | 10049272
[8 empty] | 10049273 | safi_valvelashset_15 | safi_valvelashset_15 | 6677 | safi_valvelashset_15 |  | 10049273
[8 empty] | 10049274 | safi_valvelashset_16 | safi_valvelashset_16 | 6678 | safi_valvelashset_16 |  | 10049274
[8 empty] | 10049275 | safi_valvelashset_17 | safi_valvelashset_17 | 6679 | safi_valvelashset_17 |  | 10049275
[8 empty] | 10049276 | safi_valvelashset_18 | safi_valvelashset_18 | 6680 | safi_valvelashset_18 |  | 10049276
[8 empty] | 10049277 | safi_valvelashset_19 | safi_valvelashset_19 | 6681 | safi_valvelashset_19 |  | 10049277
[8 empty] | 10049260 | safi_valvelashset_2 | safi_valvelashset_2 | 6682 | safi_valvelashset_2 |  | 10049260
[8 empty] | 10049278 | safi_valvelashset_20 | safi_valvelashset_20 | 6683 | safi_valvelashset_20 |  | 10049278
[8 empty] | 10049279 | safi_valvelashset_21 | safi_valvelashset_21 | 6684 | safi_valvelashset_21 |  | 10049279
[8 empty] | 10049280 | safi_valvelashset_22 | safi_valvelashset_22 | 6685 | safi_valvelashset_22 |  | 10049280
[8 empty] | 10049281 | safi_valvelashset_23 | safi_valvelashset_23 | 6686 | safi_valvelashset_23 |  | 10049281
[8 empty] | 10049282 | safi_valvelashset_24 | safi_valvelashset_24 | 6687 | safi_valvelashset_24 |  | 10049282
[8 empty] | 10049261 | safi_valvelashset_3 | safi_valvelashset_3 | 6688 | safi_valvelashset_3 |  | 10049261
[8 empty] | 10049262 | safi_valvelashset_4 | safi_valvelashset_4 | 6689 | safi_valvelashset_4 |  | 10049262
[8 empty] | 10049263 | safi_valvelashset_5 | safi_valvelashset_5 | 6690 | safi_valvelashset_5 |  | 10049263
[8 empty] | 10049264 | safi_valvelashset_6 | safi_valvelashset_6 | 6691 | safi_valvelashset_6 |  | 10049264
[8 empty] | 10049265 | safi_valvelashset_7 | safi_valvelashset_7 | 6692 | safi_valvelashset_7 |  | 10049265
[8 empty] | 10049266 | safi_valvelashset_8 | safi_valvelashset_8 | 6693 | safi_valvelashset_8 |  | 10049266
[8 empty] | 10049267 | safi_valvelashset_9 | safi_valvelashset_9 | 6694 | safi_valvelashset_9 |  | 10049267
[8 empty] | 10049211 | safi_win3_1 | Safi W3 Z1 | 6695 | safi_win3_1 | °CA | 10049211
[8 empty] | 10049220 | safi_win3_10 | Safi W3 Z10 | 6696 | safi_win3_10 | °CA | 10049220
[8 empty] | 10049221 | safi_win3_11 | Safi W3 Z11 | 6697 | safi_win3_11 | °CA | 10049221
[8 empty] | 10049222 | safi_win3_12 | Safi W3 Z12 | 6698 | safi_win3_12 | °CA | 10049222
[8 empty] | 10049223 | safi_win3_13 | Safi W3 Z13 | 6699 | safi_win3_13 | °CA | 10049223
[8 empty] | 10049224 | safi_win3_14 | Safi W3 Z14 | 6700 | safi_win3_14 | °CA | 10049224
[8 empty] | 10049225 | safi_win3_15 | Safi W3 Z15 | 6701 | safi_win3_15 | °CA | 10049225
[8 empty] | 10049226 | safi_win3_16 | Safi W3 Z16 | 6702 | safi_win3_16 | °CA | 10049226
[8 empty] | 10049227 | safi_win3_17 | Safi W3 Z17 | 6703 | safi_win3_17 | °CA | 10049227
[8 empty] | 10049228 | safi_win3_18 | Safi W3 Z18 | 6704 | safi_win3_18 | °CA | 10049228
[8 empty] | 10049229 | safi_win3_19 | Safi W3 Z19 | 6705 | safi_win3_19 | °CA | 10049229
[8 empty] | 10049212 | safi_win3_2 | Safi W3 Z2 | 6706 | safi_win3_2 | °CA | 10049212
[8 empty] | 10049230 | safi_win3_20 | Safi W3 Z20 | 6707 | safi_win3_20 | °CA | 10049230
[8 empty] | 10049231 | safi_win3_21 | Safi W3 Z21 | 6708 | safi_win3_21 | °CA | 10049231
[8 empty] | 10049232 | safi_win3_22 | Safi W3 Z22 | 6709 | safi_win3_22 | °CA | 10049232
[8 empty] | 10049233 | safi_win3_23 | Safi W3 Z23 | 6710 | safi_win3_23 | °CA | 10049233
[8 empty] | 10049234 | safi_win3_24 | Safi W3 Z24 | 6711 | safi_win3_24 | °CA | 10049234
[8 empty] | 10049213 | safi_win3_3 | Safi W3 Z3 | 6712 | safi_win3_3 | °CA | 10049213
[8 empty] | 10049214 | safi_win3_4 | Safi W3 Z4 | 6713 | safi_win3_4 | °CA | 10049214
[8 empty] | 10049215 | safi_win3_5 | Safi W3 Z5 | 6714 | safi_win3_5 | °CA | 10049215
[8 empty] | 10049216 | safi_win3_6 | Safi W3 Z6 | 6715 | safi_win3_6 | °CA | 10049216
[8 empty] | 10049217 | safi_win3_7 | Safi W3 Z7 | 6716 | safi_win3_7 | °CA | 10049217
[8 empty] | 10049218 | safi_win3_8 | Safi W3 Z8 | 6717 | safi_win3_8 | °CA | 10049218
[8 empty] | 10049219 | safi_win3_9 | Safi W3 Z9 | 6718 | safi_win3_9 | °CA | 10049219
[8 empty] | 10049235 | safi_win4_1 | Safi W4 Z1 | 6719 | safi_win4_1 | °CA | 10049235
[8 empty] | 10049244 | safi_win4_10 | Safi W4 Z10 | 6720 | safi_win4_10 | °CA | 10049244
[8 empty] | 10049245 | safi_win4_11 | Safi W4 Z11 | 6721 | safi_win4_11 | °CA | 10049245
[8 empty] | 10049246 | safi_win4_12 | Safi W4 Z12 | 6722 | safi_win4_12 | °CA | 10049246
[8 empty] | 10049247 | safi_win4_13 | Safi W4 Z13 | 6723 | safi_win4_13 | °CA | 10049247
[8 empty] | 10049248 | safi_win4_14 | Safi W4 Z14 | 6724 | safi_win4_14 | °CA | 10049248
[8 empty] | 10049249 | safi_win4_15 | Safi W4 Z15 | 6725 | safi_win4_15 | °CA | 10049249
[8 empty] | 10049250 | safi_win4_16 | Safi W4 Z16 | 6726 | safi_win4_16 | °CA | 10049250
[8 empty] | 10049251 | safi_win4_17 | Safi W4 Z17 | 6727 | safi_win4_17 | °CA | 10049251
[8 empty] | 10049252 | safi_win4_18 | Safi W4 Z18 | 6728 | safi_win4_18 | °CA | 10049252
[8 empty] | 10049253 | safi_win4_19 | Safi W4 Z19 | 6729 | safi_win4_19 | °CA | 10049253
[8 empty] | 10049236 | safi_win4_2 | Safi W4 Z2 | 6730 | safi_win4_2 | °CA | 10049236
[8 empty] | 10049254 | safi_win4_20 | Safi W4 Z20 | 6731 | safi_win4_20 | °CA | 10049254
[8 empty] | 10049255 | safi_win4_21 | Safi W4 Z21 | 6732 | safi_win4_21 | °CA | 10049255
[8 empty] | 10049256 | safi_win4_22 | Safi W4 Z22 | 6733 | safi_win4_22 | °CA | 10049256
[8 empty] | 10049257 | safi_win4_23 | Safi W4 Z23 | 6734 | safi_win4_23 | °CA | 10049257
[8 empty] | 10049258 | safi_win4_24 | Safi W4 Z24 | 6735 | safi_win4_24 | °CA | 10049258
[8 empty] | 10049237 | safi_win4_3 | Safi W4 Z3 | 6736 | safi_win4_3 | °CA | 10049237
[8 empty] | 10049238 | safi_win4_4 | Safi W4 Z4 | 6737 | safi_win4_4 | °CA | 10049238
[8 empty] | 10049239 | safi_win4_5 | Safi W4 Z5 | 6738 | safi_win4_5 | °CA | 10049239
[8 empty] | 10049240 | safi_win4_6 | Safi W4 Z6 | 6739 | safi_win4_6 | °CA | 10049240
[8 empty] | 10049241 | safi_win4_7 | Safi W4 Z7 | 6740 | safi_win4_7 | °CA | 10049241
[8 empty] | 10049242 | safi_win4_8 | Safi W4 Z8 | 6741 | safi_win4_8 | °CA | 10049242
[8 empty] | 10049243 | safi_win4_9 | Safi W4 Z9 | 6742 | safi_win4_9 | °CA | 10049243
[8 empty] | 1040156 | SCR_Catalyst_RUL | SCR_Catalyst_RUL | 6743 | SCR_Catalyst_RUL | oph | 1040156
[8 empty] | 10050037 | SendingDataCondition | SendingDataCondition | 6744 | SendingDataCondition |  | 10050037
[8 empty] | 10050036 | SendingDataConditionNumeric | SendingDataConditionNumeric | 6745 | SendingDataConditionNumeric |  | 10050036
[8 empty] | 10009055 | SlowDownTime00 | Slow Down Time | 6746 | SlowDownTime00 |  | 10009055
[8 empty] | 10009064 | SlowDownTime01 | SlowDownTime01 | 6747 | SlowDownTime01 |  | 10009064
[8 empty] | 10009056 | SlowDownTime02 | SlowDownTime02 | 6748 | SlowDownTime02 |  | 10009056
[8 empty] | 10009074 | SlowDownTime03 | SlowDownTime03 | 6749 | SlowDownTime03 |  | 10009074
[8 empty] | 10009065 | SlowDownTime04 | SlowDownTime04 | 6750 | SlowDownTime04 |  | 10009065
[8 empty] | 10009066 | SlowDownTime05 | SlowDownTime05 | 6751 | SlowDownTime05 |  | 10009066
[8 empty] | 10009067 | SlowDownTime06 | SlowDownTime06 | 6752 | SlowDownTime06 |  | 10009067
[8 empty] | 10009068 | SlowDownTime07 | SlowDownTime07 | 6753 | SlowDownTime07 |  | 10009068
[8 empty] | 10009069 | SlowDownTime08 | SlowDownTime08 | 6754 | SlowDownTime08 |  | 10009069
[8 empty] | 10009070 | SlowDownTime09 | SlowDownTime09 | 6755 | SlowDownTime09 |  | 10009070
[8 empty] | 10009071 | SlowDownTime10 | SlowDownTime10 | 6756 | SlowDownTime10 |  | 10009071
[8 empty] | 10009072 | SlowDownTime11 | SlowDownTime11 | 6757 | SlowDownTime11 |  | 10009072
[8 empty] | 10009073 | SlowDownTime12 | SlowDownTime12 | 6758 | SlowDownTime12 |  | 10009073
[8 empty] | 10009058 | SlowDownTime13 | SlowDownTime13 | 6759 | SlowDownTime13 |  | 10009058
[8 empty] | 10009057 | SlowDownTime14 | SlowDownTime14 | 6760 | SlowDownTime14 |  | 10009057
[8 empty] | 10009059 | SlowDownTime15 | SlowDownTime15 | 6761 | SlowDownTime15 |  | 10009059
[8 empty] | 10009060 | SlowDownTime16 | SlowDownTime16 | 6762 | SlowDownTime16 |  | 10009060
[8 empty] | 10009061 | SlowDownTime17 | SlowDownTime17 | 6763 | SlowDownTime17 |  | 10009061
[8 empty] | 10009062 | SlowDownTime18 | SlowDownTime18 | 6764 | SlowDownTime18 |  | 10009062
[8 empty] | 10009063 | SlowDownTime19 | SlowDownTime19 | 6765 | SlowDownTime19 |  | 10009063
[8 empty] | 1040182 | spark_plug_maintenance_IV01 | spark_plug_maintenance_IV01 | 6766 | spark_plug_maintenance_IV01 | kV | 1040182
[8 empty] | 1040183 | spark_plug_maintenance_IV02 | spark_plug_maintenance_IV02 | 6767 | spark_plug_maintenance_IV02 | kV | 1040183
[8 empty] | 1040184 | spark_plug_maintenance_IV03 | spark_plug_maintenance_IV03 | 6768 | spark_plug_maintenance_IV03 | kV | 1040184
[8 empty] | 1040185 | spark_plug_maintenance_IV04 | spark_plug_maintenance_IV04 | 6769 | spark_plug_maintenance_IV04 | kV | 1040185
[8 empty] | 1040186 | spark_plug_maintenance_IV05 | spark_plug_maintenance_IV05 | 6770 | spark_plug_maintenance_IV05 | kV | 1040186
[8 empty] | 1040187 | spark_plug_maintenance_IV06 | spark_plug_maintenance_IV06 | 6771 | spark_plug_maintenance_IV06 | kV | 1040187
[8 empty] | 1040188 | spark_plug_maintenance_IV07 | spark_plug_maintenance_IV07 | 6772 | spark_plug_maintenance_IV07 | kV | 1040188
[8 empty] | 1040189 | spark_plug_maintenance_IV08 | spark_plug_maintenance_IV08 | 6773 | spark_plug_maintenance_IV08 | kV | 1040189
[8 empty] | 1040190 | spark_plug_maintenance_IV09 | spark_plug_maintenance_IV09 | 6774 | spark_plug_maintenance_IV09 | kV | 1040190
[8 empty] | 1040191 | spark_plug_maintenance_IV10 | spark_plug_maintenance_IV10 | 6775 | spark_plug_maintenance_IV10 | kV | 1040191
[8 empty] | 1040192 | spark_plug_maintenance_IV11 | spark_plug_maintenance_IV11 | 6776 | spark_plug_maintenance_IV11 | kV | 1040192
[8 empty] | 1040193 | spark_plug_maintenance_IV12 | spark_plug_maintenance_IV12 | 6777 | spark_plug_maintenance_IV12 | kV | 1040193
[8 empty] | 1040194 | spark_plug_maintenance_IV13 | spark_plug_maintenance_IV13 | 6778 | spark_plug_maintenance_IV13 | kV | 1040194
[8 empty] | 1040195 | spark_plug_maintenance_IV14 | spark_plug_maintenance_IV14 | 6779 | spark_plug_maintenance_IV14 | kV | 1040195
[8 empty] | 1040196 | spark_plug_maintenance_IV15 | spark_plug_maintenance_IV15 | 6780 | spark_plug_maintenance_IV15 | kV | 1040196
[8 empty] | 1040197 | spark_plug_maintenance_IV16 | spark_plug_maintenance_IV16 | 6781 | spark_plug_maintenance_IV16 | kV | 1040197
[8 empty] | 1040198 | spark_plug_maintenance_IV17 | spark_plug_maintenance_IV17 | 6782 | spark_plug_maintenance_IV17 | kV | 1040198
[8 empty] | 1040199 | spark_plug_maintenance_IV18 | spark_plug_maintenance_IV18 | 6783 | spark_plug_maintenance_IV18 | kV | 1040199
[8 empty] | 1040200 | spark_plug_maintenance_IV19 | spark_plug_maintenance_IV19 | 6784 | spark_plug_maintenance_IV19 | kV | 1040200
[8 empty] | 1040201 | spark_plug_maintenance_IV20 | spark_plug_maintenance_IV20 | 6785 | spark_plug_maintenance_IV20 | kV | 1040201
[8 empty] | 1040202 | spark_plug_maintenance_IV21 | spark_plug_maintenance_IV21 | 6786 | spark_plug_maintenance_IV21 | kV | 1040202
[8 empty] | 1040203 | spark_plug_maintenance_IV22 | spark_plug_maintenance_IV22 | 6787 | spark_plug_maintenance_IV22 | kV | 1040203
[8 empty] | 1040204 | spark_plug_maintenance_IV23 | spark_plug_maintenance_IV23 | 6788 | spark_plug_maintenance_IV23 | kV | 1040204
[8 empty] | 1040205 | spark_plug_maintenance_IV24 | spark_plug_maintenance_IV24 | 6789 | spark_plug_maintenance_IV24 | kV | 1040205
[8 empty] | 1040118 | Spark_Plug_RUL01 | Spark_Plug_RUL01 | 6790 | Spark_Plug_RUL01 | oph | 1040118
[8 empty] | 1040119 | Spark_Plug_RUL02 | Spark_Plug_RUL02 | 6791 | Spark_Plug_RUL02 | oph | 1040119
[8 empty] | 1040120 | Spark_Plug_RUL03 | Spark_Plug_RUL03 | 6792 | Spark_Plug_RUL03 | oph | 1040120
[8 empty] | 1040121 | Spark_Plug_RUL04 | Spark_Plug_RUL04 | 6793 | Spark_Plug_RUL04 | oph | 1040121
[8 empty] | 1040122 | Spark_Plug_RUL05 | Spark_Plug_RUL05 | 6794 | Spark_Plug_RUL05 | oph | 1040122
[8 empty] | 1040123 | Spark_Plug_RUL06 | Spark_Plug_RUL06 | 6795 | Spark_Plug_RUL06 | oph | 1040123
[8 empty] | 1040124 | Spark_Plug_RUL07 | Spark_Plug_RUL07 | 6796 | Spark_Plug_RUL07 | oph | 1040124
[8 empty] | 1040125 | Spark_Plug_RUL08 | Spark_Plug_RUL08 | 6797 | Spark_Plug_RUL08 | oph | 1040125
[8 empty] | 1040126 | Spark_Plug_RUL09 | Spark_Plug_RUL09 | 6798 | Spark_Plug_RUL09 | oph | 1040126
[8 empty] | 1040127 | Spark_Plug_RUL10 | Spark_Plug_RUL10 | 6799 | Spark_Plug_RUL10 | oph | 1040127
[8 empty] | 1040128 | Spark_Plug_RUL11 | Spark_Plug_RUL11 | 6800 | Spark_Plug_RUL11 | oph | 1040128
[8 empty] | 1040129 | Spark_Plug_RUL12 | Spark_Plug_RUL12 | 6801 | Spark_Plug_RUL12 | oph | 1040129
[8 empty] | 1040130 | Spark_Plug_RUL13 | Spark_Plug_RUL13 | 6802 | Spark_Plug_RUL13 | oph | 1040130
[8 empty] | 1040131 | Spark_Plug_RUL14 | Spark_Plug_RUL14 | 6803 | Spark_Plug_RUL14 | oph | 1040131
[8 empty] | 1040132 | Spark_Plug_RUL15 | Spark_Plug_RUL15 | 6804 | Spark_Plug_RUL15 | oph | 1040132
[8 empty] | 1040133 | Spark_Plug_RUL16 | Spark_Plug_RUL16 | 6805 | Spark_Plug_RUL16 | oph | 1040133
[8 empty] | 1040134 | Spark_Plug_RUL17 | Spark_Plug_RUL17 | 6806 | Spark_Plug_RUL17 | oph | 1040134
[8 empty] | 1040135 | Spark_Plug_RUL18 | Spark_Plug_RUL18 | 6807 | Spark_Plug_RUL18 | oph | 1040135
[8 empty] | 1040136 | Spark_Plug_RUL19 | Spark_Plug_RUL19 | 6808 | Spark_Plug_RUL19 | oph | 1040136
[8 empty] | 1040137 | Spark_Plug_RUL20 | Spark_Plug_RUL20 | 6809 | Spark_Plug_RUL20 | oph | 1040137
[8 empty] | 1040138 | Spark_Plug_RUL21 | Spark_Plug_RUL21 | 6810 | Spark_Plug_RUL21 | oph | 1040138
[8 empty] | 1040139 | Spark_Plug_RUL22 | Spark_Plug_RUL22 | 6811 | Spark_Plug_RUL22 | oph | 1040139
[8 empty] | 1040140 | Spark_Plug_RUL23 | Spark_Plug_RUL23 | 6812 | Spark_Plug_RUL23 | oph | 1040140
[8 empty] | 1040141 | Spark_Plug_RUL24 | Spark_Plug_RUL24 | 6813 | Spark_Plug_RUL24 | oph | 1040141
[8 empty] | 1019439 | SPW_calc_starts_per_week | SPW_calc_starts_per_week | 6814 | SPW_calc_starts_per_week | Starts | 1019439
[8 empty] | 10008985 | StartsCnt_Statistic | StartsCnt_Statistic | 6815 | StartsCnt_Statistic |  | 10008985
[8 empty] | 10049519 | synchronization_bmcb_on | OP NetP | 6816 | synchronization_bmcb_on |  | 10049519
[8 empty] | 10049587 | systeminfo_availablememory | systeminfo_availablememory | 6817 | systeminfo_availablememory | MB | 10049587
[8 empty] | 10049588 | systeminfo_cpuutilization | systeminfo_cpuutilization | 6818 | systeminfo_cpuutilization | % | 10049588
[8 empty] | 10049594 | systeminfo_diskwriteperformance | systeminfo_diskwriteperformance | 6819 | systeminfo_diskwriteperformance |  | 10049594
[8 empty] | 10049595 | systeminfo_externaldrive_averageerasecount | systeminfo_externaldrive_averageerasecount | 6820 | systeminfo_externaldrive_averageerasecount |  | 10049595
[8 empty] | 10049596 | systeminfo_externaldrive_lifetimepercentage | systeminfo_externaldrive_lifetimepercentage | 6821 | systeminfo_externaldrive_lifetimepercentage | % | 10049596
[8 empty] | 10049598 | systeminfo_externaldrive_poweronhours | systeminfo_externaldrive_poweronhours | 6822 | systeminfo_externaldrive_poweronhours | h | 10049598
[8 empty] | 10049600 | systeminfo_freediskspace | systeminfo_freediskspace | 6823 | systeminfo_freediskspace | MB | 10049600
[8 empty] | 10049601 | systeminfo_internaldrive_averageerasecount | systeminfo_internaldrive_averageerasecount | 6824 | systeminfo_internaldrive_averageerasecount |  | 10049601
[8 empty] | 10049602 | systeminfo_internaldrive_lifetimepercentage | systeminfo_internaldrive_lifetimepercentage | 6825 | systeminfo_internaldrive_lifetimepercentage | % | 10049602
[8 empty] | 10049604 | systeminfo_internaldrive_poweronhours | systeminfo_internaldrive_poweronhours | 6826 | systeminfo_internaldrive_poweronhours | h | 10049604
[8 empty] | 10049606 | systeminfo_systemuptime | systeminfo_systemuptime | 6827 | systeminfo_systemuptime | h | 10049606
[8 empty] | 10049291 | t_ch_t1hp_a | T11 A | 6828 | t_ch_t1hp_a | °C | 10049291
[8 empty] | 10049292 | t_ch_t1hp_b | T11 B | 6829 | t_ch_t1hp_b | °C | 10049292
[8 empty] | 10049293 | t_egahptc_a | t_egahptc_a | 6830 | t_egahptc_a | °C | 10049293
[8 empty] | 10049294 | t_egahptc_b | t_egahptc_b | 6831 | t_egahptc_b | °C | 10049294
[8 empty] | 10049295 | t_egbhptc_a | t_egbhptc_a | 6832 | t_egbhptc_a | °C | 10049295
[8 empty] | 10049296 | t_egbhptc_b | t_egbhptc_b | 6833 | t_egbhptc_b | °C | 10049296
[8 empty] | 10049831 | TC_SurgeEvents | TC_SurgeEvents | 6834 | TC_SurgeEvents |  | 10049831
[8 empty] | 16572 | TecJet_GasDiffPress | TJ Gas DP | 6835 | TecJet_GasDiffPress | mbar | 16572
[8 empty] | 16573 | TecJet_GasDiffPress2 | TecJet_GasDiffPress2 | 6836 | TecJet_GasDiffPress2 | mbar | 16573
[8 empty] | 19245 | TecJet_GasDiffPress3 | TecJet_GasDiffPress3 | 6837 | TecJet_GasDiffPress3 | mbar | 19245
[8 empty] | 19246 | TecJet_GasDiffPress4 | TecJet_GasDiffPress4 | 6838 | TecJet_GasDiffPress4 | mbar | 19246
[8 empty] | 16574 | TecJet_GasFlow1 | TJ Gas Flow | 6839 | TecJet_GasFlow1 |  | 16574
[8 empty] | 16617 | TecJet_GasFlow2 | TecJet_GasFlow2 | 6840 | TecJet_GasFlow2 |  | 16617
[8 empty] | 19247 | TecJet_GasFlow3 | TecJet_GasFlow3 | 6841 | TecJet_GasFlow3 |  | 19247
[8 empty] | 19248 | TecJet_GasFlow4 | TecJet_GasFlow4 | 6842 | TecJet_GasFlow4 |  | 19248
[8 empty] | 16575 | TecJet_GasPress1 | TJ Gas P | 6843 | TecJet_GasPress1 | mbar | 16575
[8 empty] | 16576 | TecJet_GasPress2 | TecJet_GasPress2 | 6844 | TecJet_GasPress2 | mbar | 16576
[8 empty] | 19249 | TecJet_GasPress3 | TecJet_GasPress3 | 6845 | TecJet_GasPress3 | mbar | 19249
[8 empty] | 19250 | TecJet_GasPress4 | TecJet_GasPress4 | 6846 | TecJet_GasPress4 | mbar | 19250
[8 empty] | 16577 | TecJet_GasTemp1 | TJ Gas T | 6847 | TecJet_GasTemp1 | °C | 16577
[8 empty] | 16588 | TecJet_GasTemp2 | TecJet_GasTemp2 | 6848 | TecJet_GasTemp2 | °C | 16588
[8 empty] | 19251 | TecJet_GasTemp3 | TecJet_GasTemp3 | 6849 | TecJet_GasTemp3 | °C | 19251
[8 empty] | 19252 | TecJet_GasTemp4 | TecJet_GasTemp4 | 6850 | TecJet_GasTemp4 | °C | 19252
[8 empty] | 89 | TecJet_Lambda1 | LambdaTJ | 6851 | TecJet_Lambda1 | a/f | 89
[8 empty] | 16578 | TecJet_Lambda2 | TecJet_Lambda2 | 6852 | TecJet_Lambda2 | a/f | 16578
[8 empty] | 16579 | TecJet_Lambda3 | TecJet_Lambda3 | 6853 | TecJet_Lambda3 | a/f | 16579
[8 empty] | 16580 | TecJet_Lambda4 | TecJet_Lambda4 | 6854 | TecJet_Lambda4 | a/f | 16580
[8 empty] | 16581 | TecJet_ValvePos1 | TJ pos | 6855 | TecJet_ValvePos1 | % | 16581
[8 empty] | 16618 | TecJet_ValvePos2 | TecJet_ValvePos2 | 6856 | TecJet_ValvePos2 | % | 16618
[8 empty] | 19253 | TecJet_ValvePos3 | TecJet_ValvePos3 | 6857 | TecJet_ValvePos3 | % | 19253
[8 empty] | 19254 | TecJet_ValvePos4 | TecJet_ValvePos4 | 6858 | TecJet_ValvePos4 | % | 19254
[8 empty] | 10049827 | thermalreactor_bpos_thr_val_mid | thermalreactor_bpos_thr_val_mid | 6859 | thermalreactor_bpos_thr_val_mid |  | 10049827
[8 empty] | 10049828 | thermalreactor_icnt_ophours_reactor | thermalreactor_icnt_ophours_reactor | 6860 | thermalreactor_icnt_ophours_reactor | h | 10049828
[8 empty] | 10049826 | thermalreactor_rt_thr_chamber | thermalreactor_rt_thr_chamber | 6861 | thermalreactor_rt_thr_chamber | °C | 10049826
[8 empty] | 1040084 | turbocharger_post_cooling_detection | turbocharger_post_cooling_detection | 6862 | turbocharger_post_cooling_detection | count | 1040084
[8 empty] | 1040170 | turbocharger_post_cooling_detection_lpa | turbocharger_post_cooling_detection_lpa | 6863 | turbocharger_post_cooling_detection_lpa | count | 1040170
[8 empty] | 1040171 | turbocharger_post_cooling_detection_lpb | turbocharger_post_cooling_detection_lpb | 6864 | turbocharger_post_cooling_detection_lpb | count | 1040171
[8 empty] | 1040172 | turbocharger_post_cooling_v2_cumulative_counter | turbocharger_post_cooling_v2_cumulative_counter | 6865 | turbocharger_post_cooling_v2_cumulative_counter | count | 1040172
[8 empty] | 1040058 | valverecession_cyl01_deltaOphSinceInit | valverecession_cyl01_deltaOphSinceInit | 6866 | valverecession_cyl01_deltaOphSinceInit | oph | 1040058
[8 empty] | 10049003 | valverecession_cyl01_new_cyl_head | valverecession_cyl01_new_cyl_head | 6867 | valverecession_cyl01_new_cyl_head |  | 10049003
[8 empty] | 1040059 | valverecession_cyl02_deltaOphSinceInit | valverecession_cyl02_deltaOphSinceInit | 6868 | valverecession_cyl02_deltaOphSinceInit | oph | 1040059
[8 empty] | 10049004 | valverecession_cyl02_new_cyl_head | valverecession_cyl02_new_cyl_head | 6869 | valverecession_cyl02_new_cyl_head |  | 10049004
[8 empty] | 1040060 | valverecession_cyl03_deltaOphSinceInit | valverecession_cyl03_deltaOphSinceInit | 6870 | valverecession_cyl03_deltaOphSinceInit | oph | 1040060
[8 empty] | 10049005 | valverecession_cyl03_new_cyl_head | valverecession_cyl03_new_cyl_head | 6871 | valverecession_cyl03_new_cyl_head |  | 10049005
[8 empty] | 1040061 | valverecession_cyl04_deltaOphSinceInit | valverecession_cyl04_deltaOphSinceInit | 6872 | valverecession_cyl04_deltaOphSinceInit | oph | 1040061
[8 empty] | 10049006 | valverecession_cyl04_new_cyl_head | valverecession_cyl04_new_cyl_head | 6873 | valverecession_cyl04_new_cyl_head |  | 10049006
[8 empty] | 1040062 | valverecession_cyl05_deltaOphSinceInit | valverecession_cyl05_deltaOphSinceInit | 6874 | valverecession_cyl05_deltaOphSinceInit | oph | 1040062
[8 empty] | 10049007 | valverecession_cyl05_new_cyl_head | valverecession_cyl05_new_cyl_head | 6875 | valverecession_cyl05_new_cyl_head |  | 10049007
[8 empty] | 1040063 | valverecession_cyl06_deltaOphSinceInit | valverecession_cyl06_deltaOphSinceInit | 6876 | valverecession_cyl06_deltaOphSinceInit | oph | 1040063
[8 empty] | 10049008 | valverecession_cyl06_new_cyl_head | valverecession_cyl06_new_cyl_head | 6877 | valverecession_cyl06_new_cyl_head |  | 10049008
[8 empty] | 1040064 | valverecession_cyl07_deltaOphSinceInit | valverecession_cyl07_deltaOphSinceInit | 6878 | valverecession_cyl07_deltaOphSinceInit | oph | 1040064
[8 empty] | 10049009 | valverecession_cyl07_new_cyl_head | valverecession_cyl07_new_cyl_head | 6879 | valverecession_cyl07_new_cyl_head |  | 10049009
[8 empty] | 1040065 | valverecession_cyl08_deltaOphSinceInit | valverecession_cyl08_deltaOphSinceInit | 6880 | valverecession_cyl08_deltaOphSinceInit | oph | 1040065
[8 empty] | 10049010 | valverecession_cyl08_new_cyl_head | valverecession_cyl08_new_cyl_head | 6881 | valverecession_cyl08_new_cyl_head |  | 10049010
[8 empty] | 1040066 | valverecession_cyl09_deltaOphSinceInit | valverecession_cyl09_deltaOphSinceInit | 6882 | valverecession_cyl09_deltaOphSinceInit | oph | 1040066
[8 empty] | 10049011 | valverecession_cyl09_new_cyl_head | valverecession_cyl09_new_cyl_head | 6883 | valverecession_cyl09_new_cyl_head |  | 10049011
[8 empty] | 1040067 | valverecession_cyl10_deltaOphSinceInit | valverecession_cyl10_deltaOphSinceInit | 6884 | valverecession_cyl10_deltaOphSinceInit | oph | 1040067
[8 empty] | 10049012 | valverecession_cyl10_new_cyl_head | valverecession_cyl10_new_cyl_head | 6885 | valverecession_cyl10_new_cyl_head |  | 10049012
[8 empty] | 1040068 | valverecession_cyl11_deltaOphSinceInit | valverecession_cyl11_deltaOphSinceInit | 6886 | valverecession_cyl11_deltaOphSinceInit | oph | 1040068
[8 empty] | 10049013 | valverecession_cyl11_new_cyl_head | valverecession_cyl11_new_cyl_head | 6887 | valverecession_cyl11_new_cyl_head |  | 10049013
[8 empty] | 1040069 | valverecession_cyl12_deltaOphSinceInit | valverecession_cyl12_deltaOphSinceInit | 6888 | valverecession_cyl12_deltaOphSinceInit | oph | 1040069
[8 empty] | 10049014 | valverecession_cyl12_new_cyl_head | valverecession_cyl12_new_cyl_head | 6889 | valverecession_cyl12_new_cyl_head |  | 10049014
[8 empty] | 1040070 | valverecession_cyl13_deltaOphSinceInit | valverecession_cyl13_deltaOphSinceInit | 6890 | valverecession_cyl13_deltaOphSinceInit | oph | 1040070
[8 empty] | 10049015 | valverecession_cyl13_new_cyl_head | valverecession_cyl13_new_cyl_head | 6891 | valverecession_cyl13_new_cyl_head |  | 10049015
[8 empty] | 1040071 | valverecession_cyl14_deltaOphSinceInit | valverecession_cyl14_deltaOphSinceInit | 6892 | valverecession_cyl14_deltaOphSinceInit | oph | 1040071
[8 empty] | 10049016 | valverecession_cyl14_new_cyl_head | valverecession_cyl14_new_cyl_head | 6893 | valverecession_cyl14_new_cyl_head |  | 10049016
[8 empty] | 1040072 | valverecession_cyl15_deltaOphSinceInit | valverecession_cyl15_deltaOphSinceInit | 6894 | valverecession_cyl15_deltaOphSinceInit | oph | 1040072
[8 empty] | 10049017 | valverecession_cyl15_new_cyl_head | valverecession_cyl15_new_cyl_head | 6895 | valverecession_cyl15_new_cyl_head |  | 10049017
[8 empty] | 1040073 | valverecession_cyl16_deltaOphSinceInit | valverecession_cyl16_deltaOphSinceInit | 6896 | valverecession_cyl16_deltaOphSinceInit | oph | 1040073
[8 empty] | 10049018 | valverecession_cyl16_new_cyl_head | valverecession_cyl16_new_cyl_head | 6897 | valverecession_cyl16_new_cyl_head |  | 10049018
[8 empty] | 1040074 | valverecession_cyl17_deltaOphSinceInit | valverecession_cyl17_deltaOphSinceInit | 6898 | valverecession_cyl17_deltaOphSinceInit | oph | 1040074
[8 empty] | 10049019 | valverecession_cyl17_new_cyl_head | valverecession_cyl17_new_cyl_head | 6899 | valverecession_cyl17_new_cyl_head |  | 10049019
[8 empty] | 1040075 | valverecession_cyl18_deltaOphSinceInit | valverecession_cyl18_deltaOphSinceInit | 6900 | valverecession_cyl18_deltaOphSinceInit | oph | 1040075
[8 empty] | 10049020 | valverecession_cyl18_new_cyl_head | valverecession_cyl18_new_cyl_head | 6901 | valverecession_cyl18_new_cyl_head |  | 10049020
[8 empty] | 1040076 | valverecession_cyl19_deltaOphSinceInit | valverecession_cyl19_deltaOphSinceInit | 6902 | valverecession_cyl19_deltaOphSinceInit | oph | 1040076
[8 empty] | 10049021 | valverecession_cyl19_new_cyl_head | valverecession_cyl19_new_cyl_head | 6903 | valverecession_cyl19_new_cyl_head |  | 10049021
[8 empty] | 1040077 | valverecession_cyl20_deltaOphSinceInit | valverecession_cyl20_deltaOphSinceInit | 6904 | valverecession_cyl20_deltaOphSinceInit | oph | 1040077
[8 empty] | 10049022 | valverecession_cyl20_new_cyl_head | valverecession_cyl20_new_cyl_head | 6905 | valverecession_cyl20_new_cyl_head |  | 10049022
[8 empty] | 1040078 | valverecession_cyl21_deltaOphSinceInit | valverecession_cyl21_deltaOphSinceInit | 6906 | valverecession_cyl21_deltaOphSinceInit | oph | 1040078
[8 empty] | 10049023 | valverecession_cyl21_new_cyl_head | valverecession_cyl21_new_cyl_head | 6907 | valverecession_cyl21_new_cyl_head |  | 10049023
[8 empty] | 1040079 | valverecession_cyl22_deltaOphSinceInit | valverecession_cyl22_deltaOphSinceInit | 6908 | valverecession_cyl22_deltaOphSinceInit | oph | 1040079
[8 empty] | 10049024 | valverecession_cyl22_new_cyl_head | valverecession_cyl22_new_cyl_head | 6909 | valverecession_cyl22_new_cyl_head |  | 10049024
[8 empty] | 1040080 | valverecession_cyl23_deltaOphSinceInit | valverecession_cyl23_deltaOphSinceInit | 6910 | valverecession_cyl23_deltaOphSinceInit | oph | 1040080
[8 empty] | 10049025 | valverecession_cyl23_new_cyl_head | valverecession_cyl23_new_cyl_head | 6911 | valverecession_cyl23_new_cyl_head |  | 10049025
[8 empty] | 1040081 | valverecession_cyl24_deltaOphSinceInit | valverecession_cyl24_deltaOphSinceInit | 6912 | valverecession_cyl24_deltaOphSinceInit | oph | 1040081
[8 empty] | 10049026 | valverecession_cyl24_new_cyl_head | valverecession_cyl24_new_cyl_head | 6913 | valverecession_cyl24_new_cyl_head |  | 10049026
[8 empty] | 1039962 | valverecession_lev_cyl01_deltaVRSinceInit | valverecession_lev_cyl01_deltaVRSinceInit | 6914 | valverecession_lev_cyl01_deltaVRSinceInit | mm | 1039962
[8 empty] | 1039866 | valverecession_lev_cyl01_init | valverecession_lev_cyl01_init | 6915 | valverecession_lev_cyl01_init | mm | 1039866
[8 empty] | 1039963 | valverecession_lev_cyl02_deltaVRSinceInit | valverecession_lev_cyl02_deltaVRSinceInit | 6916 | valverecession_lev_cyl02_deltaVRSinceInit | mm | 1039963
[8 empty] | 1039867 | valverecession_lev_cyl02_init | valverecession_lev_cyl02_init | 6917 | valverecession_lev_cyl02_init | mm | 1039867
[8 empty] | 1039964 | valverecession_lev_cyl03_deltaVRSinceInit | valverecession_lev_cyl03_deltaVRSinceInit | 6918 | valverecession_lev_cyl03_deltaVRSinceInit | mm | 1039964
[8 empty] | 1039868 | valverecession_lev_cyl03_init | valverecession_lev_cyl03_init | 6919 | valverecession_lev_cyl03_init | mm | 1039868
[8 empty] | 1039965 | valverecession_lev_cyl04_deltaVRSinceInit | valverecession_lev_cyl04_deltaVRSinceInit | 6920 | valverecession_lev_cyl04_deltaVRSinceInit | mm | 1039965
[8 empty] | 1039869 | valverecession_lev_cyl04_init | valverecession_lev_cyl04_init | 6921 | valverecession_lev_cyl04_init | mm | 1039869
[8 empty] | 1039966 | valverecession_lev_cyl05_deltaVRSinceInit | valverecession_lev_cyl05_deltaVRSinceInit | 6922 | valverecession_lev_cyl05_deltaVRSinceInit | mm | 1039966
[8 empty] | 1039870 | valverecession_lev_cyl05_init | valverecession_lev_cyl05_init | 6923 | valverecession_lev_cyl05_init | mm | 1039870
[8 empty] | 1039967 | valverecession_lev_cyl06_deltaVRSinceInit | valverecession_lev_cyl06_deltaVRSinceInit | 6924 | valverecession_lev_cyl06_deltaVRSinceInit | mm | 1039967
[8 empty] | 1039871 | valverecession_lev_cyl06_init | valverecession_lev_cyl06_init | 6925 | valverecession_lev_cyl06_init | mm | 1039871
[8 empty] | 1039968 | valverecession_lev_cyl07_deltaVRSinceInit | valverecession_lev_cyl07_deltaVRSinceInit | 6926 | valverecession_lev_cyl07_deltaVRSinceInit | mm | 1039968
[8 empty] | 1039872 | valverecession_lev_cyl07_init | valverecession_lev_cyl07_init | 6927 | valverecession_lev_cyl07_init | mm | 1039872
[8 empty] | 1039969 | valverecession_lev_cyl08_deltaVRSinceInit | valverecession_lev_cyl08_deltaVRSinceInit | 6928 | valverecession_lev_cyl08_deltaVRSinceInit | mm | 1039969
[8 empty] | 1039873 | valverecession_lev_cyl08_init | valverecession_lev_cyl08_init | 6929 | valverecession_lev_cyl08_init | mm | 1039873
[8 empty] | 1039970 | valverecession_lev_cyl09_deltaVRSinceInit | valverecession_lev_cyl09_deltaVRSinceInit | 6930 | valverecession_lev_cyl09_deltaVRSinceInit | mm | 1039970
[8 empty] | 1039874 | valverecession_lev_cyl09_init | valverecession_lev_cyl09_init | 6931 | valverecession_lev_cyl09_init | mm | 1039874
[8 empty] | 1039971 | valverecession_lev_cyl10_deltaVRSinceInit | valverecession_lev_cyl10_deltaVRSinceInit | 6932 | valverecession_lev_cyl10_deltaVRSinceInit | mm | 1039971
[8 empty] | 1039875 | valverecession_lev_cyl10_init | valverecession_lev_cyl10_init | 6933 | valverecession_lev_cyl10_init | mm | 1039875
[8 empty] | 1039972 | valverecession_lev_cyl11_deltaVRSinceInit | valverecession_lev_cyl11_deltaVRSinceInit | 6934 | valverecession_lev_cyl11_deltaVRSinceInit | mm | 1039972
[8 empty] | 1039876 | valverecession_lev_cyl11_init | valverecession_lev_cyl11_init | 6935 | valverecession_lev_cyl11_init | mm | 1039876
[8 empty] | 1039973 | valverecession_lev_cyl12_deltaVRSinceInit | valverecession_lev_cyl12_deltaVRSinceInit | 6936 | valverecession_lev_cyl12_deltaVRSinceInit | mm | 1039973
[8 empty] | 1039877 | valverecession_lev_cyl12_init | valverecession_lev_cyl12_init | 6937 | valverecession_lev_cyl12_init | mm | 1039877
[8 empty] | 1039974 | valverecession_lev_cyl13_deltaVRSinceInit | valverecession_lev_cyl13_deltaVRSinceInit | 6938 | valverecession_lev_cyl13_deltaVRSinceInit | mm | 1039974
[8 empty] | 1039878 | valverecession_lev_cyl13_init | valverecession_lev_cyl13_init | 6939 | valverecession_lev_cyl13_init | mm | 1039878
[8 empty] | 1039975 | valverecession_lev_cyl14_deltaVRSinceInit | valverecession_lev_cyl14_deltaVRSinceInit | 6940 | valverecession_lev_cyl14_deltaVRSinceInit | mm | 1039975
[8 empty] | 1039879 | valverecession_lev_cyl14_init | valverecession_lev_cyl14_init | 6941 | valverecession_lev_cyl14_init | mm | 1039879
[8 empty] | 1039976 | valverecession_lev_cyl15_deltaVRSinceInit | valverecession_lev_cyl15_deltaVRSinceInit | 6942 | valverecession_lev_cyl15_deltaVRSinceInit | mm | 1039976
[8 empty] | 1039880 | valverecession_lev_cyl15_init | valverecession_lev_cyl15_init | 6943 | valverecession_lev_cyl15_init | mm | 1039880
[8 empty] | 1039977 | valverecession_lev_cyl16_deltaVRSinceInit | valverecession_lev_cyl16_deltaVRSinceInit | 6944 | valverecession_lev_cyl16_deltaVRSinceInit | mm | 1039977
[8 empty] | 1039881 | valverecession_lev_cyl16_init | valverecession_lev_cyl16_init | 6945 | valverecession_lev_cyl16_init | mm | 1039881
[8 empty] | 1039978 | valverecession_lev_cyl17_deltaVRSinceInit | valverecession_lev_cyl17_deltaVRSinceInit | 6946 | valverecession_lev_cyl17_deltaVRSinceInit | mm | 1039978
[8 empty] | 1039882 | valverecession_lev_cyl17_init | valverecession_lev_cyl17_init | 6947 | valverecession_lev_cyl17_init | mm | 1039882
[8 empty] | 1039979 | valverecession_lev_cyl18_deltaVRSinceInit | valverecession_lev_cyl18_deltaVRSinceInit | 6948 | valverecession_lev_cyl18_deltaVRSinceInit | mm | 1039979
[8 empty] | 1039883 | valverecession_lev_cyl18_init | valverecession_lev_cyl18_init | 6949 | valverecession_lev_cyl18_init | mm | 1039883
[8 empty] | 1039980 | valverecession_lev_cyl19_deltaVRSinceInit | valverecession_lev_cyl19_deltaVRSinceInit | 6950 | valverecession_lev_cyl19_deltaVRSinceInit | mm | 1039980
[8 empty] | 1039884 | valverecession_lev_cyl19_init | valverecession_lev_cyl19_init | 6951 | valverecession_lev_cyl19_init | mm | 1039884
[8 empty] | 1039981 | valverecession_lev_cyl20_deltaVRSinceInit | valverecession_lev_cyl20_deltaVRSinceInit | 6952 | valverecession_lev_cyl20_deltaVRSinceInit | mm | 1039981
[8 empty] | 1039885 | valverecession_lev_cyl20_init | valverecession_lev_cyl20_init | 6953 | valverecession_lev_cyl20_init | mm | 1039885
[8 empty] | 1039982 | valverecession_lev_cyl21_deltaVRSinceInit | valverecession_lev_cyl21_deltaVRSinceInit | 6954 | valverecession_lev_cyl21_deltaVRSinceInit | mm | 1039982
[8 empty] | 1039886 | valverecession_lev_cyl21_init | valverecession_lev_cyl21_init | 6955 | valverecession_lev_cyl21_init | mm | 1039886
[8 empty] | 1039983 | valverecession_lev_cyl22_deltaVRSinceInit | valverecession_lev_cyl22_deltaVRSinceInit | 6956 | valverecession_lev_cyl22_deltaVRSinceInit | mm | 1039983
[8 empty] | 1039887 | valverecession_lev_cyl22_init | valverecession_lev_cyl22_init | 6957 | valverecession_lev_cyl22_init | mm | 1039887
[8 empty] | 1039984 | valverecession_lev_cyl23_deltaVRSinceInit | valverecession_lev_cyl23_deltaVRSinceInit | 6958 | valverecession_lev_cyl23_deltaVRSinceInit | mm | 1039984
[8 empty] | 1039888 | valverecession_lev_cyl23_init | valverecession_lev_cyl23_init | 6959 | valverecession_lev_cyl23_init | mm | 1039888
[8 empty] | 1039985 | valverecession_lev_cyl24_deltaVRSinceInit | valverecession_lev_cyl24_deltaVRSinceInit | 6960 | valverecession_lev_cyl24_deltaVRSinceInit | mm | 1039985
[8 empty] | 1039889 | valverecession_lev_cyl24_init | valverecession_lev_cyl24_init | 6961 | valverecession_lev_cyl24_init | mm | 1039889
[8 empty] | 1039986 | valverecession_liv_cyl01_deltaVRSinceInit | valverecession_liv_cyl01_deltaVRSinceInit | 6962 | valverecession_liv_cyl01_deltaVRSinceInit | mm | 1039986
[8 empty] | 1039890 | valverecession_liv_cyl01_init | valverecession_liv_cyl01_init | 6963 | valverecession_liv_cyl01_init | mm | 1039890
[8 empty] | 1039987 | valverecession_liv_cyl02_deltaVRSinceInit | valverecession_liv_cyl02_deltaVRSinceInit | 6964 | valverecession_liv_cyl02_deltaVRSinceInit | mm | 1039987
[8 empty] | 1039891 | valverecession_liv_cyl02_init | valverecession_liv_cyl02_init | 6965 | valverecession_liv_cyl02_init | mm | 1039891
[8 empty] | 1039988 | valverecession_liv_cyl03_deltaVRSinceInit | valverecession_liv_cyl03_deltaVRSinceInit | 6966 | valverecession_liv_cyl03_deltaVRSinceInit | mm | 1039988
[8 empty] | 1039892 | valverecession_liv_cyl03_init | valverecession_liv_cyl03_init | 6967 | valverecession_liv_cyl03_init | mm | 1039892
[8 empty] | 1039989 | valverecession_liv_cyl04_deltaVRSinceInit | valverecession_liv_cyl04_deltaVRSinceInit | 6968 | valverecession_liv_cyl04_deltaVRSinceInit | mm | 1039989
[8 empty] | 1039893 | valverecession_liv_cyl04_init | valverecession_liv_cyl04_init | 6969 | valverecession_liv_cyl04_init | mm | 1039893
[8 empty] | 1039990 | valverecession_liv_cyl05_deltaVRSinceInit | valverecession_liv_cyl05_deltaVRSinceInit | 6970 | valverecession_liv_cyl05_deltaVRSinceInit | mm | 1039990
[8 empty] | 1039894 | valverecession_liv_cyl05_init | valverecession_liv_cyl05_init | 6971 | valverecession_liv_cyl05_init | mm | 1039894
[8 empty] | 1039991 | valverecession_liv_cyl06_deltaVRSinceInit | valverecession_liv_cyl06_deltaVRSinceInit | 6972 | valverecession_liv_cyl06_deltaVRSinceInit | mm | 1039991
[8 empty] | 1039895 | valverecession_liv_cyl06_init | valverecession_liv_cyl06_init | 6973 | valverecession_liv_cyl06_init | mm | 1039895
[8 empty] | 1039992 | valverecession_liv_cyl07_deltaVRSinceInit | valverecession_liv_cyl07_deltaVRSinceInit | 6974 | valverecession_liv_cyl07_deltaVRSinceInit | mm | 1039992
[8 empty] | 1039896 | valverecession_liv_cyl07_init | valverecession_liv_cyl07_init | 6975 | valverecession_liv_cyl07_init | mm | 1039896
[8 empty] | 1039993 | valverecession_liv_cyl08_deltaVRSinceInit | valverecession_liv_cyl08_deltaVRSinceInit | 6976 | valverecession_liv_cyl08_deltaVRSinceInit | mm | 1039993
[8 empty] | 1039897 | valverecession_liv_cyl08_init | valverecession_liv_cyl08_init | 6977 | valverecession_liv_cyl08_init | mm | 1039897
[8 empty] | 1039994 | valverecession_liv_cyl09_deltaVRSinceInit | valverecession_liv_cyl09_deltaVRSinceInit | 6978 | valverecession_liv_cyl09_deltaVRSinceInit | mm | 1039994
[8 empty] | 1039898 | valverecession_liv_cyl09_init | valverecession_liv_cyl09_init | 6979 | valverecession_liv_cyl09_init | mm | 1039898
[8 empty] | 1039995 | valverecession_liv_cyl10_deltaVRSinceInit | valverecession_liv_cyl10_deltaVRSinceInit | 6980 | valverecession_liv_cyl10_deltaVRSinceInit | mm | 1039995
[8 empty] | 1039899 | valverecession_liv_cyl10_init | valverecession_liv_cyl10_init | 6981 | valverecession_liv_cyl10_init | mm | 1039899
[8 empty] | 1039996 | valverecession_liv_cyl11_deltaVRSinceInit | valverecession_liv_cyl11_deltaVRSinceInit | 6982 | valverecession_liv_cyl11_deltaVRSinceInit | mm | 1039996
[8 empty] | 1039900 | valverecession_liv_cyl11_init | valverecession_liv_cyl11_init | 6983 | valverecession_liv_cyl11_init | mm | 1039900
[8 empty] | 1039997 | valverecession_liv_cyl12_deltaVRSinceInit | valverecession_liv_cyl12_deltaVRSinceInit | 6984 | valverecession_liv_cyl12_deltaVRSinceInit | mm | 1039997
[8 empty] | 1039901 | valverecession_liv_cyl12_init | valverecession_liv_cyl12_init | 6985 | valverecession_liv_cyl12_init | mm | 1039901
[8 empty] | 1039998 | valverecession_liv_cyl13_deltaVRSinceInit | valverecession_liv_cyl13_deltaVRSinceInit | 6986 | valverecession_liv_cyl13_deltaVRSinceInit | mm | 1039998
[8 empty] | 1039902 | valverecession_liv_cyl13_init | valverecession_liv_cyl13_init | 6987 | valverecession_liv_cyl13_init | mm | 1039902
[8 empty] | 1039999 | valverecession_liv_cyl14_deltaVRSinceInit | valverecession_liv_cyl14_deltaVRSinceInit | 6988 | valverecession_liv_cyl14_deltaVRSinceInit | mm | 1039999
[8 empty] | 1039903 | valverecession_liv_cyl14_init | valverecession_liv_cyl14_init | 6989 | valverecession_liv_cyl14_init | mm | 1039903
[8 empty] | 1040000 | valverecession_liv_cyl15_deltaVRSinceInit | valverecession_liv_cyl15_deltaVRSinceInit | 6990 | valverecession_liv_cyl15_deltaVRSinceInit | mm | 1040000
[8 empty] | 1039904 | valverecession_liv_cyl15_init | valverecession_liv_cyl15_init | 6991 | valverecession_liv_cyl15_init | mm | 1039904
[8 empty] | 1040001 | valverecession_liv_cyl16_deltaVRSinceInit | valverecession_liv_cyl16_deltaVRSinceInit | 6992 | valverecession_liv_cyl16_deltaVRSinceInit | mm | 1040001
[8 empty] | 1039905 | valverecession_liv_cyl16_init | valverecession_liv_cyl16_init | 6993 | valverecession_liv_cyl16_init | mm | 1039905
[8 empty] | 1040002 | valverecession_liv_cyl17_deltaVRSinceInit | valverecession_liv_cyl17_deltaVRSinceInit | 6994 | valverecession_liv_cyl17_deltaVRSinceInit | mm | 1040002
[8 empty] | 1039906 | valverecession_liv_cyl17_init | valverecession_liv_cyl17_init | 6995 | valverecession_liv_cyl17_init | mm | 1039906
[8 empty] | 1040003 | valverecession_liv_cyl18_deltaVRSinceInit | valverecession_liv_cyl18_deltaVRSinceInit | 6996 | valverecession_liv_cyl18_deltaVRSinceInit | mm | 1040003
[8 empty] | 1039907 | valverecession_liv_cyl18_init | valverecession_liv_cyl18_init | 6997 | valverecession_liv_cyl18_init | mm | 1039907
[8 empty] | 1040004 | valverecession_liv_cyl19_deltaVRSinceInit | valverecession_liv_cyl19_deltaVRSinceInit | 6998 | valverecession_liv_cyl19_deltaVRSinceInit | mm | 1040004
[8 empty] | 1039908 | valverecession_liv_cyl19_init | valverecession_liv_cyl19_init | 6999 | valverecession_liv_cyl19_init | mm | 1039908
[8 empty] | 1040005 | valverecession_liv_cyl20_deltaVRSinceInit | valverecession_liv_cyl20_deltaVRSinceInit | 7000 | valverecession_liv_cyl20_deltaVRSinceInit | mm | 1040005
[8 empty] | 1039909 | valverecession_liv_cyl20_init | valverecession_liv_cyl20_init | 7001 | valverecession_liv_cyl20_init | mm | 1039909
[8 empty] | 1040006 | valverecession_liv_cyl21_deltaVRSinceInit | valverecession_liv_cyl21_deltaVRSinceInit | 7002 | valverecession_liv_cyl21_deltaVRSinceInit | mm | 1040006
[8 empty] | 1039910 | valverecession_liv_cyl21_init | valverecession_liv_cyl21_init | 7003 | valverecession_liv_cyl21_init | mm | 1039910
[8 empty] | 1040007 | valverecession_liv_cyl22_deltaVRSinceInit | valverecession_liv_cyl22_deltaVRSinceInit | 7004 | valverecession_liv_cyl22_deltaVRSinceInit | mm | 1040007
[8 empty] | 1039911 | valverecession_liv_cyl22_init | valverecession_liv_cyl22_init | 7005 | valverecession_liv_cyl22_init | mm | 1039911
[8 empty] | 1040008 | valverecession_liv_cyl23_deltaVRSinceInit | valverecession_liv_cyl23_deltaVRSinceInit | 7006 | valverecession_liv_cyl23_deltaVRSinceInit | mm | 1040008
[8 empty] | 1039912 | valverecession_liv_cyl23_init | valverecession_liv_cyl23_init | 7007 | valverecession_liv_cyl23_init | mm | 1039912
[8 empty] | 1040009 | valverecession_liv_cyl24_deltaVRSinceInit | valverecession_liv_cyl24_deltaVRSinceInit | 7008 | valverecession_liv_cyl24_deltaVRSinceInit | mm | 1040009
[8 empty] | 1039913 | valverecession_liv_cyl24_init | valverecession_liv_cyl24_init | 7009 | valverecession_liv_cyl24_init | mm | 1039913
[8 empty] | 1040010 | valverecession_rev_cyl01_deltaVRSinceInit | valverecession_rev_cyl01_deltaVRSinceInit | 7010 | valverecession_rev_cyl01_deltaVRSinceInit | mm | 1040010
[8 empty] | 1039914 | valverecession_rev_cyl01_init | valverecession_rev_cyl01_init | 7011 | valverecession_rev_cyl01_init | mm | 1039914
[8 empty] | 1040011 | valverecession_rev_cyl02_deltaVRSinceInit | valverecession_rev_cyl02_deltaVRSinceInit | 7012 | valverecession_rev_cyl02_deltaVRSinceInit | mm | 1040011
[8 empty] | 1039915 | valverecession_rev_cyl02_init | valverecession_rev_cyl02_init | 7013 | valverecession_rev_cyl02_init | mm | 1039915
[8 empty] | 1040012 | valverecession_rev_cyl03_deltaVRSinceInit | valverecession_rev_cyl03_deltaVRSinceInit | 7014 | valverecession_rev_cyl03_deltaVRSinceInit | mm | 1040012
[8 empty] | 1039916 | valverecession_rev_cyl03_init | valverecession_rev_cyl03_init | 7015 | valverecession_rev_cyl03_init | mm | 1039916
[8 empty] | 1040013 | valverecession_rev_cyl04_deltaVRSinceInit | valverecession_rev_cyl04_deltaVRSinceInit | 7016 | valverecession_rev_cyl04_deltaVRSinceInit | mm | 1040013
[8 empty] | 1039917 | valverecession_rev_cyl04_init | valverecession_rev_cyl04_init | 7017 | valverecession_rev_cyl04_init | mm | 1039917
[8 empty] | 1040014 | valverecession_rev_cyl05_deltaVRSinceInit | valverecession_rev_cyl05_deltaVRSinceInit | 7018 | valverecession_rev_cyl05_deltaVRSinceInit | mm | 1040014
[8 empty] | 1039918 | valverecession_rev_cyl05_init | valverecession_rev_cyl05_init | 7019 | valverecession_rev_cyl05_init | mm | 1039918
[8 empty] | 1040015 | valverecession_rev_cyl06_deltaVRSinceInit | valverecession_rev_cyl06_deltaVRSinceInit | 7020 | valverecession_rev_cyl06_deltaVRSinceInit | mm | 1040015
[8 empty] | 1039919 | valverecession_rev_cyl06_init | valverecession_rev_cyl06_init | 7021 | valverecession_rev_cyl06_init | mm | 1039919
[8 empty] | 1040016 | valverecession_rev_cyl07_deltaVRSinceInit | valverecession_rev_cyl07_deltaVRSinceInit | 7022 | valverecession_rev_cyl07_deltaVRSinceInit | mm | 1040016
[8 empty] | 1039920 | valverecession_rev_cyl07_init | valverecession_rev_cyl07_init | 7023 | valverecession_rev_cyl07_init | mm | 1039920
[8 empty] | 1040017 | valverecession_rev_cyl08_deltaVRSinceInit | valverecession_rev_cyl08_deltaVRSinceInit | 7024 | valverecession_rev_cyl08_deltaVRSinceInit | mm | 1040017
[8 empty] | 1039921 | valverecession_rev_cyl08_init | valverecession_rev_cyl08_init | 7025 | valverecession_rev_cyl08_init | mm | 1039921
[8 empty] | 1040018 | valverecession_rev_cyl09_deltaVRSinceInit | valverecession_rev_cyl09_deltaVRSinceInit | 7026 | valverecession_rev_cyl09_deltaVRSinceInit | mm | 1040018
[8 empty] | 1039922 | valverecession_rev_cyl09_init | valverecession_rev_cyl09_init | 7027 | valverecession_rev_cyl09_init | mm | 1039922
[8 empty] | 1040019 | valverecession_rev_cyl10_deltaVRSinceInit | valverecession_rev_cyl10_deltaVRSinceInit | 7028 | valverecession_rev_cyl10_deltaVRSinceInit | mm | 1040019
[8 empty] | 1039923 | valverecession_rev_cyl10_init | valverecession_rev_cyl10_init | 7029 | valverecession_rev_cyl10_init | mm | 1039923
[8 empty] | 1040020 | valverecession_rev_cyl11_deltaVRSinceInit | valverecession_rev_cyl11_deltaVRSinceInit | 7030 | valverecession_rev_cyl11_deltaVRSinceInit | mm | 1040020
[8 empty] | 1039924 | valverecession_rev_cyl11_init | valverecession_rev_cyl11_init | 7031 | valverecession_rev_cyl11_init | mm | 1039924
[8 empty] | 1040021 | valverecession_rev_cyl12_deltaVRSinceInit | valverecession_rev_cyl12_deltaVRSinceInit | 7032 | valverecession_rev_cyl12_deltaVRSinceInit | mm | 1040021
[8 empty] | 1039925 | valverecession_rev_cyl12_init | valverecession_rev_cyl12_init | 7033 | valverecession_rev_cyl12_init | mm | 1039925
[8 empty] | 1040022 | valverecession_rev_cyl13_deltaVRSinceInit | valverecession_rev_cyl13_deltaVRSinceInit | 7034 | valverecession_rev_cyl13_deltaVRSinceInit | mm | 1040022
[8 empty] | 1039926 | valverecession_rev_cyl13_init | valverecession_rev_cyl13_init | 7035 | valverecession_rev_cyl13_init | mm | 1039926
[8 empty] | 1040023 | valverecession_rev_cyl14_deltaVRSinceInit | valverecession_rev_cyl14_deltaVRSinceInit | 7036 | valverecession_rev_cyl14_deltaVRSinceInit | mm | 1040023
[8 empty] | 1039927 | valverecession_rev_cyl14_init | valverecession_rev_cyl14_init | 7037 | valverecession_rev_cyl14_init | mm | 1039927
[8 empty] | 1040024 | valverecession_rev_cyl15_deltaVRSinceInit | valverecession_rev_cyl15_deltaVRSinceInit | 7038 | valverecession_rev_cyl15_deltaVRSinceInit | mm | 1040024
[8 empty] | 1039928 | valverecession_rev_cyl15_init | valverecession_rev_cyl15_init | 7039 | valverecession_rev_cyl15_init | mm | 1039928
[8 empty] | 1040025 | valverecession_rev_cyl16_deltaVRSinceInit | valverecession_rev_cyl16_deltaVRSinceInit | 7040 | valverecession_rev_cyl16_deltaVRSinceInit | mm | 1040025
[8 empty] | 1039929 | valverecession_rev_cyl16_init | valverecession_rev_cyl16_init | 7041 | valverecession_rev_cyl16_init | mm | 1039929
[8 empty] | 1040026 | valverecession_rev_cyl17_deltaVRSinceInit | valverecession_rev_cyl17_deltaVRSinceInit | 7042 | valverecession_rev_cyl17_deltaVRSinceInit | mm | 1040026
[8 empty] | 1039930 | valverecession_rev_cyl17_init | valverecession_rev_cyl17_init | 7043 | valverecession_rev_cyl17_init | mm | 1039930
[8 empty] | 1040027 | valverecession_rev_cyl18_deltaVRSinceInit | valverecession_rev_cyl18_deltaVRSinceInit | 7044 | valverecession_rev_cyl18_deltaVRSinceInit | mm | 1040027
[8 empty] | 1039931 | valverecession_rev_cyl18_init | valverecession_rev_cyl18_init | 7045 | valverecession_rev_cyl18_init | mm | 1039931
[8 empty] | 1040028 | valverecession_rev_cyl19_deltaVRSinceInit | valverecession_rev_cyl19_deltaVRSinceInit | 7046 | valverecession_rev_cyl19_deltaVRSinceInit | mm | 1040028
[8 empty] | 1039932 | valverecession_rev_cyl19_init | valverecession_rev_cyl19_init | 7047 | valverecession_rev_cyl19_init | mm | 1039932
[8 empty] | 1040029 | valverecession_rev_cyl20_deltaVRSinceInit | valverecession_rev_cyl20_deltaVRSinceInit | 7048 | valverecession_rev_cyl20_deltaVRSinceInit | mm | 1040029
[8 empty] | 1039933 | valverecession_rev_cyl20_init | valverecession_rev_cyl20_init | 7049 | valverecession_rev_cyl20_init | mm | 1039933
[8 empty] | 1040030 | valverecession_rev_cyl21_deltaVRSinceInit | valverecession_rev_cyl21_deltaVRSinceInit | 7050 | valverecession_rev_cyl21_deltaVRSinceInit | mm | 1040030
[8 empty] | 1039934 | valverecession_rev_cyl21_init | valverecession_rev_cyl21_init | 7051 | valverecession_rev_cyl21_init | mm | 1039934
[8 empty] | 1040031 | valverecession_rev_cyl22_deltaVRSinceInit | valverecession_rev_cyl22_deltaVRSinceInit | 7052 | valverecession_rev_cyl22_deltaVRSinceInit | mm | 1040031
[8 empty] | 1039935 | valverecession_rev_cyl22_init | valverecession_rev_cyl22_init | 7053 | valverecession_rev_cyl22_init | mm | 1039935
[8 empty] | 1040032 | valverecession_rev_cyl23_deltaVRSinceInit | valverecession_rev_cyl23_deltaVRSinceInit | 7054 | valverecession_rev_cyl23_deltaVRSinceInit | mm | 1040032
[8 empty] | 1039936 | valverecession_rev_cyl23_init | valverecession_rev_cyl23_init | 7055 | valverecession_rev_cyl23_init | mm | 1039936
[8 empty] | 1040033 | valverecession_rev_cyl24_deltaVRSinceInit | valverecession_rev_cyl24_deltaVRSinceInit | 7056 | valverecession_rev_cyl24_deltaVRSinceInit | mm | 1040033
[8 empty] | 1039937 | valverecession_rev_cyl24_init | valverecession_rev_cyl24_init | 7057 | valverecession_rev_cyl24_init | mm | 1039937
[8 empty] | 1040034 | valverecession_riv_cyl01_deltaVRSinceInit | valverecession_riv_cyl01_deltaVRSinceInit | 7058 | valverecession_riv_cyl01_deltaVRSinceInit | mm | 1040034
[8 empty] | 1039938 | valverecession_riv_cyl01_init | valverecession_riv_cyl01_init | 7059 | valverecession_riv_cyl01_init | mm | 1039938
[8 empty] | 1040035 | valverecession_riv_cyl02_deltaVRSinceInit | valverecession_riv_cyl02_deltaVRSinceInit | 7060 | valverecession_riv_cyl02_deltaVRSinceInit | mm | 1040035
[8 empty] | 1039939 | valverecession_riv_cyl02_init | valverecession_riv_cyl02_init | 7061 | valverecession_riv_cyl02_init | mm | 1039939
[8 empty] | 1040036 | valverecession_riv_cyl03_deltaVRSinceInit | valverecession_riv_cyl03_deltaVRSinceInit | 7062 | valverecession_riv_cyl03_deltaVRSinceInit | mm | 1040036
[8 empty] | 1039940 | valverecession_riv_cyl03_init | valverecession_riv_cyl03_init | 7063 | valverecession_riv_cyl03_init | mm | 1039940
[8 empty] | 1040037 | valverecession_riv_cyl04_deltaVRSinceInit | valverecession_riv_cyl04_deltaVRSinceInit | 7064 | valverecession_riv_cyl04_deltaVRSinceInit | mm | 1040037
[8 empty] | 1039941 | valverecession_riv_cyl04_init | valverecession_riv_cyl04_init | 7065 | valverecession_riv_cyl04_init | mm | 1039941
[8 empty] | 1040038 | valverecession_riv_cyl05_deltaVRSinceInit | valverecession_riv_cyl05_deltaVRSinceInit | 7066 | valverecession_riv_cyl05_deltaVRSinceInit | mm | 1040038
[8 empty] | 1039942 | valverecession_riv_cyl05_init | valverecession_riv_cyl05_init | 7067 | valverecession_riv_cyl05_init | mm | 1039942
[8 empty] | 1040039 | valverecession_riv_cyl06_deltaVRSinceInit | valverecession_riv_cyl06_deltaVRSinceInit | 7068 | valverecession_riv_cyl06_deltaVRSinceInit | mm | 1040039
[8 empty] | 1039943 | valverecession_riv_cyl06_init | valverecession_riv_cyl06_init | 7069 | valverecession_riv_cyl06_init | mm | 1039943
[8 empty] | 1040040 | valverecession_riv_cyl07_deltaVRSinceInit | valverecession_riv_cyl07_deltaVRSinceInit | 7070 | valverecession_riv_cyl07_deltaVRSinceInit | mm | 1040040
[8 empty] | 1039944 | valverecession_riv_cyl07_init | valverecession_riv_cyl07_init | 7071 | valverecession_riv_cyl07_init | mm | 1039944
[8 empty] | 1040041 | valverecession_riv_cyl08_deltaVRSinceInit | valverecession_riv_cyl08_deltaVRSinceInit | 7072 | valverecession_riv_cyl08_deltaVRSinceInit | mm | 1040041
[8 empty] | 1039945 | valverecession_riv_cyl08_init | valverecession_riv_cyl08_init | 7073 | valverecession_riv_cyl08_init | mm | 1039945
[8 empty] | 1040042 | valverecession_riv_cyl09_deltaVRSinceInit | valverecession_riv_cyl09_deltaVRSinceInit | 7074 | valverecession_riv_cyl09_deltaVRSinceInit | mm | 1040042
[8 empty] | 1039946 | valverecession_riv_cyl09_init | valverecession_riv_cyl09_init | 7075 | valverecession_riv_cyl09_init | mm | 1039946
[8 empty] | 1040043 | valverecession_riv_cyl10_deltaVRSinceInit | valverecession_riv_cyl10_deltaVRSinceInit | 7076 | valverecession_riv_cyl10_deltaVRSinceInit | mm | 1040043
[8 empty] | 1039947 | valverecession_riv_cyl10_init | valverecession_riv_cyl10_init | 7077 | valverecession_riv_cyl10_init | mm | 1039947
[8 empty] | 1040044 | valverecession_riv_cyl11_deltaVRSinceInit | valverecession_riv_cyl11_deltaVRSinceInit | 7078 | valverecession_riv_cyl11_deltaVRSinceInit | mm | 1040044
[8 empty] | 1039948 | valverecession_riv_cyl11_init | valverecession_riv_cyl11_init | 7079 | valverecession_riv_cyl11_init | mm | 1039948
[8 empty] | 1040045 | valverecession_riv_cyl12_deltaVRSinceInit | valverecession_riv_cyl12_deltaVRSinceInit | 7080 | valverecession_riv_cyl12_deltaVRSinceInit | mm | 1040045
[8 empty] | 1039949 | valverecession_riv_cyl12_init | valverecession_riv_cyl12_init | 7081 | valverecession_riv_cyl12_init | mm | 1039949
[8 empty] | 1040046 | valverecession_riv_cyl13_deltaVRSinceInit | valverecession_riv_cyl13_deltaVRSinceInit | 7082 | valverecession_riv_cyl13_deltaVRSinceInit | mm | 1040046
[8 empty] | 1039950 | valverecession_riv_cyl13_init | valverecession_riv_cyl13_init | 7083 | valverecession_riv_cyl13_init | mm | 1039950
[8 empty] | 1040047 | valverecession_riv_cyl14_deltaVRSinceInit | valverecession_riv_cyl14_deltaVRSinceInit | 7084 | valverecession_riv_cyl14_deltaVRSinceInit | mm | 1040047
[8 empty] | 1039951 | valverecession_riv_cyl14_init | valverecession_riv_cyl14_init | 7085 | valverecession_riv_cyl14_init | mm | 1039951
[8 empty] | 1040048 | valverecession_riv_cyl15_deltaVRSinceInit | valverecession_riv_cyl15_deltaVRSinceInit | 7086 | valverecession_riv_cyl15_deltaVRSinceInit | mm | 1040048
[8 empty] | 1039952 | valverecession_riv_cyl15_init | valverecession_riv_cyl15_init | 7087 | valverecession_riv_cyl15_init | mm | 1039952
[8 empty] | 1040049 | valverecession_riv_cyl16_deltaVRSinceInit | valverecession_riv_cyl16_deltaVRSinceInit | 7088 | valverecession_riv_cyl16_deltaVRSinceInit | mm | 1040049
[8 empty] | 1039953 | valverecession_riv_cyl16_init | valverecession_riv_cyl16_init | 7089 | valverecession_riv_cyl16_init | mm | 1039953
[8 empty] | 1040050 | valverecession_riv_cyl17_deltaVRSinceInit | valverecession_riv_cyl17_deltaVRSinceInit | 7090 | valverecession_riv_cyl17_deltaVRSinceInit | mm | 1040050
[8 empty] | 1039954 | valverecession_riv_cyl17_init | valverecession_riv_cyl17_init | 7091 | valverecession_riv_cyl17_init | mm | 1039954
[8 empty] | 1040051 | valverecession_riv_cyl18_deltaVRSinceInit | valverecession_riv_cyl18_deltaVRSinceInit | 7092 | valverecession_riv_cyl18_deltaVRSinceInit | mm | 1040051
[8 empty] | 1039955 | valverecession_riv_cyl18_init | valverecession_riv_cyl18_init | 7093 | valverecession_riv_cyl18_init | mm | 1039955
[8 empty] | 1040052 | valverecession_riv_cyl19_deltaVRSinceInit | valverecession_riv_cyl19_deltaVRSinceInit | 7094 | valverecession_riv_cyl19_deltaVRSinceInit | mm | 1040052
[8 empty] | 1039956 | valverecession_riv_cyl19_init | valverecession_riv_cyl19_init | 7095 | valverecession_riv_cyl19_init | mm | 1039956
[8 empty] | 1040053 | valverecession_riv_cyl20_deltaVRSinceInit | valverecession_riv_cyl20_deltaVRSinceInit | 7096 | valverecession_riv_cyl20_deltaVRSinceInit | mm | 1040053
[8 empty] | 1039957 | valverecession_riv_cyl20_init | valverecession_riv_cyl20_init | 7097 | valverecession_riv_cyl20_init | mm | 1039957
[8 empty] | 1040054 | valverecession_riv_cyl21_deltaVRSinceInit | valverecession_riv_cyl21_deltaVRSinceInit | 7098 | valverecession_riv_cyl21_deltaVRSinceInit | mm | 1040054
[8 empty] | 1039958 | valverecession_riv_cyl21_init | valverecession_riv_cyl21_init | 7099 | valverecession_riv_cyl21_init | mm | 1039958
[8 empty] | 1040055 | valverecession_riv_cyl22_deltaVRSinceInit | valverecession_riv_cyl22_deltaVRSinceInit | 7100 | valverecession_riv_cyl22_deltaVRSinceInit | mm | 1040055
[8 empty] | 1039959 | valverecession_riv_cyl22_init | valverecession_riv_cyl22_init | 7101 | valverecession_riv_cyl22_init | mm | 1039959
[8 empty] | 1040056 | valverecession_riv_cyl23_deltaVRSinceInit | valverecession_riv_cyl23_deltaVRSinceInit | 7102 | valverecession_riv_cyl23_deltaVRSinceInit | mm | 1040056
[8 empty] | 1039960 | valverecession_riv_cyl23_init | valverecession_riv_cyl23_init | 7103 | valverecession_riv_cyl23_init | mm | 1039960
[8 empty] | 1040057 | valverecession_riv_cyl24_deltaVRSinceInit | valverecession_riv_cyl24_deltaVRSinceInit | 7104 | valverecession_riv_cyl24_deltaVRSinceInit | mm | 1040057
[8 empty] | 1039961 | valverecession_riv_cyl24_init | valverecession_riv_cyl24_init | 7105 | valverecession_riv_cyl24_init | mm | 1039961
[8 empty] | 175 | Various_Bits_ColAlarm | Various_Bits_ColAlarm | 7106 | Various_Bits_ColAlarm |  | 175
[8 empty] | 19074 | Various_Bits_CollAlarm | Alarm ? | 7107 | Various_Bits_CollAlarm |  | 19074
[8 empty] | 16615 | Various_Bits_CollWarning | Wanrning ? | 7108 | Various_Bits_CollWarning |  | 16615
[8 empty] | 183 | Various_Bits_GenSwitchOn | OP Switch on | 7109 | Various_Bits_GenSwitchOn |  | 183
[8 empty] | 180 | Various_Bits_OperationOn | OP on | 7110 | Various_Bits_OperationOn |  | 180
[8 empty] | 998 | Various_EngineStatus | Status No | 7111 | Various_EngineStatus |  | 998
[8 empty] | 19255 | Various_SetValues_SetWasteGate | Various_SetValues_SetWasteGate | 7112 | Various_SetValues_SetWasteGate | % | 19255
[8 empty] | 181 | Various_Values_PosThrottle | DK pos | 7113 | Various_Values_PosThrottle | % | 181
[8 empty] | 19083 | Various_Values_PosThrottleA1 | Various_Values_PosThrottleA1 | 7114 | Various_Values_PosThrottleA1 | % | 19083
[8 empty] | 19084 | Various_Values_PosThrottleA2 | Various_Values_PosThrottleA2 | 7115 | Various_Values_PosThrottleA2 | % | 19084
[8 empty] | 16582 | Various_Values_PosThrottleB1 | Various_Values_PosThrottleB1 | 7116 | Various_Values_PosThrottleB1 | % | 16582
[8 empty] | 16583 | Various_Values_PosThrottleB2 | Various_Values_PosThrottleB2 | 7117 | Various_Values_PosThrottleB2 | % | 16583
[8 empty] | 103 | Various_Values_PosTurboBypass | BP pos | 7118 | Various_Values_PosTurboBypass | % | 103
[8 empty] | 16584 | Various_Values_PosTurboBypassA1 | Various_Values_PosTurboBypassA1 | 7119 | Various_Values_PosTurboBypassA1 | % | 16584
[8 empty] | 16590 | Various_Values_PosTurboBypassA2 | Various_Values_PosTurboBypassA2 | 7120 | Various_Values_PosTurboBypassA2 | % | 16590
[8 empty] | 16585 | Various_Values_PosTurboBypassB1 | Various_Values_PosTurboBypassB1 | 7121 | Various_Values_PosTurboBypassB1 | % | 16585
[8 empty] | 16586 | Various_Values_PosTurboBypassB2 | Various_Values_PosTurboBypassB2 | 7122 | Various_Values_PosTurboBypassB2 | % | 16586
[8 empty] | 19073 | Various_Values_PosWasteGateA | Various_Values_PosWasteGateA | 7123 | Various_Values_PosWasteGateA | % | 19073
[8 empty] | 16589 | Various_Values_PosWasteGateB | Various_Values_PosWasteGateB | 7124 | Various_Values_PosWasteGateB | % | 16589
[11 empty] | 7125 | Various_Values_PressBoost | bar | 104
[11 empty] | 7126 | Various_Values_PressBoostP2 |  | 20144
[11 empty] | 7127 | Various_Values_PressBoostP2A | bar | 19085
[11 empty] | 7128 | Various_Values_PressBoostP2B | bar | 19256
[11 empty] | 7129 | Various_Values_PressBoostP2sA | bar | 19086
[11 empty] | 7130 | Various_Values_PressBoostP2sB | bar | 19257
[11 empty] | 7131 | Various_Values_PressBoostUnfilt |  | 105
[11 empty] | 7132 | Various_Values_SetPosThrottleA1 | % | 19096
[11 empty] | 7133 | Various_Values_SetPosThrottleA2 | % | 19097
[11 empty] | 7134 | Various_Values_SetPosThrottleB1 | % | 19098
[11 empty] | 7135 | Various_Values_SetPosThrottleB2 | % | 19099
[11 empty] | 7136 | Various_Values_SetPosTurboBypassA1 | % | 19087
[11 empty] | 7137 | Various_Values_SetPosTurboBypassA2 | % | 19088
[11 empty] | 7138 | Various_Values_SetPosTurboBypassB1 | % | 19089
[11 empty] | 7139 | Various_Values_SetPosTurboBypassB2 | % | 19090
[11 empty] | 7140 | Various_Values_SetPressBoost | bar | 106
[11 empty] | 7141 | Various_Values_SetSpeed | rpm | 182
[11 empty] | 7142 | Various_Values_SpeedAct | rpm | 107
[11 empty] | 7143 | Various_Values_TempIntakeAir | C | 79
[11 empty] | 7144 | Various_Values_TempMixture | C | 81
[11 empty] | 7145 | Various_Values_TempT2A | °C | 19258
[11 empty] | 7146 | Various_Values_TempT2B | °C | 19927
[11 empty] | 7147 | Various_Values_TempT2sA | °C | 19091
[11 empty] | 7148 | Various_Values_TempT2sB | °C | 19259

## properties
| Serial Number | Application Type | Asset Type | AssetStatusOracle | Catalyst Model | Commissioning Date | Contract Organization Unit | Contract.Service Contract End Counter | Contract.Service Contract End Date | Contract.Service Contract Start Counter | Contract.Service Contract Start Date | Contract.Service Contract Type | Contract.Warranty End Date | Contract.Warranty Start Date | Contract.Warranty Type | Control System Type | Country | CSA Region | Customer Engine Number | Design Number | End Customer | Engine ID | Engine Series | Engine Type | Engine Version | EngineSerialNumberOracle | Exhaust After-Treatment System Model | Field Validation - Additional Details | Field Validation - Contact Person | Field Validation - Description | Field Validation - Flag | Field Validation - Start Date | Gas Type | Gas Type2 | Generator Model | Generator Serial Number | IB Alternator Item Number | IB Alternator Manufacturer | IB Cat2 | IB City | IB Control Software | IB Customer Service Manager | IB Distribution Channel | IB Frequency | IB HQ Duns Number | IB Item Description Engine | IB ItemInstance Unit | IB ItemNumber Unit | IB Leanox | IB NOX | IB Operating Unit | IB Party Name Owner | IB Postal code | IB Project Name | IB Region | IB Service Region | IB Site Customer Name | IB Site Name | IB Status | Orig Commissioning | IB Unit Item Instance Type2 | Party Number Owner | Piston Type | PM Schedule Category | Product Program | Remote Monitored | Service Area | Territory | Turbocharger 1 Model | Turbocharger 1 Serial Number | Turbocharger 2 Model | Turbocharger 2 Serial Number | Turbocharger 3 Model | Turbocharger 3 Serial Number | Turbocharger 4 Model | Turbocharger 4 Serial Number | Unit Serial Number | Unit Type
| IB ItemNumber Engine | Application Type | Asset Type | AssetStatusOracle | Catalyst Model | Commissioning Date | Contract Organization Unit | Contract.Service Contract End Counter | Contract.Service Contract End Date | Contract.Service Contract Start Counter | Contract.Service Contract Start Date | Contract.Service Contract Type | Contract.Warranty End Date | Contract.Warranty Start Date | Contract.Warranty Type | Control System Type | Country | CSA Region | Customer Engine Number | Design Number | End Customer | Engine ID | Engine Series | Engine Type | Engine Version | EngineSerialNumberOracle | Exhaust After-Treatment System Model | Field Validation - Additional Details | Field Validation - Contact Person | Field Validation - Description | Field Validation - Flag | Field Validation - Start Date | Gas Type | Gas Type2 | Generator Model | Generator Serial Number | IB Alternator Item Number | IB Alternator Manufacturer | IB Cat2 | IB City | IB Control Software | IB Customer Service Manager | IB Distribution Channel | IB Frequency | IB HQ Duns Number | IB Item Description Engine | IB ItemInstance Unit | IB ItemNumber Unit | IB Leanox | IB NOX | IB Operating Unit | IB Party Name Owner | IB Postal code | IB Project Name | IB Region | IB Service Region | IB Site Customer Name | IB Site Name | IB Status | IB Unit Commissioning Date | IB Unit Item Instance Type2 | Party Number Owner | Piston Type | PM Schedule Category | Product Program | Remote Monitored | Service Area | Territory | Turbocharger 1 Model | Turbocharger 1 Serial Number | Turbocharger 2 Model | Turbocharger 2 Serial Number | Turbocharger 3 Model | Turbocharger 3 Serial Number | Turbocharger 4 Model | Turbocharger 4 Serial Number | Unit Serial Number | Unit Type | UnitSerialNumberOracle | Name
0 | 1145166 | Industry | GE Jenbacher Engine | Active | -- | 2016-12-09 | [9 empty] | XT3 | IT |  | 2 | T241 | POLYNT SPA | M02 | 6 | 624 | H01 | GEJ-1145166 |  | Cylinder Head (c/w Cooling water upgrade), Power Unit, Exhaust Line, Exhaust Line Gaskets and Exhaust connecting pipes. Installation OPH: 31291 OPH Validation duration: 10000 OPH | Emma Lambert | FV173 - J624 Systems Release | true | 1602769950821 | NG1 | n.a. | LSA 56 BL75 | 605201De01 | 1213507 | Leroy Somer | -- | SCANZOROSCIATE | V3.40.0beta | Emiliano Salvemini | Key Account | 50 | 428362057 | ENG JMS 624 H01 50__J_T241 | 4075908 | 1145174 | L | 500 mg/Nm3 | Jenbacher | AB IMPIANTI | 24020 | AB ENERGY 624 - 10 | EU Direct | EU Direct | POLYNT SPA | Polynt | Active | 2016-12-09 | UNIT | 3252 | Steel | standard 30-60 | 2014 | No | Italy | IT Lombardy | P135-H45 | PT000629 | Z140-H75 | PT000630 | P135-H45 | PT000628 | Z140-H75 | PT000631 | 1145174 | JMS | GEJ-1145174 | POLYNT - 2 (1145166-T241) --> Sept
1 | 1175579 | Industry |  | Active Docu incomplete | C | 2016-08-22 | DE | 119999 | 2031-07-31 | 0 | 2016-08-01 | PREVENTIVE AND CORRECTIVE |  |  |  | XT4 | DE | DE | 5 | T966 | BMW AG | M05 | 6 | 616 | F01 | GEJ-1175579 | No | [5 empty] | NG1 | n.a. | LSA 54 ZL105 | 607380De01 | 1215590 | Leroy Somer | C | REGENSBURG | n.a. | Kai Spieker | Direct Channel | 50 |  | ENG JMS 616 F01 50__J_T966 | 4470170 | 1175578 | L | 500 mg/Nm3 | Jenbacher | BMW AG | 93055 | BMW REGENSBURG 5 | Germany | Germany | BMW AG | BMW REGENSBURG M5 | Active Docu incomplete | 2016-08-22 | UNIT | 5959 | Steel | standard 30-60 | 2015 | Yes | DE Region South | DE Region South | TCR16-42714 A | 116815 | TCR16-42714 B | 116816 |  |  |  |  | 1175578 | JMS | GEJ-1175578 | REGENSBURG
2 | 1184199 | Industry | GE Jenbacher Engine | Active | -- | 2016-12-22 | [9 empty] | XT4 | DE |  | 1 | U233 | ROCHE DIAGNOSTICS GMBH | M01 | 6 | 624 | H02 | GEJ-1184199 | No | Installation OPH: 25208 Validation Duration: 10000 | For FV only - Emma Lambert | FV173 - J624 Systems Release | true | 1589439101080 | NG1 | n.a. | TD125-F2K9 | T-03646 | 1222808 | TDPS | -- | PENZBERG | V4.03.00 | Dieter Schmidt | Direct Channel | 50 | 507298656 | ENG JMS 624 H02 50__J_U233 | 4531463 | 1184196 | L | 250 mg/Nm3 | Jenbacher | ENERGAS BHKW GMBH | 82377 | ROCHE PENZBERG KWKK | Germany | Germany | ROCHE DIAGNOSTICS GMBH | ROCHE PENZBERG KWKK | Active | 2016-12-22 | UNIT | 3802 | Steel | standard 30-60 | 2015 | Yes | DE Region South | DE Region South | P135-H45 | PT000936 | P135-H45 | PT000937 | Z140-H75 | PT000938 | Z140-H75 | PT000939 | 1184196 | JMS | GEJ-1184196 | ROCHE PENZBERG KWKK
3 | 1198719 | Industry | GE Jenbacher Engine | Active | C | 2017-03-31 |  | 59999 | 2027-03-31 | 0 | 2016-12-02 | PREVENTIVE AND CORRECTIVE |  |  |  | XT4 | BE | NL | 2 | U658 | ECOGEN ENERGY SYSTEMS BVBA | M02 | 6 | 616 | F12 | GEJ-1198719 | No | [5 empty] | NG1 | n.a. | LSA 54 ZL105 | 608026De01 | 1228964 | Leroy Somer | C | WEVELGEM | V4.03.00 | Barteld Jonkman | Channel Partner | 50 |  | ENG JMS 616 F412 50__J_U658 | 4657658 | 1198718 | L | 250 mg/Nm3 | Jenbacher | ECOGEN ENERGY SYSTEMS BVBA | 8560 | ALPRO M2 616F412 BE | EU Direct | EU Direct | ECOGEN ENERGY SYSTEMS BVBA | Alpro 616 | Active | 2017-03-31 | UNIT | 88517 | Steel | standard 30-60 | 2016 | Yes | NL South | HQ Jenbach | A135-H56 | 564721 | A135-H56 | 564720 |  |  |  |  | 1198718 | JMS | GEJ-1198718 | ECOGEN ENERGY SYSTEMS BVBA
4 | 1243360 | Industry |  | Not Commissioned | C | 2011-07-04 | DE | 119999 | 2031-07-31 | 0 | 2010-07-19 | PREVENTIVE AND CORRECTIVE |  |  |  | XT3 | DE | DE | 3 | I448 | BMW AG | M03 | 6 | 616 | J01 | JEN-1243360 | No | [5 empty] | NG1 | n.a. | DIG 142 d/4 | 8430506A404 | 1203563 | AVK | C | REGENSBURG | V3.10.0 | Kai Spieker | Direct Channel | 50 |  | Repairs.ENG.JMS.616 | 1247405 | 1014841 | L | 500 | Jenbacher | BMW AG | 93055 | BMW REGENSBURG | Germany | Germany | BMW AG | BMW REGENSBURG M3 | Temporarily Inactive | 2012-10-28 | UNIT | 5959 |  | standard 30-60 |  | Yes | DE Region South | DE Region South | A135-H66 | 594624 | A135-H66 | 594625 |  |  |  |  | 1014841 | JMS | GEJ-1014841 | BMW REGENSBURG M3
5 | 1243362 | Industry |  | Not Commissioned | C |  | DE | 119999 | 2031-07-31 | 0 | 2010-07-19 | PREVENTIVE AND CORRECTIVE |  |  |  | XT3 | DE | DE | 2 | I448 | BMW AG | M02 | 6 | 616 | J01 | JEN-1243362 | No | [5 empty] | NG1 | n.a. | DIG 142 d/4 | 8430506A304 | 1203563 | AVK | C | REGENSBURG | V3.10.0 | Kai Spieker | Direct Channel | 50 |  | Repairs.ENG.JMS.616 | 1235405 | 1014851 | L | 500 | Jenbacher | BMW AG | 93055 | BMW REGENSBURG | Germany | Germany | BMW AG | BMW REGENSBURG M2 | Temporarily Inactive | 2011-07-04 | UNIT | 5959 |  | standard 30-60 |  | No | DE Region South | DE Region South | A135-H66 | HT595239 | A135-H66 | HT595239 |  |  |  |  | 1014851 | JMS | GEJ-1014851 | REGENSBURG
6 | 1250575 | Industry |  | Not Commissioned | -- | 2019-09-03 | [6 empty] | 2021-05-08 | 2019-09-03 | WARRANTY_NEW_UNITS | XT4 | RU |  | M02 | Y199 | MAX MOTORS | M01 | 6 | 624 | K01 | JEN-1250575 | No | Installation OPH: 0 Validation Duration: 10000 OPH | For FV only - Emma Lambert | FV173 - J624 Systems Release | true | 1593248148528 | NG1 | n.a. | DIG 142 i/4 | 8434599A002 | 1080000 | AVK | -- | SOCHI | V4.05.01 | Vasily Kopissky | Channel Partner | 50 | 565559379 | Repairs.ENG.JMS.624 | 5526323 | 1386029 | L | 500 mg/Nm3 | Jenbacher | MAX MOTORS | 354000 | ABINSK 1-3 | RCIS | RCIS | MAX MOTORS | ABINSK | Active Docu incomplete | 2019-09-03 | UNIT | 6243 |  | standard 30-60 |  | No | Distributor | HQ Jenbach | Z140-H75 | PT002079 | Z140-H75 | PT002080 | P135-H45 | PT002077 | P135-H45 | PT002078 | 1386029 | JMS | GEJ-1386029 | ABINSK
7 | 1250578 | Industry |  | Active Docu incomplete | -- | 2020-11-19 | [6 empty] | 2021-09-26 | 2020-09-27 | WARRANTY_EXTENDED | XT4 | PK |  | 1 | X243 | PROSPERITY WEAVING MILLS LTD | M01 | 6 | 624 | K505 | JEN-1250578 | No | [5 empty] | NG1 | n.a. | LSA 56 BL75 | 609284DE01 | 1221961 | Leroy Somer | -- | LAHORE | V4.04.00 | Amir Hashmi | Channel Partner | 50 | 645478397 | Repairs.ENG.JMS.624 | 5241121 | 1351409 | L | 500 mg/Nm3 | Jenbacher | M/S ORIENT ENERGY SYSTEMS (PVT) LTD | 54660 | PROSPERITY WEAVING MILLS | META-SA | META-SA | PROSPERITY WEAVING MILLS LTD | PROSPERITY WEAVING MILLS LTD | Active | 2018-10-15 | UNIT | 3929 |  | standard 30-60 |  | Yes | Distributor | HQ Jenbach | Z140-H75 | PT001700 | Z140-H75 | PT001701 | P135-H45 | PT001698 | P135-H45 | PT001699 | 1351409 | JMS | GEJ-1351409 | PROSPERITY WEAVING MILLS LTD - 1 (1351388-X243)
8 | 1310773 | Industry | GE Jenbacher Engine | Active | -- | 2017-04-12 |  | 59999 | 2026-08-15 | 0 | 2016-08-16 | PREVENTIVE AND CORRECTIVE |  |  |  | XT4 | PT | ES | 1 | U763 | SOTERNIX - PRODUCAO DE ENERGIA, ACE | M01 | 6 | 616 | F11 | GEJ-1310773 | No | [5 empty] | NG1 | n.a. | LSA 54 VL90 | 608100De01 | 1237545 | Leroy Somer | -- | BARCELOS (BARCELOS ) | V4.03.00 | Ana Montoyo | Direct Channel | 50 | 336079640 | ENG JMS 616 J11 50__J_U763 | 4664831 | 1310786 | L | 500 mg/Nm3 | Jenbacher | SOTERNIX - PRODUCAO DE ENERGIA, ACE | 4750-823 | SOTERNIX RENOVE | EU Indirect/LATAM | EU Indirect/LATAM | SOTERNIX - PRODUCAO DE ENERGIA, ACE | SOTERNIX RENOVE | Active | 2017-04-12 | UNIT | 6940 | Steel | standard 30-60 | 2016 | Yes | ES West | PT Portugal | A135-H56 | 564149 | A135-H56 | 564150 |  |  |  |  | 1310786 | JMS | GEJ-1310786 | SOTERNIX RENOVE
9 | 1319133 | Supply of Buildings |  | Active Docu incomplete | -- | 2020-08-25 | DE | 119999 | 2031-07-31 | 1902-09-26 | 2016-08-01 | PREVENTIVE AND CORRECTIVE |  |  |  | XT4 | DE | DE | 4 | V008 | BMW AG | M04 | 6 | 620 | F01 | GEJ-1319133 | No | [5 empty] | NG1 | n.a. | LSA 56 BM60 | 609174DE01 | 1238444 | Leroy Somer | -- | MUENCHEN | V4.04.00 | Kai Spieker | Direct Channel | 50 |  | ENG JMS 620 F01 50__J_V008 | 5296190 | 1319132 | L | 500 | Jenbacher | BMW AG | 80935 | BMW MÜNCHEN 1.50 | Germany | Germany | BMW AG | BMW MÜNCHEN | Active Docu incomplete | 2020-08-25 | UNIT | 5959 | ST | standard 30-60 | 2016 | Yes | DE Region South | DE Region South | A140-H55 | 575524 | A140-H55 | 575521 |  |  |  |  | 1319132 | JMS | GEJ-1319132 | BMW MÜNCHEN
10 | 1319138 | Supply of Buildings |  | Active Docu incomplete | -- | 2020-01-01 | DE | 119999 | 2031-07-31 | 1902-09-26 | 2016-08-01 | PREVENTIVE AND CORRECTIVE |  |  |  | XT4 | DE | DE | 2 | V008 | BMW AG | M02 | 6 | 620 | F01 | GEJ-1319138 | No | [5 empty] | NG1 | n.a. | LSA 56 BM60 | 609173DE01 | 1238444 | Leroy Somer | -- | MÜNCHEN | V4.04.00 | Kai Spieker | Direct Channel | 50 |  | ENG JMS 620 F01 50__J_V008 | 5291138 | 1319137 | L | 500 | Jenbacher | BMW AG | 80788 | BMW MÜNCHEN 1.50 | Germany | Germany | BMW AG | BMW MÜNCHEN | Active Docu incomplete | 2020-01-01 | UNIT | 5959 | ST | standard 30-60 | 2016 | Yes | DE Region South | DE Region South | A140-H55 | 575518 | A140-H55 | 575523 |  |  |  |  | 1319137 | JMS | GEJ-1319137 | BMW MÜNCHEN
11 | 1319151 | Supply of Buildings |  | Active Docu incomplete | -- | 2020-08-25 | DE | 119999 | 2031-07-31 | 1902-09-26 | 2016-08-01 | PREVENTIVE AND CORRECTIVE | 2021-03-02 | 2020-01-02 | WARRANTY_NEW_UNITS | XT4 | DE | DE | 1 | V008 | BMW AG | M01 | 6 | 620 | F01 | GEJ-1319151 | No | [5 empty] | NG1 | n.a. | LSA 56 BM60 | 609175DE01 | 1241303 | Leroy Somer | -- | MÜNCHEN | V4.04.00 | Kai Spieker | Direct Channel | 50 |  | ENG JMS 620 F01 50__J_V008 | 5293132 | 1319126 | L | 500 | Jenbacher | BMW AG | 80788 | BMW MÜNCHEN 1.50 | Germany | Germany | BMW AG | BMW MÜNCHEN | Active Docu incomplete | 2020-08-25 | UNIT | 5959 | ST | standard 30-60 | 2016 | Yes | DE Region South | DE Region South | A140-H55 | 571247 | A140-H55 | 571246 |  |  |  |  | 1319126 | JMS | GEJ-1319126 | BMW MÜNCHEN
12 | 1319157 | Supply of Buildings |  | Active Docu incomplete | -- | 2020-01-01 | DE | 119999 | 2031-07-31 | 1902-09-26 | 2016-08-01 | PREVENTIVE AND CORRECTIVE |  |  |  | XT4 | DE | DE | 3 | V008 | BMW AG | M03 | 6 | 620 | F01 | GEJ-1319157 | No | [5 empty] | NG1 | n.a. | LSA 56 BM60 | 609176DE01 | 1241303 | Leroy Somer | -- | MÜNCHEN | V4.04.00 | Kai Spieker | Direct Channel | 50 |  | ENG JMS 620 F01 50__J_V008 | 5292148 | 1319156 | L | 500 | Jenbacher | BMW AG | 80788 | BMW MÜNCHEN 1.50 | Germany | Germany | BMW AG | BMW MÜNCHEN | Active Docu incomplete | 2020-01-01 | UNIT | 5959 | ST | standard 30-60 | 2016 | No | DE Region South | DE Region South | A140-H55 | 575525 | A140-H55 | 575522 |  |  |  |  | 1319156 | JMS | GEJ-1319156 | BMW MÜNCHEN
13 | 1319997 | Supply of Buildings |  | Active Docu incomplete | C | 2019-09-16 | DE | 119999 | 2031-07-31 | 1902-09-26 | 2016-08-01 | PREVENTIVE AND CORRECTIVE |  |  |  | XT4 | DE | DE | 2 | U779 | BMW AG | M02 | 6 | 624 | H01 | GEJ-1319997 | No | [5 empty] | NG1 | n.a. | LSA 56 BUL85 | 608625DE01 | 1237506 | Leroy Somer | C | MÜNCHEN | V4.04.00 | Kai Spieker | Direct Channel | 50 |  | ENG JMS 624 H01 50__J_U779 | 5232103 | 1319996 | L | 500 | Jenbacher | BMW AG | 80809 | BMW MÜNCHEN 1.10 | Germany | Germany | BMW AG | BMW MÜNCHEN | Active Docu incomplete | 2019-09-16 | UNIT | 5959 | ST | standard 30-60 | 2016 | No | DE Region South | DE Region South | LPR5 | 00010/17 | LPR5 | 00011/17 | HSR4 | 00015/18 | HSR4 | 00016/18 | 1319996 | JMS | GEJ-1319996 | BMW MÜNCHEN
14 | 1320022 | Supply of Buildings |  | Active Docu incomplete | C | 2019-09-16 | DE | 119999 | 2031-07-31 | 1902-09-26 | 2016-08-01 | PREVENTIVE AND CORRECTIVE |  |  |  | XT4 | DE | DE | 1 | U779 | BMW AG | M01 | 6 | 624 | H01 | GEJ-1320022 | No | Installation OPH: 3985 OPH Installation starts: 864 starts | For Field Validation only - Emma Lambert | FV193 - Pre-chamber Sealing - New Material | true | 1589760000000 | NG1 | n.a. | LSA 56 BUL85 | 608624DE01 | 1237506 | Leroy Somer | C | MÜNCHEN | V4.04.00 | Kai Spieker | Direct Channel | 50 |  | ENG JMS 624 H01 50__J_U779 | 5223101 | 1320019 | L | 500 | Jenbacher | BMW AG | 80809 | BMW MÜNCHEN 1.10 | Germany | Germany | BMW AG | BMW MÜNCHEN | Active Docu incomplete | 2019-09-16 | UNIT | 5959 | ST | standard 30-60 | 2016 | No | DE Region South | DE Region South | LPR5 | 00012/18 | LPR5 | 00013/18 | HSR4 | 00018/18 | HSR4 | 00019/18 | 1320019 | JMS | GEJ-1320019 | BMW MÜNCHEN
15 | 1320030 | Supply of Buildings |  | Active Docu incomplete | C | 2019-09-16 | DE | 119999 | 2031-07-31 | 1902-09-26 | 2016-08-01 | PREVENTIVE AND CORRECTIVE |  |  |  | XT4 | DE | DE | 3 | U779 | BMW AG | M03 | 6 | 624 | H01 | GEJ-1320030 | No | [5 empty] | NG1 | n.a. | LSA 56 BUL85 | 608626DE01 | 1237506 | Leroy Somer | C | MÜNCHEN | V4.04.00 | Kai Spieker | Direct Channel | 50 |  | ENG JMS 624 H01 50__J_U779 | 5233096 | 1320027 | L | 500 | Jenbacher | BMW AG | 80809 | BMW MÜNCHEN 1.10 | Germany | Germany | BMW AG | BMW MÜNCHEN | Active Docu incomplete | 2019-09-16 | UNIT | 5959 | ST | standard 30-60 | 2016 | No | DE Region South | DE Region South | LPR5 | 00006/17 | LPR5 | 00007/17 | HSR4 | 00010/18 | HSR4 | 00011/18 | 1320027 | JMS | GEJ-1320027 | BMW MÜNCHEN
16 | 1320072 | Supply of Buildings |  | Active Docu incomplete | C | 2019-01-09 | DE | 119999 | 2031-07-31 | 0 | 2016-08-01 | PREVENTIVE AND CORRECTIVE |  |  |  | XT4 | DE | DE | 4 | U781 | BMW AG | M04 | 6 | 624 | H01 | GEJ-1320072 | No | Installation OPH: 6315 Validation Duration: 10000 OPH | For FV only: Emma Lambert | FV173 - J624 Systems Release 2 | true | 1581056760000 | NG1 | n.a. | LSA 56 BUL85 | 608958DE01 | 1237506 | Leroy Somer | C | LANDSHUT | V4.04.00 | Kai Spieker | Direct Channel | 50 |  | ENG JMS 624 H01 50__J_U781 | 5172340 | 1320069 | L | 500 | Jenbacher | BMW AG | 84030 | BMW LANDSHUT 4.10 | Germany | Germany | BMW AG | BMW LANDSHUT 4.10 | Active Docu incomplete | 2019-01-09 | UNIT | 5959 | ST | standard 30-60 | 2016 | Yes | DE Region South | DE Region South | P135-H45 | PT001599 | P135-H45 | PT001598 | Z140-H75 | PT001602 | Z140-H75 | PT001603 | 1320069 | JMS | GEJ-1320069 | BMW LANDSHUT 4.10
17 | 1320090 | Supply of Buildings |  | Active Docu incomplete | C | 2019-01-07 | DE | 119999 | 2031-07-31 | 0 | 2016-08-01 | PREVENTIVE AND CORRECTIVE |  |  |  | XT4 | DE | DE | 1 | U781 | BMW AG | M01 | 6 | 624 | H01 | GEJ-1320090 | No | Cylinder Head, Power Unit, Exhaust Line, Exhaust line gaskets & exhaust line connecting pipes Installation OPH: 8076 OPH / Installation Starts: 1225 Starts Validation Duration: 10000 OPH | Emma Lambert | FV173 - J624 Systems Release, FV161 - Exhaust Line | true | 1602849324946 | NG1 | n.a. | LSA 56 BUL85 | 608956De01 | 1237506 | Leroy Somer | C | LANDSHUT | V4.04.00 | Kai Spieker | Direct Channel | 50 |  | ENG JMS 624 H01 50__J_U781 | 5172128 | 1320088 | L | 500 | Jenbacher | BMW AG | 84030 | BMW LANDSHUT 4.10 | Germany | Germany | BMW AG | BMW LANDSHUT 4.10 | Active Docu incomplete | 2019-01-07 | UNIT | 5959 | ST | standard 30-60 | 2016 | Yes | DE Region South | DE Region South | Z140-H75 | PT001608 | Z140-H75 | PT001609 | P135-H45 | PT001604 | P135-H45 | PT001605 | 1320088 | JMS | GEJ-1320088 | BMW LANDSHUT M1
18 | 1320114 | Supply of Buildings |  | Active Docu incomplete | C | 2019-01-09 | DE | 119999 | 2031-07-31 | 0 | 2016-08-01 | PREVENTIVE AND CORRECTIVE |  |  |  | XT4 | DE | DE | 3 | U781 | BMW AG | M03 | 6 | 624 | H01 | GEJ-1320114 | No | Validation rebuild due Jan '20 | For FV only: Emma Lambert | FV173 - J624 Systems Release 2 | true |  | NG1 | n.a. | LSA 56 BUL85 | 608957DE01 | 1237506 | Leroy Somer | C | LANDSHUT | V4.04.00 | Kai Spieker | Direct Channel | 50 |  | ENG JMS 624 H01 50__J_U781 | 5172154 | 1320113 | L | 500 | Jenbacher | BMW AG | 84030 | BMW LANDSHUT 4.10 | Germany | Germany | BMW AG | BMW LANDSHUT 4.10 | Active Docu incomplete | 2019-01-09 | UNIT | 5959 | ST | standard 30-60 | 2016 | Yes | DE Region South | DE Region South | Z140-H75 | PT001610 | Z140-H75 | PT001611 | P135-H45 | PT001606 | P135-H45 | PT001607 | 1320113 | JMS | GEJ-1320113 | BMW LANDSHUT 4.10
19 | 1325927 | Supply of Buildings |  | Active Docu incomplete | -- | 2017-11-02 | [9 empty] | XT4 | FR |  | 1 | V229 | CLARKE ENERGY FRANCE SASU | M01 | 6 | 624 | H12 | GEJ-1325927 | No | [5 empty] | NG1 | n.a. | LSA 56 BUL85 | 608494De01 | 1232305 | LS | -- | BOUC BEL AIR | V4.04.00 | Francois Zerf | Channel Partner | 50 | 572828007 | ENG JMS 624 H312 50__J_V229 | 5006590 | 1325933 | L | 250 mg/Nm3 | Jenbacher | CLARKE ENERGY FRANCE SASU | 13320 | COGE LES COURONNERIES | EU Indirect/LATAM | EU Indirect/LATAM | CLARKE ENERGY FRANCE SASU | LES COURONNERIES | Active Docu incomplete | 2017-11-02 | UNIT | 5566 | ST | standard 30-60 | 2016 | Yes | Distributor | HQ Jenbach | Z140-H75 | PT001335 | Z140-H75 | PT001336 | P135-H45 | PT001333 | P135-H45 | PT001334 | 1325933 | JMS | GEJ-1325933 | LES COURONNERIES
20 | 1339812 | Supply of Buildings |  | Active Docu incomplete | -- | 2018-11-23 | [9 empty] | XT4 | FR |  | 1 | V624 | CLARKE ENERGY FRANCE SASU | M01 | 6 | 612 | J12 | GEJ-1339812 | No | [5 empty] | NG1 | n.a. | LVSI 804 W2 | P17l199180 | 1239406 | Newage Stamford | -- | BOUC BEL AIR | V4.04.00 | Francois Zerf | Channel Partner | 50 | 572828007 | ENG JMS 612 J12 50__J_V624 | 5096059 | 1339818 | L | 250 mg/Nm3 | Jenbacher | CLARKE ENERGY FRANCE SASU | 13320 | DALOMA | EU Indirect/LATAM | EU Indirect/LATAM | CLARKE ENERGY FRANCE SASU | DALOMA | Active Docu incomplete | 2018-11-23 | UNIT | 5566 | Steel | standard 30-60 | 2017 | No | Distributor | HQ Jenbach | A135-H65 | 571870 | A135-H65 | 571869 |  |  |  |  | 1339818 | JMS | GEJ-1339818 | DALOMA
21 | 1345851 | O&G Power Gen |  | Active Docu incomplete | -- | 2018-10-31 | [9 empty] | XT4 | FR |  | 3 | X077 | CLARKE ENERGY FRANCE SASU | M03 | 6 | 616 | J12 | GEJ-1345851 | No | [5 empty] | APG1 | n.a. | LSA 54 VL90 | 609179DE01 | 1240661 | Leroy Somer | -- | BOUC BEL AIR | V4.04.00 | Francois Zerf | Channel Partner | 50 | 572828007 | ENG JMS 616 J12 50__J_X077 | 5172066 | 1345853 | L | 250 mg/Nm3 | Jenbacher | CLARKE ENERGY FRANCE SASU | 13320 | COGE GAZ DE LACQ J616 | EU Indirect/LATAM | EU Indirect/LATAM | CLARKE ENERGY FRANCE SASU | GAZ DE LACQ | Active Docu incomplete | 2018-10-31 | UNIT | 5566 | ST | special gas 1-20-40-60 | 2017 | No | Distributor | HQ Jenbach | A135-H66 | 573214 | A135-H66 | 573213 |  |  |  |  | 1345853 | JMS | GEJ-1345853 | GAZ DE LACQ
22 | 1352268 | Supply of Buildings |  | Active Docu incomplete | C | 2019-10-11 | DE | 119999 | 2031-07-31 | 0 | 2016-08-01 | PREVENTIVE AND CORRECTIVE | 2021-03-20 | 2019-10-11 | WARRANTY_NEW_UNITS | XT4 | DE | DE | 6 | X263 | BMW AG | M06 | 6 | 624 | H01 | GEJ-1352268 | No | Installation OPH: 5943 Installation Starts: 462 starts | For Field Validation only - Emma Lambert | FV193 - Pre-chambert Sealing - New Material | true | 1589932800000 | NG1 | n.a. | LSA 56 BUL85 | 609620DE01 | 1242185 | Leroy Somer | C | DINGOLFING | V4.04.00 | Kai Spieker | Direct Channel | 50 |  | ENG JMS 624 H01 50__J_X263 | 5414278 | 1352336 | L | 500 | Jenbacher | BMW AG | 84130 | BMW DINGOLFING W.02.40 GEB94.5 | Germany | Germany | BMW AG | BMW DINGOLFING 2.4 | Active Docu incomplete | 2019-10-11 | UNIT | 5959 | ST | standard 30-60 | 2017 | No | DE Region South | DE Region South | Z140-H75 | PT001958 | Z140-H75 | PT001959 | P135-H45 | PT001954 | P135-H45 | PT001955 | 1352336 | JMS | GEJ-1352336 | BMW DINGOLFING 2.4
23 | 1352323 | Supply of Buildings |  | Active Docu incomplete | C | 2019-10-10 | DE | 119999 | 2031-07-31 | 0 | 2016-08-01 | PREVENTIVE AND CORRECTIVE | 2021-02-13 | 2019-10-11 | WARRANTY_NEW_UNITS | XT4 | DE | DE | 7 | X263 | BMW AG | M07 | 6 | 624 | H01 | GEJ-1352323 | No | Installation OPH: 6271 OPH Installation Starts: 535 starts | For Field Validation only - Emma Lambert | FV193 - Pre-chamber Sealing - New Material | true | 1593648000000 | NG1 | n.a. | LSA 56 BUL85 | 609621DE01 | 1242185 | Leroy Somer | C | DINGOLFING | V4.04.00 | Kai Spieker | Direct Channel | 50 |  | ENG JMS 624 H01 50__J_X263 | 5410292 | 1352333 | L | 500 | Jenbacher | BMW AG | 84130 | BMW DINGOLFING W.02.40 GEB94.5 | Germany | Germany | BMW AG | BMW DINGOLFING 2.4 | Active Docu incomplete | 2019-10-10 | UNIT | 5959 | ST | standard 30-60 | 2017 | No | DE Region South | DE Region South | Z140-H75 | PT001942 | Z140-H75 | PT001943 | P135-H45 | PT001940 | P135-H45 | PT001941 | 1352333 | JMS | GEJ-1352333 | BMW DINGOLFING 2.4
24 | 1361965 | IPP/Power producer/Utility |  | Active Docu incomplete | -- | 2019-07-19 |  | 59999 | 2030-12-16 | 1900-04-09 | 2018-12-17 | PREVENTIVE AND CORRECTIVE |  |  |  | XT4 | IT | IT | 1 | X580 | GRASTIM JV SRL | M01 | 6 | 616 | J11 | GEJ-1361965 | No | [5 empty] | NG1 | n.a. | DIG 142 d/4 | 8434560A001 | 1221105 | AVK | -- | NAPOLI | V4.04.00 | Michele Bianchini | Direct Channel | 50 |  | ENG JMS 616 J11 50__J_X580 | 5316214 | 1362087 | L | 500 mg/Nm3 | Jenbacher | GRASTIM JV SRL | 80133 | FRONERI - FERENTINO | EU Direct | EU Direct | GRASTIM JV SRL | FRONERI - FERENTINO | Active Docu incomplete | 2019-07-19 | UNIT | 7359 | Steel | standard 30-60 | 2017 | No | IT South | IT South | A135-H56 | 576453 | A135-H56 | 576452 |  |  |  |  | 1362087 | JMS | GEJ-1362087 | FRONERI - FERENTINO
25 | 1364066 | Supply of Buildings |  | Not Commissioned | -- | [10 empty] | XT4 | FR |  | 1 | X684 | CLARKE ENERGY FRANCE SASU | M01 | 6 | 620 | J12 | GEJ-1364066 | No | [5 empty] | NG1 | n.a. | LSA 56 BM60 | 609608DE01 | 1215079 | Leroy Somer | -- | BOUC BEL AIR | V4.04.00 | Francois Zerf | Channel Partner | 50 | 572828007 | ENG JMS 620 J12 50__J_X684 | 5347212 | 1364065 | L | 250 mg/Nm3 | Jenbacher | CLARKE ENERGY FRANCE SASU | 13320 | TOM VILLE J620 | EU Indirect/LATAM | EU Indirect/LATAM | CLARKE ENERGY FRANCE SASU | TOM VILLE | Not Commissioned |  | UNIT | 5566 | Steel | standard 30-60 | 2017 | No | Distributor | HQ Jenbach | A140-H65 | 576570 | A140-H65 | 576567 |  |  |  |  | 1364065 | JMS | GEJ-1364065 | TOM VILLE
26 | 1386147 | Industry |  | Active Docu incomplete | C | 2019-09-03 | [6 empty] | 2021-06-12 | 2019-09-03 | WARRANTY_NEW_UNITS | XT4 | RU |  | M06 | Y202 | MAX MOTORS | M06 | 6 | 624 | H01 | GEJ-1386147 | No | [5 empty] | NG1 | n.a. | DIG 142 i/4 | 8434641A003 | 1080000 | AVK | C | SOCHI | V4.05.01 | Vasily Kopissky | Channel Partner | 50 | 565559379 | ENG JMS 624 H01 50__J_Y202 | 5564325 | 1386133 | L | 500 mg/Nm3 | Jenbacher | MAX MOTORS | 354000 | ABINSK 6 | RCIS | RCIS | MAX MOTORS | ABINSK | Active Docu incomplete | 2019-09-03 | UNIT | 6243 | ST | standard 30-60 | 2018 | No | Distributor | HQ Jenbach | Z140-H75 | PT002195 | Z140-H75 | PT002196 | P135-H45 | PT002193 | P135-H45 | PT002194 | 1386133 | JMS | GEJ-1386133 | ABINSK
27 | 1386177 | Industry |  | Active Docu incomplete | C | 2019-09-03 | [6 empty] | 2021-07-09 | 2019-09-03 | WARRANTY_NEW_UNITS | XT4 | CH |  | M09 | Y203 | MAX MOTORS | M09 | 6 | 624 | H01 | GEJ-1386177 | No | Installation OPH: 1845 Validation Duration: 10000 OPH | For Field Validation only: Emma Lambert | FV173 - J624 Systems Release | true | 1584103440000 | NG1 | n.a. | DIG 142 i/4 | 8434677A003 | 1080000 | AVK | C | SOCHI | V4.05.01 | Vasily Kopissky | Channel Partner | 50 | 565559379 | ENG JMS 624 H01 50__J_Y203 | 5615326 | 1386198 | L | 500 mg/Nm3 | Jenbacher | MAX MOTORS | 354000 | ABINSK 7-9 | RCIS | RCIS | MAX MOTORS | ABINSK | Active Docu incomplete | 2019-09-03 | UNIT | 6243 | ST | standard 30-60 | 2018 | Yes | Distributor | HQ Jenbach | Z140-H75 | PT002177 | Z140-H75 | PT002178 | P135-H45 | PT002171 | P135-H45 | PT002174 | 1386198 | JMS | GEJ-1386198 | ABINSK
28 | 1386260 | Industry |  | Active Docu incomplete | C | 2019-09-03 | [6 empty] | 2021-07-15 | 2019-09-03 | WARRANTY_NEW_UNITS | XT4 | CH |  | M10 | Y204 | MAX MOTORS | M10 | 6 | 624 | H01 | GEJ-1386260 | No | Installation OPH: 6240 Validation duration: 10.000 OPH | For FV only: Emma Lambert | FV173 - J624 Systems Release | true | 1596621507769 | NG1 | n.a. | DIG 142 i/4 | 8434677A001 | 1080000 | AVK | C | SOCHI | V4.05.01 | Vasily Kopissky | Channel Partner | 50 | 565559379 | ENG JMS 624 H01 50__J_Y204 | 5619338 | 1386252 | L | 500 mg/Nm3 | Jenbacher | MAX MOTORS | 354000 | ABINSK 10-11 | RCIS | RCIS | MAX MOTORS | ABINSK | Active Docu incomplete | 2019-09-03 | UNIT | 6243 | ST | standard 30-60 | 2018 | Yes | Distributor | HQ Jenbach | Z140-H75 | PT002153 | Z140-H75 | PT002154 | P135-H45 | PT002149 | P135-H45 | PT001250 | 1386252 | JMS | GEJ-1386252 | ABINSK
29 | 1393153 | Industry |  | Active | -- | 2019-04-08 | [6 empty] | 2021-04-07 | 2019-04-08 | WARRANTY_NEW_UNITS | XT4 | PK |  | 1 | Y386 | BLESSED TEXTILES LIMITED | M01 | 6 | 620 | J101 | GEJ-1393153 | No | Installation OPH: 7315 OPH Validation Duration: 10000 OPH | For Field Validation only - Emma Lambert | FV175 - Power Unit | true | 1585038697567 | NG1 | n.a. | LSA 56 BM60 | 610166DE01 | 1215079 | Leroy Somer | -- | FAISALABAD | V4.05.01 | Amir Hashmi | Channel Partner | 50 | 645478397 | ENG JMS 620 J101 50__J_Y386 | 5596333 | 1393154 | L | 500 mg/Nm3 | Jenbacher | M/S ORIENT ENERGY SYSTEMS (PVT) LTD | 74900 | JMS620_SO#37366 | META-SA | META-SA | BLESSED TEXTILES LIMITED | BLESSED TEXTILE | Active | 2019-04-08 | UNIT | 3929 | ST | standard 30-60 | 2018 | No | Distributor | HQ Jenbach | A140-H65 | 582737 | A140-H65 | 582738 |  |  |  |  | 1393154 | JMS | GEJ-1393154 | BLESSED TEXTILE
30 | 1415409 | Greenhouse |  | Active Docu incomplete | -- | 2019-09-15 |  | 59999 | 2028-10-28 | 0 | 2018-10-29 | PREVENTIVE AND CORRECTIVE |  |  |  | XT4 | BE | NL | 1 | Y809 | Den Berk BV | M01 | 6 | 624 | K01 | GEJ-1415409 | No |  |  | FV202 - V17-B Redesign, FV203 - Field Oil Validation ExxonMobil Pegasus X25 | true |  | NG1 | n.a. | TD125-F2K9 | T-04945 | 1222808 | TDPS | -- | MERKSPLAS | V4.07.00 | Patrick de Jong | Direct Channel | 50 |  | ENG JMS 624 K01 50__J_Y809 | 5777326 | 1415365 | L | 500 mg/Nm3 | Jenbacher | SALMMEIR | 2330 | SALMMEIR BVBA | EU Direct | EU Direct | Den Berk BV | Salmmeir 1 | Active Docu incomplete | 2019-09-15 | UNIT | 362924 | ST | standard 30-60 | 2018 | No | NL South | HQ Jenbach | Z140-H75 | PT002371 | Z140-H75 | PT002372 | P135-H45 | PT002357 | P135-H45 | PT002358 | 1415365 | JMS | GEJ-1415365 | Salmmeir 1
31 | 1415410 | Greenhouse |  | Active Docu incomplete | -- | 2019-09-15 |  | 59999 | 2028-10-28 | 0 | 2018-10-29 | PREVENTIVE AND CORRECTIVE |  |  |  | XT4 | BE | NL | 2 | Y809 | SALMMEIR | M02 | 6 | 624 | K01 | GEJ-1415410 | No | Pre-chambers, Pre-chamber Sleeves, Pre-chamber Gaskets, Roller Tappets FV202 - Installation OPH: 6580 OPH Validation Duration: 10000 OPH FV186 - Installation OPH: 7264 OPH Validation Duration: 4000 OPH | Emma Lambert | FV202 - V17-B Redesign, FV203 - Field Oil Validation ExxonMobil Pegasus X25, FV186 - Roller Tappets | true | 1601596800000 | NG1 | n.a. | TD125-F2K9 | T-04946 | 1222808 | TDPS | -- | RIJKEVORSEL | V4.07.00 | Patrick de Jong | Direct Channel | 50 |  | ENG JMS 624 K01 50__J_Y809 | 5785330 | 1415367 | L | 500 mg/Nm3 | Jenbacher | SALMMEIR | 2310 | SALMMEIR BVBA | EU Direct | EU Direct | SALMMEIR | Salmmeir 2 | Active Docu incomplete | 2019-09-15 | UNIT | 362924 | ST | standard 30-60 | 2018 | No | NL South | HQ Jenbach | Z140-H75 | PT002373 | Z140-H75 | PT002374 | P135-H45 | PT002359 | P135-H45 | PT002360 | 1415367 | JMS | GEJ-1415367 | Salmmeir 2

## dataItems
| Activation Status | AGG_AssetAvailability | AGG_AssetPerformanceRate | AGG_AssetReliabilityRate | asset_status | ATD1 | ATD2 | Aux_CH4Cont | Q Gas P | Aux_GasRail_rDPr_SetAct | Aux_GasRail_rPr_a_Filt | Aux_GasRail_rPr_Out_Calc | Aux_GasRail_rPr_sp | Q Gas T | Q Gas B/N | Aux_O2Cont | Aux_PreChambDifPress | Aux_PreChambGasTrain_rDPr_SetAct | Aux_PreChambGasTrain_rPr_a_Filt | Aux_PreChambGasTrain_rPr_Out | Aux_PreChambGasTrain_rPr_sp | Aux_PreChambGasTrainPress | Aux_RoomTemp | Aux_rPr_Baro | Aux_StarterPressInlet | Aux_StarterPressTank | Aux_StarterSpeed | Aux_SucPress | Aux_TempOutDoor | auxiliariesgeneral_rdpr_ofu_filt | auxiliariesgeneral_reo_level | auxiliariesgeneral_rpr_eo_diff_f | auxiliariesgeneral_rpr_eoap | auxiliariesgeneral_rpr_eof_diffmon | auxiliariesgeneral_rpr_ofuafilt | auxiliariesgeneral_rpr_ofubcentrifuge | auxiliariesgeneral_rpr_ofubfilt | BaseProg_Vers | BBFRULABS_RUL | Bear_Conrod_Temp01 | Bear_Conrod_Temp02 | Bear_Conrod_Temp03 | Bear_Conrod_Temp04 | Bear_Conrod_Temp05 | Bear_Conrod_Temp06 | Bear_Conrod_Temp07 | Bear_Conrod_Temp08 | Bear_Conrod_Temp09 | Bear_Conrod_Temp10 | Bear_Conrod_Temp11 | Bear_Conrod_Temp12 | Bear_Conrod_Temp13 | Bear_Conrod_Temp14 | Bear_Conrod_Temp15 | Bear_Conrod_Temp16 | Bear_Conrod_Temp17 | Bear_Conrod_Temp18 | Bear_Conrod_Temp19 | Bear_Conrod_Temp20 | Bear_Conrod_Temp21 | Bear_Conrod_Temp22 | Bear_Conrod_Temp23 | Bear_Conrod_Temp24 | Bear_Conrod_TempMax | Bear_Main_Temp01 | Bear_Main_Temp02 | Bear_Main_Temp03 | Bear_Main_Temp04 | Bear_Main_Temp05 | Bear_Main_Temp06 | Bear_Main_Temp07 | Bear_Main_Temp08 | Bear_Main_Temp09 | Bear_Main_Temp10 | Bear_Main_Temp11 | Bear_Main_TempMax | bFS_Req | bLoad | bp_red_active | bScavDone | bSync | bT_ECW_Ok | bT_EO_Ok | ChannelPartnerRegion | chargingunit_rvol_ch_engine_norm | CMU_rDPr_AirFilt_A | CMU_rDPr_AirFilt_B | CMU_rDPr_BbFilt | CMU_rDPr_Ch_AirFilt | CMU_rDPr_Ch_FA | CMU_rDPr_Ch_HPCooler | CMU_rDPr_Ch_LPCooler | CMU_rPr_a_BbFilt | CMU_rPr_a_BbFilt_A | CMU_rPr_a_BbFilt_B | CMU_rPr_Ch_P2bFA | CMU_rPr_Ch_P2HP | CMU_rPr_Ch_P2LP | CMU_rPr_f_BbFilt | CMU_rPr_f_BbFilt_A | CMU_rPr_f_BbFilt_B | Combustion_Quality_Cyl01 | Combustion_Quality_Cyl02 | Combustion_Quality_Cyl03 | Combustion_Quality_Cyl04 | Combustion_Quality_Cyl05 | Combustion_Quality_Cyl06 | Combustion_Quality_Cyl07 | Combustion_Quality_Cyl08 | Combustion_Quality_Cyl09 | Combustion_Quality_Cyl10 | Combustion_Quality_Cyl11 | Combustion_Quality_Cyl12 | Combustion_Quality_Cyl13 | Combustion_Quality_Cyl14 | Combustion_Quality_Cyl15 | Combustion_Quality_Cyl16 | Combustion_Quality_Cyl17 | Combustion_Quality_Cyl18 | Combustion_Quality_Cyl19 | Combustion_Quality_Cyl20 | Combustion_Quality_Cyl21 | Combustion_Quality_Cyl22 | Combustion_Quality_Cyl23 | Combustion_Quality_Cyl24 | Combustion_Quality_Max_Cyl01 | Combustion_Quality_Max_Cyl02 | Combustion_Quality_Max_Cyl03 | Combustion_Quality_Max_Cyl04 | Combustion_Quality_Max_Cyl05 | Combustion_Quality_Max_Cyl06 | Combustion_Quality_Max_Cyl07 | Combustion_Quality_Max_Cyl08 | Combustion_Quality_Max_Cyl09 | Combustion_Quality_Max_Cyl10 | Combustion_Quality_Max_Cyl11 | Combustion_Quality_Max_Cyl12 | Combustion_Quality_Max_Cyl13 | Combustion_Quality_Max_Cyl14 | Combustion_Quality_Max_Cyl15 | Combustion_Quality_Max_Cyl16 | Combustion_Quality_Max_Cyl17 | Combustion_Quality_Max_Cyl18 | Combustion_Quality_Max_Cyl19 | Combustion_Quality_Max_Cyl20 | Combustion_Quality_Max_Cyl21 | Combustion_Quality_Max_Cyl22 | Combustion_Quality_Max_Cyl23 | Combustion_Quality_Max_Cyl24 | Cooling_Water_Degassing | Cooling_Water_TopUp | Count_Count1 | Count_Count2 | Count_Count3 | Count_Count4 | Count_Counter1 | Count_Counter10 | Count_Counter2 | Count_Counter3 | Count_Counter4 | Count_Counter5 | Count_Counter6 | Count_Counter7 | Count_Counter8 | Count_Counter9 | Count_Maintenance1 | Count_Maintenance2 | Count_Maintenance3 | Count_Maintenance4 | Count_Maintenance5 | Count_Maintenance6 | Count_Maintenance7 | Count_Maintenance8 | oph | Count_OpHour_Billing | Count_OpHourGenSet | Count_OpHourManual | Starts | CtrMixTemp_W | CtrMixTemp_X | CtrMixTemp_Y | CtrModule_Ctr10_W | CtrModule_Ctr10_X | CtrModule_Ctr10_Y | CtrModule_Ctr11_W | CtrModule_Ctr11_X | CtrModule_Ctr11_Y | CtrModule_Ctr12_W | CtrModule_Ctr12_X | CtrModule_Ctr12_Y | CtrModule_Ctr13_W | CtrModule_Ctr13_X | CtrModule_Ctr13_Y | CtrModule_Ctr14_W | CtrModule_Ctr14_X | CtrModule_Ctr14_Y | CtrModule_Ctr15_W | CtrModule_Ctr15_X | CtrModule_Ctr15_Y | CtrModule_Ctr16_W | CtrModule_Ctr16_X | CtrModule_Ctr16_Y | CtrModule_Ctr1_W | CtrModule_Ctr1_X | CtrModule_Ctr1_Y | CtrModule_Ctr2_W | CtrModule_Ctr2_X | CtrModule_Ctr2_Y | CtrModule_Ctr3_W | CtrModule_Ctr3_X | CtrModule_Ctr3_Y | CtrModule_Ctr4_W | CtrModule_Ctr4_X | CtrModule_Ctr4_Y | CtrModule_Ctr5_W | CtrModule_Ctr5_X | CtrModule_Ctr5_Y | CtrModule_Ctr6_W | CtrModule_Ctr6_X | CtrModule_Ctr6_Y | CtrModule_Ctr7_W | CtrModule_Ctr7_X | CtrModule_Ctr7_Y | CtrModule_Ctr8_W | CtrModule_Ctr8_X | CtrModule_Ctr8_Y | cust_analoginput_ai001_value | cust_analoginput_ai002_value | cust_analoginput_ai003_value | cust_analoginput_ai004_value | cust_analoginput_ai005_value | cust_analoginput_ai006_value | cust_analoginput_ai007_value | cust_analoginput_ai008_value | cust_analoginput_ai009_value | cust_analoginput_ai010_value | cust_analoginput_ai011_value | cust_analoginput_ai012_value | cust_analoginput_ai013_value | cust_analoginput_ai014_value | cust_analoginput_ai015_value | cust_analoginput_ai016_value | cust_analoginput_ai017_value | cust_analoginput_ai018_value | cust_analoginput_ai019_value | cust_analoginput_ai020_value | cust_analoginput_ai021_value | cust_analoginput_ai022_value | cust_analoginput_ai023_value | cust_analoginput_ai024_value | cust_analoginput_ai025_value | cust_analoginput_ai026_value | cust_analoginput_ai027_value | cust_analoginput_ai028_value | cust_analoginput_ai029_value | cust_analoginput_ai030_value | cust_analoginput_ai031_value | cust_analoginput_ai032_value | cust_analoginput_ai033_value | cust_analoginput_ai034_value | cust_analoginput_ai035_value | cust_analoginput_ai036_value | cust_analoginput_ai037_value | cust_analoginput_ai038_value | cust_analoginput_ai039_value | cust_analoginput_ai040_value | cust_analoginput_ai041_value | cust_analoginput_ai042_value | cust_analoginput_ai043_value | cust_analoginput_ai044_value | cust_analoginput_ai045_value | cust_analoginput_ai046_value | cust_analoginput_ai047_value | cust_analoginput_ai048_value | cust_analoginput_ai049_value | cust_analoginput_ai050_value | cust_analoginput_ai051_value | cust_analoginput_ai052_value | cust_analoginput_ai053_value | cust_analoginput_ai054_value | cust_analoginput_ai055_value | cust_analoginput_ai056_value | cust_analoginput_ai057_value | cust_analoginput_ai058_value | cust_analoginput_ai059_value | cust_analoginput_ai060_value | custom_dpscrcatalyst_22ccfa | custom_engine_out_nox_mg_16583c | CylState_1 | CylState_10 | CylState_11 | CylState_12 | CylState_13 | CylState_14 | CylState_15 | CylState_16 | CylState_17 | CylState_18 | CylState_19 | CylState_2 | CylState_20 | CylState_3 | CylState_4 | CylState_5 | CylState_6 | CylState_7 | CylState_8 | CylState_9 | ec_lx2_bpoc_0 | ec_lx2_bpoc_1 | ec_lx2_bpoc_10 | ec_lx2_bpoc_2 | ec_lx2_bpoc_3 | ec_lx2_bpoc_4 | ec_lx2_bpoc_5 | ec_lx2_bpoc_6 | ec_lx2_bpoc_7 | ec_lx2_bpoc_8 | ec_lx2_bpoc_9 | ec_lx2_bpoc_gas_1_0 | ec_lx2_bpoc_gas_1_0_m | ec_lx2_bpoc_gas_1_1 | ec_lx2_bpoc_gas_1_10 | ec_lx2_bpoc_gas_1_10_m | ec_lx2_bpoc_gas_1_1_m | ec_lx2_bpoc_gas_1_2 | ec_lx2_bpoc_gas_1_2_m | ec_lx2_bpoc_gas_1_3 | ec_lx2_bpoc_gas_1_3_m | ec_lx2_bpoc_gas_1_4 | ec_lx2_bpoc_gas_1_4_m | ec_lx2_bpoc_gas_1_5 | ec_lx2_bpoc_gas_1_5_m | ec_lx2_bpoc_gas_1_6 | ec_lx2_bpoc_gas_1_6_m | ec_lx2_bpoc_gas_1_7 | ec_lx2_bpoc_gas_1_7_m | ec_lx2_bpoc_gas_1_8 | ec_lx2_bpoc_gas_1_8_m | ec_lx2_bpoc_gas_1_9 | ec_lx2_bpoc_gas_1_9_m | ec_lx2_bpoc_gas_2_0 | ec_lx2_bpoc_gas_2_0_m | ec_lx2_bpoc_gas_2_1 | ec_lx2_bpoc_gas_2_10 | ec_lx2_bpoc_gas_2_10_m | ec_lx2_bpoc_gas_2_1_m | ec_lx2_bpoc_gas_2_2 | ec_lx2_bpoc_gas_2_2_m | ec_lx2_bpoc_gas_2_3 | ec_lx2_bpoc_gas_2_3_m | ec_lx2_bpoc_gas_2_4 | ec_lx2_bpoc_gas_2_4_m | ec_lx2_bpoc_gas_2_5 | ec_lx2_bpoc_gas_2_5_m | ec_lx2_bpoc_gas_2_6 | ec_lx2_bpoc_gas_2_6_m | ec_lx2_bpoc_gas_2_7 | ec_lx2_bpoc_gas_2_7_m | ec_lx2_bpoc_gas_2_8 | ec_lx2_bpoc_gas_2_8_m | ec_lx2_bpoc_gas_2_9 | ec_lx2_bpoc_gas_2_9_m | ec_lx2_bpoc_gas_3_0 | ec_lx2_bpoc_gas_3_0_m | ec_lx2_bpoc_gas_3_1 | ec_lx2_bpoc_gas_3_10 | ec_lx2_bpoc_gas_3_10_m | ec_lx2_bpoc_gas_3_1_m | ec_lx2_bpoc_gas_3_2 | ec_lx2_bpoc_gas_3_2_m | ec_lx2_bpoc_gas_3_3 | ec_lx2_bpoc_gas_3_3_m | ec_lx2_bpoc_gas_3_4 | ec_lx2_bpoc_gas_3_4_m | ec_lx2_bpoc_gas_3_5 | ec_lx2_bpoc_gas_3_5_m | ec_lx2_bpoc_gas_3_6 | ec_lx2_bpoc_gas_3_6_m | ec_lx2_bpoc_gas_3_7 | ec_lx2_bpoc_gas_3_7_m | ec_lx2_bpoc_gas_3_8 | ec_lx2_bpoc_gas_3_8_m | ec_lx2_bpoc_gas_3_9 | ec_lx2_bpoc_gas_3_9_m | ec_lx2_bpoc_gas_4_0 | ec_lx2_bpoc_gas_4_0_m | ec_lx2_bpoc_gas_4_1 | ec_lx2_bpoc_gas_4_10 | ec_lx2_bpoc_gas_4_10_m | ec_lx2_bpoc_gas_4_1_m | ec_lx2_bpoc_gas_4_2 | ec_lx2_bpoc_gas_4_2_m | ec_lx2_bpoc_gas_4_3 | ec_lx2_bpoc_gas_4_3_m | ec_lx2_bpoc_gas_4_4 | ec_lx2_bpoc_gas_4_4_m | ec_lx2_bpoc_gas_4_5 | ec_lx2_bpoc_gas_4_5_m | ec_lx2_bpoc_gas_4_6 | ec_lx2_bpoc_gas_4_6_m | ec_lx2_bpoc_gas_4_7 | ec_lx2_bpoc_gas_4_7_m | ec_lx2_bpoc_gas_4_8 | ec_lx2_bpoc_gas_4_8_m | ec_lx2_bpoc_gas_4_9 | ec_lx2_bpoc_gas_4_9_m | Efficiency_Estimate_1_Median | Efficiency_Estimtate_1 | emission_bamm_nox_noxs_engout_avg | emission_blx2_active | emission_blx2_ctrl_enable | emission_bnoxs_catout_heater_ok | emission_bnoxs_catout_nox_ok | emission_bnoxs_catout_nox_validity_ok | emission_bnoxs_catout_o2_ok | emission_bnoxs_catout_o2_validity_ok | emission_bnoxs_catout_power_ok | emission_bnoxs_engout_a_heater_ok | emission_bnoxs_engout_a_nox_ok | emission_bnoxs_engout_a_nox_validity_ok | emission_bnoxs_engout_a_o2_ok | emission_bnoxs_engout_a_o2_validity_ok | emission_bnoxs_engout_a_power_ok | emission_bnoxs_engout_b_heater_ok | emission_bnoxs_engout_b_nox_ok | emission_bnoxs_engout_b_nox_validity_ok | emission_bnoxs_engout_b_o2_ok | emission_bnoxs_engout_b_o2_validity_ok | emission_bnoxs_engout_b_power_ok | emission_bnoxs_engout_heater_ok | emission_bnoxs_engout_nox_ok | emission_bnoxs_engout_nox_validity_ok | emission_bnoxs_engout_o2_ok | emission_bnoxs_engout_o2_validity_ok | emission_bnoxs_engout_power_ok | emission_bscr_emvalve1_cg_dem | emission_bscr_emvalve1_sg_dem | emission_bscr_extemadjust_run | emission_bscr_injectvalve_urea | emission_cnt_noxs_engout_lastdiag | emission_diff_pres_cat_max | emission_icnt_nox_em_monlim_exc | emission_inoxs_catout_ophours | emission_inoxs_engout_a_ophours | emission_inoxs_engout_b_ophours | emission_inoxs_engout_ophours | emission_nox_noxs_engout_durdiag | emission_o2_noxs_engout_durdiag | emission_pc_noxs_engout_diagresult | emission_rco_em_avgshortterm | emission_rco_em_monlim_hi | emission_rco_scr_catout_avg | emission_rco_scr_cemsextcatout | emission_rco_scr_emline1 | emission_rdpr_scr_cat | emission_rflow_scr_ureadosingout | emission_rflow_scr_ureadosingunit_ff | emission_rhum_catout | emission_rno2_scr_cemsextcatout | emission_rno2_scr_emline1 | emission_rno_scr_cemsextcatout | emission_rno_scr_emline1 | emission_rnox_em_avgdaily | emission_rnox_em_avgdaily_all | emission_rnox_em_avgshortterm | emission_rnox_em_engout_set | emission_rnox_em_monlim_hi | emission_rnox_em_monlim_hitol | emission_rnox_noxs_catout | emission_rnox_noxs_catout_durdiag | emission_rnox_noxs_catout_mg | emission_rnox_noxs_engout | emission_rnox_noxs_engout_a | emission_rnox_noxs_engout_a_durdiag | emission_rnox_noxs_engout_a_mg | emission_rnox_noxs_engout_avg | emission_rnox_noxs_engout_b | emission_rnox_noxs_engout_b_durdiag | emission_rnox_noxs_engout_b_mg | emission_rnox_noxs_engout_mg | emission_rnox_noxs_engout_mg_avg | emission_rnox_scr_catout_avg | emission_ro2_noxs_catout | emission_ro2_noxs_catout_durdiag | emission_ro2_noxs_catout_filt | emission_ro2_noxs_engout | emission_ro2_noxs_engout_a | emission_ro2_noxs_engout_a_durdiag | emission_ro2_noxs_engout_a_filt | emission_ro2_noxs_engout_avg_filt | emission_ro2_noxs_engout_b | emission_ro2_noxs_engout_b_durdiag | emission_ro2_noxs_engout_b_filt | emission_ro2_noxs_engout_filt | emission_ro2_scr_cemsextcatout | emission_rpc_noxs_catout_diagresult | emission_rpc_noxs_engout_a_diagresult | emission_rpc_noxs_engout_b_diagresult | emission_rpr_scr_catin | emission_rpr_scr_catout | emission_rpr_scr_comprairsupply | emission_rpr_scr_ureadosingin | emission_rpr_scr_ureadosingout | emission_rt_scr_catavg | emission_rt_scr_catin | emission_rt_scr_catout | emission_rvol_scr_ureaconsumption | Engine_OpHour_Fixed_Timestamp | Engine_Slowdown_Time_Detection | Engine_Slowdown_Time_Monitoring_Sec | Engine_Slowdown_Time_Oil_Correction | enginecontroller_blx2_ss | enginecontroller_rhum_airin_abs | enginecontroller_rhum_airin_rel | enginecontroller_rpr_p2s_lx2 | Estimated_Compressor_Bypass_Position | Estimated_IntakeTemperatureRange | exhaust_bscavvalve | exhaust_icnt_ophours_oxi | Exhaust_NOx_NOx1 | Exhaust_NOx_NOx2 | Exhaust_NOx_O2_1 | Exhaust_NOx_O2_2 | exhaust_rpr_oxicat_diff | exhaust_rpr_oxicat_in | exhaust_rpr_oxicat_in_fast | exhaust_rpr_oxicat_in_fast_peak | Exhaust_TCSpeedA | Exhaust_TCSpeedB | Exhaust_TCSpeedLPA | Exhaust_TCSpeedLPB | Exhaust_TempBoil | Exhaust_TempCat | Exhaust_TempCatIn | Exhaust_TempCatOut | Exhaust_TempCyl01 | Exhaust_TempCyl02 | Exhaust_TempCyl03 | Exhaust_TempCyl04 | Exhaust_TempCyl05 | Exhaust_TempCyl06 | Exhaust_TempCyl07 | Exhaust_TempCyl08 | Exhaust_TempCyl09 | Exhaust_TempCyl10 | Exhaust_TempCyl11 | Exhaust_TempCyl12 | Exhaust_TempCyl13 | Exhaust_TempCyl14 | Exhaust_TempCyl15 | Exhaust_TempCyl16 | Exhaust_TempCyl17 | Exhaust_TempCyl18 | Exhaust_TempCyl19 | Exhaust_TempCyl20 | Exhaust_TempCyl21 | Exhaust_TempCyl22 | Exhaust_TempCyl23 | Exhaust_TempCyl24 | Exhaust_TempCylAvg | Exhaust_TempCylAvg_ss | Exhaust_TempCylMax | Exhaust_TempCylMax_ss | Exhaust_TempCylMin | Exhaust_TempCylMin_ss | Exhaust_TempETCIn | Exhaust_TempHexIn | Exhaust_TempHexOut | Exhaust_TempLPTCOutletA | Exhaust_TempLPTCOutletB | Exhaust_TempMaxSpread | Exhaust_TempThermReact1Avg | Exhaust_TempThermReact2Avg | G2_Knck_Abs01 | G2_Knck_Abs02 | G2_Knck_Abs03 | G2_Knck_Abs04 | G2_Knck_Abs05 | G2_Knck_Abs06 | G2_Knck_Abs07 | G2_Knck_Abs08 | G2_Knck_Abs09 | G2_Knck_Abs10 | G2_Knck_Abs11 | G2_Knck_Abs12 | G2_Knck_Abs13 | G2_Knck_Abs14 | G2_Knck_Abs15 | G2_Knck_Abs16 | G2_Knck_Abs17 | G2_Knck_Abs18 | G2_Knck_Abs19 | G2_Knck_Abs20 | G2_Knck_Rel01 | G2_Knck_Rel02 | G2_Knck_Rel03 | G2_Knck_Rel04 | G2_Knck_Rel05 | G2_Knck_Rel06 | G2_Knck_Rel07 | G2_Knck_Rel08 | G2_Knck_Rel09 | G2_Knck_Rel10 | G2_Knck_Rel11 | G2_Knck_Rel12 | G2_Knck_Rel13 | G2_Knck_Rel14 | G2_Knck_Rel15 | G2_Knck_Rel16 | G2_Knck_Rel17 | G2_Knck_Rel18 | G2_Knck_Rel19 | G2_Knck_Rel20 | gas_qualmix | gas_type | Gasmixer_AirThrot | Gasmixer_AirThrotEnc1 | Gasmixer_AirThrotEnc2 | Gasmixer_GasMix1Pos | Gasmixer_GasMix2Pos | Gasmixer_GasThrot | gastrain_icnt_gas_normm3 | gastrain_icnt_gas_opm3 | GasTrain_PressBaro | GasTrain_PressMain | gastrain_rpr_gr_avg | GasTrain_TempMain | Gen2_ContGen | generator_boilskid_fan_dem | generator_rflow_oilskid_de | generator_rflow_oilskid_nde | generator_rlev_oilskid_tank | generator_rpr_oilskid_hp_de | generator_rpr_oilskid_hp_nde | generator_rt_oilskid_tank | Generator_TempBear1 | Generator_TempBear2 | Generator_TempInlet | Generator_TempOutlet | Generator_TempWind1 | Generator_TempWind2 | Generator_TempWind3 | Generator_VoltExit | Geno_BearingTempMeasured_DriveEnd | Geno_BearingTempMeasured_NonDriveEnd | Geno_BearingTempPrediction_DriveEnd | Geno_BearingTempPrediction_NonDriveEnd | Genset_Oph_Recalculation_Start_Point | GenSet_OpHour_Fixed_Timestamp | GenSet_OpHours_Backup | halio_power_apparent_s | halio_power_fact_cos_phi | halio_rf_mmd | halio_rf_mmd_2 | halio_ru_bus_l1_2 | halio_ru_bus_l1n | halio_ru_bus_l2_3 | halio_ru_bus_l2n | halio_ru_bus_l3_1 | halio_ru_bus_l3n | halio_ru_l1_2 | halio_ru_l1n | halio_ru_l2_3 | halio_ru_l2n | halio_ru_l3_1 | halio_ru_l3n | heatingcooling_rt_ecwbeng | Hyd_OilCount_Trend_ActiveEnergy | Hyd_OilCount_Trend_AvgPower | Hyd_OilCount_Trend_DeltaOpH | Hyd_OilCount_Trend_OilConsumption | Hyd_OilCount_Trend_OilVolume | Hyd_PressCoolWat | Hyd_PressCrankCase | Hyd_PressOil | Hyd_PressOilDif | Hyd_PressOilDif1 | Hyd_PressTCOilFiltIn | Hyd_TempCoolWat | Hyd_TempOil | Hyd_TempOilPumpOut | Hyd_TempWatRet | Hyd_TempWatRetCoolOut | Hyd_TempWatRetPreEng | iDays_SinceStart | Ignition_IC_HW_Vers | Ignition_IC_SW_Vers | Ignition_ITPAvg | Ignition_ITPCyl01 | Ignition_ITPCyl02 | Ignition_ITPCyl03 | Ignition_ITPCyl04 | Ignition_ITPCyl05 | Ignition_ITPCyl06 | Ignition_ITPCyl07 | Ignition_ITPCyl08 | Ignition_ITPCyl09 | Ignition_ITPCyl10 | Ignition_ITPCyl11 | Ignition_ITPCyl12 | Ignition_ITPCyl13 | Ignition_ITPCyl14 | Ignition_ITPCyl15 | Ignition_ITPCyl16 | Ignition_ITPCyl17 | Ignition_ITPCyl18 | Ignition_ITPCyl19 | Ignition_ITPCyl20 | Ignition_ITPCyl21 | Ignition_ITPCyl22 | Ignition_ITPCyl23 | Ignition_ITPCyl24 | Ignition_SAFI_ElectTemp1 | Ignition_SAFI_ElectTemp10 | Ignition_SAFI_ElectTemp11 | Ignition_SAFI_ElectTemp12 | Ignition_SAFI_ElectTemp2 | Ignition_SAFI_ElectTemp3 | Ignition_SAFI_ElectTemp4 | Ignition_SAFI_ElectTemp5 | Ignition_SAFI_ElectTemp6 | Ignition_SAFI_ElectTemp7 | Ignition_SAFI_ElectTemp8 | Ignition_SAFI_ElectTemp9 | Ignition_SAFI_FilterVers1 | Ignition_SAFI_FilterVers10 | Ignition_SAFI_FilterVers11 | Ignition_SAFI_FilterVers12 | Ignition_SAFI_FilterVers2 | Ignition_SAFI_FilterVers3 | Ignition_SAFI_FilterVers4 | Ignition_SAFI_FilterVers5 | Ignition_SAFI_FilterVers6 | Ignition_SAFI_FilterVers7 | Ignition_SAFI_FilterVers8 | Ignition_SAFI_FilterVers9 | Ignition_SAFI_HW_Vers1 | Ignition_SAFI_HW_Vers10 | Ignition_SAFI_HW_Vers11 | Ignition_SAFI_HW_Vers12 | Ignition_SAFI_HW_Vers2 | Ignition_SAFI_HW_Vers3 | Ignition_SAFI_HW_Vers4 | Ignition_SAFI_HW_Vers5 | Ignition_SAFI_HW_Vers6 | Ignition_SAFI_HW_Vers7 | Ignition_SAFI_HW_Vers8 | Ignition_SAFI_HW_Vers9 | Ignition_SAFI_HWOpt_Vers1 | Ignition_SAFI_HWOpt_Vers10 | Ignition_SAFI_HWOpt_Vers11 | Ignition_SAFI_HWOpt_Vers12 | Ignition_SAFI_HWOpt_Vers2 | Ignition_SAFI_HWOpt_Vers3 | Ignition_SAFI_HWOpt_Vers4 | Ignition_SAFI_HWOpt_Vers5 | Ignition_SAFI_HWOpt_Vers6 | Ignition_SAFI_HWOpt_Vers7 | Ignition_SAFI_HWOpt_Vers8 | Ignition_SAFI_HWOpt_Vers9 | Ignition_SAFI_OpHours1 | Ignition_SAFI_OpHours10 | Ignition_SAFI_OpHours11 | Ignition_SAFI_OpHours12 | Ignition_SAFI_OpHours2 | Ignition_SAFI_OpHours3 | Ignition_SAFI_OpHours4 | Ignition_SAFI_OpHours5 | Ignition_SAFI_OpHours6 | Ignition_SAFI_OpHours7 | Ignition_SAFI_OpHours8 | Ignition_SAFI_OpHours9 | Ignition_SAFI_ProdDate1 | Ignition_SAFI_ProdDate10 | Ignition_SAFI_ProdDate10_day | Ignition_SAFI_ProdDate10_mon | Ignition_SAFI_ProdDate11 | Ignition_SAFI_ProdDate11_day | Ignition_SAFI_ProdDate11_mon | Ignition_SAFI_ProdDate12 | Ignition_SAFI_ProdDate12_day | Ignition_SAFI_ProdDate12_mon | Ignition_SAFI_ProdDate1_day | Ignition_SAFI_ProdDate1_mon | Ignition_SAFI_ProdDate2 | Ignition_SAFI_ProdDate2_day | Ignition_SAFI_ProdDate2_mon | Ignition_SAFI_ProdDate3 | Ignition_SAFI_ProdDate3_day | Ignition_SAFI_ProdDate3_mon | Ignition_SAFI_ProdDate4 | Ignition_SAFI_ProdDate4_day | Ignition_SAFI_ProdDate4_mon | Ignition_SAFI_ProdDate5 | Ignition_SAFI_ProdDate5_day | Ignition_SAFI_ProdDate5_mon | Ignition_SAFI_ProdDate6 | Ignition_SAFI_ProdDate6_day | Ignition_SAFI_ProdDate6_mon | Ignition_SAFI_ProdDate7 | Ignition_SAFI_ProdDate7_day | Ignition_SAFI_ProdDate7_mon | Ignition_SAFI_ProdDate8 | Ignition_SAFI_ProdDate8_day | Ignition_SAFI_ProdDate8_mon | Ignition_SAFI_ProdDate9 | Ignition_SAFI_ProdDate9_day | Ignition_SAFI_ProdDate9_mon | Ignition_SAFI_SerialNr1 | Ignition_SAFI_SerialNr10 | Ignition_SAFI_SerialNr11 | Ignition_SAFI_SerialNr12 | Ignition_SAFI_SerialNr2 | Ignition_SAFI_SerialNr3 | Ignition_SAFI_SerialNr4 | Ignition_SAFI_SerialNr5 | Ignition_SAFI_SerialNr6 | Ignition_SAFI_SerialNr7 | Ignition_SAFI_SerialNr8 | Ignition_SAFI_SerialNr9 | Ignition_SAFI_SW_Vers1 | Ignition_SAFI_SW_Vers10 | Ignition_SAFI_SW_Vers11 | Ignition_SAFI_SW_Vers12 | Ignition_SAFI_SW_Vers2 | Ignition_SAFI_SW_Vers3 | Ignition_SAFI_SW_Vers4 | Ignition_SAFI_SW_Vers5 | Ignition_SAFI_SW_Vers6 | Ignition_SAFI_SW_Vers7 | Ignition_SAFI_SW_Vers8 | Ignition_SAFI_SW_Vers9 | Ignition_SAFI_TeethError1 | Ignition_SAFI_TeethError10 | Ignition_SAFI_TeethError11 | Ignition_SAFI_TeethError12 | Ignition_SAFI_TeethError2 | Ignition_SAFI_TeethError3 | Ignition_SAFI_TeethError4 | Ignition_SAFI_TeethError5 | Ignition_SAFI_TeethError6 | Ignition_SAFI_TeethError7 | Ignition_SAFI_TeethError8 | Ignition_SAFI_TeethError9 | iSA_PICurGrad01 | iSA_PICurGrad02 | iSA_PICurGrad03 | iSA_PICurGrad04 | iSA_PICurGrad05 | iSA_PICurGrad06 | iSA_PICurGrad07 | iSA_PICurGrad08 | iSA_PICurGrad09 | iSA_PICurGrad10 | iSA_PICurGrad11 | iSA_PICurGrad12 | iSA_PICurGrad13 | iSA_PICurGrad14 | iSA_PICurGrad15 | iSA_PICurGrad16 | iSA_PICurGrad17 | iSA_PICurGrad18 | iSA_PICurGrad19 | iSA_PICurGrad20 | Issue_Eng_OpHour | Issue_GenSet_OpHour | item_count | Knock_KLS90_CurrSensor1 | Knock_KLS90_CurrSensor2 | Knock_KLS98_IntKnock_Cyl01 | Knock_KLS98_IntKnock_Cyl02 | Knock_KLS98_IntKnock_Cyl03 | Knock_KLS98_IntKnock_Cyl04 | Knock_KLS98_IntKnock_Cyl05 | Knock_KLS98_IntKnock_Cyl06 | Knock_KLS98_IntKnock_Cyl07 | Knock_KLS98_IntKnock_Cyl08 | Knock_KLS98_IntKnock_Cyl09 | Knock_KLS98_IntKnock_Cyl10 | Knock_KLS98_IntKnock_Cyl11 | Knock_KLS98_IntKnock_Cyl12 | Knock_KLS98_IntKnock_Cyl13 | Knock_KLS98_IntKnock_Cyl14 | Knock_KLS98_IntKnock_Cyl15 | Knock_KLS98_IntKnock_Cyl16 | Knock_KLS98_IntKnock_Cyl17 | Knock_KLS98_IntKnock_Cyl18 | Knock_KLS98_IntKnock_Cyl19 | Knock_KLS98_IntKnock_Cyl20 | Knock_KLS98_IntKnock_Cyl21 | Knock_KLS98_IntKnock_Cyl22 | Knock_KLS98_IntKnock_Cyl23 | Knock_KLS98_IntKnock_Cyl24 | Safi W1 Z01 | Safi W1 Z02 | Safi W1 Z03 | Safi W1 Z04 | Safi W1 Z05 | Safi W1 Z06 | Safi W1 Z07 | Safi W1 Z08 | Safi W1 Z09 | Safi W1 Z10 | Safi W1 Z11 | Safi W1 Z12 | Safi W1 Z13 | Safi W1 Z14 | Safi W1 Z15 | Safi W1 Z16 | Safi W1 Z17 | Safi W1 Z18 | Safi W1 Z19 | Safi W1 Z20 | Safi W1 Z21 | Safi W1 Z22 | Safi W1 Z23 | Safi W1 Z24 | Knock_KLS98_SW_Vers | Knock_PBC_KnockPress_Avg | Knock_PBC_KnockPress_Cyl01 | Knock_PBC_KnockPress_Cyl02 | Knock_PBC_KnockPress_Cyl03 | Knock_PBC_KnockPress_Cyl04 | Knock_PBC_KnockPress_Cyl05 | Knock_PBC_KnockPress_Cyl06 | Knock_PBC_KnockPress_Cyl07 | Knock_PBC_KnockPress_Cyl08 | Knock_PBC_KnockPress_Cyl09 | Knock_PBC_KnockPress_Cyl10 | Knock_PBC_KnockPress_Cyl11 | Knock_PBC_KnockPress_Cyl12 | Knock_PBC_KnockPress_Cyl13 | Knock_PBC_KnockPress_Cyl14 | Knock_PBC_KnockPress_Cyl15 | Knock_PBC_KnockPress_Cyl16 | Knock_PBC_KnockPress_Cyl17 | Knock_PBC_KnockPress_Cyl18 | Knock_PBC_KnockPress_Cyl19 | Knock_PBC_KnockPress_Cyl20 | Knock_PBC_KnockPress_Cyl21 | Knock_PBC_KnockPress_Cyl22 | Knock_PBC_KnockPress_Cyl23 | Knock_PBC_KnockPress_Cyl24 | Knock_PBC_KnockPress_Max | Knock_PBC_KnockPress_Min | Knock_PBC_PMax_Avg | Knock_PBC_PMax_Cyl01 | Knock_PBC_PMax_Cyl02 | Knock_PBC_PMax_Cyl03 | Knock_PBC_PMax_Cyl04 | Knock_PBC_PMax_Cyl05 | Knock_PBC_PMax_Cyl06 | Knock_PBC_PMax_Cyl07 | Knock_PBC_PMax_Cyl08 | Knock_PBC_PMax_Cyl09 | Knock_PBC_PMax_Cyl10 | Knock_PBC_PMax_Cyl11 | Knock_PBC_PMax_Cyl12 | Knock_PBC_PMax_Cyl13 | Knock_PBC_PMax_Cyl14 | Knock_PBC_PMax_Cyl15 | Knock_PBC_PMax_Cyl16 | Knock_PBC_PMax_Cyl17 | Knock_PBC_PMax_Cyl18 | Knock_PBC_PMax_Cyl19 | Knock_PBC_PMax_Cyl20 | Knock_PBC_PMax_Cyl21 | Knock_PBC_PMax_Cyl22 | Knock_PBC_PMax_Cyl23 | Knock_PBC_PMax_Cyl24 | Knock_PBC_PMax_Max | Knock_PBC_PMax_Min | Safi W2 Z01 | Safi W2 Z02 | Safi W2 Z03 | Safi W2 Z04 | Safi W2 Z05 | Safi W2 Z06 | Safi W2 Z07 | Safi W2 Z08 | Safi W2 Z09 | Safi W2 Z10 | Safi W2 Z11 | Safi W2 Z12 | Safi W2 Z13 | Safi W2 Z14 | Safi W2 Z15 | Safi W2 Z16 | Safi W2 Z17 | Safi W2 Z18 | Safi W2 Z19 | Safi W2 Z20 | Safi W2 Z21 | Safi W2 Z22 | Safi W2 Z23 | Safi W2 Z24 | Leanox_P2Error | Leanox_P2Set | Leanox_RatioMix | LVRT_Events | manualdata_valverecession_EngineOpH | manualdata_valverecession_EngineStarts | manualdata_valverecession_lev_cyl01 | manualdata_valverecession_lev_cyl02 | manualdata_valverecession_lev_cyl03 | manualdata_valverecession_lev_cyl04 | manualdata_valverecession_lev_cyl05 | manualdata_valverecession_lev_cyl06 | manualdata_valverecession_lev_cyl07 | manualdata_valverecession_lev_cyl08 | manualdata_valverecession_lev_cyl09 | manualdata_valverecession_lev_cyl10 | manualdata_valverecession_lev_cyl11 | manualdata_valverecession_lev_cyl12 | manualdata_valverecession_lev_cyl13 | manualdata_valverecession_lev_cyl14 | manualdata_valverecession_lev_cyl15 | manualdata_valverecession_lev_cyl16 | manualdata_valverecession_lev_cyl17 | manualdata_valverecession_lev_cyl18 | manualdata_valverecession_lev_cyl19 | manualdata_valverecession_lev_cyl20 | manualdata_valverecession_lev_cyl21 | manualdata_valverecession_lev_cyl22 | manualdata_valverecession_lev_cyl23 | manualdata_valverecession_lev_cyl24 | manualdata_valverecession_liv_cyl01 | manualdata_valverecession_liv_cyl02 | manualdata_valverecession_liv_cyl03 | manualdata_valverecession_liv_cyl04 | manualdata_valverecession_liv_cyl05 | manualdata_valverecession_liv_cyl06 | manualdata_valverecession_liv_cyl07 | manualdata_valverecession_liv_cyl08 | manualdata_valverecession_liv_cyl09 | manualdata_valverecession_liv_cyl10 | manualdata_valverecession_liv_cyl11 | manualdata_valverecession_liv_cyl12 | manualdata_valverecession_liv_cyl13 | manualdata_valverecession_liv_cyl14 | manualdata_valverecession_liv_cyl15 | manualdata_valverecession_liv_cyl16 | manualdata_valverecession_liv_cyl17 | manualdata_valverecession_liv_cyl18 | manualdata_valverecession_liv_cyl19 | manualdata_valverecession_liv_cyl20 | manualdata_valverecession_liv_cyl21 | manualdata_valverecession_liv_cyl22 | manualdata_valverecession_liv_cyl23 | manualdata_valverecession_liv_cyl24 | manualdata_valverecession_rev_cyl01 | manualdata_valverecession_rev_cyl02 | manualdata_valverecession_rev_cyl03 | manualdata_valverecession_rev_cyl04 | manualdata_valverecession_rev_cyl05 | manualdata_valverecession_rev_cyl06 | manualdata_valverecession_rev_cyl07 | manualdata_valverecession_rev_cyl08 | manualdata_valverecession_rev_cyl09 | manualdata_valverecession_rev_cyl10 | manualdata_valverecession_rev_cyl11 | manualdata_valverecession_rev_cyl12 | manualdata_valverecession_rev_cyl13 | manualdata_valverecession_rev_cyl14 | manualdata_valverecession_rev_cyl15 | manualdata_valverecession_rev_cyl16 | manualdata_valverecession_rev_cyl17 | manualdata_valverecession_rev_cyl18 | manualdata_valverecession_rev_cyl19 | manualdata_valverecession_rev_cyl20 | manualdata_valverecession_rev_cyl21 | manualdata_valverecession_rev_cyl22 | manualdata_valverecession_rev_cyl23 | manualdata_valverecession_rev_cyl24 | manualdata_valverecession_riv_cyl01 | manualdata_valverecession_riv_cyl02 | manualdata_valverecession_riv_cyl03 | manualdata_valverecession_riv_cyl04 | manualdata_valverecession_riv_cyl05 | manualdata_valverecession_riv_cyl06 | manualdata_valverecession_riv_cyl07 | manualdata_valverecession_riv_cyl08 | manualdata_valverecession_riv_cyl09 | manualdata_valverecession_riv_cyl10 | manualdata_valverecession_riv_cyl11 | manualdata_valverecession_riv_cyl12 | manualdata_valverecession_riv_cyl13 | manualdata_valverecession_riv_cyl14 | manualdata_valverecession_riv_cyl15 | manualdata_valverecession_riv_cyl16 | manualdata_valverecession_riv_cyl17 | manualdata_valverecession_riv_cyl18 | manualdata_valverecession_riv_cyl19 | manualdata_valverecession_riv_cyl20 | manualdata_valverecession_riv_cyl21 | manualdata_valverecession_riv_cyl22 | manualdata_valverecession_riv_cyl23 | manualdata_valverecession_riv_cyl24 | MMD_CountEnergAct | MMD_CountEnergActReturn | MMD_CountEnergReact | MMD_CountEnergReactReturn | MMD_CurrAvg | MMD_HW_Vers1 | MMD_HW_Vers2 | MMD_PowerReact | MMD_SW_Vers1 | MMD_SW_Vers2 | MMD_VoltAvg | Module_Vers_AmmBase | Module_Vers_AuxiliariesGeneral | Module_Vers_CBM | Module_Vers_ChargingUnit | Module_Vers_Coupling | Module_Vers_Customized | Module_Vers_Emission | Module_Vers_EngineController | Module_Vers_EngineGeneral | Module_Vers_Exhaust | Module_Vers_GasMeteringUnit | Module_Vers_Gasmixer | Module_Vers_Gastrain | Module_Vers_Generator | Module_Vers_Grid | Module_Vers_HalIO | Module_Vers_HeatingCooling | Module_Vers_IC | Module_Vers_Ignition | Module_Vers_KLS98 | Module_Vers_Knocking | Module_Vers_MONIC | Module_Vers_NotConnected | Module_Vers_Opstate | Module_Vers_ParaBase | Module_Vers_SAFI | Module_Vers_Synchronization | Module_Vers_ThermalReactor | Module_Vers_Ventilation | Module_Vers_Visu | ModuleNumber | Monic_VoltAvg | Monic_VoltCyl01 | Monic_VoltCyl02 | Monic_VoltCyl03 | Monic_VoltCyl04 | Monic_VoltCyl05 | Monic_VoltCyl06 | Monic_VoltCyl07 | Monic_VoltCyl08 | Monic_VoltCyl09 | Monic_VoltCyl10 | Monic_VoltCyl11 | Monic_VoltCyl12 | Monic_VoltCyl13 | Monic_VoltCyl14 | Monic_VoltCyl15 | Monic_VoltCyl16 | Monic_VoltCyl17 | Monic_VoltCyl18 | Monic_VoltCyl19 | Monic_VoltCyl20 | Monic_VoltCyl21 | Monic_VoltCyl22 | Monic_VoltCyl23 | Monic_VoltCyl24 | Monic_VoltMax | Monic_VoltMin | OFRUL_RUL | oil_amb_temp | oil_cal_zero | oil_condition | oil_fe_bin_cnt_1 | oil_fe_bin_cnt_2 | oil_fe_bin_cnt_3 | oil_fe_bin_cnt_4 | oil_fe_bin_cnt_5 | oil_fe_bin_cnt_6 | oil_fe_bin_cnt_7 | oil_fe_bin_size_1 | oil_fe_bin_size_2 | oil_fe_bin_size_3 | oil_fe_bin_size_4 | oil_fe_bin_size_5 | oil_fe_bin_size_6 | oil_fe_bin_size_7 | oil_fe_mass | oil_gastops_status | oil_hw_version | oil_max_amb_temp | oil_nfe_bin_cnt_1 | oil_nfe_bin_cnt_2 | oil_nfe_bin_cnt_3 | oil_nfe_bin_cnt_4 | oil_nfe_bin_cnt_5 | oil_nfe_bin_cnt_6 | oil_nfe_bin_cnt_7 | oil_node_address | oil_oil_temp | Oil_Remaining_Useful_Life | Oil_Sample_Aluminium | Oil_Sample_Antimony | Oil_Sample_Appearance | Oil_Sample_Barium | Oil_Sample_Booked_In_Date | Oil_Sample_Boron | Oil_Sample_Cadmium | Oil_Sample_Calcium | Oil_Sample_Chromium | Oil_Sample_Colour | Oil_Sample_Conductivity | Oil_Sample_Copper | Oil_Sample_Date_Taken | Oil_Sample_Density15 | Oil_Sample_Glycol | Oil_Sample_Id | Oil_Sample_Insolubles | Oil_Sample_IPH | Oil_Sample_Iron | Oil_Sample_Lab_Memo | Oil_Sample_Lead | Oil_Sample_Magnesium | Oil_Sample_Manganese | Oil_Sample_Molybdenum | Oil_Sample_Nickel | Oil_Sample_Nitration | Oil_Sample_Oil_Added | Oil_Sample_Oil_Condition | Oil_Sample_Oil_Hours | Oil_Sample_Oxidation | Oil_Sample_Phosphorus | Oil_Sample_Potassium | Oil_Sample_Receipt_Date | Oil_Sample_Silicon | Oil_Sample_Silver | Oil_Sample_Sodium | Oil_Sample_TAN | Oil_Sample_TBN | Oil_Sample_Ticket_Number | Oil_Sample_Tin | Oil_Sample_Titanium | Oil_Sample_Unit_Hours | Oil_Sample_Vanadium | Oil_Sample_Viscosity100 | Oil_Sample_Viscosity40 | Oil_Sample_Water | Oil_Sample_Zinc | oil_serial_number | oil_serial_number_hi | oil_serial_type | oil_sw_version | Status | OperationalConditionNumeric | OperationalState | OpH_Jumps | OpH_Spikes | OpHours_BackUp_Counter | OPHSR_calc_OphToStart | opstate_iidx_omss | opstate_iidx_rss | out_ha_rf_mmd_busbar_1 | out_ha_rf_mmd_synch1_1 | out_ha_rf_mmd_synch1_2 | out_ha_rf_mmd_synch2_1 | out_ha_rf_mmd_synch2_2 | p_reddelta_ch4_norm | p_reddelta_ch_t1hp_norm | p_reddelta_cospctr_f_norm | p_reddelta_cospctr_t_norm | p_reddelta_cospctr_u_norm | p_reddelta_cv_norm | p_reddelta_egt_norm | p_reddelta_eta_gen_norm | p_reddelta_evu_norm | p_reddelta_gaspr_norm | p_reddelta_hictr_norm | p_reddelta_hum_norm | p_reddelta_knck_opti_norm | p_reddelta_leanox_norm | p_reddelta_pbc_norm | p_reddelta_pr_cc_norm | p_reddelta_pr_gr_norm | p_reddelta_pr_pcgt_norm | p_reddelta_suctpr_norm | p_reddelta_t_ecw_norm | p_reddelta_t_genairin_norm | p_reddelta_t_genswitchcab_norm | p_reddelta_t_hwr_norm | p_reddelta_t_inairer_norm | p_reddelta_t_oil_norm | p_reddelta_t_transformer_norm | p_reddelta_tc_norm | p_unred | Para_Aux_AirStart_HysMaxInlet | Para_Aux_AirStart_HysMin1 | Para_Aux_AirStart_HysMinInlet | Para_Aux_AirStart_LimitMaxInlet | Para_Aux_AirStart_LimitMin1 | Para_Aux_AirStart_LimitMinInlet | Para_Aux_AirStart_N_AirStarter_Exist | Para_Aux_AirStart_Pr_AirStarter_Supply_Exist | Para_Aux_AirStart_Pr_AirStarter_Supply_HiHi | Para_Aux_AirStart_Pr_AirStarter_Supply_LoLo | Para_Aux_AirStart_Pr_AirStarter_SupplyScalMax | Para_Aux_AirStart_Pr_AirStarter_SupplyScalMin | Para_Aux_AirStart_Pr_AirStarter_Tank_Exist | Para_Aux_AirStart_Pr_AirStarter_Tank_Lo | Para_Aux_AirStart_Pr_AirStarter_TankScalMax | Para_Aux_AirStart_Pr_AirStarter_TankScalMin | Para_Aux_AirStart_StartTime | Para_Aux_AirStart_tiAirStarter_OnTime | Para_Aux_AuxChC_Visible | Para_Aux_BarometricPress_Pr_Baro_Exist | Para_Aux_BarometricPress_Pr_Baro_site | Para_Aux_BarometricPress_Pr_Baro_siteDevMax | Para_Aux_BHV_Active | Para_Aux_BoP_BOP_ChCoolCirc_Act | Para_Aux_BoP_BOP_EmCoolCirc_Act | Para_Aux_BoP_BOP_ERVent_Act | Para_Aux_BoP_BOP_ExhGasSys_Act | Para_Aux_BoP_BOP_HeatCirc_Act | Para_Aux_BoP_BOP_MainGasPrep_Act | Para_Aux_CDP_Active | Para_Aux_ChargeCooler_ChC_CtrNum | Para_Aux_ChargeCooler_CHC_Heating_active | Para_Aux_ChargeCooler_ChC_NumDemAux | Para_Aux_ChargeCooler_ChC_NumStages | Para_Aux_ChargeCooler_ChC_OpMode | Para_Aux_ChargeCooler_ChC_ValPosHyHi_On | Para_Aux_ChargeCooler_ChC_ValPosLimHi_On | Para_Aux_ChargeCooler_ChC_ValPosLimStageDown | Para_Aux_ChargeCooler_ChC_ValPosLimStageUp | Para_Aux_ChargeCooler_tiChC_DelayOff | Para_Aux_ChargeCooler_tiChC_DelayStageDown | Para_Aux_ChargeCooler_tiChC_DelayStageUp | Para_Aux_DumpRad_DelaySwitchOffCooler | Para_Aux_DumpRad_DelaySwitchOffRadStep | Para_Aux_DumpRad_DelaySwitchOnRadStep | Para_Aux_DumpRad_EC_St1onlyP | Para_Aux_DumpRad_HysSwitchOnCooler | Para_Aux_DumpRad_LimitSwitchOffRadStepPos | Para_Aux_DumpRad_LimitSwitchOnCooler | Para_Aux_DumpRad_LimitSwitchOnRadStepPos | Para_Aux_DumpRad_NumbAll | Para_Aux_DumpRad_NumbAux | Para_Aux_DumpRad_SelectCtr | Para_Aux_DumpRad_Type | Para_Aux_FireProtFlap1_InlAir_visible | Para_Aux_FireProtFlap1_OutlAir_visible | Para_Aux_FireProtFlap2_InlAir_visible | Para_Aux_FireProtFlap2_OutlAir_visible | Para_Aux_FreshOilPump_tiFreshOilPump_RTC_Time | Para_Aux_GasRail_ActBlowOffDiffPressMax | Para_Aux_GasRail_AirPressCorr | Para_Aux_GasRail_BlowOffValveOnTimeMax | Para_Aux_GasRail_BlowOffValveOnTimeMin | Para_Aux_GasRail_ChargePress1 | Para_Aux_GasRail_ChargePress2 | Para_Aux_GasRail_DiffPress1 | Para_Aux_GasRail_DiffPress2 | Para_Aux_GasRail_HysBlowOffDiffMax | Para_Aux_GasRail_LimitBlowOffDiffMax | Para_Aux_GasRail_LimitPressHigh | Para_Aux_GasRail_LimitPressLow | Para_Aux_GasRail_PressCtrAdjBoost | Para_Aux_GasRail_RampSetPressChange | Para_Aux_GasRail_SetPressFix | Para_Aux_GasRail_SetPressFixTime | Para_Aux_GasRail_SetPressRangeBegin | Para_Aux_GasRail_SetPressRangeEnd | Para_Aux_GasRail_SpeedLimitValveClose | Para_Aux_GasTrain1_ActMeasure | Para_Aux_GasTrain1_HysMax1 | Para_Aux_GasTrain1_HysMax2 | Para_Aux_GasTrain1_HysMin1 | Para_Aux_GasTrain1_HysMin2 | Para_Aux_GasTrain1_LimitMax1 | Para_Aux_GasTrain1_LimitMax2 | Para_Aux_GasTrain1_LimitMin1 | Para_Aux_GasTrain1_LimitMin2 | Para_Aux_GasTrain1_Range20mA | Para_Aux_GasTrain1_Range4mA | Para_Aux_HWF_Active | Para_Aux_IntakeAir_HysOpenInLouv | Para_Aux_IntakeAir_HysStartInVent | Para_Aux_IntakeAir_LimitOpenInLouv | Para_Aux_IntakeAir_LimitStartInVent | Para_Aux_IntakeAir_TempIntakeAirWarn | Para_Aux_IntakeAirPress_ActMeasure | Para_Aux_IntakeAirPress_HysMax1 | Para_Aux_IntakeAirPress_HysMin1 | Para_Aux_IntakeAirPress_LimitMax1 | Para_Aux_IntakeAirPress_LimitMin1 | Para_Aux_IntakeAirPress_Range20mA | Para_Aux_IntakeAirPress_Range4mA | Para_Aux_ManOpMode_ManAuxCtr_Active | Para_Aux_ManOpMode_tiManAuxCtr_Max | Para_Aux_OutAirER_Fan_FU | Para_Aux_OutDoor_Hys1 | Para_Aux_OutDoor_Hys2 | Para_Aux_OutDoor_Hys3 | Para_Aux_OutDoor_Hys4 | Para_Aux_OutDoor_Limit1 | Para_Aux_OutDoor_Limit2 | Para_Aux_OutDoor_Limit3 | Para_Aux_OutDoor_Limit4 | Para_Aux_PreChambDifPress_ActMeasure | Para_Aux_PreChambDifPress_HysMax | Para_Aux_PreChambDifPress_HysMin | Para_Aux_PreChambDifPress_LimitMax | Para_Aux_PreChambDifPress_LimitMaxP1 | Para_Aux_PreChambDifPress_LimitMaxP2 | Para_Aux_PreChambDifPress_LimitMin | Para_Aux_PreChambDifPress_LimitMinP1 | Para_Aux_PreChambDifPress_LimitMinP2 | Para_Aux_PreChambDifPress_Range20mA | Para_Aux_PreChambDifPress_Range4mA | Para_Aux_PreChambDifPress_SwitchPointHysMax | Para_Aux_PreChambDifPress_SwitchPointLimitMax | Para_Aux_PreChambGasComp_CompOff | Para_Aux_PreChambGasComp_CompOn | Para_Aux_PreChambGasComp_Max | Para_Aux_PreChambGasComp_MaxHys | Para_Aux_PreChambGasComp_Min | Para_Aux_PreChambGasComp_MinHys | Para_Aux_PreChambGasComp_Pr_PCGComp_Active | Para_Aux_PreChambGasTrain_ActMeasure | Para_Aux_PreChambGasTrain_ActMeasureTemp | Para_Aux_PreChambGasTrain_BoostPress1 | Para_Aux_PreChambGasTrain_BoostPress2 | Para_Aux_PreChambGasTrain_DiffPress1 | Para_Aux_PreChambGasTrain_DiffPress2 | Para_Aux_PreChambGasTrain_HysMax1 | Para_Aux_PreChambGasTrain_HysMax2 | Para_Aux_PreChambGasTrain_HysMin | Para_Aux_PreChambGasTrain_HysMin2 | Para_Aux_PreChambGasTrain_LimitMax1 | Para_Aux_PreChambGasTrain_LimitMax2 | Para_Aux_PreChambGasTrain_LimitMin | Para_Aux_PreChambGasTrain_LimitMin2 | Para_Aux_PreChambGasTrain_RampSetPressChange | Para_Aux_PreChambGasTrain_Range20mA | Para_Aux_PreChambGasTrain_Range4mA | Para_Aux_PreChambGasTrain_RangeBeginSetPress | Para_Aux_PreChambGasTrain_RangeEndSetPress | Para_Aux_PreChambGasTrain_SigAdjustBoost | Para_Aux_RoomVent_Act_ERV_AirFlowMon | Para_Aux_RoomVent_ActPurgecycle | Para_Aux_RoomVent_HysMaxRoomTemp | Para_Aux_RoomVent_HysRoomTemp | Para_Aux_RoomVent_HysRTStartVent | Para_Aux_RoomVent_HysRTStartVentStandby | Para_Aux_RoomVent_HysRTVentStep2 | Para_Aux_RoomVent_LimitRoomTemp | Para_Aux_RoomVent_LimitRTStartVent | Para_Aux_RoomVent_LimitRTStartVentStandby | Para_Aux_RoomVent_LimitRTVentStep2 | Para_Aux_RoomVent_MaxRoomTemp | Para_Aux_RoomVent_PurgeTimeMax | Para_Aux_RoomVent_SetpointRTCtr | Para_Aux_RoomVent_SetpointRTCtrStandby | Para_Aux_Ventilation_CircLouvre_Pos_CircLou1_Active | Para_Aux_Ventilation_CircLouvre_Pos_CircLou1_ScalMax | Para_Aux_Ventilation_CircLouvre_Pos_CircLou1_ScalMin | Para_Aux_Ventilation_CircLouvre_Pos_CircLou2_Active | Para_Aux_Ventilation_CircLouvre_Pos_CircLou2_ScalMax | Para_Aux_Ventilation_CircLouvre_Pos_CircLou2_ScalMin | Para_Aux_Ventilation_CircLouvre_T_InAirER_Rel_CircOp | Para_Aux_Ventilation_CircLouvre_T_InAirER_Rel_CircOp_Hy | Para_Aux_Ventilation_Ctr_RDP_OutlVE_Dep_EngP | Para_Aux_Ventilation_Ctr_RDP_OutlVE_Dep_InlVent | Para_Aux_Ventilation_ER_VentColdCountryMode | Para_Aux_Ventilation_InletLouvre_InlVent_Ctr_InlLou_Active | Para_Aux_Ventilation_InletLouvre_Pos_InlLou1_Active | Para_Aux_Ventilation_InletLouvre_Pos_InlLou1_ScalMax | Para_Aux_Ventilation_InletLouvre_Pos_InlLou1_ScalMin | Para_Aux_Ventilation_InletLouvre_Pos_InlLou2_Active | Para_Aux_Ventilation_InletLouvre_Pos_InlLou2_ScalMax | Para_Aux_Ventilation_InletLouvre_Pos_InlLou2_ScalMin | Para_Aux_Ventilation_InletLouvre_PosLim_InlLou_Rel_ERV | Para_Aux_Ventilation_InletLouvre_PosLim_InlLou_Rel_ERV_Hy | Para_Aux_Ventilation_InletLouvre_PosLim_InlLou_Rel_FC_ER | Para_Aux_Ventilation_InletLouvre_PosLim_InlLou_Rel_FC_ER_Hy | Para_Aux_Ventilation_InletLouvre_TypeCtr_InlLou_ERV | Para_Aux_Ventilation_InletLouvre_TypeFeedback_InlLou_ERV | Para_Aux_Ventilation_Louvers | Para_Aux_Ventilation_OutletLouvre_OutlVent_Ctr_OutlLou_Active | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou1_Active | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou1_ScalMax | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou1_ScalMin | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou2_Active | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou2_ScalMax | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou2_ScalMin | Para_Aux_Ventilation_OutletLouvre_PosLim_OutlLou_Rel_ERV | Para_Aux_Ventilation_OutletLouvre_PosLim_OutlLou_Rel_ERV_Hy | Para_Aux_Ventilation_OutletLouvre_PosLim_OutlLou_Rel_FC_ER | Para_Aux_Ventilation_OutletLouvre_PosLim_OutlLou_Rel_FC_ER_Hy | Para_Aux_Ventilation_OutletLouvre_TypeCtr_OutlLou_ERV | Para_Aux_Ventilation_OutletLouvre_TypeFeedback_OutlLou_ERV | Para_Aux_Ventilation_PrDiff_ER_Active | Para_Aux_Ventilation_PrDiff_ER_Lim_High | Para_Aux_Ventilation_PrDiff_ER_Lim_High_Hy | Para_Aux_Ventilation_PrDiff_ER_Lim_Low | Para_Aux_Ventilation_PrDiff_ER_Lim_Low_Hy | Para_Aux_Ventilation_PrDiff_ER_ScalMax | Para_Aux_Ventilation_PrDiff_ER_ScalMin | Para_Aux_Ventilation_Purgecycle_Active | Para_Aux_Ventilation_Scal_CtrInlVentER_Set_Max | Para_Aux_Ventilation_Scal_CtrInlVentER_Set_Min | Para_Aux_Ventilation_Scal_OffSetMax_CtrOutlVent | Para_Aux_Ventilation_Scal_OffSetMax_Pel | Para_Aux_Ventilation_Scal_OffSetMin_CtrOutlVent | Para_Aux_Ventilation_Scal_OffSetMin_Pel | Para_Aux_Ventilation_Scal_PmaxEl | Para_Aux_Ventilation_Scal_PminEl | Para_Aux_Ventilation_Vent_SpeedDif | Para_Aux_Ventilation_VISA | Para_base_tvisversion_xx | Para_base_tvisversion_xxbase_tvisversion_yy | Para_Bearing_ConrodAlarm | Para_Bearing_MainLimit | Para_CtrModule_Ctr1_ActStep_NEx | Para_CtrModule_Ctr1_CycleTime | Para_CtrModule_Ctr1_DComp | Para_CtrModule_Ctr1_DCompTune | Para_CtrModule_Ctr1_DCompWMax | Para_CtrModule_Ctr1_DCompWMin | Para_CtrModule_Ctr1_DeadBand | Para_CtrModule_Ctr1_Format | Para_CtrModule_Ctr1_IComp | Para_CtrModule_Ctr1_ICompTune | Para_CtrModule_Ctr1_ICompWMax | Para_CtrModule_Ctr1_ICompWMin | Para_CtrModule_Ctr1_InvertCtrTune | Para_CtrModule_Ctr1_Name | Para_CtrModule_Ctr1_NameF | Para_CtrModule_Ctr1_OptWorkPoint | Para_CtrModule_Ctr1_PComp | Para_CtrModule_Ctr1_PCompTune | Para_CtrModule_Ctr1_PCompWMax | Para_CtrModule_Ctr1_PCompWMin | Para_CtrModule_Ctr1_RangeBegin | Para_CtrModule_Ctr1_RangeEnd | Para_CtrModule_Ctr1_Unit | Para_CtrModule_Ctr1_UserLevelIntExt | Para_CtrModule_Ctr1_UserLevelManAut | Para_CtrModule_Ctr1_UserLevelSet | Para_CtrModule_Ctr1_UserLevelTune | Para_CtrModule_Ctr1_WMax | Para_CtrModule_Ctr1_WMin | Para_CtrModule_Ctr1_WRampNeg | Para_CtrModule_Ctr1_WRampPos | Para_CtrModule_Ctr1_WStart | Para_CtrModule_Ctr1_YBlock | Para_CtrModule_Ctr1_YHl | Para_CtrModule_Ctr1_YMax | Para_CtrModule_Ctr1_YMin | Para_CtrModule_Ctr1_YRampNeg | Para_CtrModule_Ctr1_YRampPos | Para_CtrModule_Ctr1_YRampTune | Para_CtrModule_Ctr2_ActStep_NEx | Para_CtrModule_Ctr2_CycleTime | Para_CtrModule_Ctr2_DComp | Para_CtrModule_Ctr2_DCompTune | Para_CtrModule_Ctr2_DCompWMax | Para_CtrModule_Ctr2_DCompWMin | Para_CtrModule_Ctr2_DeadBand | Para_CtrModule_Ctr2_Format | Para_CtrModule_Ctr2_IComp | Para_CtrModule_Ctr2_ICompTune | Para_CtrModule_Ctr2_ICompWMax | Para_CtrModule_Ctr2_ICompWMin | Para_CtrModule_Ctr2_InvertCtrTune | Para_CtrModule_Ctr2_Name | Para_CtrModule_Ctr2_NameF | Para_CtrModule_Ctr2_OptWorkPoint | Para_CtrModule_Ctr2_PComp | Para_CtrModule_Ctr2_PCompTune | Para_CtrModule_Ctr2_PCompWMax | Para_CtrModule_Ctr2_PCompWMin | Para_CtrModule_Ctr2_RangeBegin | Para_CtrModule_Ctr2_RangeEnd | Para_CtrModule_Ctr2_Unit | Para_CtrModule_Ctr2_UserLevelIntExt | Para_CtrModule_Ctr2_UserLevelManAut | Para_CtrModule_Ctr2_UserLevelSet | Para_CtrModule_Ctr2_UserLevelTune | Para_CtrModule_Ctr2_WMax | Para_CtrModule_Ctr2_WMin | Para_CtrModule_Ctr2_WRampNeg | Para_CtrModule_Ctr2_WRampPos | Para_CtrModule_Ctr2_WStart | Para_CtrModule_Ctr2_YBlock | Para_CtrModule_Ctr2_YHl | Para_CtrModule_Ctr2_YMax | Para_CtrModule_Ctr2_YMin | Para_CtrModule_Ctr2_YRampNeg | Para_CtrModule_Ctr2_YRampPos | Para_CtrModule_Ctr2_YRampTune | Para_CtrModule_Ctr3_ActStep_NEx | Para_CtrModule_Ctr3_CycleTime | Para_CtrModule_Ctr3_DComp | Para_CtrModule_Ctr3_DCompTune | Para_CtrModule_Ctr3_DCompWMax | Para_CtrModule_Ctr3_DCompWMin | Para_CtrModule_Ctr3_DeadBand | Para_CtrModule_Ctr3_Format | Para_CtrModule_Ctr3_IComp | Para_CtrModule_Ctr3_ICompTune | Para_CtrModule_Ctr3_ICompWMax | Para_CtrModule_Ctr3_ICompWMin | Para_CtrModule_Ctr3_InvertCtrTune | Para_CtrModule_Ctr3_Name | Para_CtrModule_Ctr3_NameF | Para_CtrModule_Ctr3_OptWorkPoint | Para_CtrModule_Ctr3_PComp | Para_CtrModule_Ctr3_PCompTune | Para_CtrModule_Ctr3_PCompWMax | Para_CtrModule_Ctr3_PCompWMin | Para_CtrModule_Ctr3_RangeBegin | Para_CtrModule_Ctr3_RangeEnd | Para_CtrModule_Ctr3_Unit | Para_CtrModule_Ctr3_UserLevelIntExt | Para_CtrModule_Ctr3_UserLevelManAut | Para_CtrModule_Ctr3_UserLevelSet | Para_CtrModule_Ctr3_UserLevelTune | Para_CtrModule_Ctr3_WMax | Para_CtrModule_Ctr3_WMin | Para_CtrModule_Ctr3_WRampNeg | Para_CtrModule_Ctr3_WRampPos | Para_CtrModule_Ctr3_WStart | Para_CtrModule_Ctr3_YBlock | Para_CtrModule_Ctr3_YHl | Para_CtrModule_Ctr3_YMax | Para_CtrModule_Ctr3_YMin | Para_CtrModule_Ctr3_YRampNeg | Para_CtrModule_Ctr3_YRampPos | Para_CtrModule_Ctr3_YRampTune | Para_CtrModule_Ctr4_ActStep_NEx | Para_CtrModule_Ctr4_CycleTime | Para_CtrModule_Ctr4_DComp | Para_CtrModule_Ctr4_DCompTune | Para_CtrModule_Ctr4_DCompWMax | Para_CtrModule_Ctr4_DCompWMin | Para_CtrModule_Ctr4_DeadBand | Para_CtrModule_Ctr4_Format | Para_CtrModule_Ctr4_IComp | Para_CtrModule_Ctr4_ICompTune | Para_CtrModule_Ctr4_ICompWMax | Para_CtrModule_Ctr4_ICompWMin | Para_CtrModule_Ctr4_InvertCtrTune | Para_CtrModule_Ctr4_Name | Para_CtrModule_Ctr4_NameF | Para_CtrModule_Ctr4_OptWorkPoint | Para_CtrModule_Ctr4_PComp | Para_CtrModule_Ctr4_PCompTune | Para_CtrModule_Ctr4_PCompWMax | Para_CtrModule_Ctr4_PCompWMin | Para_CtrModule_Ctr4_RangeBegin | Para_CtrModule_Ctr4_RangeEnd | Para_CtrModule_Ctr4_Unit | Para_CtrModule_Ctr4_UserLevelIntExt | Para_CtrModule_Ctr4_UserLevelManAut | Para_CtrModule_Ctr4_UserLevelSet | Para_CtrModule_Ctr4_UserLevelTune | Para_CtrModule_Ctr4_WMax | Para_CtrModule_Ctr4_WMin | Para_CtrModule_Ctr4_WRampNeg | Para_CtrModule_Ctr4_WRampPos | Para_CtrModule_Ctr4_WStart | Para_CtrModule_Ctr4_YBlock | Para_CtrModule_Ctr4_YHl | Para_CtrModule_Ctr4_YMax | Para_CtrModule_Ctr4_YMin | Para_CtrModule_Ctr4_YRampNeg | Para_CtrModule_Ctr4_YRampPos | Para_CtrModule_Ctr4_YRampTune | Para_CtrModule_Ctr5_CycleTime | Para_CtrModule_Ctr5_DComp | Para_CtrModule_Ctr5_DCompTune | Para_CtrModule_Ctr5_DCompWMax | Para_CtrModule_Ctr5_DCompWMin | Para_CtrModule_Ctr5_DeadBand | Para_CtrModule_Ctr5_Format | Para_CtrModule_Ctr5_IComp | Para_CtrModule_Ctr5_ICompTune | Para_CtrModule_Ctr5_ICompWMax | Para_CtrModule_Ctr5_ICompWMin | Para_CtrModule_Ctr5_InvertCtrTune | Para_CtrModule_Ctr5_Name | Para_CtrModule_Ctr5_NameF | Para_CtrModule_Ctr5_OptWorkPoint | Para_CtrModule_Ctr5_PComp | Para_CtrModule_Ctr5_PCompTune | Para_CtrModule_Ctr5_PCompWMax | Para_CtrModule_Ctr5_PCompWMin | Para_CtrModule_Ctr5_RangeBegin | Para_CtrModule_Ctr5_RangeEnd | Para_CtrModule_Ctr5_Unit | Para_CtrModule_Ctr5_UserLevelIntExt | Para_CtrModule_Ctr5_UserLevelManAut | Para_CtrModule_Ctr5_UserLevelSet | Para_CtrModule_Ctr5_UserLevelTune | Para_CtrModule_Ctr5_WMax | Para_CtrModule_Ctr5_WMin | Para_CtrModule_Ctr5_WRampNeg | Para_CtrModule_Ctr5_WRampPos | Para_CtrModule_Ctr5_WStart | Para_CtrModule_Ctr5_YBlock | Para_CtrModule_Ctr5_YHl | Para_CtrModule_Ctr5_YMax | Para_CtrModule_Ctr5_YMin | Para_CtrModule_Ctr5_YRampNeg | Para_CtrModule_Ctr5_YRampPos | Para_CtrModule_Ctr5_YRampTune | Para_CtrModule_Ctr6_CycleTime | Para_CtrModule_Ctr6_DComp | Para_CtrModule_Ctr6_DCompTune | Para_CtrModule_Ctr6_DCompWMax | Para_CtrModule_Ctr6_DCompWMin | Para_CtrModule_Ctr6_DeadBand | Para_CtrModule_Ctr6_Format | Para_CtrModule_Ctr6_IComp | Para_CtrModule_Ctr6_ICompTune | Para_CtrModule_Ctr6_ICompWMax | Para_CtrModule_Ctr6_ICompWMin | Para_CtrModule_Ctr6_InvertCtrTune | Para_CtrModule_Ctr6_Name | Para_CtrModule_Ctr6_NameF | Para_CtrModule_Ctr6_OptWorkPoint | Para_CtrModule_Ctr6_PComp | Para_CtrModule_Ctr6_PCompTune | Para_CtrModule_Ctr6_PCompWMax | Para_CtrModule_Ctr6_PCompWMin | Para_CtrModule_Ctr6_RangeBegin | Para_CtrModule_Ctr6_RangeEnd | Para_CtrModule_Ctr6_Unit | Para_CtrModule_Ctr6_UserLevelIntExt | Para_CtrModule_Ctr6_UserLevelManAut | Para_CtrModule_Ctr6_UserLevelSet | Para_CtrModule_Ctr6_UserLevelTune | Para_CtrModule_Ctr6_WMax | Para_CtrModule_Ctr6_WMin | Para_CtrModule_Ctr6_WRampNeg | Para_CtrModule_Ctr6_WRampPos | Para_CtrModule_Ctr6_WStart | Para_CtrModule_Ctr6_YBlock | Para_CtrModule_Ctr6_YHl | Para_CtrModule_Ctr6_YMax | Para_CtrModule_Ctr6_YMin | Para_CtrModule_Ctr6_YRampNeg | Para_CtrModule_Ctr6_YRampPos | Para_CtrModule_Ctr6_YRampTune | Para_CtrModule_Ctr7_CycleTime | Para_CtrModule_Ctr7_DComp | Para_CtrModule_Ctr7_DCompTune | Para_CtrModule_Ctr7_DCompWMax | Para_CtrModule_Ctr7_DCompWMin | Para_CtrModule_Ctr7_DeadBand | Para_CtrModule_Ctr7_Format | Para_CtrModule_Ctr7_IComp | Para_CtrModule_Ctr7_ICompTune | Para_CtrModule_Ctr7_ICompWMax | Para_CtrModule_Ctr7_ICompWMin | Para_CtrModule_Ctr7_InvertCtrTune | Para_CtrModule_Ctr7_Name | Para_CtrModule_Ctr7_NameF | Para_CtrModule_Ctr7_OptWorkPoint | Para_CtrModule_Ctr7_PComp | Para_CtrModule_Ctr7_PCompTune | Para_CtrModule_Ctr7_PCompWMax | Para_CtrModule_Ctr7_PCompWMin | Para_CtrModule_Ctr7_RangeBegin | Para_CtrModule_Ctr7_RangeEnd | Para_CtrModule_Ctr7_Unit | Para_CtrModule_Ctr7_UserLevelIntExt | Para_CtrModule_Ctr7_UserLevelManAut | Para_CtrModule_Ctr7_UserLevelSet | Para_CtrModule_Ctr7_UserLevelTune | Para_CtrModule_Ctr7_WMax | Para_CtrModule_Ctr7_WMin | Para_CtrModule_Ctr7_WRampNeg | Para_CtrModule_Ctr7_WRampPos | Para_CtrModule_Ctr7_WStart | Para_CtrModule_Ctr7_YBlock | Para_CtrModule_Ctr7_YHl | Para_CtrModule_Ctr7_YMax | Para_CtrModule_Ctr7_YMin | Para_CtrModule_Ctr7_YRampNeg | Para_CtrModule_Ctr7_YRampPos | Para_CtrModule_Ctr7_YRampTune | Para_CtrModule_Ctr8_CycleTime | Para_CtrModule_Ctr8_DComp | Para_CtrModule_Ctr8_DCompTune | Para_CtrModule_Ctr8_DCompWMax | Para_CtrModule_Ctr8_DCompWMin | Para_CtrModule_Ctr8_DeadBand | Para_CtrModule_Ctr8_Format | Para_CtrModule_Ctr8_IComp | Para_CtrModule_Ctr8_ICompTune | Para_CtrModule_Ctr8_ICompWMax | Para_CtrModule_Ctr8_ICompWMin | Para_CtrModule_Ctr8_InvertCtrTune | Para_CtrModule_Ctr8_Name | Para_CtrModule_Ctr8_NameF | Para_CtrModule_Ctr8_OptWorkPoint | Para_CtrModule_Ctr8_PComp | Para_CtrModule_Ctr8_PCompTune | Para_CtrModule_Ctr8_PCompWMax | Para_CtrModule_Ctr8_PCompWMin | Para_CtrModule_Ctr8_RangeBegin | Para_CtrModule_Ctr8_RangeEnd | Para_CtrModule_Ctr8_Unit | Para_CtrModule_Ctr8_UserLevelIntExt | Para_CtrModule_Ctr8_UserLevelManAut | Para_CtrModule_Ctr8_UserLevelSet | Para_CtrModule_Ctr8_UserLevelTune | Para_CtrModule_Ctr8_WMax | Para_CtrModule_Ctr8_WMin | Para_CtrModule_Ctr8_WRampNeg | Para_CtrModule_Ctr8_WRampPos | Para_CtrModule_Ctr8_WStart | Para_CtrModule_Ctr8_YBlock | Para_CtrModule_Ctr8_YHl | Para_CtrModule_Ctr8_YMax | Para_CtrModule_Ctr8_YMin | Para_CtrModule_Ctr8_YRampNeg | Para_CtrModule_Ctr8_YRampPos | Para_CtrModule_Ctr8_YRampTune | Para_CtrModule_CtrX10_CycleTime | Para_CtrModule_CtrX10_DComp | Para_CtrModule_CtrX10_DCompTune | Para_CtrModule_CtrX10_DeadBand | Para_CtrModule_CtrX10_IComp | Para_CtrModule_CtrX10_ICompTune | Para_CtrModule_CtrX10_InvertCtrTune | Para_CtrModule_CtrX10_PComp | Para_CtrModule_CtrX10_PCompTune | Para_CtrModule_CtrX10_RangeBegin | Para_CtrModule_CtrX10_RangeEnd | Para_CtrModule_CtrX10_UserLevelIntExt | Para_CtrModule_CtrX10_UserLevelManAut | Para_CtrModule_CtrX10_UserLevelSet | Para_CtrModule_CtrX10_UserLevelTune | Para_CtrModule_CtrX10_WMax | Para_CtrModule_CtrX10_WMin | Para_CtrModule_CtrX10_WRampNeg | Para_CtrModule_CtrX10_WRampPos | Para_CtrModule_CtrX10_WStart | Para_CtrModule_CtrX10_YBlock | Para_CtrModule_CtrX10_YHl | Para_CtrModule_CtrX10_YMax | Para_CtrModule_CtrX10_YMin | Para_CtrModule_CtrX10_YRampNeg | Para_CtrModule_CtrX10_YRampPos | Para_CtrModule_CtrX10_YRampTune | Para_CtrModule_CtrX11_CycleTime | Para_CtrModule_CtrX11_DComp | Para_CtrModule_CtrX11_DCompTune | Para_CtrModule_CtrX11_DeadBand | Para_CtrModule_CtrX11_IComp | Para_CtrModule_CtrX11_ICompTune | Para_CtrModule_CtrX11_InvertCtrTune | Para_CtrModule_CtrX11_PComp | Para_CtrModule_CtrX11_PCompTune | Para_CtrModule_CtrX11_RangeBegin | Para_CtrModule_CtrX11_RangeEnd | Para_CtrModule_CtrX11_UserLevelIntExt | Para_CtrModule_CtrX11_UserLevelManAut | Para_CtrModule_CtrX11_UserLevelSet | Para_CtrModule_CtrX11_UserLevelTune | Para_CtrModule_CtrX11_WMax | Para_CtrModule_CtrX11_WMin | Para_CtrModule_CtrX11_WRampNeg | Para_CtrModule_CtrX11_WRampPos | Para_CtrModule_CtrX11_WStart | Para_CtrModule_CtrX11_YBlock | Para_CtrModule_CtrX11_YHl | Para_CtrModule_CtrX11_YMax | Para_CtrModule_CtrX11_YMin | Para_CtrModule_CtrX11_YRampNeg | Para_CtrModule_CtrX11_YRampPos | Para_CtrModule_CtrX11_YRampTune | Para_CtrModule_CtrX12_CycleTime | Para_CtrModule_CtrX12_DComp | Para_CtrModule_CtrX12_DCompTune | Para_CtrModule_CtrX12_DeadBand | Para_CtrModule_CtrX12_IComp | Para_CtrModule_CtrX12_ICompTune | Para_CtrModule_CtrX12_InvertCtrTune | Para_CtrModule_CtrX12_PComp | Para_CtrModule_CtrX12_PCompTune | Para_CtrModule_CtrX12_RangeBegin | Para_CtrModule_CtrX12_RangeEnd | Para_CtrModule_CtrX12_UserLevelIntExt | Para_CtrModule_CtrX12_UserLevelManAut | Para_CtrModule_CtrX12_UserLevelSet | Para_CtrModule_CtrX12_UserLevelTune | Para_CtrModule_CtrX12_WMax | Para_CtrModule_CtrX12_WMin | Para_CtrModule_CtrX12_WRampNeg | Para_CtrModule_CtrX12_WRampPos | Para_CtrModule_CtrX12_WStart | Para_CtrModule_CtrX12_YBlock | Para_CtrModule_CtrX12_YHl | Para_CtrModule_CtrX12_YMax | Para_CtrModule_CtrX12_YMin | Para_CtrModule_CtrX12_YRampNeg | Para_CtrModule_CtrX12_YRampPos | Para_CtrModule_CtrX12_YRampTune | Para_CtrModule_CtrX13_CycleTime | Para_CtrModule_CtrX13_DCompTune | Para_CtrModule_CtrX13_DeadBand | Para_CtrModule_CtrX13_ICompTune | Para_CtrModule_CtrX13_InvertCtrTune | Para_CtrModule_CtrX13_PCompTune | Para_CtrModule_CtrX13_RangeBegin | Para_CtrModule_CtrX13_RangeEnd | Para_CtrModule_CtrX13_UserLevelIntExt | Para_CtrModule_CtrX13_UserLevelManAut | Para_CtrModule_CtrX13_UserLevelSet | Para_CtrModule_CtrX13_UserLevelTune | Para_CtrModule_CtrX13_WMax | Para_CtrModule_CtrX13_WMin | Para_CtrModule_CtrX13_WRampNeg | Para_CtrModule_CtrX13_WRampPos | Para_CtrModule_CtrX13_WStart | Para_CtrModule_CtrX13_YBlock | Para_CtrModule_CtrX13_YHl | Para_CtrModule_CtrX13_YMax | Para_CtrModule_CtrX13_YMin | Para_CtrModule_CtrX13_YRampTune | Para_CtrModule_CtrX14_CycleTime | Para_CtrModule_CtrX14_DCompTune | Para_CtrModule_CtrX14_DeadBand | Para_CtrModule_CtrX14_ICompTune | Para_CtrModule_CtrX14_InvertCtrTune | Para_CtrModule_CtrX14_PCompTune | Para_CtrModule_CtrX14_RangeBegin | Para_CtrModule_CtrX14_RangeEnd | Para_CtrModule_CtrX14_UserLevelIntExt | Para_CtrModule_CtrX14_UserLevelManAut | Para_CtrModule_CtrX14_UserLevelSet | Para_CtrModule_CtrX14_UserLevelTune | Para_CtrModule_CtrX14_WMax | Para_CtrModule_CtrX14_WMin | Para_CtrModule_CtrX14_WRampNeg | Para_CtrModule_CtrX14_WRampPos | Para_CtrModule_CtrX14_WStart | Para_CtrModule_CtrX14_YBlock | Para_CtrModule_CtrX14_YHl | Para_CtrModule_CtrX14_YMax | Para_CtrModule_CtrX14_YMin | Para_CtrModule_CtrX14_YRampTune | Para_CtrModule_CtrX15_CycleTime | Para_CtrModule_CtrX15_DCompTune | Para_CtrModule_CtrX15_DeadBand | Para_CtrModule_CtrX15_ICompTune | Para_CtrModule_CtrX15_InvertCtrTune | Para_CtrModule_CtrX15_PCompTune | Para_CtrModule_CtrX15_RangeBegin | Para_CtrModule_CtrX15_RangeEnd | Para_CtrModule_CtrX15_UserLevelIntExt | Para_CtrModule_CtrX15_UserLevelManAut | Para_CtrModule_CtrX15_UserLevelSet | Para_CtrModule_CtrX15_UserLevelTune | Para_CtrModule_CtrX15_WMax | Para_CtrModule_CtrX15_WMin | Para_CtrModule_CtrX15_WRampNeg | Para_CtrModule_CtrX15_WRampPos | Para_CtrModule_CtrX15_WStart | Para_CtrModule_CtrX15_YBlock | Para_CtrModule_CtrX15_YHl | Para_CtrModule_CtrX15_YMax | Para_CtrModule_CtrX15_YMin | Para_CtrModule_CtrX15_YRampTune | Para_CtrModule_CtrX16_CycleTime | Para_CtrModule_CtrX16_DCompTune | Para_CtrModule_CtrX16_DeadBand | Para_CtrModule_CtrX16_ICompTune | Para_CtrModule_CtrX16_InvertCtrTune | Para_CtrModule_CtrX16_PCompTune | Para_CtrModule_CtrX16_RangeBegin | Para_CtrModule_CtrX16_RangeEnd | Para_CtrModule_CtrX16_UserLevelIntExt | Para_CtrModule_CtrX16_UserLevelManAut | Para_CtrModule_CtrX16_UserLevelSet | Para_CtrModule_CtrX16_UserLevelTune | Para_CtrModule_CtrX16_WMax | Para_CtrModule_CtrX16_WMin | Para_CtrModule_CtrX16_WRampNeg | Para_CtrModule_CtrX16_WRampPos | Para_CtrModule_CtrX16_WStart | Para_CtrModule_CtrX16_YBlock | Para_CtrModule_CtrX16_YHl | Para_CtrModule_CtrX16_YMax | Para_CtrModule_CtrX16_YMin | Para_CtrModule_CtrX16_YRampTune | Para_Custom_AnalogIn_10_CustAnaIn_MinMaxActive10 | Para_Custom_AnalogIn_10_CustAnaIn_Typ10 | Para_Custom_AnalogIn_10_Hystereses | Para_Custom_AnalogIn_10_LimitHi | Para_Custom_AnalogIn_10_LimitHiHi | Para_Custom_AnalogIn_10_LimitLo | Para_Custom_AnalogIn_10_LimitLoLo | Para_Custom_AnalogIn_11_CustAnaIn_MinMaxActive11 | Para_Custom_AnalogIn_11_CustAnaIn_Typ11 | Para_Custom_AnalogIn_11_Hystereses | Para_Custom_AnalogIn_11_LimitHi | Para_Custom_AnalogIn_11_LimitHiHi | Para_Custom_AnalogIn_11_LimitLo | Para_Custom_AnalogIn_11_LimitLoLo | Para_Custom_AnalogIn_12_CustAnaIn_MinMaxActive12 | Para_Custom_AnalogIn_12_CustAnaIn_Typ12 | Para_Custom_AnalogIn_12_Hystereses | Para_Custom_AnalogIn_12_LimitHi | Para_Custom_AnalogIn_12_LimitHiHi | Para_Custom_AnalogIn_12_LimitLo | Para_Custom_AnalogIn_12_LimitLoLo | Para_Custom_AnalogIn_13_CustAnaIn_MinMaxActive13 | Para_Custom_AnalogIn_13_CustAnaIn_Typ13 | Para_Custom_AnalogIn_13_Hystereses | Para_Custom_AnalogIn_13_LimitHi | Para_Custom_AnalogIn_13_LimitHiHi | Para_Custom_AnalogIn_13_LimitLo | Para_Custom_AnalogIn_13_LimitLoLo | Para_Custom_AnalogIn_14_CustAnaIn_MinMaxActive14 | Para_Custom_AnalogIn_14_CustAnaIn_Typ14 | Para_Custom_AnalogIn_14_Hystereses | Para_Custom_AnalogIn_14_LimitHi | Para_Custom_AnalogIn_14_LimitHiHi | Para_Custom_AnalogIn_14_LimitLo | Para_Custom_AnalogIn_14_LimitLoLo | Para_Custom_AnalogIn_15_CustAnaIn_MinMaxActive15 | Para_Custom_AnalogIn_15_CustAnaIn_Typ15 | Para_Custom_AnalogIn_15_Hystereses | Para_Custom_AnalogIn_15_LimitHi | Para_Custom_AnalogIn_15_LimitHiHi | Para_Custom_AnalogIn_15_LimitLo | Para_Custom_AnalogIn_15_LimitLoLo | Para_Custom_AnalogIn_16_CustAnaIn_MinMaxActive16 | Para_Custom_AnalogIn_16_CustAnaIn_Typ16 | Para_Custom_AnalogIn_16_Hystereses | Para_Custom_AnalogIn_16_LimitHi | Para_Custom_AnalogIn_16_LimitHiHi | Para_Custom_AnalogIn_16_LimitLo | Para_Custom_AnalogIn_16_LimitLoLo | Para_Custom_AnalogIn_17_CustAnaIn_Active17 | Para_Custom_AnalogIn_17_CustAnaIn_MinMaxActive17 | Para_Custom_AnalogIn_17_CustAnaIn_Set4mA17 | Para_Custom_AnalogIn_17_CustAnaIn_Typ17 | Para_Custom_AnalogIn_17_Hystereses | Para_Custom_AnalogIn_17_LimitHi | Para_Custom_AnalogIn_17_LimitHiHi | Para_Custom_AnalogIn_17_LimitLo | Para_Custom_AnalogIn_17_LimitLoLo | Para_Custom_AnalogIn_17_ScaleMax | Para_Custom_AnalogIn_17_ScaleMin | Para_Custom_AnalogIn_18_CustAnaIn_Active18 | Para_Custom_AnalogIn_18_CustAnaIn_MinMaxActive18 | Para_Custom_AnalogIn_18_CustAnaIn_Set4mA18 | Para_Custom_AnalogIn_18_CustAnaIn_Typ18 | Para_Custom_AnalogIn_18_Hystereses | Para_Custom_AnalogIn_18_LimitHi | Para_Custom_AnalogIn_18_LimitHiHi | Para_Custom_AnalogIn_18_LimitLo | Para_Custom_AnalogIn_18_LimitLoLo | Para_Custom_AnalogIn_18_ScaleMax | Para_Custom_AnalogIn_18_ScaleMin | Para_Custom_AnalogIn_19_CustAnaIn_Active19 | Para_Custom_AnalogIn_19_CustAnaIn_MinMaxActive19 | Para_Custom_AnalogIn_19_CustAnaIn_Set4mA19 | Para_Custom_AnalogIn_19_CustAnaIn_Typ19 | Para_Custom_AnalogIn_19_Hystereses | Para_Custom_AnalogIn_19_LimitHi | Para_Custom_AnalogIn_19_LimitHiHi | Para_Custom_AnalogIn_19_LimitLo | Para_Custom_AnalogIn_19_LimitLoLo | Para_Custom_AnalogIn_19_ScaleMax | Para_Custom_AnalogIn_19_ScaleMin | Para_Custom_AnalogIn_1_CustAnaIn_MinMaxActive1 | Para_Custom_AnalogIn_1_CustAnaIn_Typ1 | Para_Custom_AnalogIn_1_Hystereses | Para_Custom_AnalogIn_1_LimitHi | Para_Custom_AnalogIn_1_LimitHiHi | Para_Custom_AnalogIn_1_LimitLo | Para_Custom_AnalogIn_1_LimitLoLo | Para_Custom_AnalogIn_20_CustAnaIn_Active20 | Para_Custom_AnalogIn_20_CustAnaIn_MinMaxActive20 | Para_Custom_AnalogIn_20_CustAnaIn_Set4mA20 | Para_Custom_AnalogIn_20_CustAnaIn_Typ20 | Para_Custom_AnalogIn_20_Hystereses | Para_Custom_AnalogIn_20_LimitHi | Para_Custom_AnalogIn_20_LimitHiHi | Para_Custom_AnalogIn_20_LimitLo | Para_Custom_AnalogIn_20_LimitLoLo | Para_Custom_AnalogIn_20_ScaleMax | Para_Custom_AnalogIn_20_ScaleMin | Para_Custom_AnalogIn_21_CustAnaIn_Active21 | Para_Custom_AnalogIn_21_CustAnaIn_MinMaxActive21 | Para_Custom_AnalogIn_21_CustAnaIn_Set4mA21 | Para_Custom_AnalogIn_21_CustAnaIn_Typ21 | Para_Custom_AnalogIn_21_Hystereses | Para_Custom_AnalogIn_21_LimitHi | Para_Custom_AnalogIn_21_LimitHiHi | Para_Custom_AnalogIn_21_LimitLo | Para_Custom_AnalogIn_21_LimitLoLo | Para_Custom_AnalogIn_21_ScaleMax | Para_Custom_AnalogIn_21_ScaleMin | Para_Custom_AnalogIn_22_CustAnaIn_Active22 | Para_Custom_AnalogIn_22_CustAnaIn_MinMaxActive22 | Para_Custom_AnalogIn_22_CustAnaIn_Set4mA22 | Para_Custom_AnalogIn_22_CustAnaIn_Typ22 | Para_Custom_AnalogIn_22_Hystereses | Para_Custom_AnalogIn_22_LimitHi | Para_Custom_AnalogIn_22_LimitHiHi | Para_Custom_AnalogIn_22_LimitLo | Para_Custom_AnalogIn_22_LimitLoLo | Para_Custom_AnalogIn_22_ScaleMax | Para_Custom_AnalogIn_22_ScaleMin | Para_Custom_AnalogIn_23_CustAnaIn_Active23 | Para_Custom_AnalogIn_23_CustAnaIn_MinMaxActive23 | Para_Custom_AnalogIn_23_CustAnaIn_Set4mA23 | Para_Custom_AnalogIn_23_CustAnaIn_Typ23 | Para_Custom_AnalogIn_23_Hystereses | Para_Custom_AnalogIn_23_LimitHi | Para_Custom_AnalogIn_23_LimitHiHi | Para_Custom_AnalogIn_23_LimitLo | Para_Custom_AnalogIn_23_LimitLoLo | Para_Custom_AnalogIn_23_ScaleMax | Para_Custom_AnalogIn_23_ScaleMin | Para_Custom_AnalogIn_24_CustAnaIn_Active24 | Para_Custom_AnalogIn_24_CustAnaIn_MinMaxActive24 | Para_Custom_AnalogIn_24_CustAnaIn_Set4mA24 | Para_Custom_AnalogIn_24_CustAnaIn_Typ24 | Para_Custom_AnalogIn_24_Hystereses | Para_Custom_AnalogIn_24_LimitHi | Para_Custom_AnalogIn_24_LimitHiHi | Para_Custom_AnalogIn_24_LimitLo | Para_Custom_AnalogIn_24_LimitLoLo | Para_Custom_AnalogIn_24_ScaleMax | Para_Custom_AnalogIn_24_ScaleMin | Para_Custom_AnalogIn_25_CustAnaIn_Active25 | Para_Custom_AnalogIn_25_CustAnaIn_MinMaxActive25 | Para_Custom_AnalogIn_25_CustAnaIn_Set4mA25 | Para_Custom_AnalogIn_25_CustAnaIn_Typ25 | Para_Custom_AnalogIn_25_Hystereses | Para_Custom_AnalogIn_25_LimitHi | Para_Custom_AnalogIn_25_LimitHiHi | Para_Custom_AnalogIn_25_LimitLo | Para_Custom_AnalogIn_25_LimitLoLo | Para_Custom_AnalogIn_25_ScaleMax | Para_Custom_AnalogIn_25_ScaleMin | Para_Custom_AnalogIn_26_CustAnaIn_Active26 | Para_Custom_AnalogIn_26_CustAnaIn_MinMaxActive26 | Para_Custom_AnalogIn_26_CustAnaIn_Set4mA26 | Para_Custom_AnalogIn_26_CustAnaIn_Typ26 | Para_Custom_AnalogIn_26_Hystereses | Para_Custom_AnalogIn_26_LimitHi | Para_Custom_AnalogIn_26_LimitHiHi | Para_Custom_AnalogIn_26_LimitLo | Para_Custom_AnalogIn_26_LimitLoLo | Para_Custom_AnalogIn_26_ScaleMax | Para_Custom_AnalogIn_26_ScaleMin | Para_Custom_AnalogIn_27_CustAnaIn_Active27 | Para_Custom_AnalogIn_27_CustAnaIn_MinMaxActive27 | Para_Custom_AnalogIn_27_CustAnaIn_Set4mA27 | Para_Custom_AnalogIn_27_CustAnaIn_Typ27 | Para_Custom_AnalogIn_27_Hystereses | Para_Custom_AnalogIn_27_LimitHi | Para_Custom_AnalogIn_27_LimitHiHi | Para_Custom_AnalogIn_27_LimitLo | Para_Custom_AnalogIn_27_LimitLoLo | Para_Custom_AnalogIn_27_ScaleMax | Para_Custom_AnalogIn_27_ScaleMin | Para_Custom_AnalogIn_28_CustAnaIn_Active28 | Para_Custom_AnalogIn_28_CustAnaIn_MinMaxActive28 | Para_Custom_AnalogIn_28_CustAnaIn_Set4mA28 | Para_Custom_AnalogIn_28_CustAnaIn_Typ28 | Para_Custom_AnalogIn_28_Hystereses | Para_Custom_AnalogIn_28_LimitHi | Para_Custom_AnalogIn_28_LimitHiHi | Para_Custom_AnalogIn_28_LimitLo | Para_Custom_AnalogIn_28_LimitLoLo | Para_Custom_AnalogIn_28_ScaleMax | Para_Custom_AnalogIn_28_ScaleMin | Para_Custom_AnalogIn_29_CustAnaIn_Active29 | Para_Custom_AnalogIn_29_CustAnaIn_MinMaxActive29 | Para_Custom_AnalogIn_29_CustAnaIn_Set4mA29 | Para_Custom_AnalogIn_29_CustAnaIn_Typ29 | Para_Custom_AnalogIn_29_Hystereses | Para_Custom_AnalogIn_29_LimitHi | Para_Custom_AnalogIn_29_LimitHiHi | Para_Custom_AnalogIn_29_LimitLo | Para_Custom_AnalogIn_29_LimitLoLo | Para_Custom_AnalogIn_29_ScaleMax | Para_Custom_AnalogIn_29_ScaleMin | Para_Custom_AnalogIn_2_CustAnaIn_MinMaxActive2 | Para_Custom_AnalogIn_2_CustAnaIn_Typ2 | Para_Custom_AnalogIn_2_Hystereses | Para_Custom_AnalogIn_2_LimitHi | Para_Custom_AnalogIn_2_LimitHiHi | Para_Custom_AnalogIn_2_LimitLo | Para_Custom_AnalogIn_2_LimitLoLo | Para_Custom_AnalogIn_30_CustAnaIn_Active30 | Para_Custom_AnalogIn_30_CustAnaIn_MinMaxActive30 | Para_Custom_AnalogIn_30_CustAnaIn_Set4mA30 | Para_Custom_AnalogIn_30_CustAnaIn_Typ30 | Para_Custom_AnalogIn_30_Hystereses | Para_Custom_AnalogIn_30_LimitHi | Para_Custom_AnalogIn_30_LimitHiHi | Para_Custom_AnalogIn_30_LimitLo | Para_Custom_AnalogIn_30_LimitLoLo | Para_Custom_AnalogIn_30_ScaleMax | Para_Custom_AnalogIn_30_ScaleMin | Para_Custom_AnalogIn_31_CustAnaIn_Active31 | Para_Custom_AnalogIn_31_CustAnaIn_MinMaxActive31 | Para_Custom_AnalogIn_31_CustAnaIn_Set4mA31 | Para_Custom_AnalogIn_31_CustAnaIn_Typ31 | Para_Custom_AnalogIn_31_Hystereses | Para_Custom_AnalogIn_31_LimitHi | Para_Custom_AnalogIn_31_LimitHiHi | Para_Custom_AnalogIn_31_LimitLo | Para_Custom_AnalogIn_31_LimitLoLo | Para_Custom_AnalogIn_31_ScaleMax | Para_Custom_AnalogIn_31_ScaleMin | Para_Custom_AnalogIn_32_CustAnaIn_Active32 | Para_Custom_AnalogIn_32_CustAnaIn_MinMaxActive32 | Para_Custom_AnalogIn_32_CustAnaIn_Set4mA32 | Para_Custom_AnalogIn_32_CustAnaIn_Typ32 | Para_Custom_AnalogIn_32_Hystereses | Para_Custom_AnalogIn_32_LimitHi | Para_Custom_AnalogIn_32_LimitHiHi | Para_Custom_AnalogIn_32_LimitLo | Para_Custom_AnalogIn_32_LimitLoLo | Para_Custom_AnalogIn_32_ScaleMax | Para_Custom_AnalogIn_32_ScaleMin | Para_Custom_AnalogIn_33_CustAnaIn_Active33 | Para_Custom_AnalogIn_33_CustAnaIn_MinMaxActive33 | Para_Custom_AnalogIn_33_CustAnaIn_Set4mA33 | Para_Custom_AnalogIn_33_CustAnaIn_Typ33 | Para_Custom_AnalogIn_33_Hystereses | Para_Custom_AnalogIn_33_LimitHi | Para_Custom_AnalogIn_33_LimitHiHi | Para_Custom_AnalogIn_33_LimitLo | Para_Custom_AnalogIn_33_LimitLoLo | Para_Custom_AnalogIn_33_ScaleMax | Para_Custom_AnalogIn_33_ScaleMin | Para_Custom_AnalogIn_34_CustAnaIn_Active34 | Para_Custom_AnalogIn_34_CustAnaIn_MinMaxActive34 | Para_Custom_AnalogIn_34_CustAnaIn_Set4mA34 | Para_Custom_AnalogIn_34_CustAnaIn_Typ34 | Para_Custom_AnalogIn_34_Hystereses | Para_Custom_AnalogIn_34_LimitHi | Para_Custom_AnalogIn_34_LimitHiHi | Para_Custom_AnalogIn_34_LimitLo | Para_Custom_AnalogIn_34_LimitLoLo | Para_Custom_AnalogIn_34_ScaleMax | Para_Custom_AnalogIn_34_ScaleMin | Para_Custom_AnalogIn_35_CustAnaIn_Active35 | Para_Custom_AnalogIn_35_CustAnaIn_MinMaxActive35 | Para_Custom_AnalogIn_35_CustAnaIn_Set4mA35 | Para_Custom_AnalogIn_35_CustAnaIn_Typ35 | Para_Custom_AnalogIn_35_Hystereses | Para_Custom_AnalogIn_35_LimitHi | Para_Custom_AnalogIn_35_LimitHiHi | Para_Custom_AnalogIn_35_LimitLo | Para_Custom_AnalogIn_35_LimitLoLo | Para_Custom_AnalogIn_35_ScaleMax | Para_Custom_AnalogIn_35_ScaleMin | Para_Custom_AnalogIn_36_CustAnaIn_Active36 | Para_Custom_AnalogIn_36_CustAnaIn_MinMaxActive36 | Para_Custom_AnalogIn_36_CustAnaIn_Set4mA36 | Para_Custom_AnalogIn_36_CustAnaIn_Typ36 | Para_Custom_AnalogIn_36_Hystereses | Para_Custom_AnalogIn_36_LimitHi | Para_Custom_AnalogIn_36_LimitHiHi | Para_Custom_AnalogIn_36_LimitLo | Para_Custom_AnalogIn_36_LimitLoLo | Para_Custom_AnalogIn_36_ScaleMax | Para_Custom_AnalogIn_36_ScaleMin | Para_Custom_AnalogIn_37_CustAnaIn_Active37 | Para_Custom_AnalogIn_37_CustAnaIn_MinMaxActive37 | Para_Custom_AnalogIn_37_CustAnaIn_Set4mA37 | Para_Custom_AnalogIn_37_CustAnaIn_Typ37 | Para_Custom_AnalogIn_37_Hystereses | Para_Custom_AnalogIn_37_LimitHi | Para_Custom_AnalogIn_37_LimitHiHi | Para_Custom_AnalogIn_37_LimitLo | Para_Custom_AnalogIn_37_LimitLoLo | Para_Custom_AnalogIn_37_ScaleMax | Para_Custom_AnalogIn_37_ScaleMin | Para_Custom_AnalogIn_38_CustAnaIn_Active38 | Para_Custom_AnalogIn_38_CustAnaIn_MinMaxActive38 | Para_Custom_AnalogIn_38_CustAnaIn_Set4mA38 | Para_Custom_AnalogIn_38_CustAnaIn_Typ38 | Para_Custom_AnalogIn_38_Hystereses | Para_Custom_AnalogIn_38_LimitHi | Para_Custom_AnalogIn_38_LimitHiHi | Para_Custom_AnalogIn_38_LimitLo | Para_Custom_AnalogIn_38_LimitLoLo | Para_Custom_AnalogIn_38_ScaleMax | Para_Custom_AnalogIn_38_ScaleMin | Para_Custom_AnalogIn_39_CustAnaIn_Active39 | Para_Custom_AnalogIn_39_CustAnaIn_MinMaxActive39 | Para_Custom_AnalogIn_39_CustAnaIn_Set4mA39 | Para_Custom_AnalogIn_39_CustAnaIn_Typ39 | Para_Custom_AnalogIn_39_Hystereses | Para_Custom_AnalogIn_39_LimitHi | Para_Custom_AnalogIn_39_LimitHiHi | Para_Custom_AnalogIn_39_LimitLo | Para_Custom_AnalogIn_39_LimitLoLo | Para_Custom_AnalogIn_39_ScaleMax | Para_Custom_AnalogIn_39_ScaleMin | Para_Custom_AnalogIn_3_CustAnaIn_MinMaxActive3 | Para_Custom_AnalogIn_3_CustAnaIn_Typ3 | Para_Custom_AnalogIn_3_Hystereses | Para_Custom_AnalogIn_3_LimitHi | Para_Custom_AnalogIn_3_LimitHiHi | Para_Custom_AnalogIn_3_LimitLo | Para_Custom_AnalogIn_3_LimitLoLo | Para_Custom_AnalogIn_40_CustAnaIn_Active40 | Para_Custom_AnalogIn_40_CustAnaIn_MinMaxActive40 | Para_Custom_AnalogIn_40_CustAnaIn_Set4mA40 | Para_Custom_AnalogIn_40_CustAnaIn_Typ40 | Para_Custom_AnalogIn_40_Hystereses | Para_Custom_AnalogIn_40_LimitHi | Para_Custom_AnalogIn_40_LimitHiHi | Para_Custom_AnalogIn_40_LimitLo | Para_Custom_AnalogIn_40_LimitLoLo | Para_Custom_AnalogIn_40_ScaleMax | Para_Custom_AnalogIn_40_ScaleMin | Para_Custom_AnalogIn_41_CustAnaIn_Active41 | Para_Custom_AnalogIn_41_CustAnaIn_MinMaxActive41 | Para_Custom_AnalogIn_41_CustAnaIn_Set4mA41 | Para_Custom_AnalogIn_41_CustAnaIn_Typ41 | Para_Custom_AnalogIn_41_Hystereses | Para_Custom_AnalogIn_41_LimitHi | Para_Custom_AnalogIn_41_LimitHiHi | Para_Custom_AnalogIn_41_LimitLo | Para_Custom_AnalogIn_41_LimitLoLo | Para_Custom_AnalogIn_41_ScaleMax | Para_Custom_AnalogIn_41_ScaleMin | Para_Custom_AnalogIn_42_CustAnaIn_Active42 | Para_Custom_AnalogIn_42_CustAnaIn_MinMaxActive42 | Para_Custom_AnalogIn_42_CustAnaIn_Set4mA42 | Para_Custom_AnalogIn_42_CustAnaIn_Typ42 | Para_Custom_AnalogIn_42_Hystereses | Para_Custom_AnalogIn_42_LimitHi | Para_Custom_AnalogIn_42_LimitHiHi | Para_Custom_AnalogIn_42_LimitLo | Para_Custom_AnalogIn_42_LimitLoLo | Para_Custom_AnalogIn_42_ScaleMax | Para_Custom_AnalogIn_42_ScaleMin | Para_Custom_AnalogIn_43_CustAnaIn_Active43 | Para_Custom_AnalogIn_43_CustAnaIn_MinMaxActive43 | Para_Custom_AnalogIn_43_CustAnaIn_Set4mA43 | Para_Custom_AnalogIn_43_CustAnaIn_Typ43 | Para_Custom_AnalogIn_43_Hystereses | Para_Custom_AnalogIn_43_LimitHi | Para_Custom_AnalogIn_43_LimitHiHi | Para_Custom_AnalogIn_43_LimitLo | Para_Custom_AnalogIn_43_LimitLoLo | Para_Custom_AnalogIn_43_ScaleMax | Para_Custom_AnalogIn_43_ScaleMin | Para_Custom_AnalogIn_44_CustAnaIn_Active44 | Para_Custom_AnalogIn_44_CustAnaIn_MinMaxActive44 | Para_Custom_AnalogIn_44_CustAnaIn_Set4mA44 | Para_Custom_AnalogIn_44_CustAnaIn_Typ44 | Para_Custom_AnalogIn_44_Hystereses | Para_Custom_AnalogIn_44_LimitHi | Para_Custom_AnalogIn_44_LimitHiHi | Para_Custom_AnalogIn_44_LimitLo | Para_Custom_AnalogIn_44_LimitLoLo | Para_Custom_AnalogIn_44_ScaleMax | Para_Custom_AnalogIn_44_ScaleMin | Para_Custom_AnalogIn_45_CustAnaIn_Active45 | Para_Custom_AnalogIn_45_CustAnaIn_MinMaxActive45 | Para_Custom_AnalogIn_45_CustAnaIn_Set4mA45 | Para_Custom_AnalogIn_45_CustAnaIn_Typ45 | Para_Custom_AnalogIn_45_Hystereses | Para_Custom_AnalogIn_45_LimitHi | Para_Custom_AnalogIn_45_LimitHiHi | Para_Custom_AnalogIn_45_LimitLo | Para_Custom_AnalogIn_45_LimitLoLo | Para_Custom_AnalogIn_45_ScaleMax | Para_Custom_AnalogIn_45_ScaleMin | Para_Custom_AnalogIn_46_CustAnaIn_Active46 | Para_Custom_AnalogIn_46_CustAnaIn_MinMaxActive46 | Para_Custom_AnalogIn_46_CustAnaIn_Set4mA46 | Para_Custom_AnalogIn_46_CustAnaIn_Typ46 | Para_Custom_AnalogIn_46_Hystereses | Para_Custom_AnalogIn_46_LimitHi | Para_Custom_AnalogIn_46_LimitHiHi | Para_Custom_AnalogIn_46_LimitLo | Para_Custom_AnalogIn_46_LimitLoLo | Para_Custom_AnalogIn_46_ScaleMax | Para_Custom_AnalogIn_46_ScaleMin | Para_Custom_AnalogIn_47_CustAnaIn_Active47 | Para_Custom_AnalogIn_47_CustAnaIn_MinMaxActive47 | Para_Custom_AnalogIn_47_CustAnaIn_Set4mA47 | Para_Custom_AnalogIn_47_CustAnaIn_Typ47 | Para_Custom_AnalogIn_47_Hystereses | Para_Custom_AnalogIn_47_LimitHi | Para_Custom_AnalogIn_47_LimitHiHi | Para_Custom_AnalogIn_47_LimitLo | Para_Custom_AnalogIn_47_LimitLoLo | Para_Custom_AnalogIn_47_ScaleMax | Para_Custom_AnalogIn_47_ScaleMin | Para_Custom_AnalogIn_48_CustAnaIn_Active48 | Para_Custom_AnalogIn_48_CustAnaIn_MinMaxActive48 | Para_Custom_AnalogIn_48_CustAnaIn_Set4mA48 | Para_Custom_AnalogIn_48_CustAnaIn_Typ48 | Para_Custom_AnalogIn_48_Hystereses | Para_Custom_AnalogIn_48_LimitHi | Para_Custom_AnalogIn_48_LimitHiHi | Para_Custom_AnalogIn_48_LimitLo | Para_Custom_AnalogIn_48_LimitLoLo | Para_Custom_AnalogIn_48_ScaleMax | Para_Custom_AnalogIn_48_ScaleMin | Para_Custom_AnalogIn_49_CustAnaIn_Active49 | Para_Custom_AnalogIn_49_CustAnaIn_MinMaxActive49 | Para_Custom_AnalogIn_49_CustAnaIn_Set4mA49 | Para_Custom_AnalogIn_49_CustAnaIn_Typ49 | Para_Custom_AnalogIn_49_Hystereses | Para_Custom_AnalogIn_49_LimitHi | Para_Custom_AnalogIn_49_LimitHiHi | Para_Custom_AnalogIn_49_LimitLo | Para_Custom_AnalogIn_49_LimitLoLo | Para_Custom_AnalogIn_49_ScaleMax | Para_Custom_AnalogIn_49_ScaleMin | Para_Custom_AnalogIn_4_CustAnaIn_MinMaxActive4 | Para_Custom_AnalogIn_4_CustAnaIn_Typ4 | Para_Custom_AnalogIn_4_Hystereses | Para_Custom_AnalogIn_4_LimitHi | Para_Custom_AnalogIn_4_LimitHiHi | Para_Custom_AnalogIn_4_LimitLo | Para_Custom_AnalogIn_4_LimitLoLo | Para_Custom_AnalogIn_50_CustAnaIn_Active50 | Para_Custom_AnalogIn_50_CustAnaIn_MinMaxActive50 | Para_Custom_AnalogIn_50_CustAnaIn_Set4mA50 | Para_Custom_AnalogIn_50_CustAnaIn_Typ50 | Para_Custom_AnalogIn_50_Hystereses | Para_Custom_AnalogIn_50_LimitHi | Para_Custom_AnalogIn_50_LimitHiHi | Para_Custom_AnalogIn_50_LimitLo | Para_Custom_AnalogIn_50_LimitLoLo | Para_Custom_AnalogIn_50_ScaleMax | Para_Custom_AnalogIn_50_ScaleMin | Para_Custom_AnalogIn_51_CustAnaIn_Active51 | Para_Custom_AnalogIn_51_CustAnaIn_MinMaxActive51 | Para_Custom_AnalogIn_51_CustAnaIn_Set4mA51 | Para_Custom_AnalogIn_51_CustAnaIn_Typ51 | Para_Custom_AnalogIn_51_Hystereses | Para_Custom_AnalogIn_51_LimitHi | Para_Custom_AnalogIn_51_LimitHiHi | Para_Custom_AnalogIn_51_LimitLo | Para_Custom_AnalogIn_51_LimitLoLo | Para_Custom_AnalogIn_51_ScaleMax | Para_Custom_AnalogIn_51_ScaleMin | Para_Custom_AnalogIn_52_CustAnaIn_Active52 | Para_Custom_AnalogIn_52_CustAnaIn_MinMaxActive52 | Para_Custom_AnalogIn_52_CustAnaIn_Set4mA52 | Para_Custom_AnalogIn_52_CustAnaIn_Typ52 | Para_Custom_AnalogIn_52_Hystereses | Para_Custom_AnalogIn_52_LimitHi | Para_Custom_AnalogIn_52_LimitHiHi | Para_Custom_AnalogIn_52_LimitLo | Para_Custom_AnalogIn_52_LimitLoLo | Para_Custom_AnalogIn_52_ScaleMax | Para_Custom_AnalogIn_52_ScaleMin | Para_Custom_AnalogIn_53_CustAnaIn_Active53 | Para_Custom_AnalogIn_53_CustAnaIn_MinMaxActive53 | Para_Custom_AnalogIn_53_CustAnaIn_Set4mA53 | Para_Custom_AnalogIn_53_CustAnaIn_Typ53 | Para_Custom_AnalogIn_53_Hystereses | Para_Custom_AnalogIn_53_LimitHi | Para_Custom_AnalogIn_53_LimitHiHi | Para_Custom_AnalogIn_53_LimitLo | Para_Custom_AnalogIn_53_LimitLoLo | Para_Custom_AnalogIn_53_ScaleMax | Para_Custom_AnalogIn_53_ScaleMin | Para_Custom_AnalogIn_54_CustAnaIn_Active54 | Para_Custom_AnalogIn_54_CustAnaIn_MinMaxActive54 | Para_Custom_AnalogIn_54_CustAnaIn_Set4mA54 | Para_Custom_AnalogIn_54_CustAnaIn_Typ54 | Para_Custom_AnalogIn_54_Hystereses | Para_Custom_AnalogIn_54_LimitHi | Para_Custom_AnalogIn_54_LimitHiHi | Para_Custom_AnalogIn_54_LimitLo | Para_Custom_AnalogIn_54_LimitLoLo | Para_Custom_AnalogIn_54_ScaleMax | Para_Custom_AnalogIn_54_ScaleMin | Para_Custom_AnalogIn_55_CustAnaIn_Active55 | Para_Custom_AnalogIn_55_CustAnaIn_MinMaxActive55 | Para_Custom_AnalogIn_55_CustAnaIn_Set4mA55 | Para_Custom_AnalogIn_55_CustAnaIn_Typ55 | Para_Custom_AnalogIn_55_Hystereses | Para_Custom_AnalogIn_55_LimitHi | Para_Custom_AnalogIn_55_LimitHiHi | Para_Custom_AnalogIn_55_LimitLo | Para_Custom_AnalogIn_55_LimitLoLo | Para_Custom_AnalogIn_55_ScaleMax | Para_Custom_AnalogIn_55_ScaleMin | Para_Custom_AnalogIn_56_CustAnaIn_Active56 | Para_Custom_AnalogIn_56_CustAnaIn_MinMaxActive56 | Para_Custom_AnalogIn_56_CustAnaIn_Set4mA56 | Para_Custom_AnalogIn_56_CustAnaIn_Typ56 | Para_Custom_AnalogIn_56_Hystereses | Para_Custom_AnalogIn_56_LimitHi | Para_Custom_AnalogIn_56_LimitHiHi | Para_Custom_AnalogIn_56_LimitLo | Para_Custom_AnalogIn_56_LimitLoLo | Para_Custom_AnalogIn_56_ScaleMax | Para_Custom_AnalogIn_56_ScaleMin | Para_Custom_AnalogIn_57_CustAnaIn_Active57 | Para_Custom_AnalogIn_57_CustAnaIn_MinMaxActive57 | Para_Custom_AnalogIn_57_CustAnaIn_Set4mA57 | Para_Custom_AnalogIn_57_CustAnaIn_Typ57 | Para_Custom_AnalogIn_57_Hystereses | Para_Custom_AnalogIn_57_LimitHi | Para_Custom_AnalogIn_57_LimitHiHi | Para_Custom_AnalogIn_57_LimitLo | Para_Custom_AnalogIn_57_LimitLoLo | Para_Custom_AnalogIn_57_ScaleMax | Para_Custom_AnalogIn_57_ScaleMin | Para_Custom_AnalogIn_58_CustAnaIn_Active58 | Para_Custom_AnalogIn_58_CustAnaIn_MinMaxActive58 | Para_Custom_AnalogIn_58_CustAnaIn_Set4mA58 | Para_Custom_AnalogIn_58_CustAnaIn_Typ58 | Para_Custom_AnalogIn_58_Hystereses | Para_Custom_AnalogIn_58_LimitHi | Para_Custom_AnalogIn_58_LimitHiHi | Para_Custom_AnalogIn_58_LimitLo | Para_Custom_AnalogIn_58_LimitLoLo | Para_Custom_AnalogIn_58_ScaleMax | Para_Custom_AnalogIn_58_ScaleMin | Para_Custom_AnalogIn_59_CustAnaIn_Active59 | Para_Custom_AnalogIn_59_CustAnaIn_MinMaxActive59 | Para_Custom_AnalogIn_59_CustAnaIn_Set4mA59 | Para_Custom_AnalogIn_59_CustAnaIn_Typ59 | Para_Custom_AnalogIn_59_Hystereses | Para_Custom_AnalogIn_59_LimitHi | Para_Custom_AnalogIn_59_LimitHiHi | Para_Custom_AnalogIn_59_LimitLo | Para_Custom_AnalogIn_59_LimitLoLo | Para_Custom_AnalogIn_59_ScaleMax | Para_Custom_AnalogIn_59_ScaleMin | Para_Custom_AnalogIn_5_CustAnaIn_MinMaxActive5 | Para_Custom_AnalogIn_5_CustAnaIn_Typ5 | Para_Custom_AnalogIn_5_Hystereses | Para_Custom_AnalogIn_5_LimitHi | Para_Custom_AnalogIn_5_LimitHiHi | Para_Custom_AnalogIn_5_LimitLo | Para_Custom_AnalogIn_5_LimitLoLo | Para_Custom_AnalogIn_60_CustAnaIn_Active60 | Para_Custom_AnalogIn_60_CustAnaIn_MinMaxActive60 | Para_Custom_AnalogIn_60_CustAnaIn_Set4mA60 | Para_Custom_AnalogIn_60_CustAnaIn_Typ60 | Para_Custom_AnalogIn_60_Hystereses | Para_Custom_AnalogIn_60_LimitHi | Para_Custom_AnalogIn_60_LimitHiHi | Para_Custom_AnalogIn_60_LimitLo | Para_Custom_AnalogIn_60_LimitLoLo | Para_Custom_AnalogIn_60_ScaleMax | Para_Custom_AnalogIn_60_ScaleMin | Para_Custom_AnalogIn_6_CustAnaIn_MinMaxActive6 | Para_Custom_AnalogIn_6_CustAnaIn_Typ6 | Para_Custom_AnalogIn_6_Hystereses | Para_Custom_AnalogIn_6_LimitHi | Para_Custom_AnalogIn_6_LimitHiHi | Para_Custom_AnalogIn_6_LimitLo | Para_Custom_AnalogIn_6_LimitLoLo | Para_Custom_AnalogIn_7_CustAnaIn_MinMaxActive7 | Para_Custom_AnalogIn_7_CustAnaIn_Typ7 | Para_Custom_AnalogIn_7_Hystereses | Para_Custom_AnalogIn_7_LimitHi | Para_Custom_AnalogIn_7_LimitHiHi | Para_Custom_AnalogIn_7_LimitLo | Para_Custom_AnalogIn_7_LimitLoLo | Para_Custom_AnalogIn_8_CustAnaIn_MinMaxActive8 | Para_Custom_AnalogIn_8_CustAnaIn_Typ8 | Para_Custom_AnalogIn_8_Hystereses | Para_Custom_AnalogIn_8_LimitHi | Para_Custom_AnalogIn_8_LimitHiHi | Para_Custom_AnalogIn_8_LimitLo | Para_Custom_AnalogIn_8_LimitLoLo | Para_Custom_AnalogIn_9_CustAnaIn_MinMaxActive9 | Para_Custom_AnalogIn_9_CustAnaIn_Typ9 | Para_Custom_AnalogIn_9_Hystereses | Para_Custom_AnalogIn_9_LimitHi | Para_Custom_AnalogIn_9_LimitHiHi | Para_Custom_AnalogIn_9_LimitLo | Para_Custom_AnalogIn_9_LimitLoLo | Para_Custom_AnalogOut_AO10_HardwareScaleMax | Para_Custom_AnalogOut_AO10_HardwareScaleMin | Para_Custom_AnalogOut_AO10_ScaleMax | Para_Custom_AnalogOut_AO10_ScaleMin | Para_Custom_AnalogOut_AO11_HardwareScaleMax | Para_Custom_AnalogOut_AO11_HardwareScaleMin | Para_Custom_AnalogOut_AO11_ScaleMax | Para_Custom_AnalogOut_AO11_ScaleMin | Para_Custom_AnalogOut_AO12_HardwareScaleMax | Para_Custom_AnalogOut_AO12_HardwareScaleMin | Para_Custom_AnalogOut_AO12_ScaleMax | Para_Custom_AnalogOut_AO12_ScaleMin | Para_Custom_AnalogOut_AO13_HardwareScaleMax | Para_Custom_AnalogOut_AO13_HardwareScaleMin | Para_Custom_AnalogOut_AO13_ScaleMax | Para_Custom_AnalogOut_AO13_ScaleMin | Para_Custom_AnalogOut_AO14_HardwareScaleMax | Para_Custom_AnalogOut_AO14_HardwareScaleMin | Para_Custom_AnalogOut_AO14_ScaleMax | Para_Custom_AnalogOut_AO14_ScaleMin | Para_Custom_AnalogOut_AO15_HardwareScaleMax | Para_Custom_AnalogOut_AO15_HardwareScaleMin | Para_Custom_AnalogOut_AO15_ScaleMax | Para_Custom_AnalogOut_AO15_ScaleMin | Para_Custom_AnalogOut_AO16_HardwareScaleMax | Para_Custom_AnalogOut_AO16_HardwareScaleMin | Para_Custom_AnalogOut_AO16_ScaleMax | Para_Custom_AnalogOut_AO16_ScaleMin | Para_Custom_AnalogOut_AO1_HardwareScaleMax | Para_Custom_AnalogOut_AO1_HardwareScaleMin | Para_Custom_AnalogOut_AO1_ScaleMax | Para_Custom_AnalogOut_AO1_ScaleMin | Para_Custom_AnalogOut_AO2_HardwareScaleMax | Para_Custom_AnalogOut_AO2_HardwareScaleMin | Para_Custom_AnalogOut_AO2_ScaleMax | Para_Custom_AnalogOut_AO2_ScaleMin | Para_Custom_AnalogOut_AO3_HardwareScaleMax | Para_Custom_AnalogOut_AO3_HardwareScaleMin | Para_Custom_AnalogOut_AO3_ScaleMax | Para_Custom_AnalogOut_AO3_ScaleMin | Para_Custom_AnalogOut_AO4_HardwareScaleMax | Para_Custom_AnalogOut_AO4_HardwareScaleMin | Para_Custom_AnalogOut_AO4_ScaleMax | Para_Custom_AnalogOut_AO4_ScaleMin | Para_Custom_AnalogOut_AO5_HardwareScaleMax | Para_Custom_AnalogOut_AO5_HardwareScaleMin | Para_Custom_AnalogOut_AO5_ScaleMax | Para_Custom_AnalogOut_AO5_ScaleMin | Para_Custom_AnalogOut_AO6_HardwareScaleMax | Para_Custom_AnalogOut_AO6_HardwareScaleMin | Para_Custom_AnalogOut_AO6_ScaleMax | Para_Custom_AnalogOut_AO6_ScaleMin | Para_Custom_AnalogOut_AO7_HardwareScaleMax | Para_Custom_AnalogOut_AO7_HardwareScaleMin | Para_Custom_AnalogOut_AO7_ScaleMax | Para_Custom_AnalogOut_AO7_ScaleMin | Para_Custom_AnalogOut_AO8_HardwareScaleMax | Para_Custom_AnalogOut_AO8_HardwareScaleMin | Para_Custom_AnalogOut_AO8_ScaleMax | Para_Custom_AnalogOut_AO8_ScaleMin | Para_Custom_AnalogOut_AO9_HardwareScaleMax | Para_Custom_AnalogOut_AO9_HardwareScaleMin | Para_Custom_AnalogOut_AO9_ScaleMax | Para_Custom_AnalogOut_AO9_ScaleMin | Para_Custom_Status_AuxCust_Active1 | Para_Custom_Status_AuxCust_Active10 | Para_Custom_Status_AuxCust_Active11 | Para_Custom_Status_AuxCust_Active12 | Para_Custom_Status_AuxCust_Active13 | Para_Custom_Status_AuxCust_Active14 | Para_Custom_Status_AuxCust_Active15 | Para_Custom_Status_AuxCust_Active16 | Para_Custom_Status_AuxCust_Active17 | Para_Custom_Status_AuxCust_Active18 | Para_Custom_Status_AuxCust_Active19 | Para_Custom_Status_AuxCust_Active2 | Para_Custom_Status_AuxCust_Active20 | Para_Custom_Status_AuxCust_Active21 | Para_Custom_Status_AuxCust_Active22 | Para_Custom_Status_AuxCust_Active23 | Para_Custom_Status_AuxCust_Active24 | Para_Custom_Status_AuxCust_Active25 | Para_Custom_Status_AuxCust_Active26 | Para_Custom_Status_AuxCust_Active27 | Para_Custom_Status_AuxCust_Active28 | Para_Custom_Status_AuxCust_Active29 | Para_Custom_Status_AuxCust_Active3 | Para_Custom_Status_AuxCust_Active30 | Para_Custom_Status_AuxCust_Active31 | Para_Custom_Status_AuxCust_Active32 | Para_Custom_Status_AuxCust_Active33 | Para_Custom_Status_AuxCust_Active34 | Para_Custom_Status_AuxCust_Active35 | Para_Custom_Status_AuxCust_Active36 | Para_Custom_Status_AuxCust_Active37 | Para_Custom_Status_AuxCust_Active38 | Para_Custom_Status_AuxCust_Active39 | Para_Custom_Status_AuxCust_Active4 | Para_Custom_Status_AuxCust_Active40 | Para_Custom_Status_AuxCust_Active5 | Para_Custom_Status_AuxCust_Active6 | Para_Custom_Status_AuxCust_Active7 | Para_Custom_Status_AuxCust_Active8 | Para_Custom_Status_AuxCust_Active9 | Para_Cylinder_Bearing_Pc_T_CBearing_Sig_Lo | Para_Cylinder_Bearing_T_CBearing_Exist | Para_Cylinder_Bearing_T_CBearing_Hi | Para_Cylinder_Bearing_T_CBearing_Hi_Offset | Para_Cylinder_Bearing_T_CBearing_HiHi | Para_Cylinder_Bearing_T_CBearing_MDev_HiHi | Para_Cylinder_Bearing_T_MBearing_Exist | Para_Cylinder_Bearing_T_MBearing_Hi | Para_Cylinder_Bearing_T_MBearing_HiHi | Para_Cylinder_Bearing_T_MBearing_MDev_HiHi | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset1 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset10 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset11 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset12 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset13 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset14 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset15 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset16 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset17 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset18 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset19 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset2 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset20 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset21 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset22 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset23 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset24 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset3 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset4 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset5 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset6 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset7 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset8 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset9 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset_Active | Para_Cylinder_Ignition_CA_AdvTimeLim | Para_Cylinder_Ignition_CA_Ign_OP_Power1 | Para_Cylinder_Ignition_CA_Ign_OP_Power2 | Para_Cylinder_Ignition_CA_Ign_OP_Power3 | Para_Cylinder_Ignition_CA_Ign_OP_Power4 | Para_Cylinder_Ignition_CA_Ign_OP_Speed1 | Para_Cylinder_Ignition_CA_Ign_OP_Speed2 | Para_Cylinder_Ignition_CA_Ign_OP_Speed3 | Para_Cylinder_Ignition_CA_Ign_OP_Speed4 | Para_Cylinder_Ignition_CA_RetTimeLim | Para_Cylinder_Ignition_MisfCont | Para_Cylinder_Ignition_MORIS_CoilType0_Current | Para_Cylinder_Ignition_MORIS_CoilType0_Time | Para_Cylinder_Ignition_MORIS_SparkChar1_Current | Para_Cylinder_Ignition_MORIS_SparkChar1_Time | Para_Cylinder_Ignition_MORIS_SparkChar2_Current | Para_Cylinder_Ignition_MORIS_SparkChar2_Time | Para_Cylinder_Ignition_MORIS_SparkChar3_Current | Para_Cylinder_Ignition_MORIS_SparkChar3_Time | Para_Cylinder_Ignition_MORIS_SparkChar4_Current | Para_Cylinder_Ignition_MORIS_SparkChar4_Time | Para_Cylinder_Ignition_MORIS_SparkChar5_Current | Para_Cylinder_Ignition_MORIS_SparkChar5_Time | Para_Cylinder_Ignition_MORIS_SparkChar6_Current | Para_Cylinder_Ignition_MORIS_VarSparkDur_DynSparkDuration | Para_Cylinder_Ignition_MORIS_VarSparkDur_P_Act_DynSpark_Limit_Nom | Para_Cylinder_Ignition_MORIS_VarSparkDur_usDurationIdle | Para_Cylinder_Knock_CA_IP_Knck_Max | Para_Cylinder_Knock_Kno_Int_MinLim | Para_Cylinder_Knock_Kno_IP_Scale_StP | Para_Cylinder_Knock_Kno_P2s_Inc_EnP | Para_Cylinder_Knock_Kno_P2s_Inc_StP | Para_Cylinder_Knock_Kno_Pmax_CylMax | Para_Cylinder_Knock_Kno_Pmax_Red_EnP_dlt | Para_Cylinder_Knock_Kno_Pmax_Red_StP | Para_Cylinder_Knock_PBC_Pr_PBC_Knck_Heavy | Para_Cylinder_Knock_PBC_Pr_PBC_Knck_Lim | Para_Cylinder_Knock_Pmax_Knck_Max | Para_Cylinder_Knock_Pr_P2s_Knck_Max | Para_Cylinder_Monic1_delay | Para_Cylinder_Monic1_limit | Para_Cylinder_Monic2_delay | Para_Cylinder_Monic2_limit | Para_Cylinder_Monic3_delay | Para_Cylinder_Monic3_limit | Para_Cylinder_Monic4_delay | Para_Cylinder_Monic4_limit | Para_Cylinder_Monic_Ign_LimitMonitorActive1 | Para_Cylinder_Monic_Ign_LimitMonitorActive2 | Para_Cylinder_Monic_Ign_LimitMonitorActive3 | Para_Cylinder_Monic_Ign_LimitMonitorActive4 | Para_Cylinder_PBC_CoVControl_CoV_Set100 | Para_Cylinder_PBC_CoVControl_CoV_Set50 | Para_Cylinder_PBC_CoVControl_CoVCtr_Act | Para_Cylinder_PBC_CoVControl_CoVCtr_ki | Para_Cylinder_PBC_CoVControl_CoVCtr_kp | Para_Cylinder_PBC_CoVControl_Pr_CoV_p2s_Range | Para_Cylinder_PBC_MFB50Control_CA_MFB50_ITPOfs_early | Para_Cylinder_PBC_MFB50Control_CA_MFB50_ITPOfs_late | Para_Cylinder_PBC_MFB50Control_CA_MFB50_set100 | Para_Cylinder_PBC_MFB50Control_CA_MFB50_set50 | Para_Cylinder_PBC_MFB50Control_MFB50_ITP_ratio | Para_Cylinder_PBC_MFB50Control_MFB50Contr_Ena | Para_Cylinder_PBC_MFB50Control_MFB50Ctr_ki | Para_Cylinder_PBC_MFB50Control_MFB50Ctr_kp | Para_Cylinder_PBC_Num_IMEP_Misf_Lim | Para_Cylinder_PBC_P_PBC_Act_Hys | Para_Cylinder_PBC_P_PBC_Act_SP | Para_Cylinder_PBC_Pr_CPP_AbsLim_LHE | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_cur_gradient | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_duration | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_set_current | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_set_duration | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time1 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time10 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time11 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time12 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time13 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time14 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time15 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time16 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time17 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time18 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time19 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time2 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time20 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time21 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time22 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time23 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time24 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time3 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time4 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time5 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time6 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time7 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time8 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time9 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_var_limit_Idle | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_var_limit_Load | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_var_limit_Start | Para_Cylinder_PI_CorrectCurrCtr_SA_PI_currCtr_delay | Para_Cylinder_PI_CorrectCurrCtr_SA_PI_currCtr_duration | Para_Cylinder_PI_CorrectCurrCtr_SA_PI_currCtr_level | Para_Cylinder_PI_CorrectCurrCtr_SA_PI_currCtr_rate | Para_Cylinder_PI_CurrentProfile_SA_PI_curr1_current | Para_Cylinder_PI_CurrentProfile_SA_PI_curr1_duration | Para_Cylinder_PI_CurrentProfile_SA_PI_curr2_current | Para_Cylinder_PI_CurrentProfile_SA_PI_curr2_duration | Para_Cylinder_PI_CurrentProfile_SA_PI_curr3_current | Para_Cylinder_PI_CurrentProfile_SA_PI_curr3_duration | Para_Cylinder_PI_CurrentProfile_SA_PI_curr4_current | Para_Cylinder_PI_CurrentRecovery_SA_PI_recov_current | Para_Cylinder_PI_CurrentRecovery_SA_PI_recov_delay | Para_Cylinder_PI_CurrentRecovery_SA_PI_recov_duration | Para_Cylinder_PI_Demagnet_PIDemagActive | Para_Cylinder_PI_Demagnet_SA_PI_demag_delay | Para_Cylinder_PI_Demagnet_SA_PI_demag_duration | Para_Cylinder_PI_Demagnet_SA_PI_demag_up_limit | Para_Cylinder_PI_MisfCyl_Max_Norm | Para_Cylinder_PI_P_MisfCtr_Hys_Norm | Para_Cylinder_PI_P_MisfCtr_SP_Norm | Para_Cylinder_PI_PullInCurrCheck_SA_PI_pudet_duration | Para_Cylinder_PI_PullInCurrCheck_SA_PI_pudet_level | Para_Cylinder_PI_PullInCurrCheck_SA_PI_pudet_st_time | Para_Cylinder_PI_SA_CyclPIOnDuringMisf | Para_Cylinder_PI_SA_PIValveType | Para_Cylinder_PI_ti_OpTi_MisCyl_Trig | Para_Cylinder_PI_ti_OpTi_MisfCyl | Para_Electrical_GeneratCtr_ChoiceSet_PF_CosPCtr_PF_Set1 | Para_Electrical_GeneratCtr_PF_Customer_Selected | Para_Electrical_GeneratCtr_QLimit_Q_OverExc_Lim | Para_Electrical_GeneratCtr_QLimit_Q_UnderExc_Lim | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h0 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h1 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h2 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h3 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h4 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h5 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m0 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m1 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m2 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m3 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m4 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m5 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set0 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set1 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set2 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set3 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set4 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set5 | Para_Electrical_GeneratCtr_Voltage_F_Gen_Match_Max | Para_Electrical_GeneratCtr_Voltage_F_Gen_Match_Min | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map0 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map10 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map2 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map4 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map6 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map8 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set0 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set1 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set2 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set3 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set4 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set5 | Para_Electrical_GeneratCtr_Voltage_U_adj_gcb_ext_hilo_a | Para_Electrical_GeneratCtr_Voltage_U_adj_gcb_mmd_calc_a | Para_Electrical_GeneratCtr_Voltage_U_adj_mcb_ext_hilo_a | Para_Electrical_GeneratCtr_Voltage_U_adj_mcb_mmd_calc_a | Para_Electrical_GeneratCtr_Voltage_U_Gen_match_delta | Para_Electrical_GeneratCtr_Voltage_U_Gen_P_Ena | Para_Electrical_GeneratCtr_Voltage_U_Gen_Rmp_Inc | Para_Electrical_GeneratCtr_Voltage_U_Gen_spd_match | Para_Electrical_Generator_F_GenBear_DE1_Active | Para_Electrical_Generator_F_GenBear_DE2_Active | Para_Electrical_Generator_F_GenBear_NDE1_Active | Para_Electrical_Generator_F_GenBear_NDE2_Active | Para_Electrical_Generator_F_GenBear_ScalMax | Para_Electrical_Generator_F_GenBear_ScalMin | Para_Electrical_Generator_T_GenAirIn2_Active | Para_Electrical_Generator_T_Pred_GenAirIn_Rate | Para_Electrical_Generator_T_Pred_GenAirIn_Start | Para_Electrical_Generator_ti_Gen_VoltReg_Fail | Para_Electrical_Generator_tiF_GenBear_Hi | Para_Electrical_Generator_tiF_GenBear_HiHi | Para_Electrical_Generator_tiP_Gen_Reverse | Para_Electrical_Generator_tiP_Gen_Reverse2 | Para_Electrical_Generator_tiP_Reverse_Mon_Ena | Para_Electrical_Generator_tiPF_CosPCtr_del | Para_Electrical_Generator_U_Gen_Contr_Sel | Para_Electrical_Generator_U_Gen_Nom_2 | Para_Electrical_Grid_GridCodeDyn_GrC_CapStop | Para_Electrical_Grid_GridCodeDyn_GrC_Prof_Active0 | Para_Electrical_Grid_GridCodeDyn_GrC_Prof_Active1 | Para_Electrical_Grid_GridCodeDyn_GrC_Prof_Active2 | Para_Electrical_Grid_GridCodeDyn_GridCode_Active | Para_Electrical_Grid_GridCodeDyn_GridCode_Prof23_Active | Para_Electrical_Grid_GridCodeDyn_GridCodeMonitoringOnly | Para_Electrical_Grid_GridCodeDyn_ti_GrC_Prof0 | Para_Electrical_Grid_GridCodeDyn_ti_GrC_Prof1 | Para_Electrical_Grid_GridCodeDyn_ti_GrC_Prof2 | Para_Electrical_Grid_GridCodeDyn_U_GrC_Prof_Norm0 | Para_Electrical_Grid_GridCodeDyn_U_GrC_Prof_Norm1 | Para_Electrical_Grid_GridCodeDyn_U_GrC_Prof_Norm2 | Para_Electrical_Grid_GridCodeStatic_DEIE_Active | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_Droop_FC_neg | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_Droop_FC_pos | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_F_FC_Deadband_neg | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_F_FC_Deadband_pos | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_F_FC_Dlt_neg | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_F_FC_Dlt_pos | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_Calc_PRamp_FC_active | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_PRamp_FC_DecGrad_Norm | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_PRamp_FC_ExtInp | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_PRamp_FC_IncGrad_Norm | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_PRamp_FC_SetCOn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_tiSetTime_FC_PRamp | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_Set_FC_COn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_Set_FC_ExtInp | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_Set_FC_Input | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_SetMarg_FC_neg | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_SetMarg_FC_pos | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_SetMarg_FC_StaInp | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TestFunction_FAct_FC_ManualTest | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TestFunction_FNom_FC_ManualTest | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TestFunction_Set_FC_Testmode | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_F_FC_Deadband_TAF_neg | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_F_FC_Deadband_TAF_pos | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_P_SetMarg_FC_TAF | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_HFRCOn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_PORCOn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_RRCOn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_SORCOn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_SRCOn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_TimeActFunctCOn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_TOR2COn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_TORCOn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_POR | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_RR | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_SOR | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_SR | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_TOR | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_TOR2 | Para_Electrical_Grid_GridCodeStatic_PowerLimit_P_DEIE_ScalMax | Para_Electrical_Grid_GridCodeStatic_PowerLimit_P_DEIE_ScalMin | Para_Electrical_Grid_GridCodeStatic_tiDelayDEIE | Para_Electrical_Grid_Synchronization_ADL_Enable | Para_Electrical_Grid_Synchronization_BB_ClosCondLimits_Active | Para_Electrical_Grid_Synchronization_BS_Acc_Active | Para_Electrical_Grid_Synchronization_BS_Enable | Para_Electrical_Grid_Synchronization_BS_OnlyMan | Para_Electrical_Grid_Synchronization_C_CB_Enable | Para_Electrical_Grid_Synchronization_EngOpAfterMIF_Enable | Para_Electrical_Grid_Synchronization_F_BB_ClosCond_Hy | Para_Electrical_Grid_Synchronization_F_BB_ClosCond_LimHi | Para_Electrical_Grid_Synchronization_F_BB_ClosCond_LimLo | Para_Electrical_Grid_Synchronization_GCB_MainsCutOff_Active | Para_Electrical_Grid_Synchronization_GenDeexit_Enable | Para_Electrical_Grid_Synchronization_IslandOp_Enable | Para_Electrical_Grid_Synchronization_MCB_Ctr_Cust | Para_Electrical_Grid_Synchronization_MCB_Enable | Para_Electrical_Grid_Synchronization_MCB_ReSw2Mns_Enable | Para_Electrical_Grid_Synchronization_MCB_SyMMD2 | Para_Electrical_Grid_Synchronization_MIF_Enable | Para_Electrical_Grid_Synchronization_Mns_Enable | Para_Electrical_Grid_Synchronization_MSy | Para_Electrical_Grid_Synchronization_N_BS_Acc_LimHi | Para_Electrical_Grid_Synchronization_OnlyIsland_Enable | Para_Electrical_Grid_Synchronization_SyActive | Para_Electrical_Grid_Synchronization_tiBB_ClosCond_Delay | Para_Electrical_Grid_Synchronization_tiBB_ClosCondAftMnsFail_Delay | Para_Electrical_Grid_Synchronization_tiMainsOkDelay | Para_Electrical_Grid_Synchronization_tiMCB_COf_GCB_OpF | Para_Electrical_Grid_Synchronization_tiMIF | Para_Electrical_Grid_Synchronization_U_BB_ClosCond_Hy_Norm | Para_Electrical_Grid_Synchronization_U_BB_ClosCond_LimHi_Norm | Para_Electrical_Grid_Synchronization_U_BB_ClosCond_LimLo_Norm | Para_Electrical_Grid_Synchronization_U_Gen_DeEx_LimLo | Para_Electrical_MMD_MMD1_Ang_DiffMax1 | Para_Electrical_MMD_MMD1_Ang_PhiSync11 | Para_Electrical_MMD_MMD1_Aron_Act1 | Para_Electrical_MMD_MMD1_Bus3PhaseCircuit_Act1 | Para_Electrical_MMD_MMD1_F_DiffMin1 | Para_Electrical_MMD_MMD1_F_Nom1 | Para_Electrical_MMD_MMD1_F_Over1 | Para_Electrical_MMD_MMD1_F_Under1 | Para_Electrical_MMD_MMD1_Gen3PhaseCircuit_Act1 | Para_Electrical_MMD_MMD1_I_CurrRange1 | Para_Electrical_MMD_MMD1_I_GenNom1 | Para_Electrical_MMD_MMD1_I_Short1 | Para_Electrical_MMD_MMD1_MMDSynch_Act1 | Para_Electrical_MMD_MMD1_Mul_U_Bus1 | Para_Electrical_MMD_MMD1_Ti_F_OverDel1 | Para_Electrical_MMD_MMD1_Ti_F_UnderDel1 | Para_Electrical_MMD_MMD1_Ti_I_ShortDel1 | Para_Electrical_MMD_MMD1_Ti_U_AsymDel1 | Para_Electrical_MMD_MMD1_Ti_V_Over1 | Para_Electrical_MMD_MMD1_Ti_V_Under1 | Para_Electrical_MMD_MMD1_Ti_V_Under21 | Para_Electrical_MMD_MMD1_U_Asym1 | Para_Electrical_MMD_MMD1_U_BusNom1 | Para_Electrical_MMD_MMD1_U_DeadBus1 | Para_Electrical_MMD_MMD1_U_DeadSync1 | Para_Electrical_MMD_MMD1_U_DiffMax1 | Para_Electrical_MMD_MMD1_U_Gen_Nom1 | Para_Electrical_MMD_MMD1_U_Range1 | Para_Electrical_MMD_MMD1_U_RangeBus1 | Para_Electrical_MMD_MMD1_U_RangeSync11 | Para_Electrical_MMD_MMD1_U_RangeSync21 | Para_Electrical_MMD_MMD1_U_SyncNom1 | Para_Electrical_MMD_MMD1_V_Over1 | Para_Electrical_MMD_MMD1_V_Under1 | Para_Electrical_MMD_MMD1_V_Under21 | Para_Electrical_MMD_MMD2_Act | Para_Electrical_MMD_MMD2_Ang_DiffMax2 | Para_Electrical_MMD_MMD2_Ang_PhiSync12 | Para_Electrical_MMD_MMD2_Aron_Act2 | Para_Electrical_MMD_MMD2_Bus3PhaseCircuit_Act2 | Para_Electrical_MMD_MMD2_F_DiffMin2 | Para_Electrical_MMD_MMD2_F_Nom2 | Para_Electrical_MMD_MMD2_F_Over2 | Para_Electrical_MMD_MMD2_F_Under2 | Para_Electrical_MMD_MMD2_Gen3PhaseCircuit_Act2 | Para_Electrical_MMD_MMD2_I_CurrRange2 | Para_Electrical_MMD_MMD2_I_GenNom2 | Para_Electrical_MMD_MMD2_I_Short2 | Para_Electrical_MMD_MMD2_MMDSynch_Act2 | Para_Electrical_MMD_MMD2_Mul_U_Bus2 | Para_Electrical_MMD_MMD2_Mul_U_Sync12 | Para_Electrical_MMD_MMD2_Ti_F_OverDel2 | Para_Electrical_MMD_MMD2_Ti_F_UnderDel2 | Para_Electrical_MMD_MMD2_Ti_I_ShortDel2 | Para_Electrical_MMD_MMD2_Ti_U_AsymDel2 | Para_Electrical_MMD_MMD2_Ti_V_Over2 | Para_Electrical_MMD_MMD2_Ti_V_Under2 | Para_Electrical_MMD_MMD2_Ti_V_Under22 | Para_Electrical_MMD_MMD2_U_Asym2 | Para_Electrical_MMD_MMD2_U_BusNom2 | Para_Electrical_MMD_MMD2_U_DeadBus2 | Para_Electrical_MMD_MMD2_U_DeadSync2 | Para_Electrical_MMD_MMD2_U_DiffMax2 | Para_Electrical_MMD_MMD2_U_Gen_Nom2 | Para_Electrical_MMD_MMD2_U_Range2 | Para_Electrical_MMD_MMD2_U_RangeBus2 | Para_Electrical_MMD_MMD2_U_RangeSync12 | Para_Electrical_MMD_MMD2_U_RangeSync22 | Para_Electrical_MMD_MMD2_U_SyncNom2 | Para_Electrical_MMD_MMD2_V_Over2 | Para_Electrical_MMD_MMD2_V_Under2 | Para_Electrical_MMD_MMD2_V_Under22 | Para_emission_bco_scr_emline1_exist | Para_emission_bem_avgcalc_start | Para_emission_bem_avgcalc_steadystate | Para_emission_bno2_scr_emline1_exist | Para_emission_bno_scr_emline1_exist | Para_emission_bnoxs_heating_active | Para_emission_bscr_active | Para_emission_bt_scr_catin_exist | Para_emission_bt_scr_catout_exist | Para_emission_iidx_em_avgmon_option | Para_emission_iidx_noxs_config | Para_emission_iidx_scr_extemoption | Para_emission_inoxs_lifetime | Para_emission_rco_em_catout_mg_hi | Para_emission_rnox_em_catout_mg_hi | Para_emission_rnox_em_catout_mg_hitol | Para_emission_rnox_em_catout_mg_set | Para_emission_rnox_em_engout_mg_hi | Para_emission_rnox_em_engout_mg_hitol | Para_emission_rnox_em_engout_mg_set | Para_emission_rnox_noxs_catout_offs | Para_emission_rnox_noxs_engout_a_offs | Para_emission_rnox_noxs_engout_b_offs | Para_emission_rnox_noxs_engout_dev_hi | Para_emission_rnox_noxs_engout_offs | Para_emission_ro2_noxs_catout_offs | Para_emission_ro2_noxs_engout_a_offs | Para_emission_ro2_noxs_engout_b_offs | Para_emission_ro2_noxs_engout_dev_hi | Para_emission_ro2_noxs_engout_offs | Para_emission_ro2_reference | Para_emission_rp_scr_ureadosingunit_release | Para_emission_rratio_no2_nox_catout | Para_emission_rratio_no2_nox_engout | Para_emission_rt_scr_catin_hi | Para_emission_rt_scr_catout_hi | Para_emission_rt_scr_ureadosingunit_release | Para_emission_tiem_avgcalc_timebase | Para_emission_tiscr_eac_durationstartup | Para_emission_tiscr_emline_purgingwaiting | Para_EngDat_AccessNr | Para_EngDat_Act2StageTC | Para_EngDat_Act3WayKat | Para_EngDat_ActAutGas | Para_EngDat_ActAuxCool | Para_EngDat_ActAuxVent | Para_EngDat_ActCodinox | Para_EngDat_ActExhReactor | Para_EngDat_ActGasMix_NEx | Para_EngDat_ActHumidity | Para_EngDat_ActIC900 | Para_EngDat_ActIsolatedOp | Para_EngDat_ActKLS90_NEx | Para_EngDat_ActKLS98 | Para_EngDat_ActKLS98Misf_NEx | Para_EngDat_ActLIVC | Para_EngDat_ActMixTempCtr | Para_EngDat_ActMMU2_NEx | Para_EngDat_ActMonic | Para_EngDat_ActNOx | Para_EngDat_ActOilCount | Para_EngDat_ActOutDoorTemp | Para_EngDat_ActOxyKat | Para_EngDat_ActPFCtr | Para_EngDat_ActPlantCtr1 | Para_EngDat_ActPlantCtr10 | Para_EngDat_ActPlantCtr11 | Para_EngDat_ActPlantCtr12 | Para_EngDat_ActPlantCtr13 | Para_EngDat_ActPlantCtr14 | Para_EngDat_ActPlantCtr15 | Para_EngDat_ActPlantCtr16 | Para_EngDat_ActPlantCtr2 | Para_EngDat_ActPlantCtr3 | Para_EngDat_ActPlantCtr4 | Para_EngDat_ActPlantCtr5 | Para_EngDat_ActPlantCtr6 | Para_EngDat_ActPlantCtr7 | Para_EngDat_ActPlantCtr8 | Para_EngDat_ActPreChambGasComp | Para_EngDat_ActPRedTempIntakeAir | Para_EngDat_ActPRedTurboSpeed | Para_EngDat_ActReceiveDataBus1 | Para_EngDat_ActReceiveDataBus2 | Para_EngDat_ActReserveAnalog | Para_EngDat_ActReservePar | Para_EngDat_ActRoomTemp | Para_EngDat_ActSAFI | Para_EngDat_ActSpecGM | Para_EngDat_ActSpecialGas | Para_EngDat_ActTecJet | Para_EngDat_ActTempIntakeAir | Para_EngDat_ActTurboBypass | Para_EngDat_ActTurboSpeedA | Para_EngDat_ActTurboSpeedB | Para_EngDat_ActTurboSpeedLPA | Para_EngDat_ActTurboSpeedLPB | Para_EngDat_ActUniIO | Para_EngDat_ActWasteGate | Para_EngDat_ApplicationName_NEx | Para_EngDat_ApplicationType_NEx | Para_EngDat_BasisUpdateVers_NEx | Para_EngDat_CompRate | Para_EngDat_EngineNr_NEx | Para_EngDat_EngineType_NEx | Para_EngDat_GroupAccessNr | Para_EngDat_GroupAccessNr2 | Para_EngDat_GroupAccessNr3 | Para_EngDat_LanguageID_NEx | Para_EngDat_ModBusSlaveIDLink1 | Para_EngDat_ModBusSlaveIDLink2 | Para_EngDat_ModInertia | Para_EngDat_NumbGasmixer | Para_EngDat_NumbGasTrain | Para_EngDat_NumbGasTyp | Para_EngDat_NumbTecjet | Para_EngDat_NumbTurboBypass | Para_EngDat_Tempc_NEx | Para_EngDat_Tempt_NEx | Para_EngDat_Tempu_NEx | Para_EngDat_TurboBypass4_20mA | Para_EngDat_VersRPS_NEx | Para_EngDat_VersSPS_NEx | Para_EngDat_VersVIS_NEx | Para_EngDat_VisuUpdateVers_NEx | Para_Engine_ChargeTempCtr_DComp | Para_Engine_ChargeTempCtr_deadband | Para_Engine_ChargeTempCtr_dW_down | Para_Engine_ChargeTempCtr_dW_up | Para_Engine_ChargeTempCtr_dY_max | Para_Engine_ChargeTempCtr_IComp | Para_Engine_ChargeTempCtr_Kp_manualAdjust | Para_Engine_ChargeTempCtr_nvert | Para_Engine_ChargeTempCtr_PComp | Para_Engine_ChargeTempCtr_Pos_ChC_Valve_ScalMax | Para_Engine_ChargeTempCtr_Pos_ChC_Valve_ScalMin | Para_Engine_ChargeTempCtr_Pos_ChCValve | Para_Engine_ChargeTempCtr_t_min_pulse_down | Para_Engine_ChargeTempCtr_t_min_pulse_up | Para_Engine_ChargeTempCtr_t_period_down | Para_Engine_ChargeTempCtr_t_period_up | Para_Engine_ChargeTempCtr_Tn_manualAdjust | Para_Engine_ChargeTempCtr_Tv_manualAdjust | Para_Engine_ChargeTempCtr_WMax | Para_Engine_ChargeTempCtr_WMin | Para_Engine_ChargeTempCtr_Y_block | Para_Engine_ChargeTempCtr_YMax | Para_Engine_ChargeTempCtr_YMin | Para_Engine_Charging_AirFilterDiffPress_DPr_AirFilt_Exist | Para_Engine_Charging_AirFilterDiffPress_DPr_AirFilt_Hi_incr | Para_Engine_Charging_AirFilterDiffPress_DPr_AirFilt_Lo | Para_Engine_Charging_Pos_CBV_Ref_WG | Para_Engine_Charging_Pressure_DPr_Ch_FA_Hi | Para_Engine_Charging_Pressure_DPr_Ch_HPCooler_Hi | Para_Engine_Charging_Pressure_DPr_Ch_LPCooler_Hi | Para_Engine_Charging_Pressure_Pr_Ch_P1LP_A_Exist | Para_Engine_Charging_Pressure_Pr_Ch_P1LP_B_Exist | Para_Engine_Charging_Pressure_Pr_Ch_P1LPScalMax | Para_Engine_Charging_Pressure_Pr_Ch_P1LPScalMin | Para_Engine_Charging_Pressure_Pr_Ch_P2bFA_Exist | Para_Engine_Charging_Pressure_Pr_Ch_P2bFAScalMax | Para_Engine_Charging_Pressure_Pr_Ch_P2bFAScalMin | Para_Engine_Charging_Pressure_Pr_Ch_P2HP_A_Exist | Para_Engine_Charging_Pressure_Pr_Ch_P2HP_B_Exist | Para_Engine_Charging_Pressure_Pr_Ch_P2HP_Exist | Para_Engine_Charging_Pressure_Pr_Ch_P2HPScalMax | Para_Engine_Charging_Pressure_Pr_Ch_P2HPScalMin | Para_Engine_Charging_Pressure_Pr_Ch_P2LP_A_Exist | Para_Engine_Charging_Pressure_Pr_Ch_P2LP_B_Exist | Para_Engine_Charging_Pressure_Pr_Ch_P2LP_Exist | Para_Engine_Charging_Pressure_Pr_Ch_P2LPScalMax | Para_Engine_Charging_Pressure_Pr_Ch_P2LPScalMin | Para_Engine_Charging_Temp_T_Ch_T1LP_A_Exist | Para_Engine_Charging_Temp_T_Ch_T1LP_B_Exist | Para_Engine_Charging_Temp_T_Ch_T1LP_Exist | Para_Engine_Charging_Temp_T_Ch_T1LP_Hi | Para_Engine_Charging_tiWG_SS_Del | Para_Engine_Charging_WG_Check_Ena | Para_Engine_Charging_WG_Man | Para_Engine_Coupling_Comm1_Baud | Para_Engine_Coupling_Comm1_Parity | Para_Engine_Coupling_Comm1_PB_SlaveID1 | Para_Engine_Coupling_Comm1_PB_SlaveID2 | Para_Engine_Coupling_Comm1_PN_SlaveID1 | Para_Engine_Coupling_Comm1_Stopbit | Para_Engine_Coupling_Comm2_Baud | Para_Engine_Coupling_Comm2_Parity | Para_Engine_Coupling_Comm2_PB_SlaveID1 | Para_Engine_Coupling_Comm2_PB_SlaveID2 | Para_Engine_Coupling_Comm2_PN_SlaveID1 | Para_Engine_Coupling_Comm2_Stopbit | Para_Engine_Coupling_Comm_IPaddr_first_TCP | Para_Engine_Coupling_Comm_IPaddr_fourth_TCP | Para_Engine_Coupling_Comm_IPaddr_second_TCP | Para_Engine_Coupling_Comm_IPaddr_third_TCP | Para_Engine_Coupling_Comm_PortID_TCP | Para_Engine_Coupling_Comm_SlaveID_TCP | Para_Engine_Coupling_Comm_SubMask_first_TCP | Para_Engine_Coupling_Comm_SubMask_fourth_TCP | Para_Engine_Coupling_Comm_SubMask_second_TCP | Para_Engine_Coupling_Comm_SubMask_third_TCP | Para_Engine_Coupling_Idx_Comm1_Interface | Para_Engine_Coupling_Idx_Comm1_type | Para_Engine_Coupling_Idx_Comm2_Interface | Para_Engine_Coupling_Idx_Comm2_type | Para_Engine_Coupling_OPC_Rcv_Ena | Para_Engine_EngDat__IgnIC_900Active | Para_Engine_EngDat_AvailabilityTrackingOn | Para_Engine_EngDat_Country | Para_Engine_EngDat_IdleFrictionMon | Para_Engine_EngDat_IgnMon_Active | Para_Engine_EngDat_KLS98_Active | Para_Engine_EngDat_SA_Active | Para_Engine_EngDat_SDT_Avg_LoLo | Para_Engine_Island_Greenhouse_Num_Eng_LSL | Para_Engine_Island_Greenhouse_P_drift_GH_Ena | Para_Engine_Island_Greenhouse_P_Drift_Rel_Norm | Para_Engine_Island_Greenhouse_P_max_GH_Ena | Para_Engine_Island_Kp_P_Rot_Lam | Para_Engine_Island_Limit_P_LS_HyLo | Para_Engine_Island_LoadSh_LSL_Enable | Para_Engine_Island_P_el_LockTV_Norm | Para_Engine_Island_P_el_ReleaseTV_Norm | Para_Engine_Island_P_LoadReject_Active | Para_Engine_Island_P_Rot_Norm_Lam_Trig | Para_Engine_Island_Pr_CBV_Lock | Para_Engine_Island_Pr_CBV_Release | Para_Engine_Island_Ramp_P_Island_Split_DecGrad_Norm1 | Para_Engine_Island_Ramp_P_Island_Split_IncGrad_Norm1 | Para_Engine_Leanox_Comp_ZZPKorr | Para_Engine_Leanox_Gas1_Pr_Leanox_Offset_Isand1 | Para_Engine_Leanox_Gas1_Pr_P2_Dev_Lim1 | Para_Engine_Leanox_Gas2_Pr_Leanox_Offset_Isand2 | Para_Engine_Leanox_Gas2_Pr_P2_Dev_Lim2 | Para_Engine_Leanox_Gas3_Pr_Leanox_Offset_Isand3 | Para_Engine_Leanox_Gas3_Pr_P2_Dev_Lim3 | Para_Engine_Leanox_Gas4_Pr_Leanox_Offset_Isand4 | Para_Engine_Leanox_Gas4_Pr_P2_Dev_Lim4 | Para_Engine_Leanox_Gasmixer_Gas1_deadband | Para_Engine_Leanox_Gasmixer_Gas1_I | Para_Engine_Leanox_Gasmixer_Gas1_P | Para_Engine_Leanox_Gasmixer_Gas1_umax | Para_Engine_Leanox_Gasmixer_Gas1_umin | Para_Engine_Leanox_Gasmixer_Gas2_deadband | Para_Engine_Leanox_Gasmixer_Gas2_I | Para_Engine_Leanox_Gasmixer_Gas2_P | Para_Engine_Leanox_Gasmixer_Gas2_umax | Para_Engine_Leanox_Gasmixer_Gas2_umin | Para_Engine_Leanox_Gasmixer_Gas3_deadband | Para_Engine_Leanox_Gasmixer_Gas3_I | Para_Engine_Leanox_Gasmixer_Gas3_P | Para_Engine_Leanox_Gasmixer_Gas3_umax | Para_Engine_Leanox_Gasmixer_Gas3_umin | Para_Engine_Leanox_Gasmixer_Gas4_deadband | Para_Engine_Leanox_Gasmixer_Gas4_I | Para_Engine_Leanox_Gasmixer_Gas4_P | Para_Engine_Leanox_Gasmixer_Gas4_umax | Para_Engine_Leanox_Gasmixer_Gas4_umin | Para_Engine_Leanox_IdleLambdaCtr_Gas1_Pr_p2s_LLCtr1 | Para_Engine_Leanox_IdleLambdaCtr_Gas2_Pr_p2s_LLCtr2 | Para_Engine_Leanox_IdleLambdaCtr_Gas3_Pr_p2s_LLCtr3 | Para_Engine_Leanox_IdleLambdaCtr_Gas4_Pr_p2s_LLCtr4 | Para_Engine_Leanox_IdleLambdaCtr_Gasmixer_Ki_LeanoxC_GM | Para_Engine_Leanox_IdleLambdaCtr_Gasmixer_Kp_LeanoxC_GM | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Gas1_Lam_CR_Speed1 | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Gas2_Lam_CR_Speed2 | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Gas3_Lam_CR_Speed3 | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Gas4_Lam_CR_Speed4 | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Ki_LeanoxC_TJ | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Kp_LeanoxC_TJ | Para_Engine_Leanox_IdleLambdaCtr_LLCtr_ki | Para_Engine_Leanox_IdleLambdaCtr_LLCtr_kp | Para_Engine_Leanox_IdleLambdaCtr_LLLCtr_act | Para_Engine_Leanox_IdleLambdaCtr_LLLCtr_delay_Trip | Para_Engine_Leanox_IdleLambdaCtr_Pr_p2s_Win_sy_lfg | Para_Engine_Leanox_LambdaFeedFwdCtr_Gas1_Lam_Start_Offs1 | Para_Engine_Leanox_LambdaFeedFwdCtr_Gas2_Lam_Start_Offs2 | Para_Engine_Leanox_LambdaFeedFwdCtr_Gas3_Lam_Start_Offs3 | Para_Engine_Leanox_LambdaFeedFwdCtr_Gas4_Lam_Start_Offs4 | Para_Engine_Leanox_LambdaFeedFwdCtr_N_LamOffs_x1 | Para_Engine_Leanox_LambdaFeedFwdCtr_N_LamOffs_x2 | Para_Engine_Leanox_LeanoxPRED | Para_Engine_Leanox_LeanoxRamp | Para_Engine_Leanox_Pr_P2s_Set_0kW | Para_Engine_PFPDR_Adv_IP_Ena | Para_Engine_PFPDR_Auto_Ena | Para_Engine_PFPDR_BH_Auto | Para_Engine_PFPDR_CA_IP_EGT | Para_Engine_PFPDR_CA_Offs_Lim | Para_Engine_PFPDR_Ena | Para_Engine_PFPDR_Lam_Lim | Para_Engine_PFPDR_tiSS_Del | Para_Engine_Power_Ctr_CBV_N | Para_Engine_Power_Ctr_GEN2_PowCtrl_Ki | Para_Engine_Power_Ctr_GEN2_PowCtrl_Kp | Para_Engine_Power_Ctr_Pr_P2s_CtrLim | Para_Engine_Power_Ctr_TV_N | Para_Engine_Power_ExtSet_P_Set5_ExtDI_Norm | Para_Engine_Power_FastStart_CA_GEN2_fastSt | Para_Engine_Power_FastStart_FastSpeedUp | Para_Engine_Power_FastStart_FastSync | Para_Engine_Power_FastStart_GEN2_preM_Act | Para_Engine_Power_FastStart_LowTransNOx_Ena | Para_Engine_Power_FastStart_P_Ramp_Norm1 | Para_Engine_Power_FastStart_P_Ramp_Norm2 | Para_Engine_Power_FastStart_P_Ramp_Norm3 | Para_Engine_Power_FastStart_P_Ramp_Norm4 | Para_Engine_Power_FastStart_PrR_GEN2_TV_level | Para_Engine_Power_FastStart_PrR_GEN2_TV_level_Hy | Para_Engine_Power_FastStart_ti_Desired1 | Para_Engine_Power_FastStart_ti_Desired2 | Para_Engine_Power_FastStart_ti_Desired3 | Para_Engine_Power_FastStart_ti_Desired4 | Para_Engine_Power_Limit_P_GhStep_Ena | Para_Engine_Power_Limit_P_GhStep_Lim_Norm0 | Para_Engine_Power_Limit_P_GhStep_Lim_Norm1 | Para_Engine_Power_Limit_P_GhStep_Lim_Norm2 | Para_Engine_Power_Limit_P_GhStep_Lim_Norm3 | Para_Engine_Power_Limit_P_GhStep_Lim_Norm4 | Para_Engine_Power_Limit_P_LimHiHi | Para_Engine_Power_RedCrankCase_P_Red_CC | Para_Engine_Power_RedExhaust_PID_EGT_I | Para_Engine_Power_RedExhaust_PID_EGT_P | Para_Engine_Power_RedGCBTemp_P_Red_TempMax_GenCB_Active | Para_Engine_Power_RedGCBTemp_P_Red_TempMax_GenCB_Rate | Para_Engine_Power_RedTransformer_P_Red_TransformerWarning_Rate | Para_Engine_Power_RedTransformer_P_Red_TransformerWarning_Sel | Para_Engine_Remote_RemoteReqActive | Para_Engine_Remote_ResetRemActive | Para_Engine_Remote_ResetRemRiskClass | Para_Engine_SAFI_SA_Ign_Active | Para_Engine_Speed_Ctr_CBV_IdleOp_D | Para_Engine_Speed_Ctr_CBV_IdleOp_I | Para_Engine_Speed_Ctr_CBV_IdleOp_N | Para_Engine_Speed_Ctr_CBV_IdleOp_P | Para_Engine_Speed_Ctr_CBV_IdleOp_umax | Para_Engine_Speed_Ctr_CBV_IdleOp_umin | Para_Engine_Speed_Ctr_CBV_IsolatedOp_D | Para_Engine_Speed_Ctr_CBV_IsolatedOp_I | Para_Engine_Speed_Ctr_CBV_IsolatedOp_N | Para_Engine_Speed_Ctr_CBV_IsolatedOp_P | Para_Engine_Speed_Ctr_CBV_IsolatedOp_umax | Para_Engine_Speed_Ctr_CBV_IsolatedOp_umin | Para_Engine_Speed_Ctr_TV_IdleOp_a | Para_Engine_Speed_Ctr_TV_IdleOp_D | Para_Engine_Speed_Ctr_TV_IdleOp_I | Para_Engine_Speed_Ctr_TV_IdleOp_N | Para_Engine_Speed_Ctr_TV_IdleOp_P | Para_Engine_Speed_Ctr_TV_IdleOp_umax | Para_Engine_Speed_Ctr_TV_IdleOp_umin | Para_Engine_Speed_Ctr_TV_IsolatedOp_N | Para_Engine_Speed_Limit_N_EngStart_HyHi | Para_Engine_Speed_Limit_N_EngStart_LimHi | Para_Engine_Speed_N_Offs_Sync | Para_Engine_SteadyState_ChargePress_Abs | Para_Engine_SteadyState_ChargePress_Rel | Para_Engine_SteadyState_ChargePress_ti_Filt | Para_Engine_SteadyState_ChargeTemp_Abs | Para_Engine_SteadyState_ChargeTemp_Rel | Para_Engine_SteadyState_ChargeTemp_ti_Filt | Para_Engine_SteadyState_Exhaust_Abs | Para_Engine_SteadyState_Exhaust_Rel | Para_Engine_SteadyState_Exhaust_ti_Filt | Para_Engine_SteadyState_Power_Abs | Para_Engine_SteadyState_Power_Rel | Para_Engine_SteadyState_Power_ti_Filt | Para_enginecontroller_blx2_enable | Para_enginecontroller_bp2s_comp_leanoxdrift | Para_enginecontroller_ioph_nox_measure_mandatory | Para_enginecontroller_ioph_nox_measure_recommend | Para_enginecontroller_ioph_p2s_comp_leanoxdrift_reset | Para_enginecontroller_ioph_p2s_comp_leanoxdrift_sec2 | Para_enginecontroller_p2s_comp_leanoxdrift_x1 | Para_enginecontroller_p2s_comp_leanoxdrift_x2 | Para_enginecontroller_p2s_comp_leanoxdrift_y1 | Para_enginecontroller_p2s_comp_leanoxdrift_y2 | Para_enginecontroller_rcoeff_p2s_comp_sector2 | Para_enginecontroller_rlx2_steadystatefactor | Para_enginecontroller_rp_p2s_comp_leanoxdrift_sp | Para_enginecontroller_rpr_lx2_offsetlimit | Para_enginecontroller_tifilterconst_nox | Para_enginecontroller_tilx2_ctrl_tn | Para_Exhaust_ActBoil | Para_Exhaust_ActExhDevAvg | Para_Exhaust_ActExhGasScav_NEx | Para_Exhaust_ActExhMax | Para_Exhaust_ActExhTemp | Para_Exhaust_ActInHec | Para_Exhaust_ActInKat | Para_Exhaust_ActKat | Para_Exhaust_ActOutHec | Para_Exhaust_ActOutKat | Para_Exhaust_ActTempInTurboCh | Para_Exhaust_ActTempOutHec1 | Para_Exhaust_ActTempOutHec2 | Para_exhaust_boxicat_exist | Para_exhaust_bpr_oxicat_in_exist | Para_exhaust_bpr_oxicat_in_fast_exist | Para_exhaust_bpr_oxicat_out_exist | Para_exhaust_bt_oxicat_in_exist | Para_exhaust_bt_oxicat_out_exist | Para_Exhaust_CODINOX_CO2_PneumVal | Para_Exhaust_CODINOX_tiCO2_ExPSp_StartOffTime | Para_Exhaust_CODINOX_tiCO2_ExPSp_StopOffTime | Para_Exhaust_DiffPressCooler_Pr_Diff_ExGCooler_Active | Para_Exhaust_DiffPressCooler_Pr_Diff_ExGCooler_Hi | Para_Exhaust_DiffPressCooler_Pr_Diff_ExGCooler_HyHi | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_Active | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_Hi | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_Hi1 | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_Hi2 | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_HyHi | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_Lo | Para_Exhaust_EGValveEnable | Para_Exhaust_HeatExchanger_T_EGaHE1_HyHi_Trip | Para_Exhaust_HeatExchanger_T_EGaHE1_HyHi_Warn | Para_Exhaust_HeatExchanger_T_EGaHE1_LimHi_Trip | Para_Exhaust_HeatExchanger_T_EGaHE1_LimHi_Warn | Para_Exhaust_HeatExchanger_T_EGaHE2_HyHi_Trip | Para_Exhaust_HeatExchanger_T_EGaHE2_HyHi_Warn | Para_Exhaust_HeatExchanger_T_EGaHE2_LimHi_Trip | Para_Exhaust_HeatExchanger_T_EGaHE2_LimHi_Warn | Para_Exhaust_HeatExchanger_T_PlateHE_InpLimMax | Para_Exhaust_HeatExchanger_T_PlateHE_InpLimMin | Para_Exhaust_NOx_ActCtr | Para_Exhaust_NOx_ErrorMax | Para_Exhaust_NOx_O2ref | Para_Exhaust_NOx_Sensor1_ActSensor | Para_Exhaust_NOx_Sensor1_NOxOffset | Para_Exhaust_NOx_Sensor1_O2Offset | Para_Exhaust_NOx_Sensor2_ActSensor | Para_Exhaust_NOx_Sensor2_NOxOffset | Para_Exhaust_NOx_Sensor2_O2Offset | Para_Exhaust_NOx_SetNOx | Para_Exhaust_Pr_EGaHPTC_A_Active | Para_Exhaust_Pr_EGaHPTC_B_Active | Para_Exhaust_Pr_EGaLPTC_A_Active | Para_Exhaust_Pr_EGaLPTC_B_Active | Para_Exhaust_Pr_EGbHPTC_A_Active | Para_Exhaust_Pr_EGbHPTC_B_Active | Para_Exhaust_Reactor_Active | Para_Exhaust_Reactor_ActiveHys | Para_Exhaust_Reactor_AdjustRefTemp | Para_Exhaust_Reactor_FlapTimer1 | Para_Exhaust_Reactor_FlapTimer2 | Para_Exhaust_Reactor_LimitReactChamb00 | Para_Exhaust_Reactor_LimitReactChamb25 | Para_Exhaust_Reactor_LimitReactChamb50 | Para_Exhaust_Reactor_LimitReactChamb75 | Para_Exhaust_Reactor_LimitReactChambStartGasInj | Para_Exhaust_Reactor_RelTemp1 | Para_Exhaust_Reactor_RelTemp2 | Para_Exhaust_Reactor_Sel_Flap5Pos | Para_Exhaust_Reactor_Sel_FlapActEl | Para_Exhaust_Reactor_T_ThR_LimGasHy | Para_Exhaust_Reactor_T_ThR_LimPInc | Para_Exhaust_Reactor_T_ThR_SetwoGas | Para_Exhaust_Reactor_ThR_NatGas | Para_Exhaust_Reactor_ThR_woGas | Para_Exhaust_Reactor_ti_ThR_TimePInc | Para_Exhaust_Reactor_ti_ThR_ValDurationPInc | Para_Exhaust_Reactor_ti_ThR_ValIntervalPInc | Para_exhaust_rpr_eg_deflag_fast_hihi | Para_exhaust_rpr_oxicat_diff_hi | Para_exhaust_rt_oxicat_in_hi | Para_exhaust_rt_oxicat_out_hihi | Para_Exhaust_Scavenging_EGScav_ifAuxV_ok | Para_Exhaust_Scavenging_N2_NoScavGas1 | Para_Exhaust_Scavenging_N2_NoScavGas2 | Para_Exhaust_Scavenging_ScavBeStart_Active | Para_Exhaust_SCR_Active | Para_Exhaust_SCR_Dosing_Flow_Urea100 | Para_Exhaust_SCR_Dosing_Flow_Urea30 | Para_Exhaust_SCR_Dosing_Flow_Urea40 | Para_Exhaust_SCR_Dosing_Flow_Urea50 | Para_Exhaust_SCR_Dosing_Flow_Urea60 | Para_Exhaust_SCR_Dosing_Flow_Urea70 | Para_Exhaust_SCR_Dosing_Flow_Urea80 | Para_Exhaust_SCR_Dosing_Flow_Urea90 | Para_Exhaust_SCR_Dosing_Flow_Urea_Hi | Para_Exhaust_SCR_Dosing_Flow_Urea_Offs | Para_Exhaust_SCR_Dosing_Flow_Urea_ScalMax | Para_Exhaust_SCR_Dosing_Flow_Urea_ScalMin | Para_Exhaust_SCR_Dosing_Flow_Urea_Set_ScalMax | Para_Exhaust_SCR_Dosing_Flow_Urea_Set_ScalMin | Para_Exhaust_SCR_Dosing_Flow_UreaGain | Para_Exhaust_SCR_Dosing_Pr_AirSupply_Hi | Para_Exhaust_SCR_Dosing_Pr_AirSupply_Lo | Para_Exhaust_SCR_Dosing_Pr_AirSupply_ScalMax | Para_Exhaust_SCR_Dosing_Pr_AirSupply_ScalMin | Para_Exhaust_SCR_Dosing_Pr_Urea_Hi | Para_Exhaust_SCR_Dosing_Pr_Urea_Lo | Para_Exhaust_SCR_Dosing_Pr_Urea_ScalMax | Para_Exhaust_SCR_Dosing_Pr_Urea_ScalMin | Para_Exhaust_SCR_Dosing_tiAirCompressed_OfC | Para_Exhaust_SCR_Dosing_tiUreaTank_LevelLow | Para_Exhaust_SCR_Dosing_UreaCirculatePump_Exist | Para_Exhaust_SCR_Dosing_UreaPump_Service | Para_Exhaust_SCR_Emission_CEMS_Shutdown | Para_Exhaust_SCR_Emission_CEMS_SteadyState | Para_Exhaust_SCR_Emission_CO_Eng_Out_Set | Para_Exhaust_SCR_Emission_CO_SCR_Out_Hi | Para_Exhaust_SCR_Emission_CO_SCR_ScalMax | Para_Exhaust_SCR_Emission_CO_SCR_ScalMin | Para_Exhaust_SCR_Emission_Idx_NOxS_Config | Para_Exhaust_SCR_Emission_NH3_Slip_Ctrl_Active | Para_Exhaust_SCR_Emission_NO2_SCR_ScalMax | Para_Exhaust_SCR_Emission_NO2_SCR_ScalMin | Para_Exhaust_SCR_Emission_NO_Ctrl_SCR_ScalMax | Para_Exhaust_SCR_Emission_NO_Ctrl_SCR_ScalMin | Para_Exhaust_SCR_Emission_NO_NH3_Slip_Set | Para_Exhaust_SCR_Emission_NO_SCR_ScalMax | Para_Exhaust_SCR_Emission_NO_SCR_ScalMin | Para_Exhaust_SCR_Emission_NOx_Eng_Out_Set | Para_Exhaust_SCR_Emission_NOx_SCR_Out_Hi | Para_Exhaust_SCR_Emission_NOx_SCR_Out_Set | Para_Exhaust_SCR_Emission_NOxS_Eng_Out_Hi | Para_Exhaust_SCR_Emission_tiGasAnalys_Purge_Duration | Para_Exhaust_SCR_Emission_tiGasAnalys_Purge_Intervall | Para_Exhaust_SCR_Emission_tiGasAnalys_Waiting | Para_Exhaust_SCR_Emission_tiNO_AboveLimit | Para_Exhaust_SCR_Emission_tiReset_SampleGas_Valves | Para_Exhaust_SCR_P_LoadEngine_Dosing | Para_Exhaust_SCR_Pr_SCR_Hi | Para_Exhaust_SCR_Pr_SCR_In_ScalMax | Para_Exhaust_SCR_Pr_SCR_In_ScalMin | Para_Exhaust_SCR_Pr_SCR_Out_ScalMax | Para_Exhaust_SCR_Pr_SCR_Out_ScalMin | Para_Exhaust_SCR_SCR_Release | Para_Exhaust_SCR_T_SCR_Avg | Para_Exhaust_SCR_T_SCR_In_Hi | Para_Exhaust_SCR_T_SCR_In_ScalMax | Para_Exhaust_SCR_T_SCR_In_ScalMin | Para_Exhaust_SCR_T_SCR_Out_Hi | Para_Exhaust_SCR_T_SCR_Out_ScalMax | Para_Exhaust_SCR_T_SCR_Out_ScalMin | Para_Exhaust_T_EGaHPTC_A_Active | Para_Exhaust_T_EGaHPTC_B_Active | Para_Exhaust_T_EGbHPTC_A_Active | Para_Exhaust_T_EGbHPTC_B_Active | Para_Exhaust_TCSpeed2Stage_20mA_A | Para_Exhaust_TCSpeed2Stage_20mA_B | Para_Exhaust_TCSpeed2Stage_4mA_A | Para_Exhaust_TCSpeed2Stage_4mA_B | Para_Exhaust_TCSpeed2Stage_ActTempOutlet_A | Para_Exhaust_TCSpeed2Stage_ActTempOutlet_B | Para_Exhaust_TCSpeed2Stage_IncLimit | Para_Exhaust_TCSpeed2Stage_Limit | Para_Exhaust_TCSpeed2Stage_LimitHys | Para_Exhaust_TCSpeedA_20mA | Para_Exhaust_TCSpeedA_4mA | Para_Exhaust_TCSpeedA_Limit | Para_Exhaust_TCSpeedA_LimitHys | Para_Exhaust_TCSpeedB_20mA | Para_Exhaust_TCSpeedB_4mA | Para_Exhaust_TCSpeedB_Limit | Para_Exhaust_TCSpeedB_LimitHys | Para_Exhaust_TempBoilHys | Para_Exhaust_TempBoilInputMax | Para_Exhaust_TempBoilInputMin | Para_Exhaust_TempBoilTrip | Para_Exhaust_TempBoilWarning | Para_Exhaust_TempExhAvgDevNeg | Para_Exhaust_TempExhAvgDevPos | Para_Exhaust_TempExhAvgPnGr40 | Para_Exhaust_TempExhMaxPnGr40 | Para_Exhaust_TempExhMaxPnSm40 | Para_Exhaust_TempInHexHys | Para_Exhaust_TempInHexMax | Para_Exhaust_TempInKatHys | Para_Exhaust_TempInKatMax | Para_Exhaust_TempInTurboAlarm | Para_Exhaust_TempInTurboAlarmHys | Para_Exhaust_TempInTurboMax | Para_Exhaust_TempInTurboMaxHys | Para_Exhaust_TempKatAlarm | Para_Exhaust_TempKatAlarmHys | Para_Exhaust_TempKatdTMax | Para_Exhaust_TempKatdTRel | Para_Exhaust_TempKatdTRelHys | Para_Exhaust_TempKatHys | Para_Exhaust_TempKatMax | Para_Exhaust_TempOutHexHys | Para_Exhaust_TempOutHexMax | Para_Exhaust_TempOutKatHys | Para_Exhaust_TempOutKatMax | Para_Exhaust_TimeScavening | Para_Exhaust_ValveControl_EGValveRegulation | Para_Exhaust_ValveControl_Sel_EGVa_Combi | Para_Exhaust_ValveControl_Sel_EGVa_ROTORK | Para_Exhaust_ValveControl_Sel_EGVa_Torque | Para_Gas_Cnt_Gas_NormM3 | Para_Gas_Cnt_Gas_OpM3 | Para_Gas_Cnt_GasImp_Active | Para_Gas_GasData_Gas1_HCR1 | Para_Gas_GasData_Gas1_LHV1 | Para_Gas_GasData_Gas1_MinAirReq1 | Para_Gas_GasData_Gas1_StdGD1 | Para_Gas_GasData_Gas2_HCR2 | Para_Gas_GasData_Gas2_LHV2 | Para_Gas_GasData_Gas2_MinAirReq2 | Para_Gas_GasData_Gas2_StdGD2 | Para_Gas_GasData_Gas3_HCR3 | Para_Gas_GasData_Gas3_LHV3 | Para_Gas_GasData_Gas3_MinAirReq3 | Para_Gas_GasData_Gas3_StdGD3 | Para_Gas_GasData_Gas4_HCR4 | Para_Gas_GasData_Gas4_LHV4 | Para_Gas_GasData_Gas4_MinAirReq4 | Para_Gas_GasData_Gas4_StdGD4 | Para_Gas_Gasmixer_Gas1_y1 | Para_Gas_Gasmixer_Gas1_y2 | Para_Gas_Gasmixer_Gas2_y1 | Para_Gas_Gasmixer_Gas2_y2 | Para_Gas_Gasmixer_Gas3_y1 | Para_Gas_Gasmixer_Gas3_y2 | Para_Gas_Gasmixer_Gas4_y1 | Para_Gas_Gasmixer_Gas4_y2 | Para_Gas_GasMixerSpecial_N_Eng_RunUpLim | Para_Gas_GasMixerSpecial_Pos_GM_RunUpOffset | Para_Gas_GasPropValve_Gas1_Lam_TJ_Power_Offs1 | Para_Gas_GasPropValve_Gas1_Lam_TJ_Speed_Offs1 | Para_Gas_GasPropValve_Gas1_x1 | Para_Gas_GasPropValve_Gas1_x2 | Para_Gas_GasPropValve_Gas1_y1 | Para_Gas_GasPropValve_Gas1_y2 | Para_Gas_GasPropValve_Gas2_Lam_TJ_Power_Offs2 | Para_Gas_GasPropValve_Gas2_Lam_TJ_Speed_Offs2 | Para_Gas_GasPropValve_Gas2_x1 | Para_Gas_GasPropValve_Gas2_x2 | Para_Gas_GasPropValve_Gas2_y1 | Para_Gas_GasPropValve_Gas2_y2 | Para_Gas_GasPropValve_Gas3_Lam_TJ_Power_Offs3 | Para_Gas_GasPropValve_Gas3_Lam_TJ_Speed_Offs3 | Para_Gas_GasPropValve_Gas3_x1 | Para_Gas_GasPropValve_Gas3_x2 | Para_Gas_GasPropValve_Gas3_y1 | Para_Gas_GasPropValve_Gas3_y2 | Para_Gas_GasPropValve_Gas4_Lam_TJ_Power_Offs4 | Para_Gas_GasPropValve_Gas4_Lam_TJ_Speed_Offs4 | Para_Gas_GasPropValve_Gas4_x1 | Para_Gas_GasPropValve_Gas4_x2 | Para_Gas_GasPropValve_Gas4_y1 | Para_Gas_GasPropValve_Gas4_y2 | Para_Gas_GasRail_Pr_GR_I_Exist | Para_Gas_GasRail_Pr_GR_II_Exist | Para_Gas_GasRail_Pr_GR_IScalMax | Para_Gas_GasRail_Pr_GR_IScalMin | Para_Gas_GasRail_T_GR_Exist | Para_Gas_GasTrain_DPr_GR_BOV_Open_Hy | Para_Gas_GasTrain_MGT_SetActAdjustActive | Para_Gas_GasTrain_Pr_MGT_PipeLoss_Ch_P1 | Para_Gas_GasTrain_Pr_MGT_PipeLoss_Ch_P2 | Para_Gas_GasTrain_Pr_MGT_PipeLoss_P1 | Para_Gas_GasTrain_Pr_MGT_PipeLoss_P2 | Para_Gas_GasTrain_Pr_MGT_sp_offset | Para_Gas_GasTrain_Pr_MGT_spScalMax | Para_Gas_GasTrain_Pr_MGT_spScalMin | Para_Gas_GasTrain_tiBOV_Open_Max | Para_Gas_GasTrain_tiBOV_Open_Min | Para_Gas_GCActive | Para_Gas_GT_MixActive | Para_Gas_GT_MixActiveEngStop | Para_Gas_Num_GM | Para_Gas_Num_GT1_Lines | Para_Gas_P_GT_SetLim | Para_Gas_Pr_GasPrAbsActive | Para_Gas_PreChambDifPress_Pr_BlowOff_LimHi | Para_Gas_PreChambGasTrain_PCGT_SafeDevice_Exist | Para_Gas_PreChambGasTrain_PCGT_SetActAdjustActive | Para_Gas_PreChambGasTrain_Pr_PCGT_Out_Exist | Para_Gas_PreChambGasTrain_Pr_PCGT_OutScalMax | Para_Gas_PreChambGasTrain_Pr_PCGT_OutScalMin | Para_Gas_PreChambGasTrain_Pr_PCGT_sp_offset | Para_Gas_PreChambGasTrain_Pr_PCGT_spScalMax | Para_Gas_PreChambGasTrain_Pr_PCGT_spScalMin | Para_Gas_PreChambGasTrain_T_PCGAfCo_Active | Para_Gas_PreChambGasTrain_T_PCGAfCo_HyHi | Para_Gas_PreChambGasTrain_T_PCGAfCo_LimHi | Para_Gas_SpecGas_AdvGasPropValveStart_P_TJ_SG_Start_Norm | Para_Gas_SpecGas_AdvGasPropValveStart_TJ_SG_Start1 | Para_Gas_SpecGas_AdvGasPropValveStart_TJ_SG_Start2 | Para_Gas_SpecGas_AdvGasPropValveStart_TJ_SG_Start3 | Para_Gas_SpecGas_AdvGasPropValveStart_TJ_SG_Start4 | Para_Gas_SpecGas_AdvGasPropValveStart_TJ_SG_Start_Ena | Para_Gas_SpecGas_BioGas_BiogasActive | Para_Gas_SpecGas_BioGas_Msg3327Active | Para_Gas_SpecGas_BioGas_Msg3328Active | Para_Gas_SpecGas_BioGas_Msg3567Active | Para_Gas_SpecGas_BioGas_Msg3568Active | Para_Gas_SpecGas_BioGas_Msg3569Active | Para_Gas_SpecGas_BioGas_Msg3570Active | Para_Gas_SpecGas_CBV34Control_CBV34_Fun | Para_Gas_SpecGas_CBV34Control_CBV34_min | Para_Gas_SpecGas_CBV34Control_CBV34_Set | Para_Gas_SpecGas_CBV34Control_CBV34Ctr_ki | Para_Gas_SpecGas_CBV34Control_CBV34Ctr_kp | Para_Gas_SpecGas_GlowIgn_CA_SG_IP_Step | Para_Gas_SpecGas_GlowIgn_FastPowerRed_FPRGasRed | Para_Gas_SpecGas_GlowIgn_FastPowerRed_FPRGasRedOpt | Para_Gas_SpecGas_GlowIgn_FastPowerRed_FPRGasRedTime | Para_Gas_SpecGas_GlowIgn_FastPowerRed_Pos_SG_FPR_CBV | Para_Gas_SpecGas_GlowIgn_FastPowerRed_Pos_SG_FPR_TV | Para_Gas_SpecGas_GlowIgn_Pos_Gm_SG_Offs | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_Num_SG_SCO_Max | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_Num_SG_SCO_Max_DltT | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_Pos_SG_SCO_CBV | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_Pos_SG_SCO_TV | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_SG_SCO_Active | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_ti_SG_SCO_Block | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_ti_SG_SCO_DurMonDis | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_ti_SG_SCO_Max | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_ti_SG_SCO_TV | Para_Gas_SpecGas_GlowIgnPrevActive | Para_Gas_SpecGas_SG_BackFirePrev | Para_Gas_SpecGas_ti_SG_EngBlock | Para_GasData_Gas1_CalorificValue | Para_GasData_Gas1_MinAirRequirement | Para_GasData_Gas1_SpecificHeatRatio | Para_GasData_Gas1_StandGasDens | Para_GasData_Gas2_CalorificValue | Para_GasData_Gas2_MinAirRequirement | Para_GasData_Gas2_SpecificHeatRatio | Para_GasData_Gas2_StandGasDens | Para_GasData_Gas3_CalorificValue | Para_GasData_Gas3_MinAirRequirement | Para_GasData_Gas3_SpecificHeatRatio | Para_GasData_Gas3_StandGasDens | Para_GasData_Gas4_CalorificValue | Para_GasData_Gas4_MinAirRequirement | Para_GasData_Gas4_SpecificHeatRatio | Para_GasData_Gas4_StandGasDens | Para_Gasmixer_Gas1_AirTempPoint1 | Para_Gasmixer_Gas1_AirTempPoint2 | Para_Gasmixer_Gas1_GasMixPosOffsetIsland | Para_Gasmixer_Gas1_GasMixPosOffsetNet | Para_Gasmixer_Gas1_GasMixPosPoint1 | Para_Gasmixer_Gas1_GasMixPosPoint2 | Para_Gasmixer_Gas1_PosOffsetPoint1 | Para_Gasmixer_Gas1_PosOffsetPoint2 | Para_Gasmixer_Gas1_TempOilPoint1 | Para_Gasmixer_Gas1_TempOilPoint2 | Para_Gasmixer_Gas2_AirTempPoint1 | Para_Gasmixer_Gas2_AirTempPoint2 | Para_Gasmixer_Gas2_GasMixPosOffsetIsland | Para_Gasmixer_Gas2_GasMixPosOffsetNet | Para_Gasmixer_Gas2_GasMixPosPoint1 | Para_Gasmixer_Gas2_GasMixPosPoint2 | Para_Gasmixer_Gas2_PosOffsetPoint1 | Para_Gasmixer_Gas2_PosOffsetPoint2 | Para_Gasmixer_Gas2_TempOilPoint1 | Para_Gasmixer_Gas2_TempOilPoint2 | Para_Gasmixer_Gas3_AirTempPoint1 | Para_Gasmixer_Gas3_AirTempPoint2 | Para_Gasmixer_Gas3_GasMixPosOffsetIsland | Para_Gasmixer_Gas3_GasMixPosOffsetNet | Para_Gasmixer_Gas3_GasMixPosPoint1 | Para_Gasmixer_Gas3_GasMixPosPoint2 | Para_Gasmixer_Gas3_PosOffsetPoint1 | Para_Gasmixer_Gas3_PosOffsetPoint2 | Para_Gasmixer_Gas3_TempOilPoint1 | Para_Gasmixer_Gas3_TempOilPoint2 | Para_Gasmixer_Gas4_AirTempPoint1 | Para_Gasmixer_Gas4_AirTempPoint2 | Para_Gasmixer_Gas4_GasMixPosOffsetIsland | Para_Gasmixer_Gas4_GasMixPosOffsetNet | Para_Gasmixer_Gas4_GasMixPosPoint1 | Para_Gasmixer_Gas4_GasMixPosPoint2 | Para_Gasmixer_Gas4_PosOffsetPoint1 | Para_Gasmixer_Gas4_PosOffsetPoint2 | Para_Gasmixer_Gas4_TempOilPoint1 | Para_Gasmixer_Gas4_TempOilPoint2 | Para_Gasmixer_IdleLambdaCtr_Delay1 | Para_Gasmixer_IdleLambdaCtr_Delay2 | Para_Gasmixer_IdleLambdaCtr_Gas1_GasMixPosDP | Para_Gasmixer_IdleLambdaCtr_Gas1_TrPos | Para_Gasmixer_IdleLambdaCtr_Gas2_GasMixPosDP | Para_Gasmixer_IdleLambdaCtr_Gas2_TrPos | Para_Gasmixer_IdleLambdaCtr_Gas3_GasMixPosDP | Para_Gasmixer_IdleLambdaCtr_Gas3_TrPos | Para_Gasmixer_IdleLambdaCtr_Gas4_GasMixPosDP | Para_Gasmixer_IdleLambdaCtr_Gas4_TrPos | Para_Gasmixer_IdleLambdaCtr_IComp | Para_Gasmixer_IdleLambdaCtr_PComp | Para_Gasmixer_LimitAirTempMax | Para_Gasmixer_LimitAirTempMin | Para_Gasmixer_Special_FullStepAirThrot1 | Para_Gasmixer_Special_FullStepAirThrot2 | Para_Gasmixer_Special_FullStepGasThrot | Para_Gasmixer_Special_Gas1_AirThrotFull | Para_Gasmixer_Special_Gas1_OfAirThrotIdle | Para_Gasmixer_Special_Gas1_OfAirThrotNetp | Para_Gasmixer_Special_Gas1_OfAirThrotStart | Para_Gasmixer_Special_Gas2_AirThrotFull | Para_Gasmixer_Special_Gas2_OfAirThrotIdle | Para_Gasmixer_Special_Gas2_OfAirThrotNetp | Para_Gasmixer_Special_Gas2_OfAirThrotStart | Para_Gasmixer_Special_Gas3_AirThrotFull | Para_Gasmixer_Special_Gas3_OfAirThrotIdle | Para_Gasmixer_Special_Gas3_OfAirThrotNetp | Para_Gasmixer_Special_Gas3_OfAirThrotStart | Para_Gasmixer_Special_Gas4_AirThrotFull | Para_Gasmixer_Special_Gas4_OfAirThrotIdle | Para_Gasmixer_Special_Gas4_OfAirThrotNetp | Para_Gasmixer_Special_Gas4_OfAirThrotStart | Para_Gasmixer_Special_SpeedAirThrot1 | Para_Gasmixer_Special_SpeedAirThrot2 | Para_Gasmixer_Special_SpeedGasThrot | Para_Gasmixer_StepFrequency | Para_Gasmixer_StepFrequency1 | Para_Gasmixer_StepsGasmixPos | Para_Gasmixer_StepsGasmixPos1 | Para_Gasmixer_TempOilMax | Para_Gasmixer_TempOilMin | Para_GeneratCtr_ChoiceSet_ExtmAneg | Para_GeneratCtr_ChoiceSet_ExtmApos | Para_GeneratCtr_ChoiceSet_ExtPF1fix | Para_GeneratCtr_ChoiceSet_ExtPF2fix | Para_GeneratCtr_ChoiceSet_ExtPF3fix | Para_GeneratCtr_ChoiceSet_ExtPF4fix | Para_GeneratCtr_ChoiceSet_ExtPF5fix | Para_GeneratCtr_ChoiceSet_ExtSetPF1 | Para_GeneratCtr_ChoiceSet_ExtSetPF2 | Para_GeneratCtr_ChoiceSet_PFIntern | Para_GeneratCtr_ChoiceSet_Type | Para_GeneratCtr_PowerDep_PFPowPoint1 | Para_GeneratCtr_PowerDep_PFPowPoint2 | Para_GeneratCtr_PowerDep_PowPoint1 | Para_GeneratCtr_PowerDep_PowPoint2 | Para_GeneratCtr_QLimit_AppPowNom | Para_GeneratCtr_QLimit_PolarWheelLimit | Para_GeneratCtr_QLimit_PolarWheelTrip | Para_GeneratCtr_QLimit_SyncReakt | Para_GeneratCtr_TimeTable_PFTimePoint1 | Para_GeneratCtr_TimeTable_PFTimePoint2 | Para_GeneratCtr_TimeTable_PFTimePoint3 | Para_GeneratCtr_TimeTable_PFTimePoint4 | Para_GeneratCtr_TimeTable_PFTimePoint5 | Para_GeneratCtr_TimeTable_PFTimePoint6 | Para_GeneratCtr_TimeTable_TimePoint1h | Para_GeneratCtr_TimeTable_TimePoint1m | Para_GeneratCtr_TimeTable_TimePoint2h | Para_GeneratCtr_TimeTable_TimePoint2m | Para_GeneratCtr_TimeTable_TimePoint3h | Para_GeneratCtr_TimeTable_TimePoint3m | Para_GeneratCtr_TimeTable_TimePoint4h | Para_GeneratCtr_TimeTable_TimePoint4m | Para_GeneratCtr_TimeTable_TimePoint5h | Para_GeneratCtr_TimeTable_TimePoint5m | Para_GeneratCtr_TimeTable_TimePoint6h | Para_GeneratCtr_TimeTable_TimePoint6m | Para_GeneratCtr_Type | Para_GeneratCtr_Voltage_ActVoltAdjust | Para_GeneratCtr_Voltage_MaxVoltAdjNeg | Para_GeneratCtr_Voltage_MaxVoltAdjPos | Para_GeneratCtr_Voltage_PFVoltPoint1 | Para_GeneratCtr_Voltage_PFVoltPoint2 | Para_GeneratCtr_Voltage_PFVoltPoint3 | Para_GeneratCtr_Voltage_PFVoltPoint4 | Para_GeneratCtr_Voltage_PFVoltPoint5 | Para_GeneratCtr_Voltage_PFVoltPoint6 | Para_GeneratCtr_Voltage_RampeVoltAdj | Para_GeneratCtr_Voltage_VoltOffsetFullLoad | Para_GeneratCtr_Voltage_VoltOffsetIdle | Para_GeneratCtr_Voltage_VoltPoint1 | Para_GeneratCtr_Voltage_VoltPoint2 | Para_GeneratCtr_Voltage_VoltPoint3 | Para_GeneratCtr_Voltage_VoltPoint4 | Para_GeneratCtr_Voltage_VoltPoint5 | Para_GeneratCtr_Voltage_VoltPoint6 | Para_GeneratCtr_WindTempDep_PFRedWindTemp | Para_GeneratCtr_WindTempDep_TempPowRed | Para_GeneratCtr_WindTempDep_TempStartPFred | Para_Generator_ActBear1 | Para_Generator_ActBear2 | Para_Generator_ActDisplace | Para_Generator_ActInletTemp | Para_Generator_ActOutletTemp | Para_Generator_ActPt100M1_NEx | Para_Generator_ActPt100PTCWindTemp | Para_Generator_ActVoltExcit | Para_Generator_DeActDiffProtect | Para_Generator_Displace20mA | Para_Generator_Displace4mA | Para_Generator_DisplaceDelay1 | Para_Generator_DisplaceDelay2 | Para_Generator_DisplaceLimit1 | Para_Generator_DisplaceLimit2 | Para_Generator_TempBear1Alarm | Para_Generator_TempBear1Trip | Para_Generator_TempBear2Alarm | Para_Generator_TempBear2Trip | Para_Generator_TempBearAlarmHys | Para_Generator_TempBearTripHys | Para_Generator_TempWindPh123AlarmHys | Para_Generator_TempWindPh123TripHys | Para_Generator_TempWindPh1Alarm | Para_Generator_TempWindPh1Trip | Para_Generator_TempWindPh2Alarm | Para_Generator_TempWindPh2Trip | Para_Generator_TempWindPh3Alarm | Para_Generator_TempWindPh3Trip | Para_Generator_TempWindPTCAlarm | Para_Generator_TempWindPTCAlarmHys | Para_Generator_TempWindPTCTrip | Para_Generator_TempWindPTCTripHys | Para_Generator_VoltExitLimit | Para_Generator_VoltExitLimitHys | Para_Generator_VoltExitMax | Para_Generator_VoltExitMaxHys | Para_Grid_DelayStabilGrid | Para_Grid_GridCode_ActDynGridCode | Para_Grid_GridCode_ActDynGridCodeMonOnly | Para_Grid_GridCode_AngleSumLimit | Para_Grid_GridCode_CurrentChangeLimit | Para_Grid_GridCode_PolarWheelAngleLimit | Para_Grid_GridCode_PoleSlipLimit | Para_Grid_GridCode_PowerLimit | Para_Grid_GridCode_SpeedChangeLimit | Para_Grid_GridCode_StopCap | Para_Grid_GridCode_VoltageLimit | Para_Grid_GridCode_XqGen | Para_Grid_GridCodeStatic_010_Ramp_ActPRampMainFailure | Para_Grid_GridCodeStatic_010_Ramp_ActPRampUtility | Para_Grid_GridCodeStatic_010_Ramp_ActSlowRampPFC | Para_Grid_GridCodeStatic_010_Ramp_PowerFacSetpoint | Para_Grid_GridCodeStatic_010_Ramp_PRampMainFailure | Para_Grid_GridCodeStatic_010_Ramp_RampUtility | Para_Grid_GridCodeStatic_010_Ramp_TimeDelMainOk | Para_Grid_GridCodeStatic_020_PowerSet_ActPowerSetUtility | Para_Grid_GridCodeStatic_020_PowerSet_UtilityConst1 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityConst2 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityConst3 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityConst4 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityConst5 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityCurr1 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityCurr2 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityPoint1 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityPoint2 | Para_Grid_GridCodeStatic_030_PowerLimit_ActPowerLimUtility | Para_Grid_GridCodeStatic_030_PowerLimit_IntSetPoint | Para_Grid_GridCodeStatic_030_PowerLimit_LimitDemOff | Para_Grid_GridCodeStatic_030_PowerLimit_LimitDemOffHys | Para_Grid_GridCodeStatic_030_PowerLimit_LimitDemOffTimeDel | Para_Grid_GridCodeStatic_030_PowerLimit_Step1 | Para_Grid_GridCodeStatic_030_PowerLimit_Step2 | Para_Grid_GridCodeStatic_030_PowerLimit_Step3 | Para_Grid_GridCodeStatic_030_PowerLimit_Step4 | Para_Grid_GridCodeStatic_030_PowerLimit_Step5 | Para_Grid_GridCodeStatic_030_PowerLimit_UtilityCurr1 | Para_Grid_GridCodeStatic_030_PowerLimit_UtilityCurr2 | Para_Grid_GridCodeStatic_030_PowerLimit_UtilityPoint1 | Para_Grid_GridCodeStatic_030_PowerLimit_UtilityPoint2 | Para_Grid_GridCodeStatic_040_PFC_RMC_PFCRelative | Para_Grid_GridCodeStatic_040_PFC_RMC_ResponseCurve | Para_Grid_GridCodeStatic_040_PFC_RMC_RMCMargin | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_ActSetPointExt | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_BackupSetPoint | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_ChoiceFunction | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtConst1 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtConst2 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtConst3 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtConst4 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtConst5 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtCurr1 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtCurr2 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtPoint1 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtPoint2 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointInt | Para_Grid_GridCodeStatic_060_CosPhiP_ResponseCurve | Para_Grid_GridCodeStatic_070_VoltageSet_ActSetPointExt | Para_Grid_GridCodeStatic_070_VoltageSet_Backup | Para_Grid_GridCodeStatic_070_VoltageSet_ChoiceFunction | Para_Grid_GridCodeStatic_070_VoltageSet_Internal | Para_Grid_GridCodeStatic_070_VoltageSet_SetPointExtCurr1 | Para_Grid_GridCodeStatic_070_VoltageSet_SetPointExtCurr2 | Para_Grid_GridCodeStatic_070_VoltageSet_SetPointExtPoint1 | Para_Grid_GridCodeStatic_070_VoltageSet_SetPointExtPoint2 | Para_Grid_GridCodeStatic_070_VoltageSet_Unom | Para_Grid_GridCodeStatic_080_CosPhiU_ResponseCurve | Para_Grid_GridCodeStatic_090_QVolt_ResponseCurve | Para_Grid_GridCodeStatic_100_QSetIntExt_ActSetPointExt | Para_Grid_GridCodeStatic_100_QSetIntExt_BackupSetPoint | Para_Grid_GridCodeStatic_100_QSetIntExt_ChoiceFunction | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtConst1 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtConst2 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtConst3 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtConst4 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtConst5 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtCurr1 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtCurr2 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtPoint1 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtPoint2 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointInt | Para_Grid_GridCodeStatic_110_QLimit_ActSetPointExt | Para_Grid_GridCodeStatic_110_QLimit_SetPointExtCurr1 | Para_Grid_GridCodeStatic_110_QLimit_SetPointExtCurr2 | Para_Grid_GridCodeStatic_110_QLimit_SetPointExtPoint1 | Para_Grid_GridCodeStatic_110_QLimit_SetPointExtPoint2 | Para_Grid_GridCodeStatic_110_QLimit_SetPointIntLimit | Para_Grid_GridCodeStatic_120_AnalogOut_ActCosPhi4mA | Para_Grid_GridCodeStatic_120_AnalogOut_ActReactPower4mA | Para_Grid_GridCodeStatic_120_AnalogOut_CosPhiOutPoint1 | Para_Grid_GridCodeStatic_120_AnalogOut_CosPhiOutPoint2 | Para_Grid_GridCodeStatic_120_AnalogOut_ReactPowerOutPoint1 | Para_Grid_GridCodeStatic_120_AnalogOut_ReactPowerOutPoint2 | Para_halio_rpr_oxicat_in_fast_scalmax | Para_halio_rpr_oxicat_in_fast_scalmin | Para_halio_rpr_oxicat_in_scalmax | Para_halio_rpr_oxicat_in_scalmin | Para_halio_rpr_oxicat_out_scalmax | Para_halio_rpr_oxicat_out_scalmin | Para_halio_rt_oxicat_in_scalmax | Para_halio_rt_oxicat_in_scalmin | Para_halio_rt_oxicat_out_scalmax | Para_halio_rt_oxicat_out_scalmin | Para_halio_rt_scr_catscalmax | Para_halio_rt_scr_catscalmin | Para_Hyd_CoolWat_Press_20mA | Para_Hyd_CoolWat_Press_Limit1 | Para_Hyd_CoolWat_Press_Limit1Hys | Para_Hyd_CoolWat_Press_Max | Para_Hyd_CoolWat_Press_MaxHys | Para_Hyd_CoolWat_Press_Min | Para_Hyd_CoolWat_Press_Min1 | Para_Hyd_CoolWat_Press_Min1Hys | Para_Hyd_CoolWat_Press_MinHys | Para_Hyd_CoolWat_Temp_Limit1 | Para_Hyd_CoolWat_Temp_Limit1Hys | Para_Hyd_CoolWat_Temp_Limit2 | Para_Hyd_CoolWat_Temp_Limit2Hys | Para_Hyd_CoolWat_Temp_LoadEnab | Para_Hyd_CoolWat_Temp_LoadEnabHys | Para_Hyd_CoolWat_Temp_Max | Para_Hyd_CoolWat_Temp_MaxHys | Para_Hyd_CoolWat_Temp_Min | Para_Hyd_CoolWat_Temp_MinHys | Para_Hyd_CoolWat_Temp_PreHeatOff | Para_Hyd_CoolWat_Temp_PreHeatOffHys | Para_Hyd_CrankCase_20mA | Para_Hyd_CrankCase_4mA | Para_Hyd_CrankCase_Act | Para_Hyd_CrankCase_ActLimitMon | Para_Hyd_CrankCase_FreqMax | Para_Hyd_CrankCase_FreqMin | Para_Hyd_CrankCase_Limit | Para_Hyd_CrankCase_LimitHys | Para_Hyd_CrankCase_LimitWarn | Para_Hyd_CrankCase_LimitWarnHys | Para_Hyd_Oil_Counter_OilRefillOpH | Para_Hyd_Oil_Counter_PulseValue | Para_Hyd_Oil_Level_LimitClose | Para_Hyd_Oil_Level_LimitCloseHys | Para_Hyd_Oil_Level_LimitOpen | Para_Hyd_Oil_Level_LimitOpenHys | Para_Hyd_Oil_Level_Max | Para_Hyd_Oil_Level_MaxHys | Para_Hyd_Oil_Level_Min | Para_Hyd_Oil_Level_MinHys | Para_Hyd_Oil_Press_20mA | Para_Hyd_Oil_Press_DiffMax | Para_Hyd_Oil_Press_DiffMaxHys | Para_Hyd_Oil_Press_DiffMaxWarn | Para_Hyd_Oil_Press_DiffMaxWarnHys | Para_Hyd_Oil_Press_GrEqSpeed2 | Para_Hyd_Oil_Press_Hys | Para_Hyd_Oil_Press_Limit1 | Para_Hyd_Oil_Press_Limit1Hys | Para_Hyd_Oil_Press_Max | Para_Hyd_Oil_Press_MaxDelay | Para_Hyd_Oil_Press_MaxHys | Para_Hyd_Oil_Press_PreLubrLimit1 | Para_Hyd_Oil_Press_PreLubrLimit1Hys | Para_Hyd_Oil_Press_PreLubrLimit2 | Para_Hyd_Oil_Press_PreLubrLimit2Hys | Para_Hyd_Oil_Press_SmEqSpeed1 | Para_Hyd_Oil_Press_Speed1 | Para_Hyd_Oil_Press_Speed2 | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMax | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMaxHys | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMin | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMinHys | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMinWarn | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMinWarnHys | Para_Hyd_Oil_Press_TCFiltPressOutletMin1 | Para_Hyd_Oil_Press_TCFiltPressOutletMin2 | Para_Hyd_Oil_Press_TCFiltPressOutletMinHys | Para_Hyd_Oil_Press_TCFiltSpeedMin1PressOutlet | Para_Hyd_Oil_Press_TCFiltSpeedMin2PressOutlet | Para_Hyd_Oil_Press_TimeDelFiltDifPress | Para_Hyd_Oil_PressDiffFilter_Limit1 | Para_Hyd_Oil_PressDiffFilter_Limit2 | Para_Hyd_Oil_PressDiffFilter_Limit3 | Para_Hyd_Oil_PressDiffFilter_LimitDelay1 | Para_Hyd_Oil_PressDiffFilter_LimitDelay2 | Para_Hyd_Oil_PressDiffFilter_LimitDelay3 | Para_Hyd_Oil_PressDiffFilter_ReleaseTemp | Para_Hyd_Oil_PressFilterIn_20mA | Para_Hyd_Oil_PressFilterIn_4mA | Para_Hyd_Oil_PressFilterIn_ActMeasure | Para_Hyd_Oil_Temp_Limit1 | Para_Hyd_Oil_Temp_Limit1Hys | Para_Hyd_Oil_Temp_Limit2 | Para_Hyd_Oil_Temp_Limit2Hys | Para_Hyd_Oil_Temp_LimitPreWarm | Para_Hyd_Oil_Temp_LimitPreWarmHys | Para_Hyd_Oil_Temp_LoadEnab | Para_Hyd_Oil_Temp_LoadEnabHys | Para_Hyd_Oil_Temp_Max | Para_Hyd_Oil_Temp_MaxHys | Para_Hyd_Oil_Temp_Min | Para_Hyd_Oil_Temp_MinHys | Para_Hyd_Oil_TurboCh_TCType | Para_Hyd_RetWat_20mA | Para_Hyd_RetWat_Act | Para_Hyd_RetWat_ActSigTrip | Para_Hyd_RetWat_Limit | Para_Hyd_RetWat_Limit1 | Para_Hyd_RetWat_Limit1Hys | Para_Hyd_RetWat_LimitHys | Para_Hyd_RetWatCoolOut_20mA | Para_Hyd_RetWatCoolOut_Act | Para_Hyd_RetWatCoolOut_ActSigTrip | Para_Hyd_RetWatCoolOut_Limit | Para_Hyd_RetWatCoolOut_Limit1 | Para_Hyd_RetWatCoolOut_Limit1Hys | Para_Hyd_RetWatCoolOut_LimitHys | Para_Hyd_RetWatLowTemp_Act | Para_Hyd_RetWatLowTemp_Limit | Para_Hyd_RetWatLowTemp_LimitHys | Para_Hyd_RetWatPreEng_Act | Para_Hyd_RetWatPreEng_ActSigTrip | Para_Hyd_RetWatPreEng_Limit | Para_Hyd_RetWatPreEng_Limit1 | Para_Hyd_RetWatPreEng_Limit1Hys | Para_Hyd_RetWatPreEng_LimitHys | Para_Hyd_SupWat_20mA | Para_Hyd_SupWat_Act | Para_Hyd_SupWat_ActSigTrip | Para_Hyd_SupWat_Limit | Para_Hyd_SupWat_Limit1 | Para_Hyd_SupWat_Limit1Hys | Para_Hyd_SupWat_LimitHys | Para_Hydraulic_Condenser_T_CD_Re_Active | Para_Hydraulic_Condenser_T_CD_Re_HyHi | Para_Hydraulic_Condenser_T_CD_Re_LimHi | Para_Hydraulic_Condenser_T_CD_Su_Active | Para_Hydraulic_Condenser_T_CD_Su_HyHi | Para_Hydraulic_Condenser_T_CD_Su_LimHi | Para_Hydraulic_CoolWat_ECWP_MechDriven | Para_Hydraulic_CoolWat_N_ECWP_Set | Para_Hydraulic_CoolWat_Press_Pr_ECWaEng_Active | Para_Hydraulic_CoolWat_Press_Pr_ECWaEng_ScalMax | Para_Hydraulic_CoolWat_T_ECW_bChC_HT_Active | Para_Hydraulic_CoolWat_T_ECW_bECWC_Active | Para_Hydraulic_CoolWat_T_ECW_bOilC_Active | Para_Hydraulic_CoolWat_Temp_T_ECW_HyBpV | Para_Hydraulic_CoolWat_Temp_T_ECW_LimBpV | Para_Hydraulic_CoolWat_Temp_T_ECWbEng_Active | Para_Hydraulic_CoolWatModule_T_ECW_Mod_In_Active | Para_Hydraulic_CoolWatModule_T_ECW_Mod_Out_Active | Para_Hydraulic_CrankCase_DPr_BbFilt_Hi_P1 | Para_Hydraulic_CrankCase_DPr_BbFilt_Hi_P2 | Para_Hydraulic_CrankCase_DPr_BbFilt_Lo_P1 | Para_Hydraulic_CrankCase_DPr_BbFilt_Lo_P2 | Para_Hydraulic_CrankCase_DPr_BbFilt_Pstart | Para_Hydraulic_CrankCase_Pc_BbBlower_Hi | Para_Hydraulic_CrankCase_Pr_a_BbFilt_A_Exist | Para_Hydraulic_CrankCase_Pr_a_BbFilt_B_Exist | Para_Hydraulic_CrankCase_Pr_a_BbFilt_Exist | Para_Hydraulic_CrankCase_Pr_a_BbFiltScalMax | Para_Hydraulic_CrankCase_Pr_a_BbFiltScalMin | Para_Hydraulic_CrankCase_Pr_CC_Hi | Para_Hydraulic_CrankCase_Pr_CC_Lo | Para_Hydraulic_CrankCase_Pr_CCScalMax | Para_Hydraulic_CrankCase_Pr_CCScalMin | Para_Hydraulic_CrankCase_Pr_f_BbFilt_A_Exist | Para_Hydraulic_CrankCase_Pr_f_BbFilt_B_Exist | Para_Hydraulic_CrankCase_Pr_f_BbFilt_Exist | Para_Hydraulic_CrankCase_Pr_f_BbFiltScalMax | Para_Hydraulic_CrankCase_Pr_f_BbFiltScalMin | Para_Hydraulic_CrankCase_tiPr_CC_Hi | Para_Hydraulic_CrankCase_tiPr_CC_HiHi | Para_Hydraulic_HeatCircuitRetWater_T_HW_HC_Re_Active | Para_Hydraulic_HeatCircuitRetWater_T_HW_HC_Re_HyHi | Para_Hydraulic_HeatCircuitRetWater_T_HW_HC_Re_LimHi | Para_Hydraulic_HeatOutputCounter_Cnt_P_Heat | Para_Hydraulic_HeatOutputCounter_ImpVal_Cnt_P_Heat | Para_Hydraulic_HeatOutputCounter_P_Heat_Active | Para_Hydraulic_HeatOutputCounter_P_Heat_ScalMax | Para_Hydraulic_HeatOutputCounter_P_Heat_ScalMin | Para_Hydraulic_HeatWaterHigh_Pr_HW_Re_HT_Active | Para_Hydraulic_HeatWaterHigh_Pr_HW_Re_HT_ScalMax | Para_Hydraulic_HeatWaterHigh_Pr_HW_Re_HT_ScalMin | Para_Hydraulic_HeatWaterHigh_Pr_HW_Su_HT_Active | Para_Hydraulic_HeatWaterHigh_Pr_HW_Su_HT_ScalMax | Para_Hydraulic_HeatWaterLow_Pr_HW_Re_LT_Active | Para_Hydraulic_HeatWaterLow_Pr_HW_Re_LT_ScalMax | Para_Hydraulic_HeatWaterLow_Pr_HW_Re_LT_ScalMin | Para_Hydraulic_HeatWaterLow_Pr_HW_Su_LT_Active | Para_Hydraulic_HeatWaterLow_Pr_HW_Su_LT_ScalMax | Para_Hydraulic_HeatWaterLow_T_HW_Su_LT_Active | Para_Hydraulic_Oil_EO_Level_Active | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_DE_Exist | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_DE_Hi | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_DE_Lo | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_DEScalMax | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_DEScalMin | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_NDE_Exist | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_NDE_Hi | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_NDE_Lo | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_NDEScalMax | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_NDEScalMin | Para_Hydraulic_Oil_GenOilSkid_Lev_OilSkid_Tank_Exist | Para_Hydraulic_Oil_GenOilSkid_Lev_OilSkid_Tank_Lo | Para_Hydraulic_Oil_GenOilSkid_Lev_OilSkid_Tank_LoLo | Para_Hydraulic_Oil_GenOilSkid_Lev_OilSkid_TankScalMax | Para_Hydraulic_Oil_GenOilSkid_Lev_OilSkid_TankScalMin | Para_Hydraulic_Oil_GenOilSkid_Pr_OilSkid_HP_DE_Exist | Para_Hydraulic_Oil_GenOilSkid_Pr_OilSkid_HP_Lo | Para_Hydraulic_Oil_GenOilSkid_Pr_OilSkid_HP_NDE_Exist | Para_Hydraulic_Oil_GenOilSkid_Pr_OilSkid_HPScalMax | Para_Hydraulic_Oil_GenOilSkid_Pr_OilSkid_HPScalMin | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_Supply_Exist | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_Supply_Hi | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_Supply_Lo | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_SupplyScalMax | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_SupplyScalMin | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_Tank_Exist | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_Tank_Set | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_TankScalMax | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_TankScalMin | Para_Hydraulic_Oil_GenOilSkid_tiOilSkid_PumpHP_Run | Para_Hydraulic_Oil_OilFilterUnit_DPr_OFU_Filt_LimHi | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUaFilt_Active | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUaFilt_ScalMax | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUaFilt_ScalMin | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbCentrifuge_Active | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbCentrifuge_Hi | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbCentrifuge_ScalMax | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbCentrifuge_ScalMin | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbFilt_Active | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbFilt_Hi | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbFilt_ScalMax | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbFilt_ScalMin | Para_Hydraulic_Oil_OilFiltUnit_Exist | Para_Hydraulic_Oil_OilSkid_Exist | Para_Hydraulic_Oil_Press_EngTyp3_Prelub_Active | Para_Hydraulic_Oil_Press_EOP_PreHeat_Set | Para_Hydraulic_Oil_Press_EOP_PreLube_Set | Para_Hydraulic_Oil_Press_Pr_EOaP_Active | Para_Hydraulic_Oil_Press_Pr_EOaP_LimHi | Para_Hydraulic_Oil_Press_Pr_EOaP_LimHiHi | Para_Hydraulic_Oil_Press_Pr_LimHeatRel | Para_Hydraulic_Oil_PressFilterOut_Pr_EOF_After_Active | Para_Hydraulic_Oil_PressFilterOut_Pr_EOF_After_ScalMax | Para_Hydraulic_Oil_PressFilterOut_Pr_EOF_After_ScalMin | Para_Hydraulic_Oil_Quality_OQS_Active | Para_Hydraulic_Oil_Quality_OQS_Conduct_ScalMax | Para_Hydraulic_Oil_Quality_OQS_Conduct_ScalMin | Para_Hydraulic_Oil_Quality_OQS_Dielect_ScalMax | Para_Hydraulic_Oil_Quality_OQS_Dielect_ScalMin | Para_Hydraulic_Oil_Quality_OQS_Temp_ScalMax | Para_Hydraulic_Oil_Quality_OQS_Temp_ScalMin | Para_Hydraulic_Oil_Quality_OQS_Visco_ScalMax | Para_Hydraulic_Oil_Quality_OQS_Visco_ScalMin | Para_Hydraulic_Oil_ServicePrelub | Para_Hydraulic_Oil_Temp_T_EO_Pan_Active | Para_Hydraulic_Oil_Temp_T_EOaPump_Active | Para_Hydraulic_Oil_TurboCh_Pr_Oil_LPTC_In_A | Para_Hydraulic_Oil_TurboCh_Pr_Oil_LPTC_In_B | Para_Hydraulic_Oil_TurboCh_Pr_TCOaF_Active | Para_Hydraulic_Oil_TurboCh_Pr_TCObF_Active | Para_Hydraulic_Oil_TurboCh_Pr_TCObF_ScalMax | Para_Hydraulic_Oil_TurboCh_Pr_TCObF_ScalMin | Para_Hydraulic_Oil_TurboCh_TC_PostLub_Active | Para_Hydraulic_Oil_TurboCh_TC_watercooled | Para_Hydraulic_Oil_TurboCh_tiTC_Postlub | Para_Hydraulic_OilModule_Pr_EO_Mod_Out_Active | Para_Hydraulic_OilModule_Pr_EO_Mod_Out_ScalMax | Para_Hydraulic_OilModule_Pr_EO_Mod_Out_ScalMin | Para_Hydraulic_OilModule_T_EO_Mod_In_Active | Para_Hydraulic_OilModule_T_EO_Mod_Out_Active | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_ECW_Active | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_ECW_ScalMax | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_ECW_ScalMin | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_EO_Active | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_EO_ScalMax | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_EO_ScalMin | Para_Hydraulic_PreHeat_T_HW_Re_PreH_ECW_Active | Para_Hydraulic_PreHeat_T_HW_Re_PreH_EO_Active | Para_Hydraulic_PreHeat_T_HW_Su_PreH_ECW_Active | Para_Hydraulic_PreHeat_T_HW_Su_PreH_EO_Active | Para_Hydraulic_RetWatPreEng_T_HW_ReBeEng_SF_Trip | Para_Hydraulic_WasteHeatRec_ReturnPrim_T_Re_PriCirc_Active | Para_Hydraulic_WasteHeatRec_ReturnPrim_T_Re_PriCirc_HyLimHi | Para_Hydraulic_WasteHeatRec_ReturnPrim_T_Re_PriCirc_LimHi | Para_Hydraulic_WasteHeatRec_ReturnSec_T_Re_SecCirc_Active | Para_Hydraulic_WasteHeatRec_ReturnSec_T_Re_SecCirc_HyLimHi | Para_Hydraulic_WasteHeatRec_ReturnSec_T_Re_SecCirc_LimHi | Para_Hydraulic_WasteHeatRec_SupplyPrim_T_Su_PriCirc_Active | Para_Hydraulic_WasteHeatRec_SupplyPrim_T_Su_PriCirc_HyLimHi | Para_Hydraulic_WasteHeatRec_SupplyPrim_T_Su_PriCirc_LimHi | Para_Hydraulic_WasteHeatRec_SupplySec_T_Su_SecCirc_Active | Para_Hydraulic_WasteHeatRec_SupplySec_T_Su_SecCirc_HyLimHi | Para_Hydraulic_WasteHeatRec_SupplySec_T_Su_SecCirc_LimHi | Para_Ignition_ActITPTbAdap | Para_Ignition_EnergLev | Para_Ignition_ITPEarl | Para_Ignition_ITPGas1 | Para_Ignition_ITPGas2 | Para_Ignition_ITPGas3 | Para_Ignition_ITPGas4 | Para_Ignition_ITPIslandG1 | Para_Ignition_ITPIslandG2 | Para_Ignition_ITPIslandG3 | Para_Ignition_ITPIslandG4 | Para_Ignition_ITPKnockMonOffG1 | Para_Ignition_ITPKnockMonOffG2 | Para_Ignition_ITPKnockMonOffG3 | Para_Ignition_ITPKnockMonOffG4 | Para_Ignition_ITPLate | Para_Ignition_ITPMinGas1 | Para_Ignition_ITPMinGas2 | Para_Ignition_ITPMinGas3 | Para_Ignition_ITPMinGas4 | Para_Ignition_ITPTbPosAdap | Para_Ignition_mAOutput_Curr1 | Para_Ignition_mAOutput_Curr2 | Para_Ignition_mAOutput_Point1 | Para_Ignition_mAOutput_Point2 | Para_Ignition_MisfControl | Para_Ignition_MORIS_CoilType | Para_Ignition_MORIS_CoilType0_IonTimeEarl | Para_Ignition_MORIS_CoilType0_IonTimeLate | Para_Ignition_MORIS_CoilType0_MagLevelDec | Para_Ignition_MORIS_CoilType0_MagLevelInc | Para_Ignition_MORIS_CoilType0_MagLevelIon | Para_Ignition_MORIS_CoilType0_MagLevelLim | Para_Ignition_MORIS_CoilType0_PowerIgn | Para_Ignition_MORIS_CoilType0_PowerSparkLim | Para_Ignition_MORIS_CoilType0_PowerSparkRate | Para_Ignition_MORIS_CoilType0_SparkCurrIonis | Para_Ignition_MORIS_CoilType0_SparkDelayFailRate | Para_Ignition_MORIS_CoilType0_SparkDelayLim | Para_Ignition_MORIS_CoilType0_SparkDurIonis | Para_Ignition_MORIS_PowerSupplyOut | Para_Ignition_MORIS_SparkChar0_SparkCurr1 | Para_Ignition_MORIS_SparkChar0_SparkCurr2 | Para_Ignition_MORIS_SparkChar0_SparkCurr3 | Para_Ignition_MORIS_SparkChar0_SparkCurr4 | Para_Ignition_MORIS_SparkChar0_SparkCurr5 | Para_Ignition_MORIS_SparkChar0_SparkCurr6 | Para_Ignition_MORIS_SparkChar0_SparkDur1 | Para_Ignition_MORIS_SparkChar0_SparkDur2 | Para_Ignition_MORIS_SparkChar0_SparkDur3 | Para_Ignition_MORIS_SparkChar0_SparkDur4 | Para_Ignition_MORIS_SparkChar0_SparkDur5 | Para_Ignition_MORIS_SparkCurrChar | Para_Ignition_MORIS_SparkCurrDur | Para_Ignition_MORIS_SparkCurrLevel | Para_Ignition_MORIS_SparkDurTol | Para_Ignition_MORIS_SparkDurTolFailRate | Para_Ignition_OutputMon | Para_Ignition_OverSpeed | Para_Ignition_ResetPos | Para_Ignition_SecSpeed | Para_Ignition_Setting_EnergLev | Para_Ignition_Setting_OutputMon | Para_Ignition_Setting_ResetPos | Para_Ignition_Setting_SecSpeed | Para_Ignition_Setting_SpeedRelay1 | Para_Ignition_Setting_SpeedRelay2 | Para_Ignition_Setting_SpeedRelay2InvOut | Para_Ignition_Setting_SpeedRelayHys1 | Para_Ignition_Setting_SpeedRelayHys2 | Para_Ignition_SpeedRelay1 | Para_Ignition_SpeedRelay2 | Para_Ignition_SpeedRelay2InvOut | Para_Ignition_SpeedRelayHys1 | Para_Ignition_SpeedRelayHys2 | Para_Island_Advanced_ActMapVolEff | Para_Island_Advanced_ActSpeedComp | Para_Island_Advanced_CompByTimeCorr | Para_Island_Advanced_CompByValueCorr | Para_Island_Advanced_CompByValueCorrRed | Para_Island_Advanced_ITPShift | Para_Island_Advanced_SpeedCompCorrFact | Para_Island_Advanced_SpeedCompFact | Para_Island_Ctr_TbDComp | Para_Island_Ctr_TbIComp | Para_Island_Ctr_TbPComp | Para_Island_Ctr_TbYMax | Para_Island_Ctr_TbYMin | Para_Island_Ctr_TrDComp | Para_Island_Ctr_TrIComp | Para_Island_Ctr_TrPComp | Para_Island_Ctr_TrYMax | Para_Island_Ctr_TrYMin | Para_Island_LambdaAdap_FactNegPower | Para_Island_LambdaAdap_FactNegSpeed | Para_Island_LambdaAdap_FactPosPower | Para_Island_LambdaAdap_FactPosSpeed | Para_Island_LambdaAdap_TriggerLowPower | Para_Island_LambdaAdap_TriggerLowSpeed | Para_Island_LambdaAdap_TriggerUpPower | Para_Island_LambdaAdap_TriggerUpSpeed | Para_Island_Limit_LSdPowerMax | Para_Island_Limit_LSdPowerMaxDelay | Para_Island_Limit_LSdPowerMaxHys | Para_Island_Limit_LSdPowerMinAlarm | Para_Island_Limit_LSdPowerMinAlarmDelay | Para_Island_Limit_LSdPowerMinHys | Para_Island_Limit_LSdPowerMinTrip | Para_Island_Limit_LSdPowerMinTripDelay | Para_Island_Limit_LSdSpeedLimit | Para_Island_Limit_LSdSpeedLimitDelay | Para_Island_Limit_LSdSpeedLimitHys | Para_Island_LoadSh_ActOffsetCoef | Para_Island_LoadSh_LoadSh | Para_Island_LoadSh_OffsetCoef | Para_Island_OutPowerLimit_Curr1 | Para_Island_OutPowerLimit_Curr2 | Para_Island_OutPowerLimit_Point1 | Para_Island_OutPowerLimit_Point2 | Para_Island_Ramp_Ramp | Para_Knock_ActKnockMon | Para_Knock_ActKnockMonHys | Para_Knock_CylOpt_Active | Para_Knock_CylOpt_IntTimeUp | Para_Knock_CylOpt_IPAdaptIntervall | Para_Knock_CylOpt_LimitKnockInt | Para_Knock_CylOpt_MonIntervall | Para_Knock_CylOpt_PowAdaptIntervall | Para_Knock_CylOpt_ResetTimeOpt | Para_Knock_CylOpt_ResetTimeOptPred | Para_Knock_IPAdapOffsetKnockCtrGas1 | Para_Knock_IPAdapOffsetKnockCtrGas2 | Para_Knock_IPAdapOffsetKnockCtrGas3 | Para_Knock_IPAdapOffsetKnockCtrGas4 | Para_Knock_IPRedMaxKnockCtrGas1 | Para_Knock_IPRedMaxKnockCtrGas2 | Para_Knock_IPRedMaxKnockCtrGas3 | Para_Knock_IPRedMaxKnockCtrGas4 | Para_Knock_ITPMinGas1 | Para_Knock_ITPMinGas2 | Para_Knock_ITPMinGas3 | Para_Knock_ITPMinGas4 | Para_Knock_KLS90_KnockLimit1 | Para_Knock_KLS90_KnockLimit2 | Para_Knock_KLS98_AngleDurWindow1 | Para_Knock_KLS98_AngleDurWindow2 | Para_Knock_KLS98_AngleDurWindow3 | Para_Knock_KLS98_AnglePosCam | Para_Knock_KLS98_AnglePosWindow1 | Para_Knock_KLS98_AnglePosWindow2 | Para_Knock_KLS98_AnglePosWindow3 | Para_Knock_KLS98_EnabCyl1 | Para_Knock_KLS98_EnabCyl10 | Para_Knock_KLS98_EnabCyl11 | Para_Knock_KLS98_EnabCyl12 | Para_Knock_KLS98_EnabCyl13 | Para_Knock_KLS98_EnabCyl14 | Para_Knock_KLS98_EnabCyl15 | Para_Knock_KLS98_EnabCyl16 | Para_Knock_KLS98_EnabCyl17 | Para_Knock_KLS98_EnabCyl18 | Para_Knock_KLS98_EnabCyl19 | Para_Knock_KLS98_EnabCyl2 | Para_Knock_KLS98_EnabCyl20 | Para_Knock_KLS98_EnabCyl21 | Para_Knock_KLS98_EnabCyl22 | Para_Knock_KLS98_EnabCyl23 | Para_Knock_KLS98_EnabCyl24 | Para_Knock_KLS98_EnabCyl3 | Para_Knock_KLS98_EnabCyl4 | Para_Knock_KLS98_EnabCyl5 | Para_Knock_KLS98_EnabCyl6 | Para_Knock_KLS98_EnabCyl7 | Para_Knock_KLS98_EnabCyl8 | Para_Knock_KLS98_EnabCyl9 | Para_Knock_KLS98_ITPAdjustGlobCylsel | Para_Knock_KLS98_KnockFilterFunc | Para_Knock_KLS98_KnockLimit | Para_Knock_KLS98_MeasSigDist | Para_Knock_KLS98_MechNoiseMax | Para_Knock_KLS98_ValveNoiseMax | Para_Knock_PBC_AngleDurGlowI | Para_Knock_PBC_AngleDurKnock | Para_Knock_PBC_AnglePosGlowI | Para_Knock_PBC_AnglePosKnock | Para_Knock_PBC_GlobalIPAdj | Para_Knock_PBC_GlowILimit | Para_Knock_PBC_KnockLimit | Para_Knock_PBC_MeasSigLimit | Para_Knock_RedITPEnd | Para_Knock_RedITPEndNew | Para_Knock_RedITPStart | Para_Knock_RedMixTempEnd | Para_Knock_RedMixTempEndNew | Para_Knock_RedMixTempStart | Para_Knock_RedPowerEnd | Para_Knock_RedPowerEndNew | Para_Knock_RedPowerStart | Para_Knock_TempMixRedMax | Para_Knock_TimeIntDown | Para_Knock_TimeIntUp | Para_Leanox_ActILeanoxCtrIsland | Para_Leanox_ActPRedLeanox | Para_Leanox_Comp_ActITPBoostPress | Para_Leanox_Comp_ActMixtTempBoostPress | Para_Leanox_Comp_ActPowerFriction | Para_Leanox_Comp_ActSpeed | Para_Leanox_Comp_ITPDeltaPress1 | Para_Leanox_Comp_ITPDeltaPress2 | Power SetVal | Para_Leanox_Comp_ITPPower2 | Para_Leanox_Comp_ITPPowerMin | Para_Leanox_Comp_MixTempPower1 | Para_Leanox_Comp_MixTempPower2 | Para_Leanox_Comp_MixTempPowerMin | Para_Leanox_Comp_MixTempPress1 | Para_Leanox_Comp_MixTempPress2 | Para_Leanox_Gas1_CtrGasmixer_DeadBand | Para_Leanox_Gas1_CtrGasmixer_IComp | Para_Leanox_Gas1_CtrGasmixer_Limit | Para_Leanox_Gas1_CtrGasmixer_PComp | Para_Leanox_Gas1_CtrGasmixer_YMax | Para_Leanox_Gas1_CtrGasmixer_YMin | Para_Leanox_Gas1_CtrTecjet_DeadBand | Para_Leanox_Gas1_CtrTecjet_IComp | Para_Leanox_Gas1_CtrTecjet_Limit | Para_Leanox_Gas1_CtrTecjet_PComp | Para_Leanox_Gas1_CtrTecjet_YMax | Para_Leanox_Gas1_CtrTecjet_YMin | Para_Leanox_Gas1_DeltaPressIsl | Para_Leanox_Gas1_Para_DP | Para_Leanox_Gas1_Para_DPIslandAdap | Para_Leanox_Gas1_Para_P1 | Para_Leanox_Gas1_Para_P2 | Para_Leanox_Gas1_Para_PowerPoint1 | Para_Leanox_Gas1_Para_PowerPoint2 | Para_Leanox_Gas1_Para_PressurePoint1 | Para_Leanox_Gas1_Para_PressurePoint2 | Para_Leanox_Gas1_Para_SpeedPoint1 | Para_Leanox_Gas1_Para_SpeedPoint2 | Para_Leanox_Gas1_Para_T1 | Para_Leanox_Gas1_Para_TempPoint1 | Para_Leanox_Gas1_Para_TempPoint2 | Para_Leanox_Gas1_Para_W1 | Para_Leanox_Gas1_PowerAct | Para_Leanox_Gas1_PowerActHys | Para_Leanox_Gas2_CtrGasmixer_DeadBand | Para_Leanox_Gas2_CtrGasmixer_IComp | Para_Leanox_Gas2_CtrGasmixer_Limit | Para_Leanox_Gas2_CtrGasmixer_PComp | Para_Leanox_Gas2_CtrGasmixer_YMax | Para_Leanox_Gas2_CtrGasmixer_YMin | Para_Leanox_Gas2_CtrTecjet_DeadBand | Para_Leanox_Gas2_CtrTecjet_IComp | Para_Leanox_Gas2_CtrTecjet_Limit | Para_Leanox_Gas2_CtrTecjet_PComp | Para_Leanox_Gas2_CtrTecjet_YMax | Para_Leanox_Gas2_CtrTecjet_YMin | Para_Leanox_Gas2_DeltaPressIsl | Para_Leanox_Gas2_Para_DP | Para_Leanox_Gas2_Para_DPIslandAdap | Para_Leanox_Gas2_Para_P1 | Para_Leanox_Gas2_Para_P2 | Para_Leanox_Gas2_Para_PowerPoint1 | Para_Leanox_Gas2_Para_PowerPoint2 | Para_Leanox_Gas2_Para_PressurePoint1 | Para_Leanox_Gas2_Para_PressurePoint2 | Para_Leanox_Gas2_Para_SpeedPoint1 | Para_Leanox_Gas2_Para_SpeedPoint2 | Para_Leanox_Gas2_Para_T1 | Para_Leanox_Gas2_Para_TempPoint1 | Para_Leanox_Gas2_Para_TempPoint2 | Para_Leanox_Gas2_Para_W1 | Para_Leanox_Gas2_PowerAct | Para_Leanox_Gas2_PowerActHys | Para_Leanox_Gas3_CtrGasmixer_DeadBand | Para_Leanox_Gas3_CtrGasmixer_IComp | Para_Leanox_Gas3_CtrGasmixer_Limit | Para_Leanox_Gas3_CtrGasmixer_PComp | Para_Leanox_Gas3_CtrGasmixer_YMax | Para_Leanox_Gas3_CtrGasmixer_YMin | Para_Leanox_Gas3_CtrTecjet_DeadBand | Para_Leanox_Gas3_CtrTecjet_IComp | Para_Leanox_Gas3_CtrTecjet_Limit | Para_Leanox_Gas3_CtrTecjet_PComp | Para_Leanox_Gas3_CtrTecjet_YMax | Para_Leanox_Gas3_CtrTecjet_YMin | Para_Leanox_Gas3_DeltaPressIsl | Para_Leanox_Gas3_Para_DP | Para_Leanox_Gas3_Para_DPIslandAdap | Para_Leanox_Gas3_Para_P1 | Para_Leanox_Gas3_Para_P2 | Para_Leanox_Gas3_Para_PowerPoint1 | Para_Leanox_Gas3_Para_PowerPoint2 | Para_Leanox_Gas3_Para_PressurePoint1 | Para_Leanox_Gas3_Para_PressurePoint2 | Para_Leanox_Gas3_Para_SpeedPoint1 | Para_Leanox_Gas3_Para_SpeedPoint2 | Para_Leanox_Gas3_Para_T1 | Para_Leanox_Gas3_Para_TempPoint1 | Para_Leanox_Gas3_Para_TempPoint2 | Para_Leanox_Gas3_Para_W1 | Para_Leanox_Gas3_PowerAct | Para_Leanox_Gas3_PowerActHys | Para_Leanox_Gas4_CtrGasmixer_DeadBand | Para_Leanox_Gas4_CtrGasmixer_IComp | Para_Leanox_Gas4_CtrGasmixer_Limit | Para_Leanox_Gas4_CtrGasmixer_PComp | Para_Leanox_Gas4_CtrGasmixer_YMax | Para_Leanox_Gas4_CtrGasmixer_YMin | Para_Leanox_Gas4_CtrTecjet_DeadBand | Para_Leanox_Gas4_CtrTecjet_IComp | Para_Leanox_Gas4_CtrTecjet_Limit | Para_Leanox_Gas4_CtrTecjet_PComp | Para_Leanox_Gas4_CtrTecjet_YMax | Para_Leanox_Gas4_CtrTecjet_YMin | Para_Leanox_Gas4_DeltaPressIsl | Para_Leanox_Gas4_Para_DP | Para_Leanox_Gas4_Para_DPIslandAdap | Para_Leanox_Gas4_Para_P1 | Para_Leanox_Gas4_Para_P2 | Para_Leanox_Gas4_Para_PowerPoint1 | Para_Leanox_Gas4_Para_PowerPoint2 | Para_Leanox_Gas4_Para_PressurePoint1 | Para_Leanox_Gas4_Para_PressurePoint2 | Para_Leanox_Gas4_Para_SpeedPoint1 | Para_Leanox_Gas4_Para_SpeedPoint2 | Para_Leanox_Gas4_Para_T1 | Para_Leanox_Gas4_Para_TempPoint1 | Para_Leanox_Gas4_Para_TempPoint2 | Para_Leanox_Gas4_Para_W1 | Para_Leanox_Gas4_PowerAct | Para_Leanox_Gas4_PowerActHys | Para_Leanox_Humidity_ActBoostTempOffset | Para_Leanox_Humidity_BoostTempDevToICWT | Para_Leanox_Humidity_BoostTempRaiseDevTime | Para_Leanox_Humidity_BosstTempRaiseMax | Para_Leanox_Humidity_CompValKnockMonStart | Para_Leanox_Humidity_CompValPnom | Para_Leanox_Humidity_Offset | Para_Leanox_PressBoost_20mA | Para_Leanox_PressBoost_4mA | Para_Leanox_PressBoost_ActP2 | Para_Leanox_PressBoost_P2_20mA | Para_Leanox_PressBoost_P2_4mA | Para_Leanox_RampPowerRed | Para_Misfire_KLS98_Active | Para_Misfire_KLS98_ActOCA | Para_Misfire_KLS98_AngleWindowDur | Para_Misfire_KLS98_AngleWindowLimit | Para_Misfire_KLS98_Limit | Para_Misfire_Limit | Para_Misfire_PreWarn | Para_Misfire_TimeIntDown | Para_Misfire_TimeIntUp | Para_MixCharge_AirFilterDiffPress_20mA | Para_MixCharge_AirFilterDiffPress_4mA | Para_MixCharge_AirFilterDiffPress_ActPressA | Para_MixCharge_AirFilterDiffPress_ActPressB | Para_MixCharge_AirFilterDiffPress_Limit | Para_MixCharge_AirFilterDiffPress_LimitHys | Para_MixCharge_Press_Act_Pr_Ch_P1HP | Para_MixCharge_Press_Act_Pr_Ch_P1HP_A | Para_MixCharge_Press_Act_Pr_Ch_P1HP_B | Para_MixCharge_Press_Act_Pr_Ch_P2_A | Para_MixCharge_Press_Act_Pr_Ch_P2_B | Para_MixCharge_Press_Act_Pr_Ch_P2s | Para_MixCharge_Press_Act_Pr_Ch_P2s_A | Para_MixCharge_Press_Act_Pr_Ch_P2s_B | Para_MixCharge_Press_Pr_Ch_P1HPScalMax | Para_MixCharge_Press_Pr_Ch_P1HPScalMin | Para_MixCharge_Press_Pr_Ch_P2s_Diff_HiHi | Para_MixCharge_Speed_Act_N_TCHP | Para_MixCharge_Speed_Act_N_TCLP | Para_MixCharge_Speed_TCHPScalMax | Para_MixCharge_Speed_TCHPScalMin | Para_MixCharge_Speed_TCLPScalMax | Para_MixCharge_Speed_TCLPScalMin | Para_MixCharge_SpreadChargePress | Para_MixCharge_SpreadChargeTemp | Para_MixCharge_Temp_Act_T_Ch_T1HP_Exist | Para_MixCharge_Temp_ActTempInletHighpressA | Para_MixCharge_Temp_ActTempInletHighPressB | Para_MixCharge_Temp_MaxDtInletHighPress | Para_MixCharge_Temp_MaxHysDtInletHighPress | Para_MixCharge_Temp_MaxHysInletHighPress | Para_MixCharge_Temp_MaxInletHighPress | Para_MixCharge_Temp_MinHysInletHighPress | Para_MixCharge_Temp_MinInletHighPress | Para_MixTemp_Ctr_CycleTime | Para_MixTemp_Ctr_DComp | Para_MixTemp_Ctr_DCompTune | Para_MixTemp_Ctr_DeadBand | Para_MixTemp_Ctr_IComp | Para_MixTemp_Ctr_ICompTune | Para_MixTemp_Ctr_InvertCtrTune | Para_MixTemp_Ctr_PComp | Para_MixTemp_Ctr_PCompTune | Para_MixTemp_Ctr_RangeEnd | Para_MixTemp_Ctr_UserLevelIntExt | Para_MixTemp_Ctr_UserLevelManAut | Para_MixTemp_Ctr_UserLevelSet | Para_MixTemp_Ctr_UserLevelTune | Para_MixTemp_Ctr_WGas1 | Para_MixTemp_Ctr_WGas2 | Para_MixTemp_Ctr_WGas3 | Para_MixTemp_Ctr_WGas4 | Para_MixTemp_Ctr_WMax | Para_MixTemp_Ctr_WMin | Para_MixTemp_Ctr_WRampNeg | Para_MixTemp_Ctr_WRampPos | Para_MixTemp_Ctr_YBlock | Para_MixTemp_Ctr_YMax | Para_MixTemp_Ctr_YMin | Para_MixTemp_Ctr_YRampNeg | Para_MixTemp_Ctr_YRampPos | Para_MixTemp_Ctr_YRampTune | Para_MixTemp_Limit_Act_T_Ch_T2s_A_Exist | Para_MixTemp_Limit_Act_T_Ch_T2s_B_Exist | Para_MixTemp_Limit_Act_T_Ch_T2s_Exist | Para_MixTemp_Limit_TempdTMax | Para_MixTemp_Limit_TempLimit1 | Para_MixTemp_Limit_TempLimit2 | Para_MixTemp_Limit_TempLimitHys1 | Para_MixTemp_Limit_TempLimitHys2 | Para_MixTemp_Limit_TempMax | Para_MixTemp_Limit_TempMaxHys | Para_MixTemp_Limit_TempMin | Para_MixTemp_Limit_TempMinHys | Para_MMD_Aron | Para_MMD_CurrAsymetry | Para_MMD_CurrAsymetryDelay | Para_MMD_CurrNeuMax | Para_MMD_CurrNeuMaxDelay | Para_MMD_CurrRange | Para_MMD_CurrShortCircuit | Para_MMD_CurrShortCircuitDelay | Para_MMD_CurrThermOverloadProt | Para_MMD_ImpulseValue | Para_MMD_IntValue | Para_MMD_MMD1_ActSynch | Para_MMD_MMD1_Aron | Para_MMD_MMD1_Bus3PhaseCircuit | Para_MMD_MMD1_CurrAsymetryDelay | Para_MMD_MMD1_CurrNeuMax | Para_MMD_MMD1_CurrNeuMaxDelay | Para_MMD_MMD1_CurrNeuNom | Para_MMD_MMD1_CurrRange | Para_MMD_MMD1_CurrShortCircuit | Para_MMD_MMD1_CurrShortCircuitDelay | Para_MMD_MMD1_CurrThermOverloadProt | Para_MMD_MMD1_FreqDiffMax | Para_MMD_MMD1_FreqDiffMin | Para_MMD_MMD1_Gen3PhaseCircuit | Para_MMD_MMD1_ImpulseValue | Para_MMD_MMD1_IntValue | Para_MMD_MMD1_MultiplierBusBar | Para_MMD_MMD1_MultiplierIL1L3 | Para_MMD_MMD1_MultiplierSynch1 | Para_MMD_MMD1_MultiplierSynch2 | Para_MMD_MMD1_MultiplierUL1L3 | Para_MMD_MMD1_NomFreq | Para_MMD_MMD1_NomFreqConv100 | Para_MMD_MMD1_NomVolt | Para_MMD_MMD1_OverFreq | Para_MMD_MMD1_OverFreqDelay | Para_MMD_MMD1_OverVolt | Para_MMD_MMD1_OverVoltDelay | Para_MMD_MMD1_PhaseDiffMax | Para_MMD_MMD1_Power0mA | Para_MMD_MMD1_Power20mA | Para_MMD_MMD1_PowerReactMin | Para_MMD_MMD1_PowerReactMinDelay | Para_MMD_MMD1_SwitchTimePowerCB | Para_MMD_MMD1_TimeRelImpMin | Para_MMD_MMD1_TransPhaseShift | Para_MMD_MMD1_UnderFreq | Para_MMD_MMD1_UnderFreqDelay | Para_MMD_MMD1_UnderVolt | Para_MMD_MMD1_UnderVolt2 | Para_MMD_MMD1_UnderVolt2Delay | Para_MMD_MMD1_UnderVoltDelay | Para_MMD_MMD1_VoltAsymetry | Para_MMD_MMD1_VoltAsymetryDelay | Para_MMD_MMD1_VoltBusBarMin | Para_MMD_MMD1_VoltDeadBus | Para_MMD_MMD1_VoltDiffMax | Para_MMD_MMD1_VoltNomBusBar | Para_MMD_MMD1_VoltNomSynch | Para_MMD_MMD1_VoltRange | Para_MMD_MMD1_VoltRangeBus | Para_MMD_MMD1_VoltRangeSync1 | Para_MMD_MMD1_VoltRangeSync2 | Para_MMD_MMD2_ActSynch | Para_MMD_MMD2_Aron | Para_MMD_MMD2_Bus3PhaseCircuit | Para_MMD_MMD2_CurrAsymetryDelay | Para_MMD_MMD2_CurrNeuMax | Para_MMD_MMD2_CurrNeuMaxDelay | Para_MMD_MMD2_CurrNeuNom | Para_MMD_MMD2_CurrRange | Para_MMD_MMD2_CurrShortCircuit | Para_MMD_MMD2_CurrShortCircuitDelay | Para_MMD_MMD2_CurrThermOverloadProt | Para_MMD_MMD2_FreqDiffMax | Para_MMD_MMD2_FreqDiffMin | Para_MMD_MMD2_Gen3PhaseCircuit | Para_MMD_MMD2_ImpulseValue | Para_MMD_MMD2_IntValue | Para_MMD_MMD2_MultiplierBusBar | Para_MMD_MMD2_MultiplierIL1L3 | Para_MMD_MMD2_MultiplierSynch1 | Para_MMD_MMD2_MultiplierSynch2 | Para_MMD_MMD2_MultiplierUL1L3 | Para_MMD_MMD2_NomFreq | Para_MMD_MMD2_NomFreqConv100 | Para_MMD_MMD2_NomVolt | Para_MMD_MMD2_OverFreq | Para_MMD_MMD2_OverFreqDelay | Para_MMD_MMD2_OverVolt | Para_MMD_MMD2_OverVoltDelay | Para_MMD_MMD2_PhaseDiffMax | Para_MMD_MMD2_Power0mA | Para_MMD_MMD2_Power20mA | Para_MMD_MMD2_PowerReactMin | Para_MMD_MMD2_PowerReactMinDelay | Para_MMD_MMD2_SwitchTimePowerCB | Para_MMD_MMD2_TimeRelImpMin | Para_MMD_MMD2_TransPhaseShift | Para_MMD_MMD2_UnderFreq | Para_MMD_MMD2_UnderFreqDelay | Para_MMD_MMD2_UnderVolt | Para_MMD_MMD2_UnderVolt2 | Para_MMD_MMD2_UnderVolt2Delay | Para_MMD_MMD2_UnderVoltDelay | Para_MMD_MMD2_VoltAsymetry | Para_MMD_MMD2_VoltAsymetryDelay | Para_MMD_MMD2_VoltBusBarMin | Para_MMD_MMD2_VoltDeadBus | Para_MMD_MMD2_VoltDiffMax | Para_MMD_MMD2_VoltNomBusBar | Para_MMD_MMD2_VoltNomSynch | Para_MMD_MMD2_VoltRange | Para_MMD_MMD2_VoltRangeBus | Para_MMD_MMD2_VoltRangeSync1 | Para_MMD_MMD2_VoltRangeSync2 | Para_MMD_MultiplierIL1L3 | Para_MMD_MultiplierUL1L3 | Para_MMD_OverFreq | Para_MMD_OverFreqDelay | Para_MMD_OverVolt | Para_MMD_OverVoltDelay | Para_MMD_Power0mA | Para_MMD_Power20mA | Para_MMD_PowerReactMin | Para_MMD_PowerReactMinDelay | Para_MMD_Relay1 | Para_MMD_Relay2 | Para_MMD_Relay3 | Para_MMD_Relay4 | Para_MMD_Relay5 | Para_MMD_Relay6 | Para_MMD_Relay7 | Para_MMD_Relay8 | Para_MMD_UnderFreq | Para_MMD_UnderFreqDelay | Para_MMD_UnderVolt | Para_MMD_UnderVoltDelay | Para_MMD_VoltAsymetry | Para_MMD_VoltAsymetryDelay | Para_MMD_VoltRange | Para_ModulControler_Ctr10_DComp | Para_ModulControler_Ctr10_deadband | Para_ModulControler_Ctr10_dW_down | Para_ModulControler_Ctr10_dW_up | Para_ModulControler_Ctr10_dY_max | Para_ModulControler_Ctr10_IComp | Para_ModulControler_Ctr10_Kp_manualAdjust | Para_ModulControler_Ctr10_nvert | Para_ModulControler_Ctr10_PComp | Para_ModulControler_Ctr10_Pos_HW_ReValve | Para_ModulControler_Ctr10_Pos_HW_ReValve_ScalMax | Para_ModulControler_Ctr10_Pos_HW_ReValve_ScalMin | Para_ModulControler_Ctr10_t_min_pulse_down | Para_ModulControler_Ctr10_t_min_pulse_up | Para_ModulControler_Ctr10_t_period_down | Para_ModulControler_Ctr10_t_period_up | Para_ModulControler_Ctr10_Tn_manualAdjust | Para_ModulControler_Ctr10_Tv_manualAdjust | Para_ModulControler_Ctr10_WMax | Para_ModulControler_Ctr10_WMin | Para_ModulControler_Ctr10_WStart | Para_ModulControler_Ctr10_Y_block | Para_ModulControler_Ctr10_YMax | Para_ModulControler_Ctr10_YMin | Para_ModulControler_Ctr11_DComp | Para_ModulControler_Ctr11_deadband | Para_ModulControler_Ctr11_dW_down | Para_ModulControler_Ctr11_dW_up | Para_ModulControler_Ctr11_dY_max | Para_ModulControler_Ctr11_IComp | Para_ModulControler_Ctr11_Kp_manualAdjust | Para_ModulControler_Ctr11_nvert | Para_ModulControler_Ctr11_PComp | Para_ModulControler_Ctr11_Pos_HW_EC_ReValve | Para_ModulControler_Ctr11_Pos_HW_EC_ReValve_ScalMax | Para_ModulControler_Ctr11_Pos_HW_EC_ReValve_ScalMin | Para_ModulControler_Ctr11_t_min_pulse_down | Para_ModulControler_Ctr11_t_min_pulse_up | Para_ModulControler_Ctr11_t_period_down | Para_ModulControler_Ctr11_t_period_up | Para_ModulControler_Ctr11_Tn_manualAdjust | Para_ModulControler_Ctr11_Tv_manualAdjust | Para_ModulControler_Ctr11_WMax | Para_ModulControler_Ctr11_WMin | Para_ModulControler_Ctr11_WStart | Para_ModulControler_Ctr11_Y_block | Para_ModulControler_Ctr11_YMax | Para_ModulControler_Ctr11_YMin | Para_ModulControler_Ctr12_DComp | Para_ModulControler_Ctr12_deadband | Para_ModulControler_Ctr12_dW_down | Para_ModulControler_Ctr12_dW_up | Para_ModulControler_Ctr12_dY_max | Para_ModulControler_Ctr12_IComp | Para_ModulControler_Ctr12_Kp_manualAdjust | Para_ModulControler_Ctr12_nvert | Para_ModulControler_Ctr12_PComp | Para_ModulControler_Ctr12_t_min_pulse_down | Para_ModulControler_Ctr12_t_min_pulse_up | Para_ModulControler_Ctr12_t_period_down | Para_ModulControler_Ctr12_t_period_up | Para_ModulControler_Ctr12_Tn_manualAdjust | Para_ModulControler_Ctr12_Tv_manualAdjust | Para_ModulControler_Ctr12_WMax | Para_ModulControler_Ctr12_WMin | Para_ModulControler_Ctr12_WStart | Para_ModulControler_Ctr12_Y_block | Para_ModulControler_Ctr12_YMax | Para_ModulControler_Ctr12_YMin | Para_ModulControler_Ctr13_DComp | Para_ModulControler_Ctr13_deadband | Para_ModulControler_Ctr13_dW_down | Para_ModulControler_Ctr13_dW_up | Para_ModulControler_Ctr13_dY_max | Para_ModulControler_Ctr13_IComp | Para_ModulControler_Ctr13_Kp_manualAdjust | Para_ModulControler_Ctr13_nvert | Para_ModulControler_Ctr13_PComp | Para_ModulControler_Ctr13_t_min_pulse_down | Para_ModulControler_Ctr13_t_min_pulse_up | Para_ModulControler_Ctr13_t_period_down | Para_ModulControler_Ctr13_t_period_up | Para_ModulControler_Ctr13_Tn_manualAdjust | Para_ModulControler_Ctr13_Tv_manualAdjust | Para_ModulControler_Ctr13_WMax | Para_ModulControler_Ctr13_WMin | Para_ModulControler_Ctr13_WStart | Para_ModulControler_Ctr13_Y_block | Para_ModulControler_Ctr13_YMax | Para_ModulControler_Ctr13_YMin | Para_ModulControler_Ctr14_DComp | Para_ModulControler_Ctr14_deadband | Para_ModulControler_Ctr14_dW_down | Para_ModulControler_Ctr14_dW_up | Para_ModulControler_Ctr14_dY_max | Para_ModulControler_Ctr14_IComp | Para_ModulControler_Ctr14_Kp_manualAdjust | Para_ModulControler_Ctr14_nvert | Para_ModulControler_Ctr14_PComp | Para_ModulControler_Ctr14_t_min_pulse_down | Para_ModulControler_Ctr14_t_min_pulse_up | Para_ModulControler_Ctr14_t_period_down | Para_ModulControler_Ctr14_t_period_up | Para_ModulControler_Ctr14_Tn_manualAdjust | Para_ModulControler_Ctr14_Tv_manualAdjust | Para_ModulControler_Ctr14_WMax | Para_ModulControler_Ctr14_WMin | Para_ModulControler_Ctr14_WStart | Para_ModulControler_Ctr14_Y_block | Para_ModulControler_Ctr14_YMax | Para_ModulControler_Ctr14_YMin | Para_ModulControler_Ctr15_DComp | Para_ModulControler_Ctr15_deadband | Para_ModulControler_Ctr15_dW_down | Para_ModulControler_Ctr15_dW_up | Para_ModulControler_Ctr15_dY_max | Para_ModulControler_Ctr15_IComp | Para_ModulControler_Ctr15_Kp_manualAdjust | Para_ModulControler_Ctr15_nvert | Para_ModulControler_Ctr15_PComp | Para_ModulControler_Ctr15_t_min_pulse_down | Para_ModulControler_Ctr15_t_min_pulse_up | Para_ModulControler_Ctr15_t_period_down | Para_ModulControler_Ctr15_t_period_up | Para_ModulControler_Ctr15_Tn_manualAdjust | Para_ModulControler_Ctr15_Tv_manualAdjust | Para_ModulControler_Ctr15_WMax | Para_ModulControler_Ctr15_WMin | Para_ModulControler_Ctr15_WStart | Para_ModulControler_Ctr15_Y_block | Para_ModulControler_Ctr15_YMax | Para_ModulControler_Ctr15_YMin | Para_ModulControler_Ctr16_DComp | Para_ModulControler_Ctr16_deadband | Para_ModulControler_Ctr16_dW_down | Para_ModulControler_Ctr16_dW_up | Para_ModulControler_Ctr16_dY_max | Para_ModulControler_Ctr16_IComp | Para_ModulControler_Ctr16_Kp_manualAdjust | Para_ModulControler_Ctr16_nvert | Para_ModulControler_Ctr16_PComp | Para_ModulControler_Ctr16_t_min_pulse_down | Para_ModulControler_Ctr16_t_min_pulse_up | Para_ModulControler_Ctr16_t_period_down | Para_ModulControler_Ctr16_t_period_up | Para_ModulControler_Ctr16_Tn_manualAdjust | Para_ModulControler_Ctr16_Tv_manualAdjust | Para_ModulControler_Ctr16_WMax | Para_ModulControler_Ctr16_WMin | Para_ModulControler_Ctr16_WStart | Para_ModulControler_Ctr16_Y_block | Para_ModulControler_Ctr16_YMax | Para_ModulControler_Ctr16_YMin | Para_ModulControler_Ctr17_DComp | Para_ModulControler_Ctr17_deadband | Para_ModulControler_Ctr17_dW_down | Para_ModulControler_Ctr17_dW_up | Para_ModulControler_Ctr17_dY_max | Para_ModulControler_Ctr17_IComp | Para_ModulControler_Ctr17_Kp_manualAdjust | Para_ModulControler_Ctr17_nvert | Para_ModulControler_Ctr17_PComp | Para_ModulControler_Ctr17_t_min_pulse_down | Para_ModulControler_Ctr17_t_min_pulse_up | Para_ModulControler_Ctr17_t_period_down | Para_ModulControler_Ctr17_t_period_up | Para_ModulControler_Ctr17_Tn_manualAdjust | Para_ModulControler_Ctr17_Tv_manualAdjust | Para_ModulControler_Ctr17_WMax | Para_ModulControler_Ctr17_WMin | Para_ModulControler_Ctr17_WStart | Para_ModulControler_Ctr17_Y_block | Para_ModulControler_Ctr17_YMax | Para_ModulControler_Ctr17_YMin | Para_ModulControler_Ctr18_DComp | Para_ModulControler_Ctr18_deadband | Para_ModulControler_Ctr18_dW_down | Para_ModulControler_Ctr18_dW_up | Para_ModulControler_Ctr18_dY_max | Para_ModulControler_Ctr18_IComp | Para_ModulControler_Ctr18_Kp_manualAdjust | Para_ModulControler_Ctr18_nvert | Para_ModulControler_Ctr18_PComp | Para_ModulControler_Ctr18_t_min_pulse_down | Para_ModulControler_Ctr18_t_min_pulse_up | Para_ModulControler_Ctr18_t_period_down | Para_ModulControler_Ctr18_t_period_up | Para_ModulControler_Ctr18_Tn_manualAdjust | Para_ModulControler_Ctr18_Tv_manualAdjust | Para_ModulControler_Ctr18_WMax | Para_ModulControler_Ctr18_WMin | Para_ModulControler_Ctr18_WStart | Para_ModulControler_Ctr18_Y_block | Para_ModulControler_Ctr18_YMax | Para_ModulControler_Ctr18_YMin | Para_ModulControler_Ctr19_DComp | Para_ModulControler_Ctr19_deadband | Para_ModulControler_Ctr19_dW_down | Para_ModulControler_Ctr19_dW_up | Para_ModulControler_Ctr19_dY_max | Para_ModulControler_Ctr19_IComp | Para_ModulControler_Ctr19_Kp_manualAdjust | Para_ModulControler_Ctr19_nvert | Para_ModulControler_Ctr19_PComp | Para_ModulControler_Ctr19_t_min_pulse_down | Para_ModulControler_Ctr19_t_min_pulse_up | Para_ModulControler_Ctr19_t_period_down | Para_ModulControler_Ctr19_t_period_up | Para_ModulControler_Ctr19_Tn_manualAdjust | Para_ModulControler_Ctr19_Tv_manualAdjust | Para_ModulControler_Ctr19_WMax | Para_ModulControler_Ctr19_WMin | Para_ModulControler_Ctr19_WStart | Para_ModulControler_Ctr19_Y_block | Para_ModulControler_Ctr19_YMax | Para_ModulControler_Ctr19_YMin | Para_ModulControler_Ctr1_DComp | Para_ModulControler_Ctr1_deadband | Para_ModulControler_Ctr1_dY_max | Para_ModulControler_Ctr1_IComp | Para_ModulControler_Ctr1_Kp_manualAdjust | Para_ModulControler_Ctr1_nvert | Para_ModulControler_Ctr1_PComp | Para_ModulControler_Ctr1_ScaleMax | Para_ModulControler_Ctr1_ScaleMin | Para_ModulControler_Ctr1_t_min_pulse_down | Para_ModulControler_Ctr1_t_min_pulse_up | Para_ModulControler_Ctr1_t_period_down | Para_ModulControler_Ctr1_t_period_up | Para_ModulControler_Ctr1_Tn_manualAdjust | Para_ModulControler_Ctr1_Tv_manualAdjust | Para_ModulControler_Ctr1_WMax | Para_ModulControler_Ctr1_WMin | Para_ModulControler_Ctr1_WRampNeg | Para_ModulControler_Ctr1_WRampPos | Para_ModulControler_Ctr1_WStart | Para_ModulControler_Ctr1_Y_block | Para_ModulControler_Ctr1_YMax | Para_ModulControler_Ctr1_YMin | Para_ModulControler_Ctr20_DComp | Para_ModulControler_Ctr20_deadband | Para_ModulControler_Ctr20_dW_down | Para_ModulControler_Ctr20_dW_up | Para_ModulControler_Ctr20_dY_max | Para_ModulControler_Ctr20_IComp | Para_ModulControler_Ctr20_Kp_manualAdjust | Para_ModulControler_Ctr20_nvert | Para_ModulControler_Ctr20_PComp | Para_ModulControler_Ctr20_t_min_pulse_down | Para_ModulControler_Ctr20_t_min_pulse_up | Para_ModulControler_Ctr20_t_period_down | Para_ModulControler_Ctr20_t_period_up | Para_ModulControler_Ctr20_Tn_manualAdjust | Para_ModulControler_Ctr20_Tv_manualAdjust | Para_ModulControler_Ctr20_WMax | Para_ModulControler_Ctr20_WMin | Para_ModulControler_Ctr20_WStart | Para_ModulControler_Ctr20_Y_block | Para_ModulControler_Ctr20_YMax | Para_ModulControler_Ctr20_YMin | Para_ModulControler_Ctr21_DComp | Para_ModulControler_Ctr21_deadband | Para_ModulControler_Ctr21_dW_down | Para_ModulControler_Ctr21_dW_up | Para_ModulControler_Ctr21_dY_max | Para_ModulControler_Ctr21_IComp | Para_ModulControler_Ctr21_Kp_manualAdjust | Para_ModulControler_Ctr21_nvert | Para_ModulControler_Ctr21_PComp | Para_ModulControler_Ctr21_t_min_pulse_down | Para_ModulControler_Ctr21_t_min_pulse_up | Para_ModulControler_Ctr21_t_period_down | Para_ModulControler_Ctr21_t_period_up | Para_ModulControler_Ctr21_Tn_manualAdjust | Para_ModulControler_Ctr21_Tv_manualAdjust | Para_ModulControler_Ctr21_WMax | Para_ModulControler_Ctr21_WMin | Para_ModulControler_Ctr21_WStart | Para_ModulControler_Ctr21_Y_block | Para_ModulControler_Ctr21_YMax | Para_ModulControler_Ctr21_YMin | Para_ModulControler_Ctr22_DComp | Para_ModulControler_Ctr22_deadband | Para_ModulControler_Ctr22_dW_down | Para_ModulControler_Ctr22_dW_up | Para_ModulControler_Ctr22_dY_max | Para_ModulControler_Ctr22_IComp | Para_ModulControler_Ctr22_Kp_manualAdjust | Para_ModulControler_Ctr22_nvert | Para_ModulControler_Ctr22_PComp | Para_ModulControler_Ctr22_t_min_pulse_down | Para_ModulControler_Ctr22_t_min_pulse_up | Para_ModulControler_Ctr22_t_period_down | Para_ModulControler_Ctr22_t_period_up | Para_ModulControler_Ctr22_Tn_manualAdjust | Para_ModulControler_Ctr22_Tv_manualAdjust | Para_ModulControler_Ctr22_WMax | Para_ModulControler_Ctr22_WMin | Para_ModulControler_Ctr22_WStart | Para_ModulControler_Ctr22_Y_block | Para_ModulControler_Ctr22_YMax | Para_ModulControler_Ctr22_YMin | Para_ModulControler_Ctr23_DComp | Para_ModulControler_Ctr23_deadband | Para_ModulControler_Ctr23_dW_down | Para_ModulControler_Ctr23_dW_up | Para_ModulControler_Ctr23_dY_max | Para_ModulControler_Ctr23_IComp | Para_ModulControler_Ctr23_Kp_manualAdjust | Para_ModulControler_Ctr23_nvert | Para_ModulControler_Ctr23_PComp | Para_ModulControler_Ctr23_t_min_pulse_down | Para_ModulControler_Ctr23_t_min_pulse_up | Para_ModulControler_Ctr23_t_period_down | Para_ModulControler_Ctr23_t_period_up | Para_ModulControler_Ctr23_Tn_manualAdjust | Para_ModulControler_Ctr23_Tv_manualAdjust | Para_ModulControler_Ctr23_WMax | Para_ModulControler_Ctr23_WMin | Para_ModulControler_Ctr23_WStart | Para_ModulControler_Ctr23_Y_block | Para_ModulControler_Ctr23_YMax | Para_ModulControler_Ctr23_YMin | Para_ModulControler_Ctr24_DComp | Para_ModulControler_Ctr24_deadband | Para_ModulControler_Ctr24_dW_down | Para_ModulControler_Ctr24_dW_up | Para_ModulControler_Ctr24_dY_max | Para_ModulControler_Ctr24_IComp | Para_ModulControler_Ctr24_Kp_manualAdjust | Para_ModulControler_Ctr24_nvert | Para_ModulControler_Ctr24_PComp | Para_ModulControler_Ctr24_t_min_pulse_down | Para_ModulControler_Ctr24_t_min_pulse_up | Para_ModulControler_Ctr24_t_period_down | Para_ModulControler_Ctr24_t_period_up | Para_ModulControler_Ctr24_Tn_manualAdjust | Para_ModulControler_Ctr24_Tv_manualAdjust | Para_ModulControler_Ctr24_WMax | Para_ModulControler_Ctr24_WMin | Para_ModulControler_Ctr24_WStart | Para_ModulControler_Ctr24_Y_block | Para_ModulControler_Ctr24_YMax | Para_ModulControler_Ctr24_YMin | Para_ModulControler_Ctr25_DComp | Para_ModulControler_Ctr25_deadband | Para_ModulControler_Ctr25_dW_down | Para_ModulControler_Ctr25_dW_up | Para_ModulControler_Ctr25_dY_max | Para_ModulControler_Ctr25_IComp | Para_ModulControler_Ctr25_Kp_manualAdjust | Para_ModulControler_Ctr25_nvert | Para_ModulControler_Ctr25_PComp | Para_ModulControler_Ctr25_t_min_pulse_down | Para_ModulControler_Ctr25_t_min_pulse_up | Para_ModulControler_Ctr25_t_period_down | Para_ModulControler_Ctr25_t_period_up | Para_ModulControler_Ctr25_Tn_manualAdjust | Para_ModulControler_Ctr25_Tv_manualAdjust | Para_ModulControler_Ctr25_WMax | Para_ModulControler_Ctr25_WMin | Para_ModulControler_Ctr25_WStart | Para_ModulControler_Ctr25_Y_block | Para_ModulControler_Ctr25_YMax | Para_ModulControler_Ctr25_YMin | Para_ModulControler_Ctr26_DComp | Para_ModulControler_Ctr26_deadband | Para_ModulControler_Ctr26_dW_down | Para_ModulControler_Ctr26_dW_up | Para_ModulControler_Ctr26_dY_max | Para_ModulControler_Ctr26_IComp | Para_ModulControler_Ctr26_Kp_manualAdjust | Para_ModulControler_Ctr26_nvert | Para_ModulControler_Ctr26_PComp | Para_ModulControler_Ctr26_t_min_pulse_down | Para_ModulControler_Ctr26_t_min_pulse_up | Para_ModulControler_Ctr26_t_period_down | Para_ModulControler_Ctr26_t_period_up | Para_ModulControler_Ctr26_Tn_manualAdjust | Para_ModulControler_Ctr26_Tv_manualAdjust | Para_ModulControler_Ctr26_WMax | Para_ModulControler_Ctr26_WMin | Para_ModulControler_Ctr26_WStart | Para_ModulControler_Ctr26_Y_block | Para_ModulControler_Ctr26_YMax | Para_ModulControler_Ctr26_YMin | Para_ModulControler_Ctr27_DComp | Para_ModulControler_Ctr27_deadband | Para_ModulControler_Ctr27_dW_down | Para_ModulControler_Ctr27_dW_up | Para_ModulControler_Ctr27_dY_max | Para_ModulControler_Ctr27_IComp | Para_ModulControler_Ctr27_Kp_manualAdjust | Para_ModulControler_Ctr27_nvert | Para_ModulControler_Ctr27_PComp | Para_ModulControler_Ctr27_t_min_pulse_down | Para_ModulControler_Ctr27_t_min_pulse_up | Para_ModulControler_Ctr27_t_period_down | Para_ModulControler_Ctr27_t_period_up | Para_ModulControler_Ctr27_Tn_manualAdjust | Para_ModulControler_Ctr27_Tv_manualAdjust | Para_ModulControler_Ctr27_WMax | Para_ModulControler_Ctr27_WMin | Para_ModulControler_Ctr27_WStart | Para_ModulControler_Ctr27_Y_block | Para_ModulControler_Ctr27_YMax | Para_ModulControler_Ctr27_YMin | Para_ModulControler_Ctr28_DComp | Para_ModulControler_Ctr28_deadband | Para_ModulControler_Ctr28_dW_down | Para_ModulControler_Ctr28_dW_up | Para_ModulControler_Ctr28_dY_max | Para_ModulControler_Ctr28_IComp | Para_ModulControler_Ctr28_Kp_manualAdjust | Para_ModulControler_Ctr28_nvert | Para_ModulControler_Ctr28_PComp | Para_ModulControler_Ctr28_t_min_pulse_down | Para_ModulControler_Ctr28_t_min_pulse_up | Para_ModulControler_Ctr28_t_period_down | Para_ModulControler_Ctr28_t_period_up | Para_ModulControler_Ctr28_Tn_manualAdjust | Para_ModulControler_Ctr28_Tv_manualAdjust | Para_ModulControler_Ctr28_WMax | Para_ModulControler_Ctr28_WMin | Para_ModulControler_Ctr28_WStart | Para_ModulControler_Ctr28_Y_block | Para_ModulControler_Ctr28_YMax | Para_ModulControler_Ctr28_YMin | Para_ModulControler_Ctr29_DComp | Para_ModulControler_Ctr29_deadband | Para_ModulControler_Ctr29_dW_down | Para_ModulControler_Ctr29_dW_up | Para_ModulControler_Ctr29_dY_max | Para_ModulControler_Ctr29_IComp | Para_ModulControler_Ctr29_Kp_manualAdjust | Para_ModulControler_Ctr29_nvert | Para_ModulControler_Ctr29_PComp | Para_ModulControler_Ctr29_t_min_pulse_down | Para_ModulControler_Ctr29_t_min_pulse_up | Para_ModulControler_Ctr29_t_period_down | Para_ModulControler_Ctr29_t_period_up | Para_ModulControler_Ctr29_Tn_manualAdjust | Para_ModulControler_Ctr29_Tv_manualAdjust | Para_ModulControler_Ctr29_WMax | Para_ModulControler_Ctr29_WMin | Para_ModulControler_Ctr29_WStart | Para_ModulControler_Ctr29_Y_block | Para_ModulControler_Ctr29_YMax | Para_ModulControler_Ctr29_YMin | Para_ModulControler_Ctr2_DComp | Para_ModulControler_Ctr2_deadband | Para_ModulControler_Ctr2_dY_max | Para_ModulControler_Ctr2_IComp | Para_ModulControler_Ctr2_Kp_manualAdjust | Para_ModulControler_Ctr2_nvert | Para_ModulControler_Ctr2_PComp | Para_ModulControler_Ctr2_ScaleMax | Para_ModulControler_Ctr2_ScaleMin | Para_ModulControler_Ctr2_t_min_pulse_down | Para_ModulControler_Ctr2_t_min_pulse_up | Para_ModulControler_Ctr2_t_period_down | Para_ModulControler_Ctr2_t_period_up | Para_ModulControler_Ctr2_Tn_manualAdjust | Para_ModulControler_Ctr2_Tv_manualAdjust | Para_ModulControler_Ctr2_WMax | Para_ModulControler_Ctr2_WMin | Para_ModulControler_Ctr2_WRampNeg | Para_ModulControler_Ctr2_WRampPos | Para_ModulControler_Ctr2_WStart | Para_ModulControler_Ctr2_Y_block | Para_ModulControler_Ctr2_YMax | Para_ModulControler_Ctr2_YMin | Para_ModulControler_Ctr30_DComp | Para_ModulControler_Ctr30_deadband | Para_ModulControler_Ctr30_dW_down | Para_ModulControler_Ctr30_dW_up | Para_ModulControler_Ctr30_dY_max | Para_ModulControler_Ctr30_IComp | Para_ModulControler_Ctr30_Kp_manualAdjust | Para_ModulControler_Ctr30_nvert | Para_ModulControler_Ctr30_PComp | Para_ModulControler_Ctr30_t_min_pulse_down | Para_ModulControler_Ctr30_t_min_pulse_up | Para_ModulControler_Ctr30_t_period_down | Para_ModulControler_Ctr30_t_period_up | Para_ModulControler_Ctr30_Tn_manualAdjust | Para_ModulControler_Ctr30_Tv_manualAdjust | Para_ModulControler_Ctr30_WMax | Para_ModulControler_Ctr30_WMin | Para_ModulControler_Ctr30_WStart | Para_ModulControler_Ctr30_Y_block | Para_ModulControler_Ctr30_YMax | Para_ModulControler_Ctr30_YMin | Para_ModulControler_Ctr31_DComp | Para_ModulControler_Ctr31_deadband | Para_ModulControler_Ctr31_dW_down | Para_ModulControler_Ctr31_dW_up | Para_ModulControler_Ctr31_dY_max | Para_ModulControler_Ctr31_IComp | Para_ModulControler_Ctr31_Kp_manualAdjust | Para_ModulControler_Ctr31_nvert | Para_ModulControler_Ctr31_PComp | Para_ModulControler_Ctr31_t_min_pulse_down | Para_ModulControler_Ctr31_t_min_pulse_up | Para_ModulControler_Ctr31_t_period_down | Para_ModulControler_Ctr31_t_period_up | Para_ModulControler_Ctr31_Tn_manualAdjust | Para_ModulControler_Ctr31_Tv_manualAdjust | Para_ModulControler_Ctr31_WMax | Para_ModulControler_Ctr31_WMin | Para_ModulControler_Ctr31_WStart | Para_ModulControler_Ctr31_Y_block | Para_ModulControler_Ctr31_YMax | Para_ModulControler_Ctr31_YMin | Para_ModulControler_Ctr32_Ctr_Mns_AnaIn_Setp_Enable | Para_ModulControler_Ctr32_Ctr_Mns_Setp_ScalMax | Para_ModulControler_Ctr32_Ctr_Mns_Setp_ScalMin | Para_ModulControler_Ctr32_Ctr_Mns_Setp_Set4mA | Para_ModulControler_Ctr32_DComp | Para_ModulControler_Ctr32_deadband | Para_ModulControler_Ctr32_dW_down | Para_ModulControler_Ctr32_dW_up | Para_ModulControler_Ctr32_dY_max | Para_ModulControler_Ctr32_IComp | Para_ModulControler_Ctr32_Kp_manualAdjust | Para_ModulControler_Ctr32_Limit_DemGenerate_Lim_Off | Para_ModulControler_Ctr32_Limit_DemGenerate_Lim_On | Para_ModulControler_Ctr32_Limit_LimOnOff_aktiv | Para_ModulControler_Ctr32_Limit_MainsExport_max | Para_ModulControler_Ctr32_Limit_MainsExport_max_trip | Para_ModulControler_Ctr32_Limit_MainsImport_max | Para_ModulControler_Ctr32_Limit_MainsImport_max_trip | Para_ModulControler_Ctr32_Limit_Time_Dem_Off_delay | Para_ModulControler_Ctr32_Limit_Time_Dem_On_delay | Para_ModulControler_Ctr32_nvert | Para_ModulControler_Ctr32_P_Mns_AnaIn_ScalMax | Para_ModulControler_Ctr32_P_Mns_AnaIn_ScalMin | Para_ModulControler_Ctr32_P_Mns_AnaIn_Set4mA | Para_ModulControler_Ctr32_P_Mns_MMU_Enable | Para_ModulControler_Ctr32_PComp | Para_ModulControler_Ctr32_t_min_pulse_down | Para_ModulControler_Ctr32_t_min_pulse_up | Para_ModulControler_Ctr32_t_period_down | Para_ModulControler_Ctr32_t_period_up | Para_ModulControler_Ctr32_Tn_manualAdjust | Para_ModulControler_Ctr32_Tv_manualAdjust | Para_ModulControler_Ctr32_WMax | Para_ModulControler_Ctr32_WMin | Para_ModulControler_Ctr32_WStart | Para_ModulControler_Ctr32_Y_block | Para_ModulControler_Ctr32_YMax | Para_ModulControler_Ctr32_YMin | Para_ModulControler_Ctr3_DComp | Para_ModulControler_Ctr3_deadband | Para_ModulControler_Ctr3_dY_max | Para_ModulControler_Ctr3_IComp | Para_ModulControler_Ctr3_Kp_manualAdjust | Para_ModulControler_Ctr3_nvert | Para_ModulControler_Ctr3_PComp | Para_ModulControler_Ctr3_ScaleMax | Para_ModulControler_Ctr3_ScaleMin | Para_ModulControler_Ctr3_t_min_pulse_down | Para_ModulControler_Ctr3_t_min_pulse_up | Para_ModulControler_Ctr3_t_period_down | Para_ModulControler_Ctr3_t_period_up | Para_ModulControler_Ctr3_Tn_manualAdjust | Para_ModulControler_Ctr3_Tv_manualAdjust | Para_ModulControler_Ctr3_WMax | Para_ModulControler_Ctr3_WMin | Para_ModulControler_Ctr3_WRampNeg | Para_ModulControler_Ctr3_WRampPos | Para_ModulControler_Ctr3_WStart | Para_ModulControler_Ctr3_Y_block | Para_ModulControler_Ctr3_YMax | Para_ModulControler_Ctr3_YMin | Para_ModulControler_Ctr4_DComp | Para_ModulControler_Ctr4_deadband | Para_ModulControler_Ctr4_dY_max | Para_ModulControler_Ctr4_IComp | Para_ModulControler_Ctr4_Kp_manualAdjust | Para_ModulControler_Ctr4_nvert | Para_ModulControler_Ctr4_PComp | Para_ModulControler_Ctr4_ScaleMax | Para_ModulControler_Ctr4_ScaleMin | Para_ModulControler_Ctr4_t_min_pulse_down | Para_ModulControler_Ctr4_t_min_pulse_up | Para_ModulControler_Ctr4_t_period_down | Para_ModulControler_Ctr4_t_period_up | Para_ModulControler_Ctr4_Tn_manualAdjust | Para_ModulControler_Ctr4_Tv_manualAdjust | Para_ModulControler_Ctr4_WMax | Para_ModulControler_Ctr4_WMin | Para_ModulControler_Ctr4_WRampNeg | Para_ModulControler_Ctr4_WRampPos | Para_ModulControler_Ctr4_WStart | Para_ModulControler_Ctr4_Y_block | Para_ModulControler_Ctr4_YMax | Para_ModulControler_Ctr4_YMin | Para_ModulControler_Ctr5_DComp | Para_ModulControler_Ctr5_deadband | Para_ModulControler_Ctr5_dY_max | Para_ModulControler_Ctr5_IComp | Para_ModulControler_Ctr5_Kp_manualAdjust | Para_ModulControler_Ctr5_nvert | Para_ModulControler_Ctr5_PComp | Para_ModulControler_Ctr5_ScaleMax | Para_ModulControler_Ctr5_ScaleMin | Para_ModulControler_Ctr5_t_min_pulse_down | Para_ModulControler_Ctr5_t_min_pulse_up | Para_ModulControler_Ctr5_t_period_down | Para_ModulControler_Ctr5_t_period_up | Para_ModulControler_Ctr5_Tn_manualAdjust | Para_ModulControler_Ctr5_Tv_manualAdjust | Para_ModulControler_Ctr5_WMax | Para_ModulControler_Ctr5_WMin | Para_ModulControler_Ctr5_WRampNeg | Para_ModulControler_Ctr5_WRampPos | Para_ModulControler_Ctr5_WStart | Para_ModulControler_Ctr5_Y_block | Para_ModulControler_Ctr5_YMax | Para_ModulControler_Ctr5_YMin | Para_ModulControler_Ctr6_DComp | Para_ModulControler_Ctr6_deadband | Para_ModulControler_Ctr6_dY_max | Para_ModulControler_Ctr6_IComp | Para_ModulControler_Ctr6_Kp_manualAdjust | Para_ModulControler_Ctr6_nvert | Para_ModulControler_Ctr6_PComp | Para_ModulControler_Ctr6_ScaleMax | Para_ModulControler_Ctr6_ScaleMin | Para_ModulControler_Ctr6_t_min_pulse_down | Para_ModulControler_Ctr6_t_min_pulse_up | Para_ModulControler_Ctr6_t_period_down | Para_ModulControler_Ctr6_t_period_up | Para_ModulControler_Ctr6_Tn_manualAdjust | Para_ModulControler_Ctr6_Tv_manualAdjust | Para_ModulControler_Ctr6_WMax | Para_ModulControler_Ctr6_WMin | Para_ModulControler_Ctr6_WRampNeg | Para_ModulControler_Ctr6_WRampPos | Para_ModulControler_Ctr6_WStart | Para_ModulControler_Ctr6_Y_block | Para_ModulControler_Ctr6_YMax | Para_ModulControler_Ctr6_YMin | Para_ModulControler_Ctr7_DComp | Para_ModulControler_Ctr7_deadband | Para_ModulControler_Ctr7_dY_max | Para_ModulControler_Ctr7_IComp | Para_ModulControler_Ctr7_Kp_manualAdjust | Para_ModulControler_Ctr7_nvert | Para_ModulControler_Ctr7_PComp | Para_ModulControler_Ctr7_ScaleMax | Para_ModulControler_Ctr7_ScaleMin | Para_ModulControler_Ctr7_t_min_pulse_down | Para_ModulControler_Ctr7_t_min_pulse_up | Para_ModulControler_Ctr7_t_period_down | Para_ModulControler_Ctr7_t_period_up | Para_ModulControler_Ctr7_Tn_manualAdjust | Para_ModulControler_Ctr7_Tv_manualAdjust | Para_ModulControler_Ctr7_WMax | Para_ModulControler_Ctr7_WMin | Para_ModulControler_Ctr7_WRampNeg | Para_ModulControler_Ctr7_WRampPos | Para_ModulControler_Ctr7_WStart | Para_ModulControler_Ctr7_Y_block | Para_ModulControler_Ctr7_YMax | Para_ModulControler_Ctr7_YMin | Para_ModulControler_Ctr8_DComp | Para_ModulControler_Ctr8_deadband | Para_ModulControler_Ctr8_dY_max | Para_ModulControler_Ctr8_IComp | Para_ModulControler_Ctr8_Kp_manualAdjust | Para_ModulControler_Ctr8_nvert | Para_ModulControler_Ctr8_PComp | Para_ModulControler_Ctr8_ScaleMax | Para_ModulControler_Ctr8_ScaleMin | Para_ModulControler_Ctr8_t_min_pulse_down | Para_ModulControler_Ctr8_t_min_pulse_up | Para_ModulControler_Ctr8_t_period_down | Para_ModulControler_Ctr8_t_period_up | Para_ModulControler_Ctr8_Tn_manualAdjust | Para_ModulControler_Ctr8_Tv_manualAdjust | Para_ModulControler_Ctr8_WMax | Para_ModulControler_Ctr8_WMin | Para_ModulControler_Ctr8_WRampNeg | Para_ModulControler_Ctr8_WRampPos | Para_ModulControler_Ctr8_WStart | Para_ModulControler_Ctr8_Y_block | Para_ModulControler_Ctr8_YMax | Para_ModulControler_Ctr8_YMin | Para_ModulControler_Ctr_CC | Para_ModulControler_Ctr_CDSu | Para_ModulControler_Ctr_ChCHP | Para_ModulControler_Ctr_CircLou | Para_ModulControler_Ctr_Cust1 | Para_ModulControler_Ctr_Cust2 | Para_ModulControler_Ctr_Cust3 | Para_ModulControler_Ctr_Cust4 | Para_ModulControler_Ctr_Cust5 | Para_ModulControler_Ctr_Cust6 | Para_ModulControler_Ctr_Cust7 | Para_ModulControler_Ctr_Cust8 | Para_ModulControler_Ctr_ECW | Para_ModulControler_Ctr_EOVal_Active | Para_ModulControler_Ctr_EOVal_LT_Active | Para_ModulControler_Ctr_GC | Para_ModulControler_Ctr_InlLou | Para_ModulControler_Ctr_Mns_Enable | Para_ModulControler_Ctr_OutlLou_RDP | Para_ModulControler_Ctr_OutlLou_RT | Para_ModulControler_Ctr_OutlVE_RDP | Para_ModulControler_Ctr_OutlVE_RT | Para_ModulControler_Ctr_SCR_Flow | Para_ModulControler_Ctr_SCR_NOx | Para_ModulControler_CtrGenPF_Active | Para_ModulControler_CtrThR_Heater_Active | Para_Monic_ActVoltAvgMax | Para_Monic_ActVoltDif | Para_Monic_ActVoltMax | Para_Monic_ActVoltMin | Para_Monic_LimitActive | Para_Monic_LimitActiveHys | Para_Monic_TriggerVolt | Para_Monic_VoltAvgMax | Para_Monic_VoltAvgMaxDelay | Para_Monic_VoltDif | Para_Monic_VoltDifDelay | Para_Monic_VoltMax | Para_Monic_VoltMaxDelay | Para_Monic_VoltMin | Para_Monic_VoltMinDelay | Para_PBC_AI_NEx | Para_PBC_AvgPMaxLimit | Para_PBC_LimitPressMax | Para_PBC_LimitPressMaxAvg | Para_PBC_NumbCycBelowPressMax | Para_PBC_NumbCycBelowPressMean | Para_PBC_NumbCycExcPressMax | Para_PBC_NumbCycExcPressMean | Para_PBC_NumbMisfCycMin | Para_PBC_PowerRed | Para_PBC_PressMeanDevMisf | Para_PBC_PressMeanDevNeg | Para_PBC_PressMeanDevPos | Para_PBC_Sensitivity | Para_PI_20mA | Para_PI_4mA | Para_PI_ActCloseDetection | Para_PI_FailRateValveOpen | Para_PI_FailRateValveOpenTP | Para_PI_LambdaFeedFwdCtr_Gas1_OffsetStartLambda | Para_PI_LambdaFeedFwdCtr_Gas2_OffsetStartLambda | Para_PI_LambdaFeedFwdCtr_Gas3_OffsetStartLambda | Para_PI_LambdaFeedFwdCtr_Gas4_OffsetStartLambda | Para_PI_Limit_GasRailPressDiffMax | Para_PI_Limit_GasRailPressDiffMin | Para_PI_Limit_GasRailPressMax | Para_PI_Limit_GasRailPressMin | Para_PI_Limit_GasRailTempMax | Para_PI_Limit_GasRailTempMin | Para_PI_ReleaseBal | Para_PI_ValveType | Para_Power_Actual_Curr1 | Para_Power_Actual_Curr2 | Para_Power_Actual_Point1 | Para_Power_Actual_Point2 | Para_Power_Ctr_TbDComp | Para_Power_Ctr_TbIComp | Para_Power_Ctr_TbPComp | Para_Power_Ctr_TbYMax | Para_Power_Ctr_TbYMin | Para_Power_Ctr_TrDComp | Para_Power_Ctr_TrIComp | Para_Power_Ctr_TrPComp | Para_Power_Ctr_TrYMax | Para_Power_Ctr_TrYMin | Para_Power_ExtRed_Curr1 | Para_Power_ExtRed_Curr2 | Para_Power_ExtRed_Point1 | Para_Power_ExtRed_Point2 | Para_Power_ExtSet_ConstSetPoint1 | Para_Power_ExtSet_ConstSetPoint2 | Para_Power_ExtSet_ConstSetPoint3 | Para_Power_ExtSet_ConstSetPoint4 | Para_Power_ExtSet_ConstSetPoint5 | Para_Power_ExtSet_Curr1 | Para_Power_ExtSet_Curr2 | Para_Power_ExtSet_Point1 | Para_Power_ExtSet_Point2 | Para_Power_IntakeAirRed_RedFac | Para_Power_IntakeAirRed_RedFac2 | Para_Power_IntakeAirRed_Start | Para_Power_IntakeAirRed_Start2 | Para_Power_IPAdap_ActITPTbAdap | Para_Power_IPAdap_IPRedTBGas1 | Para_Power_IPAdap_IPRedTBGas2 | Para_Power_IPAdap_IPRedTBGas3 | Para_Power_IPAdap_IPRedTBGas4 | Para_Power_IPAdap_ITPTbPosAdap | Para_Power_Limit_Backfire | Para_Power_Limit_BackfireHys | Para_Power_Limit_GasChange | Para_Power_Limit_GasChangeHys | Para_Power_Limit_Perc40Pnom | Para_Power_Limit_Perc40PnomHys | Para_Power_Limit_PowerDiff | Para_Power_Limit_PowerDiffDelay | Para_Power_Limit_PowerDiffRated | Para_Power_Limit_PowerDiffRatedDelay | Para_Power_Limit_PowerLimit1 | Para_Power_Limit_PowerLimit1Hys | Para_Power_Limit_PowerRetLimit | Para_Power_Limit_PowerRetLimitHys | Para_Power_Limit_SigLoss | Para_Power_Limit_SigLossHys | Para_Power_Limit_SigOverload | Para_Power_Limit_SigOverloadHys | Para_Power_Limit_SigTrip | Para_Power_Limit_SwitchCosPhi | Para_Power_Limit_SwitchCosPhiHys | Para_Power_Nominal_Power1 | Para_Power_Nominal_Power2 | Para_Power_Nominal_Power3 | Para_Power_Nominal_Power4 | Para_Power_Nominal_PowerMin | Para_Power_Ramp_DownG1 | Para_Power_Ramp_DownG2 | Para_Power_Ramp_DownG3 | Para_Power_Ramp_DownG4 | Para_Power_Ramp_UpG1 | Para_Power_Ramp_UpG2 | Para_Power_Ramp_UpG3 | Para_Power_Ramp_UpG4 | Para_Power_RedChargeTemp_Active | Para_Power_RedChargeTemp_Fix | Para_Power_RedCoolWatTemp_Rate | Para_Power_RedCoolWatTemp_Start | Para_Power_RedGenerator_ActPowRedFreq | Para_Power_RedGenerator_ActPowRedVolt | Para_Power_RedGenerator_FreqHighStart | Para_Power_RedGenerator_FreqHighStop | Para_Power_RedGenerator_FreqLowStart | Para_Power_RedGenerator_FreqLowStop | Para_Power_RedGenerator_FreqReturn | Para_Power_RedGenerator_PowerMinFreqHigh | Para_Power_RedGenerator_PowerMinFreqLow | Para_Power_RedGenerator_PowerMinVoltHigh | Para_Power_RedGenerator_PowerMinVoltLow | Para_Power_RedGenerator_TempPowRed | Para_Power_RedGenerator_VoltHighStart | Para_Power_RedGenerator_VoltHighStop | Para_Power_RedGenerator_VoltLowStart | Para_Power_RedGenerator_VoltLowStop | Para_Power_RedGenerator_WindTempHighStart | Para_Power_RedHumidity_ActPred | Para_Power_RedHumidity_PRedLimit | Para_Power_RedOilTemp_Rate | Para_Power_RedOilTemp_Start | Para_Power_RedPreChambGasTrain_ActPowerRed | Para_Power_RedPreChambGasTrain_Rate | Para_Power_RedPreChambGasTrain_Start | Para_Power_RedRetWat_PowRedActive | Para_Power_RedRetWat_Rate | Para_Power_RedRetWat_Start | Para_Power_RedUtility_Step1 | Para_Power_RedUtility_Step2 | Para_Power_TCSpeedRed_RedValue | Para_Power_TMixRed_DeltaPG1 | Para_Power_TMixRed_DeltaPG2 | Para_Power_TMixRed_DeltaPG3 | Para_Power_TMixRed_DeltaPG4 | Para_Power_TMixRed_TempRedG1 | Para_Power_TMixRed_TempRedG2 | Para_Power_TMixRed_TempRedG3 | Para_Power_TMixRed_TempRedG4 | Para_Reserve_Analog_Active1 | Para_Reserve_Analog_Active10 | Para_Reserve_Analog_Active11 | Para_Reserve_Analog_Active12 | Para_Reserve_Analog_Active13 | Para_Reserve_Analog_Active14 | Para_Reserve_Analog_Active15 | Para_Reserve_Analog_Active16 | Para_Reserve_Analog_Active2 | Para_Reserve_Analog_Active3 | Para_Reserve_Analog_Active4 | Para_Reserve_Analog_Active5 | Para_Reserve_Analog_Active6 | Para_Reserve_Analog_Active7 | Para_Reserve_Analog_Active8 | Para_Reserve_Analog_Active9 | Para_Reserve_Analog_LiveZero1 | Para_Reserve_Analog_LiveZero10 | Para_Reserve_Analog_LiveZero11 | Para_Reserve_Analog_LiveZero12 | Para_Reserve_Analog_LiveZero13 | Para_Reserve_Analog_LiveZero14 | Para_Reserve_Analog_LiveZero15 | Para_Reserve_Analog_LiveZero16 | Para_Reserve_Analog_LiveZero2 | Para_Reserve_Analog_LiveZero3 | Para_Reserve_Analog_LiveZero4 | Para_Reserve_Analog_LiveZero5 | Para_Reserve_Analog_LiveZero6 | Para_Reserve_Analog_LiveZero7 | Para_Reserve_Analog_LiveZero8 | Para_Reserve_Analog_LiveZero9 | Para_Reserve_Analog_ScaleBegin1 | Para_Reserve_Analog_ScaleBegin10 | Para_Reserve_Analog_ScaleBegin11 | Para_Reserve_Analog_ScaleBegin12 | Para_Reserve_Analog_ScaleBegin13 | Para_Reserve_Analog_ScaleBegin14 | Para_Reserve_Analog_ScaleBegin15 | Para_Reserve_Analog_ScaleBegin16 | Para_Reserve_Analog_ScaleBegin2 | Para_Reserve_Analog_ScaleBegin3 | Para_Reserve_Analog_ScaleBegin4 | Para_Reserve_Analog_ScaleBegin5 | Para_Reserve_Analog_ScaleBegin6 | Para_Reserve_Analog_ScaleBegin7 | Para_Reserve_Analog_ScaleBegin8 | Para_Reserve_Analog_ScaleBegin9 | Para_Reserve_Analog_ScaleEnd1 | Para_Reserve_Analog_ScaleEnd10 | Para_Reserve_Analog_ScaleEnd11 | Para_Reserve_Analog_ScaleEnd12 | Para_Reserve_Analog_ScaleEnd13 | Para_Reserve_Analog_ScaleEnd14 | Para_Reserve_Analog_ScaleEnd15 | Para_Reserve_Analog_ScaleEnd16 | Para_Reserve_Analog_ScaleEnd2 | Para_Reserve_Analog_ScaleEnd3 | Para_Reserve_Analog_ScaleEnd4 | Para_Reserve_Analog_ScaleEnd5 | Para_Reserve_Analog_ScaleEnd6 | Para_Reserve_Analog_ScaleEnd7 | Para_Reserve_Analog_ScaleEnd8 | Para_Reserve_Analog_ScaleEnd9 | Para_Reserve_Para2_Par031 | Para_Reserve_Para2_Par032 | Para_Reserve_Para2_Par033 | Para_Reserve_Para2_Par034 | Para_Reserve_Para2_Par035 | Para_Reserve_Para2_Par036 | Para_Reserve_Para2_Par037 | Para_Reserve_Para2_Par038 | Para_Reserve_Para2_Par039 | Para_Reserve_Para2_Par040 | Para_Reserve_Para2_Par041 | Para_Reserve_Para2_Par042 | Para_Reserve_Para2_Par043 | Para_Reserve_Para2_Par044 | Para_Reserve_Para2_Par045 | Para_Reserve_Para2_Par046 | Para_Reserve_Para2_Par047 | Para_Reserve_Para2_Par048 | Para_Reserve_Para2_Par049 | Para_Reserve_Para2_Par050 | Para_Reserve_Para2_Par051 | Para_Reserve_Para2_Par052 | Para_Reserve_Para2_Par053 | Para_Reserve_Para2_Par054 | Para_Reserve_Para2_Par055 | Para_Reserve_Para2_Par056 | Para_Reserve_Para2_Par057 | Para_Reserve_Para2_Par058 | Para_Reserve_Para2_Par059 | Para_Reserve_Para2_Par060 | Para_Reserve_Para2_ParaName031 | Para_Reserve_Para2_ParaName032 | Para_Reserve_Para2_ParaName033 | Para_Reserve_Para2_ParaName034 | Para_Reserve_Para2_ParaName035 | Para_Reserve_Para2_ParaName036 | Para_Reserve_Para2_ParaName037 | Para_Reserve_Para2_ParaName038 | Para_Reserve_Para2_ParaName039 | Para_Reserve_Para2_ParaName040 | Para_Reserve_Para2_ParaName041 | Para_Reserve_Para2_ParaName042 | Para_Reserve_Para2_ParaName043 | Para_Reserve_Para2_ParaName044 | Para_Reserve_Para2_ParaName045 | Para_Reserve_Para2_ParaName046 | Para_Reserve_Para2_ParaName047 | Para_Reserve_Para2_ParaName048 | Para_Reserve_Para2_ParaName049 | Para_Reserve_Para2_ParaName050 | Para_Reserve_Para2_ParaName051 | Para_Reserve_Para2_ParaName052 | Para_Reserve_Para2_ParaName053 | Para_Reserve_Para2_ParaName054 | Para_Reserve_Para2_ParaName055 | Para_Reserve_Para2_ParaName056 | Para_Reserve_Para2_ParaName057 | Para_Reserve_Para2_ParaName058 | Para_Reserve_Para2_ParaName059 | Para_Reserve_Para2_ParaName060 | Para_Reserve_Para2_ParaNameF031 | Para_Reserve_Para2_ParaNameF032 | Para_Reserve_Para2_ParaNameF033 | Para_Reserve_Para2_ParaNameF034 | Para_Reserve_Para2_ParaNameF035 | Para_Reserve_Para2_ParaNameF036 | Para_Reserve_Para2_ParaNameF037 | Para_Reserve_Para2_ParaNameF038 | Para_Reserve_Para2_ParaNameF039 | Para_Reserve_Para2_ParaNameF040 | Para_Reserve_Para2_ParaNameF041 | Para_Reserve_Para2_ParaNameF042 | Para_Reserve_Para2_ParaNameF043 | Para_Reserve_Para2_ParaNameF044 | Para_Reserve_Para2_ParaNameF045 | Para_Reserve_Para2_ParaNameF046 | Para_Reserve_Para2_ParaNameF047 | Para_Reserve_Para2_ParaNameF048 | Para_Reserve_Para2_ParaNameF049 | Para_Reserve_Para2_ParaNameF050 | Para_Reserve_Para2_ParaNameF051 | Para_Reserve_Para2_ParaNameF052 | Para_Reserve_Para2_ParaNameF053 | Para_Reserve_Para2_ParaNameF054 | Para_Reserve_Para2_ParaNameF055 | Para_Reserve_Para2_ParaNameF056 | Para_Reserve_Para2_ParaNameF057 | Para_Reserve_Para2_ParaNameF058 | Para_Reserve_Para2_ParaNameF059 | Para_Reserve_Para2_ParaNameF060 | Para_Reserve_Para2_ParaUnit031 | Para_Reserve_Para2_ParaUnit032 | Para_Reserve_Para2_ParaUnit033 | Para_Reserve_Para2_ParaUnit034 | Para_Reserve_Para2_ParaUnit035 | Para_Reserve_Para2_ParaUnit036 | Para_Reserve_Para2_ParaUnit037 | Para_Reserve_Para2_ParaUnit038 | Para_Reserve_Para2_ParaUnit039 | Para_Reserve_Para2_ParaUnit040 | Para_Reserve_Para2_ParaUnit041 | Para_Reserve_Para2_ParaUnit042 | Para_Reserve_Para2_ParaUnit043 | Para_Reserve_Para2_ParaUnit044 | Para_Reserve_Para2_ParaUnit045 | Para_Reserve_Para2_ParaUnit046 | Para_Reserve_Para2_ParaUnit047 | Para_Reserve_Para2_ParaUnit048 | Para_Reserve_Para2_ParaUnit049 | Para_Reserve_Para2_ParaUnit050 | Para_Reserve_Para2_ParaUnit051 | Para_Reserve_Para2_ParaUnit052 | Para_Reserve_Para2_ParaUnit053 | Para_Reserve_Para2_ParaUnit054 | Para_Reserve_Para2_ParaUnit055 | Para_Reserve_Para2_ParaUnit056 | Para_Reserve_Para2_ParaUnit057 | Para_Reserve_Para2_ParaUnit058 | Para_Reserve_Para2_ParaUnit059 | Para_Reserve_Para2_ParaUnit060 | Para_Reserve_Para3_Par061 | Para_Reserve_Para3_Par062 | Para_Reserve_Para3_Par063 | Para_Reserve_Para3_Par064 | Para_Reserve_Para3_Par065 | Para_Reserve_Para3_Par066 | Para_Reserve_Para3_Par067 | Para_Reserve_Para3_Par068 | Para_Reserve_Para3_Par069 | Para_Reserve_Para3_Par070 | Para_Reserve_Para3_ParaName061 | Para_Reserve_Para3_ParaName062 | Para_Reserve_Para3_ParaName063 | Para_Reserve_Para3_ParaName064 | Para_Reserve_Para3_ParaName065 | Para_Reserve_Para3_ParaName066 | Para_Reserve_Para3_ParaName067 | Para_Reserve_Para3_ParaName068 | Para_Reserve_Para3_ParaName069 | Para_Reserve_Para3_ParaName070 | Para_Reserve_Para3_ParaNameF061 | Para_Reserve_Para3_ParaNameF062 | Para_Reserve_Para3_ParaNameF063 | Para_Reserve_Para3_ParaNameF064 | Para_Reserve_Para3_ParaNameF065 | Para_Reserve_Para3_ParaNameF066 | Para_Reserve_Para3_ParaNameF067 | Para_Reserve_Para3_ParaNameF068 | Para_Reserve_Para3_ParaNameF069 | Para_Reserve_Para3_ParaNameF070 | Para_Reserve_Para3_ParaUnit061 | Para_Reserve_Para3_ParaUnit062 | Para_Reserve_Para3_ParaUnit063 | Para_Reserve_Para3_ParaUnit064 | Para_Reserve_Para3_ParaUnit065 | Para_Reserve_Para3_ParaUnit066 | Para_Reserve_Para3_ParaUnit067 | Para_Reserve_Para3_ParaUnit068 | Para_Reserve_Para3_ParaUnit069 | Para_Reserve_Para3_ParaUnit070 | Para_Reserve_Para_Par001 | Para_Reserve_Para_Par002 | Para_Reserve_Para_Par003 | Para_Reserve_Para_Par004 | Para_Reserve_Para_Par005 | Para_Reserve_Para_Par006 | Para_Reserve_Para_Par007 | Para_Reserve_Para_Par008 | Para_Reserve_Para_Par009 | Para_Reserve_Para_Par010 | Para_Reserve_Para_Par011 | Para_Reserve_Para_Par012 | Para_Reserve_Para_Par013 | Para_Reserve_Para_Par014 | Para_Reserve_Para_Par015 | Para_Reserve_Para_Par016 | Para_Reserve_Para_Par017 | Para_Reserve_Para_Par018 | Para_Reserve_Para_Par019 | Para_Reserve_Para_Par020 | Para_Reserve_Para_Par021 | Para_Reserve_Para_Par022 | Para_Reserve_Para_Par023 | Para_Reserve_Para_Par024 | Para_Reserve_Para_Par025 | Para_Reserve_Para_Par026 | Para_Reserve_Para_Par027 | Para_Reserve_Para_Par028 | Para_Reserve_Para_Par029 | Para_Reserve_Para_Par030 | Para_Reserve_Para_ParaName001 | Para_Reserve_Para_ParaName002 | Para_Reserve_Para_ParaName003 | Para_Reserve_Para_ParaName004 | Para_Reserve_Para_ParaName005 | Para_Reserve_Para_ParaName006 | Para_Reserve_Para_ParaName007 | Para_Reserve_Para_ParaName008 | Para_Reserve_Para_ParaName009 | Para_Reserve_Para_ParaName010 | Para_Reserve_Para_ParaName011 | Para_Reserve_Para_ParaName012 | Para_Reserve_Para_ParaName013 | Para_Reserve_Para_ParaName014 | Para_Reserve_Para_ParaName015 | Para_Reserve_Para_ParaName016 | Para_Reserve_Para_ParaName017 | Para_Reserve_Para_ParaName018 | Para_Reserve_Para_ParaName019 | Para_Reserve_Para_ParaName020 | Para_Reserve_Para_ParaName021 | Para_Reserve_Para_ParaName022 | Para_Reserve_Para_ParaName023 | Para_Reserve_Para_ParaName024 | Para_Reserve_Para_ParaName025 | Para_Reserve_Para_ParaName026 | Para_Reserve_Para_ParaName027 | Para_Reserve_Para_ParaName028 | Para_Reserve_Para_ParaName029 | Para_Reserve_Para_ParaName030 | Para_Reserve_Para_ParaNameF001 | Para_Reserve_Para_ParaNameF002 | Para_Reserve_Para_ParaNameF003 | Para_Reserve_Para_ParaNameF004 | Para_Reserve_Para_ParaNameF005 | Para_Reserve_Para_ParaNameF006 | Para_Reserve_Para_ParaNameF007 | Para_Reserve_Para_ParaNameF008 | Para_Reserve_Para_ParaNameF009 | Para_Reserve_Para_ParaNameF010 | Para_Reserve_Para_ParaNameF011 | Para_Reserve_Para_ParaNameF012 | Para_Reserve_Para_ParaNameF013 | Para_Reserve_Para_ParaNameF014 | Para_Reserve_Para_ParaNameF015 | Para_Reserve_Para_ParaNameF016 | Para_Reserve_Para_ParaNameF017 | Para_Reserve_Para_ParaNameF018 | Para_Reserve_Para_ParaNameF019 | Para_Reserve_Para_ParaNameF020 | Para_Reserve_Para_ParaNameF021 | Para_Reserve_Para_ParaNameF022 | Para_Reserve_Para_ParaNameF023 | Para_Reserve_Para_ParaNameF024 | Para_Reserve_Para_ParaNameF025 | Para_Reserve_Para_ParaNameF026 | Para_Reserve_Para_ParaNameF027 | Para_Reserve_Para_ParaNameF028 | Para_Reserve_Para_ParaNameF029 | Para_Reserve_Para_ParaNameF030 | Para_Reserve_Para_ParaUnit001 | Para_Reserve_Para_ParaUnit002 | Para_Reserve_Para_ParaUnit003 | Para_Reserve_Para_ParaUnit004 | Para_Reserve_Para_ParaUnit005 | Para_Reserve_Para_ParaUnit006 | Para_Reserve_Para_ParaUnit007 | Para_Reserve_Para_ParaUnit008 | Para_Reserve_Para_ParaUnit009 | Para_Reserve_Para_ParaUnit010 | Para_Reserve_Para_ParaUnit011 | Para_Reserve_Para_ParaUnit012 | Para_Reserve_Para_ParaUnit013 | Para_Reserve_Para_ParaUnit014 | Para_Reserve_Para_ParaUnit015 | Para_Reserve_Para_ParaUnit016 | Para_Reserve_Para_ParaUnit017 | Para_Reserve_Para_ParaUnit018 | Para_Reserve_Para_ParaUnit019 | Para_Reserve_Para_ParaUnit020 | Para_Reserve_Para_ParaUnit021 | Para_Reserve_Para_ParaUnit022 | Para_Reserve_Para_ParaUnit023 | Para_Reserve_Para_ParaUnit024 | Para_Reserve_Para_ParaUnit025 | Para_Reserve_Para_ParaUnit026 | Para_Reserve_Para_ParaUnit027 | Para_Reserve_Para_ParaUnit028 | Para_Reserve_Para_ParaUnit029 | Para_Reserve_Para_ParaUnit030 | Para_SAFI_ActExhTemp | Para_SAFI_ActHighVolt | Para_SAFI_ActIgn | Para_SAFI_ActITPTolCheck | Para_SAFI_ActKnock | Para_SAFI_ActOCA | Para_SAFI_ActPBC | Para_SAFI_ActPI | Para_SAFI_ITPTol | Para_SAFI_ResetPos | Para_SpecGas_ActBackfireIMEP_P | Para_SpecGas_ActScavN2 | Para_SpecGas_BlockEngineRun | Para_SpecGas_CalValue_ActGas1_2 | Para_SpecGas_CalValue_ActMeasure | Para_SpecGas_CalValue_ActMinAlarm | Para_SpecGas_CalValue_ActMinSd | Para_SpecGas_CalValue_ActPowerRed | Para_SpecGas_CalValue_ContentGas1 | Para_SpecGas_CalValue_ContentGas2 | Para_SpecGas_CalValue_DefaultValGas1_2 | Para_SpecGas_CalValue_HalfLoad | Para_SpecGas_CalValue_HysMinAlarm | Para_SpecGas_CalValue_HysMinSD | Para_SpecGas_CalValue_LimitMinSd | Para_SpecGas_CalValue_Range20mA | Para_SpecGas_CalValue_Range4mA | Para_SpecGas_CalValue_StartPRed | Para_SpecGas_CalValue_SwitchPointMinAlarm | Para_SpecGas_CH4_ActGas1_2 | Para_SpecGas_CH4_ActMeasure | Para_SpecGas_CH4_ActMinAlarm | Para_SpecGas_CH4_ActMinSd | Para_SpecGas_CH4_ActPowerRed | Para_SpecGas_CH4_ContentGas1 | Para_SpecGas_CH4_ContentGas2 | Para_SpecGas_CH4_DefaultValGas1_2 | Para_SpecGas_CH4_HalfLoad | Para_SpecGas_CH4_HysMinAlarm | Para_SpecGas_CH4_HysMinSD | Para_SpecGas_CH4_LimitMinSd | Para_SpecGas_CH4_Range20mA | Para_SpecGas_CH4_Range4mA | Para_SpecGas_CH4_StartPRed | Para_SpecGas_CH4_SwitchPointMinAlarm | Para_SpecGas_GasPress_ActMaxAlarm | Para_SpecGas_GasPress_ActMeasure | Para_SpecGas_GasPress_ActMinAlarm | Para_SpecGas_GasPress_ActPowerRed | Para_SpecGas_GasPress_EndPRed | Para_SpecGas_GasPress_HysMaxAlarm | Para_SpecGas_GasPress_HysMinAlarm | Para_SpecGas_GasPress_LimitMaxAlarm | Para_SpecGas_GasPress_LimitMinAlarm | Para_SpecGas_GasPress_LimitMinAlarmDelay | Para_SpecGas_GasPress_Range20mA | Para_SpecGas_GasPress_Range4mA | Para_SpecGas_GasPress_StartPRed | Para_SpecGas_GasTemp_ActMeasure | Para_SpecGas_GasTemp_HysMax | Para_SpecGas_GasTemp_HysMin | Para_SpecGas_GasTemp_LimitMax | Para_SpecGas_GasTemp_LimitMin | Para_SpecGas_GasTemp_Range20mA | Para_SpecGas_GasTemp_Range4mA | Para_SpecGas_GasVol_ActMeasure | Para_SpecGas_GasVol_Range20mA | Para_SpecGas_GasVol_Range4mA | Para_SpecGas_GlowIgn_ActPredIPRedPBC | Para_SpecGas_GlowIgn_EmergShut_ActEmergShut | Para_SpecGas_GlowIgn_EmergShut_ActEmergShutPBC | Para_SpecGas_GlowIgn_EmergShut_BlockTimeNumbMax | Para_SpecGas_GlowIgn_EmergShut_CloseTimeGasValve | Para_SpecGas_GlowIgn_EmergShut_LimitContent | Para_SpecGas_GlowIgn_EmergShut_LimitDeltaCylTemp | Para_SpecGas_GlowIgn_EmergShut_LimitDevCylTempAvg | Para_SpecGas_GlowIgn_EmergShut_NumbMax | Para_SpecGas_GlowIgn_EmergShut_NumbMax30s | Para_SpecGas_GlowIgn_EmergShut_PowerActTempMon | Para_SpecGas_GlowIgn_EmergShut_SelfReset | Para_SpecGas_GlowIgn_EmergShut_TimeDurMonDeact | Para_SpecGas_GlowIgn_EmergShut_TimeNumbMax | Para_SpecGas_GlowIgn_EmergShut_TrPos | Para_SpecGas_GlowIgn_EmergShut_TrPosTimeDur | Para_SpecGas_GlowIgn_FastPowerRed_ActFastPowerRed | Para_SpecGas_GlowIgn_FastPowerRed_ActFastPowerRedPBC | Para_SpecGas_GlowIgn_FastPowerRed_Limitp2s | Para_SpecGas_GlowIgn_FastPowerRed_MaxNumb | Para_SpecGas_GlowIgn_FastPowerRed_PowerActive | Para_SpecGas_GlowIgn_FastPowerRed_PowerDiff | Para_SpecGas_GlowIgn_FastPowerRed_PowerSave | Para_SpecGas_GlowIgn_FastPowerRed_PowerSaveDur | Para_SpecGas_GlowIgn_FastPowerRed_TimeDiff | Para_SpecGas_GlowIgn_FastPowerRed_TimeDur | Para_SpecGas_GlowIgn_FastPowerRed_TrPos | Para_SpecGas_GlowIgn_ITPstep | Para_SpecGas_GlowIgn_LambdaOffset | Para_SpecGas_GlowIgnPrevent | Para_SpecGas_O2_ActMeasure | Para_SpecGas_O2_ActShutdownMax | Para_SpecGas_O2_HysMaxSd | Para_SpecGas_O2_LimitMaxSd | Para_SpecGas_O2_Range20mA | Para_SpecGas_O2_Range4mA | Para_SpecGas_SucPress_ActMeasure | Para_SpecGas_SucPress_ActPowerRed | Para_SpecGas_SucPress_EndPRed | Para_SpecGas_SucPress_HysMaxAlarm | Para_SpecGas_SucPress_HysMinAlarm | Para_SpecGas_SucPress_LimitMaxAlarm | Para_SpecGas_SucPress_LimitMinAlarm | Para_SpecGas_SucPress_Range20mA | Para_SpecGas_SucPress_Range4mA | Para_SpecGas_SucPress_StartPRed | Para_SpecGas_TwoIgnition | Para_SpecGas_TwoN2Valves | Para_Speed_Ctr_Active | Para_Speed_Ctr_ActStartCompBypassOpen | Para_Speed_Ctr_TrDComp | Para_Speed_Ctr_TrIComp | Para_Speed_Ctr_TrPComp | Para_Speed_Ctr_TrYMax | Para_Speed_Ctr_TrYMin | Para_Speed_ExtSet_Curr1 | Para_Speed_ExtSet_Curr2 | Para_Speed_ExtSet_Point1 | Para_Speed_ExtSet_Point2 | Para_Speed_Limit_Gr1495 | Para_Speed_Limit_Gr1495Hys | Para_Speed_Limit_Limit1 | Para_Speed_Limit_Limit1Hys | Para_Speed_Limit_OverSpeed | Para_Speed_Limit_OverSpeedHys | Para_Speed_Limit_RunUp | Para_Speed_Limit_RunUpHys | Para_Speed_Limit_Sm1505 | Para_Speed_Limit_Sm1505Hys | Para_Speed_Limit_Start | Para_Speed_Limit_StartHys | Para_Speed_Limit_StartSpeedMon | Para_Speed_Limit_StartSpeedMonHys | N nom | Para_Speed_Ramp_Ramp | Para_System_HA_Pt100InputFilter | Para_System_IPC_T_IPC_Board_LimHi | Para_System_IPC_T_IPC_CFast_LimHi | Para_System_IPC_T_IPC_Chipset_LimHi | Para_System_IPC_T_IPC_CPU_LimHi | Para_System_IPC_T_IPC_PS_LimHi | Para_Tecjet_Gas1_AirDemandMin | Para_Tecjet_Gas1_CalorificValue | Para_Tecjet_Gas1_StandGasDens | Para_Tecjet_Gas1_TecJetOffsetIsland | Para_Tecjet_Gas1_TecJetOffsetNet | Para_Tecjet_Gas1_TecJetPoint1 | Para_Tecjet_Gas1_TecJetPoint2 | Para_Tecjet_Gas1_TempOilPoint1 | Para_Tecjet_Gas1_TempOilPoint2 | Para_Tecjet_Gas2_AirDemandMin | Para_Tecjet_Gas2_CalorificValue | Para_Tecjet_Gas2_StandGasDens | Para_Tecjet_Gas2_TecJetOffsetIsland | Para_Tecjet_Gas2_TecJetOffsetNet | Para_Tecjet_Gas2_TecJetPoint1 | Para_Tecjet_Gas2_TecJetPoint2 | Para_Tecjet_Gas2_TempOilPoint1 | Para_Tecjet_Gas2_TempOilPoint2 | Para_Tecjet_Gas3_AirDemandMin | Para_Tecjet_Gas3_CalorificValue | Para_Tecjet_Gas3_StandGasDens | Para_Tecjet_Gas3_TecJetOffsetIsland | Para_Tecjet_Gas3_TecJetOffsetNet | Para_Tecjet_Gas3_TecJetPoint1 | Para_Tecjet_Gas3_TecJetPoint2 | Para_Tecjet_Gas3_TempOilPoint1 | Para_Tecjet_Gas3_TempOilPoint2 | Para_Tecjet_Gas4_AirDemandMin | Para_Tecjet_Gas4_CalorificValue | Para_Tecjet_Gas4_StandGasDens | Para_Tecjet_Gas4_TecJetOffsetIsland | Para_Tecjet_Gas4_TecJetOffsetNet | Para_Tecjet_Gas4_TecJetPoint1 | Para_Tecjet_Gas4_TecJetPoint2 | Para_Tecjet_Gas4_TempOilPoint1 | Para_Tecjet_Gas4_TempOilPoint2 | Para_Tecjet_IdleLambdaCtr_Delay1 | Para_Tecjet_IdleLambdaCtr_Delay2 | Para_Tecjet_IdleLambdaCtr_Gas1_TecJetDP | Para_Tecjet_IdleLambdaCtr_Gas1_TrPos | Para_Tecjet_IdleLambdaCtr_Gas2_TecJetDP | Para_Tecjet_IdleLambdaCtr_Gas2_TrPos | Para_Tecjet_IdleLambdaCtr_Gas3_TecJetDP | Para_Tecjet_IdleLambdaCtr_Gas3_TrPos | Para_Tecjet_IdleLambdaCtr_Gas4_TecJetDP | Para_Tecjet_IdleLambdaCtr_Gas4_TrPos | Para_Tecjet_IdleLambdaCtr_IComp | Para_Tecjet_IdleLambdaCtr_PComp | Para_Tecjet_LambdaAdapStartup_LambdaOffsetX2 | Para_Tecjet_LambdaAdapStartup_LambdaOffsetX3 | Para_Tecjet_LambdaAdapStartup_LambdaOffsetY1 | Para_Tecjet_LambdaAdapStartup_LambdaOffsetY2 | Para_Tecjet_LambdaAdapStartup_LambdaStartMin | Para_Tecjet_TempOilMax | Para_Tecjet_TempOilMin | TJ Vol Eff | Para_UniversalIO_Ana_InFirst | Para_UniversalIO_Ana_InLast | Para_UniversalIO_Ana_OutFirst | Para_UniversalIO_Ana_OutLast | Para_UniversalIO_Dig_CntFirst | Para_UniversalIO_Dig_CntLast | Para_UniversalIO_Dig_FlagFirst | Para_UniversalIO_Dig_FlagLast | Para_UniversalIO_Dig_InFirst | Para_UniversalIO_Dig_InLast | Para_UniversalIO_Dig_OutFirst | Para_UniversalIO_Dig_OutLast | Para_Visu_ActRemoteRequest | Para_Visu_Aux_ActAirInLou1 | Para_Visu_Aux_ActAirInLou2 | Para_Visu_Aux_ActAirInVent1 | Para_Visu_Aux_ActAirInVent2 | Para_Visu_Aux_ActAirInVentF | Para_Visu_Aux_ActAirOutLou | Para_Visu_Aux_ActCoolRadStage1 | Para_Visu_Aux_ActCoolRadStage2 | Para_Visu_Aux_ActCoolRadStageX | Para_Visu_Aux_ActExhGasValveBypass | Para_Visu_Aux_ActExhGasValveHeatEx | Para_Visu_Aux_ActMixCoolRadStageX | Para_Visu_Aux_ActPreHeat | Para_Visu_Aux_ActPreHeatWatPump | Para_Visu_Counter_MaintCountName1 | Para_Visu_Counter_MaintCountName1_uc_NEx | Para_Visu_Counter_MaintCountName2 | Para_Visu_Counter_MaintCountName2_uc_NEx | Para_Visu_Counter_MaintCountName3 | Para_Visu_Counter_MaintCountName3_uc_NEx | Para_Visu_Counter_MaintCountName4 | Para_Visu_Counter_MaintCountName4_uc_NEx | Para_Visu_Counter_MaintCountNameF1 | Para_Visu_Counter_MaintCountNameF1_uc_NEx | Para_Visu_Counter_MaintCountNameF2 | Para_Visu_Counter_MaintCountNameF2_uc_NEx | Para_Visu_Counter_MaintCountNameF3 | Para_Visu_Counter_MaintCountNameF3_uc_NEx | Para_Visu_Counter_MaintCountNameF4 | Para_Visu_Counter_MaintCountNameF4_uc_NEx | Para_Visu_Counter_ResCountName1 | Para_Visu_Counter_ResCountName2 | Para_Visu_Counter_ResCountName3 | Para_Visu_Counter_ResCountName4 | Para_Visu_Counter_ResCountNameF1 | Para_Visu_Counter_ResCountNameF2 | Para_Visu_Counter_ResCountNameF3 | Para_Visu_Counter_ResCountNameF4 | Para_Visu_Counter_ResCountUnit1 | Para_Visu_Counter_ResCountUnit2 | Para_Visu_Counter_ResCountUnit3 | Para_Visu_Counter_ResCountUnit4 | Para_Visu_Ele_ActGenNetPath | Para_Visu_Ele_ActNetOK_NEx | Para_Visu_Ele_ActTrGenDown | Para_Visu_Ele_ActTrGenUp | Para_Visu_Ele_ActTrNetDown | Para_Visu_Ele_ActTrNetUp | Para_Visu_Hyd_ActCoolWaterCircuit | Para_Visu_Hyd_ActDeskCooler | Para_Visu_Hyd_ActExtHeating | Para_Visu_Hyd_ActIntHeating | Para_Visu_Hyd_ActOil2Stage | Para_Visu_Hyd_ActOilPreLubPumpAC | Para_Visu_Hyd_ActOilPreLubPumpDC | Para_Visu_Hyd_ActTC | Para_Visu_UserLevelAck | PBC_HeatChar10_Cyl01 | PBC_HeatChar10_Cyl02 | PBC_HeatChar10_Cyl03 | PBC_HeatChar10_Cyl04 | PBC_HeatChar10_Cyl05 | PBC_HeatChar10_Cyl06 | PBC_HeatChar10_Cyl07 | PBC_HeatChar10_Cyl08 | PBC_HeatChar10_Cyl09 | PBC_HeatChar10_Cyl10 | PBC_HeatChar10_Cyl11 | PBC_HeatChar10_Cyl12 | PBC_HeatChar10_Cyl13 | PBC_HeatChar10_Cyl14 | PBC_HeatChar10_Cyl15 | PBC_HeatChar10_Cyl16 | PBC_HeatChar10_Cyl17 | PBC_HeatChar10_Cyl18 | PBC_HeatChar10_Cyl19 | PBC_HeatChar10_Cyl20 | PBC_HeatChar10_Cyl21 | PBC_HeatChar10_Cyl22 | PBC_HeatChar10_Cyl23 | PBC_HeatChar10_Cyl24 | PBC_HeatChar90_Cyl01 | PBC_HeatChar90_Cyl02 | PBC_HeatChar90_Cyl03 | PBC_HeatChar90_Cyl04 | PBC_HeatChar90_Cyl05 | PBC_HeatChar90_Cyl06 | PBC_HeatChar90_Cyl07 | PBC_HeatChar90_Cyl08 | PBC_HeatChar90_Cyl09 | PBC_HeatChar90_Cyl10 | PBC_HeatChar90_Cyl11 | PBC_HeatChar90_Cyl12 | PBC_HeatChar90_Cyl13 | PBC_HeatChar90_Cyl14 | PBC_HeatChar90_Cyl15 | PBC_HeatChar90_Cyl16 | PBC_HeatChar90_Cyl17 | PBC_HeatChar90_Cyl18 | PBC_HeatChar90_Cyl19 | PBC_HeatChar90_Cyl20 | PBC_HeatChar90_Cyl21 | PBC_HeatChar90_Cyl22 | PBC_HeatChar90_Cyl23 | PBC_HeatChar90_Cyl24 | PBC_HeatCharVar_Avg | PBC_HeatCharVar_Cyl01 | PBC_HeatCharVar_Cyl02 | PBC_HeatCharVar_Cyl03 | PBC_HeatCharVar_Cyl04 | PBC_HeatCharVar_Cyl05 | PBC_HeatCharVar_Cyl06 | PBC_HeatCharVar_Cyl07 | PBC_HeatCharVar_Cyl08 | PBC_HeatCharVar_Cyl09 | PBC_HeatCharVar_Cyl10 | PBC_HeatCharVar_Cyl11 | PBC_HeatCharVar_Cyl12 | PBC_HeatCharVar_Cyl13 | PBC_HeatCharVar_Cyl14 | PBC_HeatCharVar_Cyl15 | PBC_HeatCharVar_Cyl16 | PBC_HeatCharVar_Cyl17 | PBC_HeatCharVar_Cyl18 | PBC_HeatCharVar_Cyl19 | PBC_HeatCharVar_Cyl20 | PBC_HeatCharVar_Cyl21 | PBC_HeatCharVar_Cyl22 | PBC_HeatCharVar_Cyl23 | PBC_HeatCharVar_Cyl24 | PBC_HeatCharVar_Max | PBC_HeatCharVar_Min | PBC_Press49bfTDC_Avg | PBC_Press49bfTDC_Cyl01 | PBC_Press49bfTDC_Cyl02 | PBC_Press49bfTDC_Cyl03 | PBC_Press49bfTDC_Cyl04 | PBC_Press49bfTDC_Cyl05 | PBC_Press49bfTDC_Cyl06 | PBC_Press49bfTDC_Cyl07 | PBC_Press49bfTDC_Cyl08 | PBC_Press49bfTDC_Cyl09 | PBC_Press49bfTDC_Cyl10 | PBC_Press49bfTDC_Cyl11 | PBC_Press49bfTDC_Cyl12 | PBC_Press49bfTDC_Cyl13 | PBC_Press49bfTDC_Cyl14 | PBC_Press49bfTDC_Cyl15 | PBC_Press49bfTDC_Cyl16 | PBC_Press49bfTDC_Cyl17 | PBC_Press49bfTDC_Cyl18 | PBC_Press49bfTDC_Cyl19 | PBC_Press49bfTDC_Cyl20 | PBC_Press49bfTDC_Cyl21 | PBC_Press49bfTDC_Cyl22 | PBC_Press49bfTDC_Cyl23 | PBC_Press49bfTDC_Cyl24 | PBC_Press49bfTDC_Max | PBC_Press49bfTDC_Min | PBC_PressMean_Avg | PBC_PressMean_Cyl01 | PBC_PressMean_Cyl02 | PBC_PressMean_Cyl03 | PBC_PressMean_Cyl04 | PBC_PressMean_Cyl05 | PBC_PressMean_Cyl06 | PBC_PressMean_Cyl07 | PBC_PressMean_Cyl08 | PBC_PressMean_Cyl09 | PBC_PressMean_Cyl10 | PBC_PressMean_Cyl11 | PBC_PressMean_Cyl12 | PBC_PressMean_Cyl13 | PBC_PressMean_Cyl14 | PBC_PressMean_Cyl15 | PBC_PressMean_Cyl16 | PBC_PressMean_Cyl17 | PBC_PressMean_Cyl18 | PBC_PressMean_Cyl19 | PBC_PressMean_Cyl20 | PBC_PressMean_Cyl21 | PBC_PressMean_Cyl22 | PBC_PressMean_Cyl23 | PBC_PressMean_Cyl24 | PBC_PressMean_Max | PBC_PressMean_Min | PI_Commissioning | PI_Duration_Avg | PI_Duration_Cyl01 | PI_Duration_Cyl02 | PI_Duration_Cyl03 | PI_Duration_Cyl04 | PI_Duration_Cyl05 | PI_Duration_Cyl06 | PI_Duration_Cyl07 | PI_Duration_Cyl08 | PI_Duration_Cyl09 | PI_Duration_Cyl10 | PI_Duration_Cyl11 | PI_Duration_Cyl12 | PI_Duration_Cyl13 | PI_Duration_Cyl14 | PI_Duration_Cyl15 | PI_Duration_Cyl16 | PI_Duration_Cyl17 | PI_Duration_Cyl18 | PI_Duration_Cyl19 | PI_Duration_Cyl20 | PI_Duration_Cyl21 | PI_Duration_Cyl22 | PI_Duration_Cyl23 | PI_Duration_Cyl24 | PI_Duration_Max | PI_Duration_Min | PI_Man_Req | PI_Numb_SkipCyl_Act | PI_Required | PI_ResetMap | PI_SteadyState | pole_slipping_counter | P Act | Power_PowerActUnfilt | Power_PowerMax | P nom | Pred ext | Pred Bus | Pred knock | Pred misfire | Pred mixtemp | P red Act | Power_SetPower | Power_SetPowerExtInt | Power_SetPowerUnred | P11 A | P11 B | pr_egahptc_a | pr_egahptc_b | pr_egalptc_a | pr_egalptc_b | pr_egbhptc_a | pr_egbhptc_b | E since Start | h since Start | Crankcase Pressure | Oil P limit | LOC Avg | DP Oilfilter | rP_Ramp_Act | LoadRamp | rP_Targ_LastStart | rpr_oil_lptc_in_a | rpr_oil_lptc_in_b | rpr_tc_eof_after | rT_ECW_FS_Perm | rT_EGaHPTC | rT_EO_FS_Perm | rt_eo_pan | rTi_Load_0 | rTi_Load_2 | rTi_Prep_0 | rTi_Prep_1 | rTi_Prep_2 | rTi_Speedup_0 | rTi_Speedup_1 | rTi_Speedup_2 | rTi_Start_0 | rTi_Start_1 | rTi_Start_2 | rTi_SumLoad | rTi_SumSync | rTi_Sync_0 | rTi_Sync_1 | rTi_Sync_2 | rTi_Targ | Safi Temp | safi_valvelashset_1 | safi_valvelashset_10 | safi_valvelashset_11 | safi_valvelashset_12 | safi_valvelashset_13 | safi_valvelashset_14 | safi_valvelashset_15 | safi_valvelashset_16 | safi_valvelashset_17 | safi_valvelashset_18 | safi_valvelashset_19 | safi_valvelashset_2 | safi_valvelashset_20 | safi_valvelashset_21 | safi_valvelashset_22 | safi_valvelashset_23 | safi_valvelashset_24 | safi_valvelashset_3 | safi_valvelashset_4 | safi_valvelashset_5 | safi_valvelashset_6 | safi_valvelashset_7 | safi_valvelashset_8 | safi_valvelashset_9 | Safi W3 Z1 | Safi W3 Z10 | Safi W3 Z11 | Safi W3 Z12 | Safi W3 Z13 | Safi W3 Z14 | Safi W3 Z15 | Safi W3 Z16 | Safi W3 Z17 | Safi W3 Z18 | Safi W3 Z19 | Safi W3 Z2 | Safi W3 Z20 | Safi W3 Z21 | Safi W3 Z22 | Safi W3 Z23 | Safi W3 Z24 | Safi W3 Z3 | Safi W3 Z4 | Safi W3 Z5 | Safi W3 Z6 | Safi W3 Z7 | Safi W3 Z8 | Safi W3 Z9 | Safi W4 Z1 | Safi W4 Z10 | Safi W4 Z11 | Safi W4 Z12 | Safi W4 Z13 | Safi W4 Z14 | Safi W4 Z15 | Safi W4 Z16 | Safi W4 Z17 | Safi W4 Z18 | Safi W4 Z19 | Safi W4 Z2 | Safi W4 Z20 | Safi W4 Z21 | Safi W4 Z22 | Safi W4 Z23 | Safi W4 Z24 | Safi W4 Z3 | Safi W4 Z4 | Safi W4 Z5 | Safi W4 Z6 | Safi W4 Z7 | Safi W4 Z8 | Safi W4 Z9 | SCR_Catalyst_RUL | SendingDataCondition | SendingDataConditionNumeric | Slow Down Time | SlowDownTime01 | SlowDownTime02 | SlowDownTime03 | SlowDownTime04 | SlowDownTime05 | SlowDownTime06 | SlowDownTime07 | SlowDownTime08 | SlowDownTime09 | SlowDownTime10 | SlowDownTime11 | SlowDownTime12 | SlowDownTime13 | SlowDownTime14 | SlowDownTime15 | SlowDownTime16 | SlowDownTime17 | SlowDownTime18 | SlowDownTime19 | spark_plug_maintenance_IV01 | spark_plug_maintenance_IV02 | spark_plug_maintenance_IV03 | spark_plug_maintenance_IV04 | spark_plug_maintenance_IV05 | spark_plug_maintenance_IV06 | spark_plug_maintenance_IV07 | spark_plug_maintenance_IV08 | spark_plug_maintenance_IV09 | spark_plug_maintenance_IV10 | spark_plug_maintenance_IV11 | spark_plug_maintenance_IV12 | spark_plug_maintenance_IV13 | spark_plug_maintenance_IV14 | spark_plug_maintenance_IV15 | spark_plug_maintenance_IV16 | spark_plug_maintenance_IV17 | spark_plug_maintenance_IV18 | spark_plug_maintenance_IV19 | spark_plug_maintenance_IV20 | spark_plug_maintenance_IV21 | spark_plug_maintenance_IV22 | spark_plug_maintenance_IV23 | spark_plug_maintenance_IV24 | Spark_Plug_RUL01 | Spark_Plug_RUL02 | Spark_Plug_RUL03 | Spark_Plug_RUL04 | Spark_Plug_RUL05 | Spark_Plug_RUL06 | Spark_Plug_RUL07 | Spark_Plug_RUL08 | Spark_Plug_RUL09 | Spark_Plug_RUL10 | Spark_Plug_RUL11 | Spark_Plug_RUL12 | Spark_Plug_RUL13 | Spark_Plug_RUL14 | Spark_Plug_RUL15 | Spark_Plug_RUL16 | Spark_Plug_RUL17 | Spark_Plug_RUL18 | Spark_Plug_RUL19 | Spark_Plug_RUL20 | Spark_Plug_RUL21 | Spark_Plug_RUL22 | Spark_Plug_RUL23 | Spark_Plug_RUL24 | SPW_calc_starts_per_week | StartsCnt_Statistic | OP NetP | systeminfo_availablememory | systeminfo_cpuutilization | systeminfo_diskwriteperformance | systeminfo_externaldrive_averageerasecount | systeminfo_externaldrive_lifetimepercentage | systeminfo_externaldrive_poweronhours | systeminfo_freediskspace | systeminfo_internaldrive_averageerasecount | systeminfo_internaldrive_lifetimepercentage | systeminfo_internaldrive_poweronhours | systeminfo_systemuptime | T11 A | T11 B | t_egahptc_a | t_egahptc_b | t_egbhptc_a | t_egbhptc_b | TC_SurgeEvents | TJ Gas DP | TecJet_GasDiffPress2 | TecJet_GasDiffPress3 | TecJet_GasDiffPress4 | TJ Gas Flow | TecJet_GasFlow2 | TecJet_GasFlow3 | TecJet_GasFlow4 | TJ Gas P | TecJet_GasPress2 | TecJet_GasPress3 | TecJet_GasPress4 | TJ Gas T | TecJet_GasTemp2 | TecJet_GasTemp3 | TecJet_GasTemp4 | LambdaTJ | TecJet_Lambda2 | TecJet_Lambda3 | TecJet_Lambda4 | TJ pos | TecJet_ValvePos2 | TecJet_ValvePos3 | TecJet_ValvePos4 | thermalreactor_bpos_thr_val_mid | thermalreactor_icnt_ophours_reactor | thermalreactor_rt_thr_chamber | turbocharger_post_cooling_detection | turbocharger_post_cooling_detection_lpa | turbocharger_post_cooling_detection_lpb | turbocharger_post_cooling_v2_cumulative_counter | valverecession_cyl01_deltaOphSinceInit | valverecession_cyl01_new_cyl_head | valverecession_cyl02_deltaOphSinceInit | valverecession_cyl02_new_cyl_head | valverecession_cyl03_deltaOphSinceInit | valverecession_cyl03_new_cyl_head | valverecession_cyl04_deltaOphSinceInit | valverecession_cyl04_new_cyl_head | valverecession_cyl05_deltaOphSinceInit | valverecession_cyl05_new_cyl_head | valverecession_cyl06_deltaOphSinceInit | valverecession_cyl06_new_cyl_head | valverecession_cyl07_deltaOphSinceInit | valverecession_cyl07_new_cyl_head | valverecession_cyl08_deltaOphSinceInit | valverecession_cyl08_new_cyl_head | valverecession_cyl09_deltaOphSinceInit | valverecession_cyl09_new_cyl_head | valverecession_cyl10_deltaOphSinceInit | valverecession_cyl10_new_cyl_head | valverecession_cyl11_deltaOphSinceInit | valverecession_cyl11_new_cyl_head | valverecession_cyl12_deltaOphSinceInit | valverecession_cyl12_new_cyl_head | valverecession_cyl13_deltaOphSinceInit | valverecession_cyl13_new_cyl_head | valverecession_cyl14_deltaOphSinceInit | valverecession_cyl14_new_cyl_head | valverecession_cyl15_deltaOphSinceInit | valverecession_cyl15_new_cyl_head | valverecession_cyl16_deltaOphSinceInit | valverecession_cyl16_new_cyl_head | valverecession_cyl17_deltaOphSinceInit | valverecession_cyl17_new_cyl_head | valverecession_cyl18_deltaOphSinceInit | valverecession_cyl18_new_cyl_head | valverecession_cyl19_deltaOphSinceInit | valverecession_cyl19_new_cyl_head | valverecession_cyl20_deltaOphSinceInit | valverecession_cyl20_new_cyl_head | valverecession_cyl21_deltaOphSinceInit | valverecession_cyl21_new_cyl_head | valverecession_cyl22_deltaOphSinceInit | valverecession_cyl22_new_cyl_head | valverecession_cyl23_deltaOphSinceInit | valverecession_cyl23_new_cyl_head | valverecession_cyl24_deltaOphSinceInit | valverecession_cyl24_new_cyl_head | valverecession_lev_cyl01_deltaVRSinceInit | valverecession_lev_cyl01_init | valverecession_lev_cyl02_deltaVRSinceInit | valverecession_lev_cyl02_init | valverecession_lev_cyl03_deltaVRSinceInit | valverecession_lev_cyl03_init | valverecession_lev_cyl04_deltaVRSinceInit | valverecession_lev_cyl04_init | valverecession_lev_cyl05_deltaVRSinceInit | valverecession_lev_cyl05_init | valverecession_lev_cyl06_deltaVRSinceInit | valverecession_lev_cyl06_init | valverecession_lev_cyl07_deltaVRSinceInit | valverecession_lev_cyl07_init | valverecession_lev_cyl08_deltaVRSinceInit | valverecession_lev_cyl08_init | valverecession_lev_cyl09_deltaVRSinceInit | valverecession_lev_cyl09_init | valverecession_lev_cyl10_deltaVRSinceInit | valverecession_lev_cyl10_init | valverecession_lev_cyl11_deltaVRSinceInit | valverecession_lev_cyl11_init | valverecession_lev_cyl12_deltaVRSinceInit | valverecession_lev_cyl12_init | valverecession_lev_cyl13_deltaVRSinceInit | valverecession_lev_cyl13_init | valverecession_lev_cyl14_deltaVRSinceInit | valverecession_lev_cyl14_init | valverecession_lev_cyl15_deltaVRSinceInit | valverecession_lev_cyl15_init | valverecession_lev_cyl16_deltaVRSinceInit | valverecession_lev_cyl16_init | valverecession_lev_cyl17_deltaVRSinceInit | valverecession_lev_cyl17_init | valverecession_lev_cyl18_deltaVRSinceInit | valverecession_lev_cyl18_init | valverecession_lev_cyl19_deltaVRSinceInit | valverecession_lev_cyl19_init | valverecession_lev_cyl20_deltaVRSinceInit | valverecession_lev_cyl20_init | valverecession_lev_cyl21_deltaVRSinceInit | valverecession_lev_cyl21_init | valverecession_lev_cyl22_deltaVRSinceInit | valverecession_lev_cyl22_init | valverecession_lev_cyl23_deltaVRSinceInit | valverecession_lev_cyl23_init | valverecession_lev_cyl24_deltaVRSinceInit | valverecession_lev_cyl24_init | valverecession_liv_cyl01_deltaVRSinceInit | valverecession_liv_cyl01_init | valverecession_liv_cyl02_deltaVRSinceInit | valverecession_liv_cyl02_init | valverecession_liv_cyl03_deltaVRSinceInit | valverecession_liv_cyl03_init | valverecession_liv_cyl04_deltaVRSinceInit | valverecession_liv_cyl04_init | valverecession_liv_cyl05_deltaVRSinceInit | valverecession_liv_cyl05_init | valverecession_liv_cyl06_deltaVRSinceInit | valverecession_liv_cyl06_init | valverecession_liv_cyl07_deltaVRSinceInit | valverecession_liv_cyl07_init | valverecession_liv_cyl08_deltaVRSinceInit | valverecession_liv_cyl08_init | valverecession_liv_cyl09_deltaVRSinceInit | valverecession_liv_cyl09_init | valverecession_liv_cyl10_deltaVRSinceInit | valverecession_liv_cyl10_init | valverecession_liv_cyl11_deltaVRSinceInit | valverecession_liv_cyl11_init | valverecession_liv_cyl12_deltaVRSinceInit | valverecession_liv_cyl12_init | valverecession_liv_cyl13_deltaVRSinceInit | valverecession_liv_cyl13_init | valverecession_liv_cyl14_deltaVRSinceInit | valverecession_liv_cyl14_init | valverecession_liv_cyl15_deltaVRSinceInit | valverecession_liv_cyl15_init | valverecession_liv_cyl16_deltaVRSinceInit | valverecession_liv_cyl16_init | valverecession_liv_cyl17_deltaVRSinceInit | valverecession_liv_cyl17_init | valverecession_liv_cyl18_deltaVRSinceInit | valverecession_liv_cyl18_init | valverecession_liv_cyl19_deltaVRSinceInit | valverecession_liv_cyl19_init | valverecession_liv_cyl20_deltaVRSinceInit | valverecession_liv_cyl20_init | valverecession_liv_cyl21_deltaVRSinceInit | valverecession_liv_cyl21_init | valverecession_liv_cyl22_deltaVRSinceInit | valverecession_liv_cyl22_init | valverecession_liv_cyl23_deltaVRSinceInit | valverecession_liv_cyl23_init | valverecession_liv_cyl24_deltaVRSinceInit | valverecession_liv_cyl24_init | valverecession_rev_cyl01_deltaVRSinceInit | valverecession_rev_cyl01_init | valverecession_rev_cyl02_deltaVRSinceInit | valverecession_rev_cyl02_init | valverecession_rev_cyl03_deltaVRSinceInit | valverecession_rev_cyl03_init | valverecession_rev_cyl04_deltaVRSinceInit | valverecession_rev_cyl04_init | valverecession_rev_cyl05_deltaVRSinceInit | valverecession_rev_cyl05_init | valverecession_rev_cyl06_deltaVRSinceInit | valverecession_rev_cyl06_init | valverecession_rev_cyl07_deltaVRSinceInit | valverecession_rev_cyl07_init | valverecession_rev_cyl08_deltaVRSinceInit | valverecession_rev_cyl08_init | valverecession_rev_cyl09_deltaVRSinceInit | valverecession_rev_cyl09_init | valverecession_rev_cyl10_deltaVRSinceInit | valverecession_rev_cyl10_init | valverecession_rev_cyl11_deltaVRSinceInit | valverecession_rev_cyl11_init | valverecession_rev_cyl12_deltaVRSinceInit | valverecession_rev_cyl12_init | valverecession_rev_cyl13_deltaVRSinceInit | valverecession_rev_cyl13_init | valverecession_rev_cyl14_deltaVRSinceInit | valverecession_rev_cyl14_init | valverecession_rev_cyl15_deltaVRSinceInit | valverecession_rev_cyl15_init | valverecession_rev_cyl16_deltaVRSinceInit | valverecession_rev_cyl16_init | valverecession_rev_cyl17_deltaVRSinceInit | valverecession_rev_cyl17_init | valverecession_rev_cyl18_deltaVRSinceInit | valverecession_rev_cyl18_init | valverecession_rev_cyl19_deltaVRSinceInit | valverecession_rev_cyl19_init | valverecession_rev_cyl20_deltaVRSinceInit | valverecession_rev_cyl20_init | valverecession_rev_cyl21_deltaVRSinceInit | valverecession_rev_cyl21_init | valverecession_rev_cyl22_deltaVRSinceInit | valverecession_rev_cyl22_init | valverecession_rev_cyl23_deltaVRSinceInit | valverecession_rev_cyl23_init | valverecession_rev_cyl24_deltaVRSinceInit | valverecession_rev_cyl24_init | valverecession_riv_cyl01_deltaVRSinceInit | valverecession_riv_cyl01_init | valverecession_riv_cyl02_deltaVRSinceInit | valverecession_riv_cyl02_init | valverecession_riv_cyl03_deltaVRSinceInit | valverecession_riv_cyl03_init | valverecession_riv_cyl04_deltaVRSinceInit | valverecession_riv_cyl04_init | valverecession_riv_cyl05_deltaVRSinceInit | valverecession_riv_cyl05_init | valverecession_riv_cyl06_deltaVRSinceInit | valverecession_riv_cyl06_init | valverecession_riv_cyl07_deltaVRSinceInit | valverecession_riv_cyl07_init | valverecession_riv_cyl08_deltaVRSinceInit | valverecession_riv_cyl08_init | valverecession_riv_cyl09_deltaVRSinceInit | valverecession_riv_cyl09_init | valverecession_riv_cyl10_deltaVRSinceInit | valverecession_riv_cyl10_init | valverecession_riv_cyl11_deltaVRSinceInit | valverecession_riv_cyl11_init | valverecession_riv_cyl12_deltaVRSinceInit | valverecession_riv_cyl12_init | valverecession_riv_cyl13_deltaVRSinceInit | valverecession_riv_cyl13_init | valverecession_riv_cyl14_deltaVRSinceInit | valverecession_riv_cyl14_init | valverecession_riv_cyl15_deltaVRSinceInit | valverecession_riv_cyl15_init | valverecession_riv_cyl16_deltaVRSinceInit | valverecession_riv_cyl16_init | valverecession_riv_cyl17_deltaVRSinceInit | valverecession_riv_cyl17_init | valverecession_riv_cyl18_deltaVRSinceInit | valverecession_riv_cyl18_init | valverecession_riv_cyl19_deltaVRSinceInit | valverecession_riv_cyl19_init | valverecession_riv_cyl20_deltaVRSinceInit | valverecession_riv_cyl20_init | valverecession_riv_cyl21_deltaVRSinceInit | valverecession_riv_cyl21_init | valverecession_riv_cyl22_deltaVRSinceInit | valverecession_riv_cyl22_init | valverecession_riv_cyl23_deltaVRSinceInit | valverecession_riv_cyl23_init | valverecession_riv_cyl24_deltaVRSinceInit | valverecession_riv_cyl24_init | Various_Bits_ColAlarm | Alarm ? | Wanrning ? | OP Switch on | OP on | Status No | Various_SetValues_SetWasteGate | DK pos | Various_Values_PosThrottleA1 | Various_Values_PosThrottleA2 | Various_Values_PosThrottleB1 | Various_Values_PosThrottleB2 | BP pos | Various_Values_PosTurboBypassA1 | Various_Values_PosTurboBypassA2 | Various_Values_PosTurboBypassB1 | Various_Values_PosTurboBypassB2 | Various_Values_PosWasteGateA | Various_Values_PosWasteGateB
| Activation Status | AGG_AssetAvailability | AGG_AssetPerformanceRate | AGG_AssetReliabilityRate | asset_status | ATD1 | ATD2 | Aux_CH4Cont | Aux_GasPress | Aux_GasRail_rDPr_SetAct | Aux_GasRail_rPr_a_Filt | Aux_GasRail_rPr_Out_Calc | Aux_GasRail_rPr_sp | Aux_GasTemp | Aux_GasVol | Aux_O2Cont | Aux_PreChambDifPress | Aux_PreChambGasTrain_rDPr_SetAct | Aux_PreChambGasTrain_rPr_a_Filt | Aux_PreChambGasTrain_rPr_Out | Aux_PreChambGasTrain_rPr_sp | Aux_PreChambGasTrainPress | Aux_RoomTemp | Aux_rPr_Baro | Aux_StarterPressInlet | Aux_StarterPressTank | Aux_StarterSpeed | Aux_SucPress | Aux_TempOutDoor | auxiliariesgeneral_rdpr_ofu_filt | auxiliariesgeneral_reo_level | auxiliariesgeneral_rpr_eo_diff_f | auxiliariesgeneral_rpr_eoap | auxiliariesgeneral_rpr_eof_diffmon | auxiliariesgeneral_rpr_ofuafilt | auxiliariesgeneral_rpr_ofubcentrifuge | auxiliariesgeneral_rpr_ofubfilt | BaseProg_Vers | BBFRULABS_RUL | Bear_Conrod_Temp01 | Bear_Conrod_Temp02 | Bear_Conrod_Temp03 | Bear_Conrod_Temp04 | Bear_Conrod_Temp05 | Bear_Conrod_Temp06 | Bear_Conrod_Temp07 | Bear_Conrod_Temp08 | Bear_Conrod_Temp09 | Bear_Conrod_Temp10 | Bear_Conrod_Temp11 | Bear_Conrod_Temp12 | Bear_Conrod_Temp13 | Bear_Conrod_Temp14 | Bear_Conrod_Temp15 | Bear_Conrod_Temp16 | Bear_Conrod_Temp17 | Bear_Conrod_Temp18 | Bear_Conrod_Temp19 | Bear_Conrod_Temp20 | Bear_Conrod_Temp21 | Bear_Conrod_Temp22 | Bear_Conrod_Temp23 | Bear_Conrod_Temp24 | Bear_Conrod_TempMax | Bear_Main_Temp01 | Bear_Main_Temp02 | Bear_Main_Temp03 | Bear_Main_Temp04 | Bear_Main_Temp05 | Bear_Main_Temp06 | Bear_Main_Temp07 | Bear_Main_Temp08 | Bear_Main_Temp09 | Bear_Main_Temp10 | Bear_Main_Temp11 | Bear_Main_TempMax | bFS_Req | bLoad | bp_red_active | bScavDone | bSync | bT_ECW_Ok | bT_EO_Ok | ChannelPartnerRegion | chargingunit_rvol_ch_engine_norm | CMU_rDPr_AirFilt_A | CMU_rDPr_AirFilt_B | CMU_rDPr_BbFilt | CMU_rDPr_Ch_AirFilt | CMU_rDPr_Ch_FA | CMU_rDPr_Ch_HPCooler | CMU_rDPr_Ch_LPCooler | CMU_rPr_a_BbFilt | CMU_rPr_a_BbFilt_A | CMU_rPr_a_BbFilt_B | CMU_rPr_Ch_P2bFA | CMU_rPr_Ch_P2HP | CMU_rPr_Ch_P2LP | CMU_rPr_f_BbFilt | CMU_rPr_f_BbFilt_A | CMU_rPr_f_BbFilt_B | Combustion_Quality_Cyl01 | Combustion_Quality_Cyl02 | Combustion_Quality_Cyl03 | Combustion_Quality_Cyl04 | Combustion_Quality_Cyl05 | Combustion_Quality_Cyl06 | Combustion_Quality_Cyl07 | Combustion_Quality_Cyl08 | Combustion_Quality_Cyl09 | Combustion_Quality_Cyl10 | Combustion_Quality_Cyl11 | Combustion_Quality_Cyl12 | Combustion_Quality_Cyl13 | Combustion_Quality_Cyl14 | Combustion_Quality_Cyl15 | Combustion_Quality_Cyl16 | Combustion_Quality_Cyl17 | Combustion_Quality_Cyl18 | Combustion_Quality_Cyl19 | Combustion_Quality_Cyl20 | Combustion_Quality_Cyl21 | Combustion_Quality_Cyl22 | Combustion_Quality_Cyl23 | Combustion_Quality_Cyl24 | Combustion_Quality_Max_Cyl01 | Combustion_Quality_Max_Cyl02 | Combustion_Quality_Max_Cyl03 | Combustion_Quality_Max_Cyl04 | Combustion_Quality_Max_Cyl05 | Combustion_Quality_Max_Cyl06 | Combustion_Quality_Max_Cyl07 | Combustion_Quality_Max_Cyl08 | Combustion_Quality_Max_Cyl09 | Combustion_Quality_Max_Cyl10 | Combustion_Quality_Max_Cyl11 | Combustion_Quality_Max_Cyl12 | Combustion_Quality_Max_Cyl13 | Combustion_Quality_Max_Cyl14 | Combustion_Quality_Max_Cyl15 | Combustion_Quality_Max_Cyl16 | Combustion_Quality_Max_Cyl17 | Combustion_Quality_Max_Cyl18 | Combustion_Quality_Max_Cyl19 | Combustion_Quality_Max_Cyl20 | Combustion_Quality_Max_Cyl21 | Combustion_Quality_Max_Cyl22 | Combustion_Quality_Max_Cyl23 | Combustion_Quality_Max_Cyl24 | Cooling_Water_Degassing | Cooling_Water_TopUp | Count_Count1 | Count_Count2 | Count_Count3 | Count_Count4 | Count_Counter1 | Count_Counter10 | Count_Counter2 | Count_Counter3 | Count_Counter4 | Count_Counter5 | Count_Counter6 | Count_Counter7 | Count_Counter8 | Count_Counter9 | Count_Maintenance1 | Count_Maintenance2 | Count_Maintenance3 | Count_Maintenance4 | Count_Maintenance5 | Count_Maintenance6 | Count_Maintenance7 | Count_Maintenance8 | Count_OpHour | Count_OpHour_Billing | Count_OpHourGenSet | Count_OpHourManual | Count_Start | CtrMixTemp_W | CtrMixTemp_X | CtrMixTemp_Y | CtrModule_Ctr10_W | CtrModule_Ctr10_X | CtrModule_Ctr10_Y | CtrModule_Ctr11_W | CtrModule_Ctr11_X | CtrModule_Ctr11_Y | CtrModule_Ctr12_W | CtrModule_Ctr12_X | CtrModule_Ctr12_Y | CtrModule_Ctr13_W | CtrModule_Ctr13_X | CtrModule_Ctr13_Y | CtrModule_Ctr14_W | CtrModule_Ctr14_X | CtrModule_Ctr14_Y | CtrModule_Ctr15_W | CtrModule_Ctr15_X | CtrModule_Ctr15_Y | CtrModule_Ctr16_W | CtrModule_Ctr16_X | CtrModule_Ctr16_Y | CtrModule_Ctr1_W | CtrModule_Ctr1_X | CtrModule_Ctr1_Y | CtrModule_Ctr2_W | CtrModule_Ctr2_X | CtrModule_Ctr2_Y | CtrModule_Ctr3_W | CtrModule_Ctr3_X | CtrModule_Ctr3_Y | CtrModule_Ctr4_W | CtrModule_Ctr4_X | CtrModule_Ctr4_Y | CtrModule_Ctr5_W | CtrModule_Ctr5_X | CtrModule_Ctr5_Y | CtrModule_Ctr6_W | CtrModule_Ctr6_X | CtrModule_Ctr6_Y | CtrModule_Ctr7_W | CtrModule_Ctr7_X | CtrModule_Ctr7_Y | CtrModule_Ctr8_W | CtrModule_Ctr8_X | CtrModule_Ctr8_Y | cust_analoginput_ai001_value | cust_analoginput_ai002_value | cust_analoginput_ai003_value | cust_analoginput_ai004_value | cust_analoginput_ai005_value | cust_analoginput_ai006_value | cust_analoginput_ai007_value | cust_analoginput_ai008_value | cust_analoginput_ai009_value | cust_analoginput_ai010_value | cust_analoginput_ai011_value | cust_analoginput_ai012_value | cust_analoginput_ai013_value | cust_analoginput_ai014_value | cust_analoginput_ai015_value | cust_analoginput_ai016_value | cust_analoginput_ai017_value | cust_analoginput_ai018_value | cust_analoginput_ai019_value | cust_analoginput_ai020_value | cust_analoginput_ai021_value | cust_analoginput_ai022_value | cust_analoginput_ai023_value | cust_analoginput_ai024_value | cust_analoginput_ai025_value | cust_analoginput_ai026_value | cust_analoginput_ai027_value | cust_analoginput_ai028_value | cust_analoginput_ai029_value | cust_analoginput_ai030_value | cust_analoginput_ai031_value | cust_analoginput_ai032_value | cust_analoginput_ai033_value | cust_analoginput_ai034_value | cust_analoginput_ai035_value | cust_analoginput_ai036_value | cust_analoginput_ai037_value | cust_analoginput_ai038_value | cust_analoginput_ai039_value | cust_analoginput_ai040_value | cust_analoginput_ai041_value | cust_analoginput_ai042_value | cust_analoginput_ai043_value | cust_analoginput_ai044_value | cust_analoginput_ai045_value | cust_analoginput_ai046_value | cust_analoginput_ai047_value | cust_analoginput_ai048_value | cust_analoginput_ai049_value | cust_analoginput_ai050_value | cust_analoginput_ai051_value | cust_analoginput_ai052_value | cust_analoginput_ai053_value | cust_analoginput_ai054_value | cust_analoginput_ai055_value | cust_analoginput_ai056_value | cust_analoginput_ai057_value | cust_analoginput_ai058_value | cust_analoginput_ai059_value | cust_analoginput_ai060_value | custom_dpscrcatalyst_22ccfa | custom_engine_out_nox_mg_16583c | CylState_1 | CylState_10 | CylState_11 | CylState_12 | CylState_13 | CylState_14 | CylState_15 | CylState_16 | CylState_17 | CylState_18 | CylState_19 | CylState_2 | CylState_20 | CylState_3 | CylState_4 | CylState_5 | CylState_6 | CylState_7 | CylState_8 | CylState_9 | ec_lx2_bpoc_0 | ec_lx2_bpoc_1 | ec_lx2_bpoc_10 | ec_lx2_bpoc_2 | ec_lx2_bpoc_3 | ec_lx2_bpoc_4 | ec_lx2_bpoc_5 | ec_lx2_bpoc_6 | ec_lx2_bpoc_7 | ec_lx2_bpoc_8 | ec_lx2_bpoc_9 | ec_lx2_bpoc_gas_1_0 | ec_lx2_bpoc_gas_1_0_m | ec_lx2_bpoc_gas_1_1 | ec_lx2_bpoc_gas_1_10 | ec_lx2_bpoc_gas_1_10_m | ec_lx2_bpoc_gas_1_1_m | ec_lx2_bpoc_gas_1_2 | ec_lx2_bpoc_gas_1_2_m | ec_lx2_bpoc_gas_1_3 | ec_lx2_bpoc_gas_1_3_m | ec_lx2_bpoc_gas_1_4 | ec_lx2_bpoc_gas_1_4_m | ec_lx2_bpoc_gas_1_5 | ec_lx2_bpoc_gas_1_5_m | ec_lx2_bpoc_gas_1_6 | ec_lx2_bpoc_gas_1_6_m | ec_lx2_bpoc_gas_1_7 | ec_lx2_bpoc_gas_1_7_m | ec_lx2_bpoc_gas_1_8 | ec_lx2_bpoc_gas_1_8_m | ec_lx2_bpoc_gas_1_9 | ec_lx2_bpoc_gas_1_9_m | ec_lx2_bpoc_gas_2_0 | ec_lx2_bpoc_gas_2_0_m | ec_lx2_bpoc_gas_2_1 | ec_lx2_bpoc_gas_2_10 | ec_lx2_bpoc_gas_2_10_m | ec_lx2_bpoc_gas_2_1_m | ec_lx2_bpoc_gas_2_2 | ec_lx2_bpoc_gas_2_2_m | ec_lx2_bpoc_gas_2_3 | ec_lx2_bpoc_gas_2_3_m | ec_lx2_bpoc_gas_2_4 | ec_lx2_bpoc_gas_2_4_m | ec_lx2_bpoc_gas_2_5 | ec_lx2_bpoc_gas_2_5_m | ec_lx2_bpoc_gas_2_6 | ec_lx2_bpoc_gas_2_6_m | ec_lx2_bpoc_gas_2_7 | ec_lx2_bpoc_gas_2_7_m | ec_lx2_bpoc_gas_2_8 | ec_lx2_bpoc_gas_2_8_m | ec_lx2_bpoc_gas_2_9 | ec_lx2_bpoc_gas_2_9_m | ec_lx2_bpoc_gas_3_0 | ec_lx2_bpoc_gas_3_0_m | ec_lx2_bpoc_gas_3_1 | ec_lx2_bpoc_gas_3_10 | ec_lx2_bpoc_gas_3_10_m | ec_lx2_bpoc_gas_3_1_m | ec_lx2_bpoc_gas_3_2 | ec_lx2_bpoc_gas_3_2_m | ec_lx2_bpoc_gas_3_3 | ec_lx2_bpoc_gas_3_3_m | ec_lx2_bpoc_gas_3_4 | ec_lx2_bpoc_gas_3_4_m | ec_lx2_bpoc_gas_3_5 | ec_lx2_bpoc_gas_3_5_m | ec_lx2_bpoc_gas_3_6 | ec_lx2_bpoc_gas_3_6_m | ec_lx2_bpoc_gas_3_7 | ec_lx2_bpoc_gas_3_7_m | ec_lx2_bpoc_gas_3_8 | ec_lx2_bpoc_gas_3_8_m | ec_lx2_bpoc_gas_3_9 | ec_lx2_bpoc_gas_3_9_m | ec_lx2_bpoc_gas_4_0 | ec_lx2_bpoc_gas_4_0_m | ec_lx2_bpoc_gas_4_1 | ec_lx2_bpoc_gas_4_10 | ec_lx2_bpoc_gas_4_10_m | ec_lx2_bpoc_gas_4_1_m | ec_lx2_bpoc_gas_4_2 | ec_lx2_bpoc_gas_4_2_m | ec_lx2_bpoc_gas_4_3 | ec_lx2_bpoc_gas_4_3_m | ec_lx2_bpoc_gas_4_4 | ec_lx2_bpoc_gas_4_4_m | ec_lx2_bpoc_gas_4_5 | ec_lx2_bpoc_gas_4_5_m | ec_lx2_bpoc_gas_4_6 | ec_lx2_bpoc_gas_4_6_m | ec_lx2_bpoc_gas_4_7 | ec_lx2_bpoc_gas_4_7_m | ec_lx2_bpoc_gas_4_8 | ec_lx2_bpoc_gas_4_8_m | ec_lx2_bpoc_gas_4_9 | ec_lx2_bpoc_gas_4_9_m | Efficiency_Estimate_1_Median | Efficiency_Estimtate_1 | emission_bamm_nox_noxs_engout_avg | emission_blx2_active | emission_blx2_ctrl_enable | emission_bnoxs_catout_heater_ok | emission_bnoxs_catout_nox_ok | emission_bnoxs_catout_nox_validity_ok | emission_bnoxs_catout_o2_ok | emission_bnoxs_catout_o2_validity_ok | emission_bnoxs_catout_power_ok | emission_bnoxs_engout_a_heater_ok | emission_bnoxs_engout_a_nox_ok | emission_bnoxs_engout_a_nox_validity_ok | emission_bnoxs_engout_a_o2_ok | emission_bnoxs_engout_a_o2_validity_ok | emission_bnoxs_engout_a_power_ok | emission_bnoxs_engout_b_heater_ok | emission_bnoxs_engout_b_nox_ok | emission_bnoxs_engout_b_nox_validity_ok | emission_bnoxs_engout_b_o2_ok | emission_bnoxs_engout_b_o2_validity_ok | emission_bnoxs_engout_b_power_ok | emission_bnoxs_engout_heater_ok | emission_bnoxs_engout_nox_ok | emission_bnoxs_engout_nox_validity_ok | emission_bnoxs_engout_o2_ok | emission_bnoxs_engout_o2_validity_ok | emission_bnoxs_engout_power_ok | emission_bscr_emvalve1_cg_dem | emission_bscr_emvalve1_sg_dem | emission_bscr_extemadjust_run | emission_bscr_injectvalve_urea | emission_cnt_noxs_engout_lastdiag | emission_diff_pres_cat_max | emission_icnt_nox_em_monlim_exc | emission_inoxs_catout_ophours | emission_inoxs_engout_a_ophours | emission_inoxs_engout_b_ophours | emission_inoxs_engout_ophours | emission_nox_noxs_engout_durdiag | emission_o2_noxs_engout_durdiag | emission_pc_noxs_engout_diagresult | emission_rco_em_avgshortterm | emission_rco_em_monlim_hi | emission_rco_scr_catout_avg | emission_rco_scr_cemsextcatout | emission_rco_scr_emline1 | emission_rdpr_scr_cat | emission_rflow_scr_ureadosingout | emission_rflow_scr_ureadosingunit_ff | emission_rhum_catout | emission_rno2_scr_cemsextcatout | emission_rno2_scr_emline1 | emission_rno_scr_cemsextcatout | emission_rno_scr_emline1 | emission_rnox_em_avgdaily | emission_rnox_em_avgdaily_all | emission_rnox_em_avgshortterm | emission_rnox_em_engout_set | emission_rnox_em_monlim_hi | emission_rnox_em_monlim_hitol | emission_rnox_noxs_catout | emission_rnox_noxs_catout_durdiag | emission_rnox_noxs_catout_mg | emission_rnox_noxs_engout | emission_rnox_noxs_engout_a | emission_rnox_noxs_engout_a_durdiag | emission_rnox_noxs_engout_a_mg | emission_rnox_noxs_engout_avg | emission_rnox_noxs_engout_b | emission_rnox_noxs_engout_b_durdiag | emission_rnox_noxs_engout_b_mg | emission_rnox_noxs_engout_mg | emission_rnox_noxs_engout_mg_avg | emission_rnox_scr_catout_avg | emission_ro2_noxs_catout | emission_ro2_noxs_catout_durdiag | emission_ro2_noxs_catout_filt | emission_ro2_noxs_engout | emission_ro2_noxs_engout_a | emission_ro2_noxs_engout_a_durdiag | emission_ro2_noxs_engout_a_filt | emission_ro2_noxs_engout_avg_filt | emission_ro2_noxs_engout_b | emission_ro2_noxs_engout_b_durdiag | emission_ro2_noxs_engout_b_filt | emission_ro2_noxs_engout_filt | emission_ro2_scr_cemsextcatout | emission_rpc_noxs_catout_diagresult | emission_rpc_noxs_engout_a_diagresult | emission_rpc_noxs_engout_b_diagresult | emission_rpr_scr_catin | emission_rpr_scr_catout | emission_rpr_scr_comprairsupply | emission_rpr_scr_ureadosingin | emission_rpr_scr_ureadosingout | emission_rt_scr_catavg | emission_rt_scr_catin | emission_rt_scr_catout | emission_rvol_scr_ureaconsumption | Engine_OpHour_Fixed_Timestamp | Engine_Slowdown_Time_Detection | Engine_Slowdown_Time_Monitoring_Sec | Engine_Slowdown_Time_Oil_Correction | enginecontroller_blx2_ss | enginecontroller_rhum_airin_abs | enginecontroller_rhum_airin_rel | enginecontroller_rpr_p2s_lx2 | Estimated_Compressor_Bypass_Position | Estimated_IntakeTemperatureRange | exhaust_bscavvalve | exhaust_icnt_ophours_oxi | Exhaust_NOx_NOx1 | Exhaust_NOx_NOx2 | Exhaust_NOx_O2_1 | Exhaust_NOx_O2_2 | exhaust_rpr_oxicat_diff | exhaust_rpr_oxicat_in | exhaust_rpr_oxicat_in_fast | exhaust_rpr_oxicat_in_fast_peak | Exhaust_TCSpeedA | Exhaust_TCSpeedB | Exhaust_TCSpeedLPA | Exhaust_TCSpeedLPB | Exhaust_TempBoil | Exhaust_TempCat | Exhaust_TempCatIn | Exhaust_TempCatOut | Exhaust_TempCyl01 | Exhaust_TempCyl02 | Exhaust_TempCyl03 | Exhaust_TempCyl04 | Exhaust_TempCyl05 | Exhaust_TempCyl06 | Exhaust_TempCyl07 | Exhaust_TempCyl08 | Exhaust_TempCyl09 | Exhaust_TempCyl10 | Exhaust_TempCyl11 | Exhaust_TempCyl12 | Exhaust_TempCyl13 | Exhaust_TempCyl14 | Exhaust_TempCyl15 | Exhaust_TempCyl16 | Exhaust_TempCyl17 | Exhaust_TempCyl18 | Exhaust_TempCyl19 | Exhaust_TempCyl20 | Exhaust_TempCyl21 | Exhaust_TempCyl22 | Exhaust_TempCyl23 | Exhaust_TempCyl24 | Exhaust_TempCylAvg | Exhaust_TempCylAvg_ss | Exhaust_TempCylMax | Exhaust_TempCylMax_ss | Exhaust_TempCylMin | Exhaust_TempCylMin_ss | Exhaust_TempETCIn | Exhaust_TempHexIn | Exhaust_TempHexOut | Exhaust_TempLPTCOutletA | Exhaust_TempLPTCOutletB | Exhaust_TempMaxSpread | Exhaust_TempThermReact1Avg | Exhaust_TempThermReact2Avg | G2_Knck_Abs01 | G2_Knck_Abs02 | G2_Knck_Abs03 | G2_Knck_Abs04 | G2_Knck_Abs05 | G2_Knck_Abs06 | G2_Knck_Abs07 | G2_Knck_Abs08 | G2_Knck_Abs09 | G2_Knck_Abs10 | G2_Knck_Abs11 | G2_Knck_Abs12 | G2_Knck_Abs13 | G2_Knck_Abs14 | G2_Knck_Abs15 | G2_Knck_Abs16 | G2_Knck_Abs17 | G2_Knck_Abs18 | G2_Knck_Abs19 | G2_Knck_Abs20 | G2_Knck_Rel01 | G2_Knck_Rel02 | G2_Knck_Rel03 | G2_Knck_Rel04 | G2_Knck_Rel05 | G2_Knck_Rel06 | G2_Knck_Rel07 | G2_Knck_Rel08 | G2_Knck_Rel09 | G2_Knck_Rel10 | G2_Knck_Rel11 | G2_Knck_Rel12 | G2_Knck_Rel13 | G2_Knck_Rel14 | G2_Knck_Rel15 | G2_Knck_Rel16 | G2_Knck_Rel17 | G2_Knck_Rel18 | G2_Knck_Rel19 | G2_Knck_Rel20 | gas_qualmix | gas_type | Gasmixer_AirThrot | Gasmixer_AirThrotEnc1 | Gasmixer_AirThrotEnc2 | Gasmixer_GasMix1Pos | Gasmixer_GasMix2Pos | Gasmixer_GasThrot | gastrain_icnt_gas_normm3 | gastrain_icnt_gas_opm3 | GasTrain_PressBaro | GasTrain_PressMain | gastrain_rpr_gr_avg | GasTrain_TempMain | Gen2_ContGen | generator_boilskid_fan_dem | generator_rflow_oilskid_de | generator_rflow_oilskid_nde | generator_rlev_oilskid_tank | generator_rpr_oilskid_hp_de | generator_rpr_oilskid_hp_nde | generator_rt_oilskid_tank | Generator_TempBear1 | Generator_TempBear2 | Generator_TempInlet | Generator_TempOutlet | Generator_TempWind1 | Generator_TempWind2 | Generator_TempWind3 | Generator_VoltExit | Geno_BearingTempMeasured_DriveEnd | Geno_BearingTempMeasured_NonDriveEnd | Geno_BearingTempPrediction_DriveEnd | Geno_BearingTempPrediction_NonDriveEnd | Genset_Oph_Recalculation_Start_Point | GenSet_OpHour_Fixed_Timestamp | GenSet_OpHours_Backup | halio_power_apparent_s | halio_power_fact_cos_phi | halio_rf_mmd | halio_rf_mmd_2 | halio_ru_bus_l1_2 | halio_ru_bus_l1n | halio_ru_bus_l2_3 | halio_ru_bus_l2n | halio_ru_bus_l3_1 | halio_ru_bus_l3n | halio_ru_l1_2 | halio_ru_l1n | halio_ru_l2_3 | halio_ru_l2n | halio_ru_l3_1 | halio_ru_l3n | heatingcooling_rt_ecwbeng | Hyd_OilCount_Trend_ActiveEnergy | Hyd_OilCount_Trend_AvgPower | Hyd_OilCount_Trend_DeltaOpH | Hyd_OilCount_Trend_OilConsumption | Hyd_OilCount_Trend_OilVolume | Hyd_PressCoolWat | Hyd_PressCrankCase | Hyd_PressOil | Hyd_PressOilDif | Hyd_PressOilDif1 | Hyd_PressTCOilFiltIn | Hyd_TempCoolWat | Hyd_TempOil | Hyd_TempOilPumpOut | Hyd_TempWatRet | Hyd_TempWatRetCoolOut | Hyd_TempWatRetPreEng | iDays_SinceStart | Ignition_IC_HW_Vers | Ignition_IC_SW_Vers | Ignition_ITPAvg | Ignition_ITPCyl01 | Ignition_ITPCyl02 | Ignition_ITPCyl03 | Ignition_ITPCyl04 | Ignition_ITPCyl05 | Ignition_ITPCyl06 | Ignition_ITPCyl07 | Ignition_ITPCyl08 | Ignition_ITPCyl09 | Ignition_ITPCyl10 | Ignition_ITPCyl11 | Ignition_ITPCyl12 | Ignition_ITPCyl13 | Ignition_ITPCyl14 | Ignition_ITPCyl15 | Ignition_ITPCyl16 | Ignition_ITPCyl17 | Ignition_ITPCyl18 | Ignition_ITPCyl19 | Ignition_ITPCyl20 | Ignition_ITPCyl21 | Ignition_ITPCyl22 | Ignition_ITPCyl23 | Ignition_ITPCyl24 | Ignition_SAFI_ElectTemp1 | Ignition_SAFI_ElectTemp10 | Ignition_SAFI_ElectTemp11 | Ignition_SAFI_ElectTemp12 | Ignition_SAFI_ElectTemp2 | Ignition_SAFI_ElectTemp3 | Ignition_SAFI_ElectTemp4 | Ignition_SAFI_ElectTemp5 | Ignition_SAFI_ElectTemp6 | Ignition_SAFI_ElectTemp7 | Ignition_SAFI_ElectTemp8 | Ignition_SAFI_ElectTemp9 | Ignition_SAFI_FilterVers1 | Ignition_SAFI_FilterVers10 | Ignition_SAFI_FilterVers11 | Ignition_SAFI_FilterVers12 | Ignition_SAFI_FilterVers2 | Ignition_SAFI_FilterVers3 | Ignition_SAFI_FilterVers4 | Ignition_SAFI_FilterVers5 | Ignition_SAFI_FilterVers6 | Ignition_SAFI_FilterVers7 | Ignition_SAFI_FilterVers8 | Ignition_SAFI_FilterVers9 | Ignition_SAFI_HW_Vers1 | Ignition_SAFI_HW_Vers10 | Ignition_SAFI_HW_Vers11 | Ignition_SAFI_HW_Vers12 | Ignition_SAFI_HW_Vers2 | Ignition_SAFI_HW_Vers3 | Ignition_SAFI_HW_Vers4 | Ignition_SAFI_HW_Vers5 | Ignition_SAFI_HW_Vers6 | Ignition_SAFI_HW_Vers7 | Ignition_SAFI_HW_Vers8 | Ignition_SAFI_HW_Vers9 | Ignition_SAFI_HWOpt_Vers1 | Ignition_SAFI_HWOpt_Vers10 | Ignition_SAFI_HWOpt_Vers11 | Ignition_SAFI_HWOpt_Vers12 | Ignition_SAFI_HWOpt_Vers2 | Ignition_SAFI_HWOpt_Vers3 | Ignition_SAFI_HWOpt_Vers4 | Ignition_SAFI_HWOpt_Vers5 | Ignition_SAFI_HWOpt_Vers6 | Ignition_SAFI_HWOpt_Vers7 | Ignition_SAFI_HWOpt_Vers8 | Ignition_SAFI_HWOpt_Vers9 | Ignition_SAFI_OpHours1 | Ignition_SAFI_OpHours10 | Ignition_SAFI_OpHours11 | Ignition_SAFI_OpHours12 | Ignition_SAFI_OpHours2 | Ignition_SAFI_OpHours3 | Ignition_SAFI_OpHours4 | Ignition_SAFI_OpHours5 | Ignition_SAFI_OpHours6 | Ignition_SAFI_OpHours7 | Ignition_SAFI_OpHours8 | Ignition_SAFI_OpHours9 | Ignition_SAFI_ProdDate1 | Ignition_SAFI_ProdDate10 | Ignition_SAFI_ProdDate10_day | Ignition_SAFI_ProdDate10_mon | Ignition_SAFI_ProdDate11 | Ignition_SAFI_ProdDate11_day | Ignition_SAFI_ProdDate11_mon | Ignition_SAFI_ProdDate12 | Ignition_SAFI_ProdDate12_day | Ignition_SAFI_ProdDate12_mon | Ignition_SAFI_ProdDate1_day | Ignition_SAFI_ProdDate1_mon | Ignition_SAFI_ProdDate2 | Ignition_SAFI_ProdDate2_day | Ignition_SAFI_ProdDate2_mon | Ignition_SAFI_ProdDate3 | Ignition_SAFI_ProdDate3_day | Ignition_SAFI_ProdDate3_mon | Ignition_SAFI_ProdDate4 | Ignition_SAFI_ProdDate4_day | Ignition_SAFI_ProdDate4_mon | Ignition_SAFI_ProdDate5 | Ignition_SAFI_ProdDate5_day | Ignition_SAFI_ProdDate5_mon | Ignition_SAFI_ProdDate6 | Ignition_SAFI_ProdDate6_day | Ignition_SAFI_ProdDate6_mon | Ignition_SAFI_ProdDate7 | Ignition_SAFI_ProdDate7_day | Ignition_SAFI_ProdDate7_mon | Ignition_SAFI_ProdDate8 | Ignition_SAFI_ProdDate8_day | Ignition_SAFI_ProdDate8_mon | Ignition_SAFI_ProdDate9 | Ignition_SAFI_ProdDate9_day | Ignition_SAFI_ProdDate9_mon | Ignition_SAFI_SerialNr1 | Ignition_SAFI_SerialNr10 | Ignition_SAFI_SerialNr11 | Ignition_SAFI_SerialNr12 | Ignition_SAFI_SerialNr2 | Ignition_SAFI_SerialNr3 | Ignition_SAFI_SerialNr4 | Ignition_SAFI_SerialNr5 | Ignition_SAFI_SerialNr6 | Ignition_SAFI_SerialNr7 | Ignition_SAFI_SerialNr8 | Ignition_SAFI_SerialNr9 | Ignition_SAFI_SW_Vers1 | Ignition_SAFI_SW_Vers10 | Ignition_SAFI_SW_Vers11 | Ignition_SAFI_SW_Vers12 | Ignition_SAFI_SW_Vers2 | Ignition_SAFI_SW_Vers3 | Ignition_SAFI_SW_Vers4 | Ignition_SAFI_SW_Vers5 | Ignition_SAFI_SW_Vers6 | Ignition_SAFI_SW_Vers7 | Ignition_SAFI_SW_Vers8 | Ignition_SAFI_SW_Vers9 | Ignition_SAFI_TeethError1 | Ignition_SAFI_TeethError10 | Ignition_SAFI_TeethError11 | Ignition_SAFI_TeethError12 | Ignition_SAFI_TeethError2 | Ignition_SAFI_TeethError3 | Ignition_SAFI_TeethError4 | Ignition_SAFI_TeethError5 | Ignition_SAFI_TeethError6 | Ignition_SAFI_TeethError7 | Ignition_SAFI_TeethError8 | Ignition_SAFI_TeethError9 | iSA_PICurGrad01 | iSA_PICurGrad02 | iSA_PICurGrad03 | iSA_PICurGrad04 | iSA_PICurGrad05 | iSA_PICurGrad06 | iSA_PICurGrad07 | iSA_PICurGrad08 | iSA_PICurGrad09 | iSA_PICurGrad10 | iSA_PICurGrad11 | iSA_PICurGrad12 | iSA_PICurGrad13 | iSA_PICurGrad14 | iSA_PICurGrad15 | iSA_PICurGrad16 | iSA_PICurGrad17 | iSA_PICurGrad18 | iSA_PICurGrad19 | iSA_PICurGrad20 | Issue_Eng_OpHour | Issue_GenSet_OpHour | item_count | Knock_KLS90_CurrSensor1 | Knock_KLS90_CurrSensor2 | Knock_KLS98_IntKnock_Cyl01 | Knock_KLS98_IntKnock_Cyl02 | Knock_KLS98_IntKnock_Cyl03 | Knock_KLS98_IntKnock_Cyl04 | Knock_KLS98_IntKnock_Cyl05 | Knock_KLS98_IntKnock_Cyl06 | Knock_KLS98_IntKnock_Cyl07 | Knock_KLS98_IntKnock_Cyl08 | Knock_KLS98_IntKnock_Cyl09 | Knock_KLS98_IntKnock_Cyl10 | Knock_KLS98_IntKnock_Cyl11 | Knock_KLS98_IntKnock_Cyl12 | Knock_KLS98_IntKnock_Cyl13 | Knock_KLS98_IntKnock_Cyl14 | Knock_KLS98_IntKnock_Cyl15 | Knock_KLS98_IntKnock_Cyl16 | Knock_KLS98_IntKnock_Cyl17 | Knock_KLS98_IntKnock_Cyl18 | Knock_KLS98_IntKnock_Cyl19 | Knock_KLS98_IntKnock_Cyl20 | Knock_KLS98_IntKnock_Cyl21 | Knock_KLS98_IntKnock_Cyl22 | Knock_KLS98_IntKnock_Cyl23 | Knock_KLS98_IntKnock_Cyl24 | Knock_KLS98_Knock_Cyl01 | Knock_KLS98_Knock_Cyl02 | Knock_KLS98_Knock_Cyl03 | Knock_KLS98_Knock_Cyl04 | Knock_KLS98_Knock_Cyl05 | Knock_KLS98_Knock_Cyl06 | Knock_KLS98_Knock_Cyl07 | Knock_KLS98_Knock_Cyl08 | Knock_KLS98_Knock_Cyl09 | Knock_KLS98_Knock_Cyl10 | Knock_KLS98_Knock_Cyl11 | Knock_KLS98_Knock_Cyl12 | Knock_KLS98_Knock_Cyl13 | Knock_KLS98_Knock_Cyl14 | Knock_KLS98_Knock_Cyl15 | Knock_KLS98_Knock_Cyl16 | Knock_KLS98_Knock_Cyl17 | Knock_KLS98_Knock_Cyl18 | Knock_KLS98_Knock_Cyl19 | Knock_KLS98_Knock_Cyl20 | Knock_KLS98_Knock_Cyl21 | Knock_KLS98_Knock_Cyl22 | Knock_KLS98_Knock_Cyl23 | Knock_KLS98_Knock_Cyl24 | Knock_KLS98_SW_Vers | Knock_PBC_KnockPress_Avg | Knock_PBC_KnockPress_Cyl01 | Knock_PBC_KnockPress_Cyl02 | Knock_PBC_KnockPress_Cyl03 | Knock_PBC_KnockPress_Cyl04 | Knock_PBC_KnockPress_Cyl05 | Knock_PBC_KnockPress_Cyl06 | Knock_PBC_KnockPress_Cyl07 | Knock_PBC_KnockPress_Cyl08 | Knock_PBC_KnockPress_Cyl09 | Knock_PBC_KnockPress_Cyl10 | Knock_PBC_KnockPress_Cyl11 | Knock_PBC_KnockPress_Cyl12 | Knock_PBC_KnockPress_Cyl13 | Knock_PBC_KnockPress_Cyl14 | Knock_PBC_KnockPress_Cyl15 | Knock_PBC_KnockPress_Cyl16 | Knock_PBC_KnockPress_Cyl17 | Knock_PBC_KnockPress_Cyl18 | Knock_PBC_KnockPress_Cyl19 | Knock_PBC_KnockPress_Cyl20 | Knock_PBC_KnockPress_Cyl21 | Knock_PBC_KnockPress_Cyl22 | Knock_PBC_KnockPress_Cyl23 | Knock_PBC_KnockPress_Cyl24 | Knock_PBC_KnockPress_Max | Knock_PBC_KnockPress_Min | Knock_PBC_PMax_Avg | Knock_PBC_PMax_Cyl01 | Knock_PBC_PMax_Cyl02 | Knock_PBC_PMax_Cyl03 | Knock_PBC_PMax_Cyl04 | Knock_PBC_PMax_Cyl05 | Knock_PBC_PMax_Cyl06 | Knock_PBC_PMax_Cyl07 | Knock_PBC_PMax_Cyl08 | Knock_PBC_PMax_Cyl09 | Knock_PBC_PMax_Cyl10 | Knock_PBC_PMax_Cyl11 | Knock_PBC_PMax_Cyl12 | Knock_PBC_PMax_Cyl13 | Knock_PBC_PMax_Cyl14 | Knock_PBC_PMax_Cyl15 | Knock_PBC_PMax_Cyl16 | Knock_PBC_PMax_Cyl17 | Knock_PBC_PMax_Cyl18 | Knock_PBC_PMax_Cyl19 | Knock_PBC_PMax_Cyl20 | Knock_PBC_PMax_Cyl21 | Knock_PBC_PMax_Cyl22 | Knock_PBC_PMax_Cyl23 | Knock_PBC_PMax_Cyl24 | Knock_PBC_PMax_Max | Knock_PBC_PMax_Min | Knock_Valve_Noise_Cyl01 | Knock_Valve_Noise_Cyl02 | Knock_Valve_Noise_Cyl03 | Knock_Valve_Noise_Cyl04 | Knock_Valve_Noise_Cyl05 | Knock_Valve_Noise_Cyl06 | Knock_Valve_Noise_Cyl07 | Knock_Valve_Noise_Cyl08 | Knock_Valve_Noise_Cyl09 | Knock_Valve_Noise_Cyl10 | Knock_Valve_Noise_Cyl11 | Knock_Valve_Noise_Cyl12 | Knock_Valve_Noise_Cyl13 | Knock_Valve_Noise_Cyl14 | Knock_Valve_Noise_Cyl15 | Knock_Valve_Noise_Cyl16 | Knock_Valve_Noise_Cyl17 | Knock_Valve_Noise_Cyl18 | Knock_Valve_Noise_Cyl19 | Knock_Valve_Noise_Cyl20 | Knock_Valve_Noise_Cyl21 | Knock_Valve_Noise_Cyl22 | Knock_Valve_Noise_Cyl23 | Knock_Valve_Noise_Cyl24 | Leanox_P2Error | Leanox_P2Set | Leanox_RatioMix | LVRT_Events | manualdata_valverecession_EngineOpH | manualdata_valverecession_EngineStarts | manualdata_valverecession_lev_cyl01 | manualdata_valverecession_lev_cyl02 | manualdata_valverecession_lev_cyl03 | manualdata_valverecession_lev_cyl04 | manualdata_valverecession_lev_cyl05 | manualdata_valverecession_lev_cyl06 | manualdata_valverecession_lev_cyl07 | manualdata_valverecession_lev_cyl08 | manualdata_valverecession_lev_cyl09 | manualdata_valverecession_lev_cyl10 | manualdata_valverecession_lev_cyl11 | manualdata_valverecession_lev_cyl12 | manualdata_valverecession_lev_cyl13 | manualdata_valverecession_lev_cyl14 | manualdata_valverecession_lev_cyl15 | manualdata_valverecession_lev_cyl16 | manualdata_valverecession_lev_cyl17 | manualdata_valverecession_lev_cyl18 | manualdata_valverecession_lev_cyl19 | manualdata_valverecession_lev_cyl20 | manualdata_valverecession_lev_cyl21 | manualdata_valverecession_lev_cyl22 | manualdata_valverecession_lev_cyl23 | manualdata_valverecession_lev_cyl24 | manualdata_valverecession_liv_cyl01 | manualdata_valverecession_liv_cyl02 | manualdata_valverecession_liv_cyl03 | manualdata_valverecession_liv_cyl04 | manualdata_valverecession_liv_cyl05 | manualdata_valverecession_liv_cyl06 | manualdata_valverecession_liv_cyl07 | manualdata_valverecession_liv_cyl08 | manualdata_valverecession_liv_cyl09 | manualdata_valverecession_liv_cyl10 | manualdata_valverecession_liv_cyl11 | manualdata_valverecession_liv_cyl12 | manualdata_valverecession_liv_cyl13 | manualdata_valverecession_liv_cyl14 | manualdata_valverecession_liv_cyl15 | manualdata_valverecession_liv_cyl16 | manualdata_valverecession_liv_cyl17 | manualdata_valverecession_liv_cyl18 | manualdata_valverecession_liv_cyl19 | manualdata_valverecession_liv_cyl20 | manualdata_valverecession_liv_cyl21 | manualdata_valverecession_liv_cyl22 | manualdata_valverecession_liv_cyl23 | manualdata_valverecession_liv_cyl24 | manualdata_valverecession_rev_cyl01 | manualdata_valverecession_rev_cyl02 | manualdata_valverecession_rev_cyl03 | manualdata_valverecession_rev_cyl04 | manualdata_valverecession_rev_cyl05 | manualdata_valverecession_rev_cyl06 | manualdata_valverecession_rev_cyl07 | manualdata_valverecession_rev_cyl08 | manualdata_valverecession_rev_cyl09 | manualdata_valverecession_rev_cyl10 | manualdata_valverecession_rev_cyl11 | manualdata_valverecession_rev_cyl12 | manualdata_valverecession_rev_cyl13 | manualdata_valverecession_rev_cyl14 | manualdata_valverecession_rev_cyl15 | manualdata_valverecession_rev_cyl16 | manualdata_valverecession_rev_cyl17 | manualdata_valverecession_rev_cyl18 | manualdata_valverecession_rev_cyl19 | manualdata_valverecession_rev_cyl20 | manualdata_valverecession_rev_cyl21 | manualdata_valverecession_rev_cyl22 | manualdata_valverecession_rev_cyl23 | manualdata_valverecession_rev_cyl24 | manualdata_valverecession_riv_cyl01 | manualdata_valverecession_riv_cyl02 | manualdata_valverecession_riv_cyl03 | manualdata_valverecession_riv_cyl04 | manualdata_valverecession_riv_cyl05 | manualdata_valverecession_riv_cyl06 | manualdata_valverecession_riv_cyl07 | manualdata_valverecession_riv_cyl08 | manualdata_valverecession_riv_cyl09 | manualdata_valverecession_riv_cyl10 | manualdata_valverecession_riv_cyl11 | manualdata_valverecession_riv_cyl12 | manualdata_valverecession_riv_cyl13 | manualdata_valverecession_riv_cyl14 | manualdata_valverecession_riv_cyl15 | manualdata_valverecession_riv_cyl16 | manualdata_valverecession_riv_cyl17 | manualdata_valverecession_riv_cyl18 | manualdata_valverecession_riv_cyl19 | manualdata_valverecession_riv_cyl20 | manualdata_valverecession_riv_cyl21 | manualdata_valverecession_riv_cyl22 | manualdata_valverecession_riv_cyl23 | manualdata_valverecession_riv_cyl24 | MMD_CountEnergAct | MMD_CountEnergActReturn | MMD_CountEnergReact | MMD_CountEnergReactReturn | MMD_CurrAvg | MMD_HW_Vers1 | MMD_HW_Vers2 | MMD_PowerReact | MMD_SW_Vers1 | MMD_SW_Vers2 | MMD_VoltAvg | Module_Vers_AmmBase | Module_Vers_AuxiliariesGeneral | Module_Vers_CBM | Module_Vers_ChargingUnit | Module_Vers_Coupling | Module_Vers_Customized | Module_Vers_Emission | Module_Vers_EngineController | Module_Vers_EngineGeneral | Module_Vers_Exhaust | Module_Vers_GasMeteringUnit | Module_Vers_Gasmixer | Module_Vers_Gastrain | Module_Vers_Generator | Module_Vers_Grid | Module_Vers_HalIO | Module_Vers_HeatingCooling | Module_Vers_IC | Module_Vers_Ignition | Module_Vers_KLS98 | Module_Vers_Knocking | Module_Vers_MONIC | Module_Vers_NotConnected | Module_Vers_Opstate | Module_Vers_ParaBase | Module_Vers_SAFI | Module_Vers_Synchronization | Module_Vers_ThermalReactor | Module_Vers_Ventilation | Module_Vers_Visu | ModuleNumber | Monic_VoltAvg | Monic_VoltCyl01 | Monic_VoltCyl02 | Monic_VoltCyl03 | Monic_VoltCyl04 | Monic_VoltCyl05 | Monic_VoltCyl06 | Monic_VoltCyl07 | Monic_VoltCyl08 | Monic_VoltCyl09 | Monic_VoltCyl10 | Monic_VoltCyl11 | Monic_VoltCyl12 | Monic_VoltCyl13 | Monic_VoltCyl14 | Monic_VoltCyl15 | Monic_VoltCyl16 | Monic_VoltCyl17 | Monic_VoltCyl18 | Monic_VoltCyl19 | Monic_VoltCyl20 | Monic_VoltCyl21 | Monic_VoltCyl22 | Monic_VoltCyl23 | Monic_VoltCyl24 | Monic_VoltMax | Monic_VoltMin | OFRUL_RUL | oil_amb_temp | oil_cal_zero | oil_condition | oil_fe_bin_cnt_1 | oil_fe_bin_cnt_2 | oil_fe_bin_cnt_3 | oil_fe_bin_cnt_4 | oil_fe_bin_cnt_5 | oil_fe_bin_cnt_6 | oil_fe_bin_cnt_7 | oil_fe_bin_size_1 | oil_fe_bin_size_2 | oil_fe_bin_size_3 | oil_fe_bin_size_4 | oil_fe_bin_size_5 | oil_fe_bin_size_6 | oil_fe_bin_size_7 | oil_fe_mass | oil_gastops_status | oil_hw_version | oil_max_amb_temp | oil_nfe_bin_cnt_1 | oil_nfe_bin_cnt_2 | oil_nfe_bin_cnt_3 | oil_nfe_bin_cnt_4 | oil_nfe_bin_cnt_5 | oil_nfe_bin_cnt_6 | oil_nfe_bin_cnt_7 | oil_node_address | oil_oil_temp | Oil_Remaining_Useful_Life | Oil_Sample_Aluminium | Oil_Sample_Antimony | Oil_Sample_Appearance | Oil_Sample_Barium | Oil_Sample_Booked_In_Date | Oil_Sample_Boron | Oil_Sample_Cadmium | Oil_Sample_Calcium | Oil_Sample_Chromium | Oil_Sample_Colour | Oil_Sample_Conductivity | Oil_Sample_Copper | Oil_Sample_Date_Taken | Oil_Sample_Density15 | Oil_Sample_Glycol | Oil_Sample_Id | Oil_Sample_Insolubles | Oil_Sample_IPH | Oil_Sample_Iron | Oil_Sample_Lab_Memo | Oil_Sample_Lead | Oil_Sample_Magnesium | Oil_Sample_Manganese | Oil_Sample_Molybdenum | Oil_Sample_Nickel | Oil_Sample_Nitration | Oil_Sample_Oil_Added | Oil_Sample_Oil_Condition | Oil_Sample_Oil_Hours | Oil_Sample_Oxidation | Oil_Sample_Phosphorus | Oil_Sample_Potassium | Oil_Sample_Receipt_Date | Oil_Sample_Silicon | Oil_Sample_Silver | Oil_Sample_Sodium | Oil_Sample_TAN | Oil_Sample_TBN | Oil_Sample_Ticket_Number | Oil_Sample_Tin | Oil_Sample_Titanium | Oil_Sample_Unit_Hours | Oil_Sample_Vanadium | Oil_Sample_Viscosity100 | Oil_Sample_Viscosity40 | Oil_Sample_Water | Oil_Sample_Zinc | oil_serial_number | oil_serial_number_hi | oil_serial_type | oil_sw_version | OperationalCondition | OperationalConditionNumeric | OperationalState | OpH_Jumps | OpH_Spikes | OpHours_BackUp_Counter | OPHSR_calc_OphToStart | opstate_iidx_omss | opstate_iidx_rss | out_ha_rf_mmd_busbar_1 | out_ha_rf_mmd_synch1_1 | out_ha_rf_mmd_synch1_2 | out_ha_rf_mmd_synch2_1 | out_ha_rf_mmd_synch2_2 | p_reddelta_ch4_norm | p_reddelta_ch_t1hp_norm | p_reddelta_cospctr_f_norm | p_reddelta_cospctr_t_norm | p_reddelta_cospctr_u_norm | p_reddelta_cv_norm | p_reddelta_egt_norm | p_reddelta_eta_gen_norm | p_reddelta_evu_norm | p_reddelta_gaspr_norm | p_reddelta_hictr_norm | p_reddelta_hum_norm | p_reddelta_knck_opti_norm | p_reddelta_leanox_norm | p_reddelta_pbc_norm | p_reddelta_pr_cc_norm | p_reddelta_pr_gr_norm | p_reddelta_pr_pcgt_norm | p_reddelta_suctpr_norm | p_reddelta_t_ecw_norm | p_reddelta_t_genairin_norm | p_reddelta_t_genswitchcab_norm | p_reddelta_t_hwr_norm | p_reddelta_t_inairer_norm | p_reddelta_t_oil_norm | p_reddelta_t_transformer_norm | p_reddelta_tc_norm | p_unred | Para_Aux_AirStart_HysMaxInlet | Para_Aux_AirStart_HysMin1 | Para_Aux_AirStart_HysMinInlet | Para_Aux_AirStart_LimitMaxInlet | Para_Aux_AirStart_LimitMin1 | Para_Aux_AirStart_LimitMinInlet | Para_Aux_AirStart_N_AirStarter_Exist | Para_Aux_AirStart_Pr_AirStarter_Supply_Exist | Para_Aux_AirStart_Pr_AirStarter_Supply_HiHi | Para_Aux_AirStart_Pr_AirStarter_Supply_LoLo | Para_Aux_AirStart_Pr_AirStarter_SupplyScalMax | Para_Aux_AirStart_Pr_AirStarter_SupplyScalMin | Para_Aux_AirStart_Pr_AirStarter_Tank_Exist | Para_Aux_AirStart_Pr_AirStarter_Tank_Lo | Para_Aux_AirStart_Pr_AirStarter_TankScalMax | Para_Aux_AirStart_Pr_AirStarter_TankScalMin | Para_Aux_AirStart_StartTime | Para_Aux_AirStart_tiAirStarter_OnTime | Para_Aux_AuxChC_Visible | Para_Aux_BarometricPress_Pr_Baro_Exist | Para_Aux_BarometricPress_Pr_Baro_site | Para_Aux_BarometricPress_Pr_Baro_siteDevMax | Para_Aux_BHV_Active | Para_Aux_BoP_BOP_ChCoolCirc_Act | Para_Aux_BoP_BOP_EmCoolCirc_Act | Para_Aux_BoP_BOP_ERVent_Act | Para_Aux_BoP_BOP_ExhGasSys_Act | Para_Aux_BoP_BOP_HeatCirc_Act | Para_Aux_BoP_BOP_MainGasPrep_Act | Para_Aux_CDP_Active | Para_Aux_ChargeCooler_ChC_CtrNum | Para_Aux_ChargeCooler_CHC_Heating_active | Para_Aux_ChargeCooler_ChC_NumDemAux | Para_Aux_ChargeCooler_ChC_NumStages | Para_Aux_ChargeCooler_ChC_OpMode | Para_Aux_ChargeCooler_ChC_ValPosHyHi_On | Para_Aux_ChargeCooler_ChC_ValPosLimHi_On | Para_Aux_ChargeCooler_ChC_ValPosLimStageDown | Para_Aux_ChargeCooler_ChC_ValPosLimStageUp | Para_Aux_ChargeCooler_tiChC_DelayOff | Para_Aux_ChargeCooler_tiChC_DelayStageDown | Para_Aux_ChargeCooler_tiChC_DelayStageUp | Para_Aux_DumpRad_DelaySwitchOffCooler | Para_Aux_DumpRad_DelaySwitchOffRadStep | Para_Aux_DumpRad_DelaySwitchOnRadStep | Para_Aux_DumpRad_EC_St1onlyP | Para_Aux_DumpRad_HysSwitchOnCooler | Para_Aux_DumpRad_LimitSwitchOffRadStepPos | Para_Aux_DumpRad_LimitSwitchOnCooler | Para_Aux_DumpRad_LimitSwitchOnRadStepPos | Para_Aux_DumpRad_NumbAll | Para_Aux_DumpRad_NumbAux | Para_Aux_DumpRad_SelectCtr | Para_Aux_DumpRad_Type | Para_Aux_FireProtFlap1_InlAir_visible | Para_Aux_FireProtFlap1_OutlAir_visible | Para_Aux_FireProtFlap2_InlAir_visible | Para_Aux_FireProtFlap2_OutlAir_visible | Para_Aux_FreshOilPump_tiFreshOilPump_RTC_Time | Para_Aux_GasRail_ActBlowOffDiffPressMax | Para_Aux_GasRail_AirPressCorr | Para_Aux_GasRail_BlowOffValveOnTimeMax | Para_Aux_GasRail_BlowOffValveOnTimeMin | Para_Aux_GasRail_ChargePress1 | Para_Aux_GasRail_ChargePress2 | Para_Aux_GasRail_DiffPress1 | Para_Aux_GasRail_DiffPress2 | Para_Aux_GasRail_HysBlowOffDiffMax | Para_Aux_GasRail_LimitBlowOffDiffMax | Para_Aux_GasRail_LimitPressHigh | Para_Aux_GasRail_LimitPressLow | Para_Aux_GasRail_PressCtrAdjBoost | Para_Aux_GasRail_RampSetPressChange | Para_Aux_GasRail_SetPressFix | Para_Aux_GasRail_SetPressFixTime | Para_Aux_GasRail_SetPressRangeBegin | Para_Aux_GasRail_SetPressRangeEnd | Para_Aux_GasRail_SpeedLimitValveClose | Para_Aux_GasTrain1_ActMeasure | Para_Aux_GasTrain1_HysMax1 | Para_Aux_GasTrain1_HysMax2 | Para_Aux_GasTrain1_HysMin1 | Para_Aux_GasTrain1_HysMin2 | Para_Aux_GasTrain1_LimitMax1 | Para_Aux_GasTrain1_LimitMax2 | Para_Aux_GasTrain1_LimitMin1 | Para_Aux_GasTrain1_LimitMin2 | Para_Aux_GasTrain1_Range20mA | Para_Aux_GasTrain1_Range4mA | Para_Aux_HWF_Active | Para_Aux_IntakeAir_HysOpenInLouv | Para_Aux_IntakeAir_HysStartInVent | Para_Aux_IntakeAir_LimitOpenInLouv | Para_Aux_IntakeAir_LimitStartInVent | Para_Aux_IntakeAir_TempIntakeAirWarn | Para_Aux_IntakeAirPress_ActMeasure | Para_Aux_IntakeAirPress_HysMax1 | Para_Aux_IntakeAirPress_HysMin1 | Para_Aux_IntakeAirPress_LimitMax1 | Para_Aux_IntakeAirPress_LimitMin1 | Para_Aux_IntakeAirPress_Range20mA | Para_Aux_IntakeAirPress_Range4mA | Para_Aux_ManOpMode_ManAuxCtr_Active | Para_Aux_ManOpMode_tiManAuxCtr_Max | Para_Aux_OutAirER_Fan_FU | Para_Aux_OutDoor_Hys1 | Para_Aux_OutDoor_Hys2 | Para_Aux_OutDoor_Hys3 | Para_Aux_OutDoor_Hys4 | Para_Aux_OutDoor_Limit1 | Para_Aux_OutDoor_Limit2 | Para_Aux_OutDoor_Limit3 | Para_Aux_OutDoor_Limit4 | Para_Aux_PreChambDifPress_ActMeasure | Para_Aux_PreChambDifPress_HysMax | Para_Aux_PreChambDifPress_HysMin | Para_Aux_PreChambDifPress_LimitMax | Para_Aux_PreChambDifPress_LimitMaxP1 | Para_Aux_PreChambDifPress_LimitMaxP2 | Para_Aux_PreChambDifPress_LimitMin | Para_Aux_PreChambDifPress_LimitMinP1 | Para_Aux_PreChambDifPress_LimitMinP2 | Para_Aux_PreChambDifPress_Range20mA | Para_Aux_PreChambDifPress_Range4mA | Para_Aux_PreChambDifPress_SwitchPointHysMax | Para_Aux_PreChambDifPress_SwitchPointLimitMax | Para_Aux_PreChambGasComp_CompOff | Para_Aux_PreChambGasComp_CompOn | Para_Aux_PreChambGasComp_Max | Para_Aux_PreChambGasComp_MaxHys | Para_Aux_PreChambGasComp_Min | Para_Aux_PreChambGasComp_MinHys | Para_Aux_PreChambGasComp_Pr_PCGComp_Active | Para_Aux_PreChambGasTrain_ActMeasure | Para_Aux_PreChambGasTrain_ActMeasureTemp | Para_Aux_PreChambGasTrain_BoostPress1 | Para_Aux_PreChambGasTrain_BoostPress2 | Para_Aux_PreChambGasTrain_DiffPress1 | Para_Aux_PreChambGasTrain_DiffPress2 | Para_Aux_PreChambGasTrain_HysMax1 | Para_Aux_PreChambGasTrain_HysMax2 | Para_Aux_PreChambGasTrain_HysMin | Para_Aux_PreChambGasTrain_HysMin2 | Para_Aux_PreChambGasTrain_LimitMax1 | Para_Aux_PreChambGasTrain_LimitMax2 | Para_Aux_PreChambGasTrain_LimitMin | Para_Aux_PreChambGasTrain_LimitMin2 | Para_Aux_PreChambGasTrain_RampSetPressChange | Para_Aux_PreChambGasTrain_Range20mA | Para_Aux_PreChambGasTrain_Range4mA | Para_Aux_PreChambGasTrain_RangeBeginSetPress | Para_Aux_PreChambGasTrain_RangeEndSetPress | Para_Aux_PreChambGasTrain_SigAdjustBoost | Para_Aux_RoomVent_Act_ERV_AirFlowMon | Para_Aux_RoomVent_ActPurgecycle | Para_Aux_RoomVent_HysMaxRoomTemp | Para_Aux_RoomVent_HysRoomTemp | Para_Aux_RoomVent_HysRTStartVent | Para_Aux_RoomVent_HysRTStartVentStandby | Para_Aux_RoomVent_HysRTVentStep2 | Para_Aux_RoomVent_LimitRoomTemp | Para_Aux_RoomVent_LimitRTStartVent | Para_Aux_RoomVent_LimitRTStartVentStandby | Para_Aux_RoomVent_LimitRTVentStep2 | Para_Aux_RoomVent_MaxRoomTemp | Para_Aux_RoomVent_PurgeTimeMax | Para_Aux_RoomVent_SetpointRTCtr | Para_Aux_RoomVent_SetpointRTCtrStandby | Para_Aux_Ventilation_CircLouvre_Pos_CircLou1_Active | Para_Aux_Ventilation_CircLouvre_Pos_CircLou1_ScalMax | Para_Aux_Ventilation_CircLouvre_Pos_CircLou1_ScalMin | Para_Aux_Ventilation_CircLouvre_Pos_CircLou2_Active | Para_Aux_Ventilation_CircLouvre_Pos_CircLou2_ScalMax | Para_Aux_Ventilation_CircLouvre_Pos_CircLou2_ScalMin | Para_Aux_Ventilation_CircLouvre_T_InAirER_Rel_CircOp | Para_Aux_Ventilation_CircLouvre_T_InAirER_Rel_CircOp_Hy | Para_Aux_Ventilation_Ctr_RDP_OutlVE_Dep_EngP | Para_Aux_Ventilation_Ctr_RDP_OutlVE_Dep_InlVent | Para_Aux_Ventilation_ER_VentColdCountryMode | Para_Aux_Ventilation_InletLouvre_InlVent_Ctr_InlLou_Active | Para_Aux_Ventilation_InletLouvre_Pos_InlLou1_Active | Para_Aux_Ventilation_InletLouvre_Pos_InlLou1_ScalMax | Para_Aux_Ventilation_InletLouvre_Pos_InlLou1_ScalMin | Para_Aux_Ventilation_InletLouvre_Pos_InlLou2_Active | Para_Aux_Ventilation_InletLouvre_Pos_InlLou2_ScalMax | Para_Aux_Ventilation_InletLouvre_Pos_InlLou2_ScalMin | Para_Aux_Ventilation_InletLouvre_PosLim_InlLou_Rel_ERV | Para_Aux_Ventilation_InletLouvre_PosLim_InlLou_Rel_ERV_Hy | Para_Aux_Ventilation_InletLouvre_PosLim_InlLou_Rel_FC_ER | Para_Aux_Ventilation_InletLouvre_PosLim_InlLou_Rel_FC_ER_Hy | Para_Aux_Ventilation_InletLouvre_TypeCtr_InlLou_ERV | Para_Aux_Ventilation_InletLouvre_TypeFeedback_InlLou_ERV | Para_Aux_Ventilation_Louvers | Para_Aux_Ventilation_OutletLouvre_OutlVent_Ctr_OutlLou_Active | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou1_Active | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou1_ScalMax | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou1_ScalMin | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou2_Active | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou2_ScalMax | Para_Aux_Ventilation_OutletLouvre_Pos_OutlLou2_ScalMin | Para_Aux_Ventilation_OutletLouvre_PosLim_OutlLou_Rel_ERV | Para_Aux_Ventilation_OutletLouvre_PosLim_OutlLou_Rel_ERV_Hy | Para_Aux_Ventilation_OutletLouvre_PosLim_OutlLou_Rel_FC_ER | Para_Aux_Ventilation_OutletLouvre_PosLim_OutlLou_Rel_FC_ER_Hy | Para_Aux_Ventilation_OutletLouvre_TypeCtr_OutlLou_ERV | Para_Aux_Ventilation_OutletLouvre_TypeFeedback_OutlLou_ERV | Para_Aux_Ventilation_PrDiff_ER_Active | Para_Aux_Ventilation_PrDiff_ER_Lim_High | Para_Aux_Ventilation_PrDiff_ER_Lim_High_Hy | Para_Aux_Ventilation_PrDiff_ER_Lim_Low | Para_Aux_Ventilation_PrDiff_ER_Lim_Low_Hy | Para_Aux_Ventilation_PrDiff_ER_ScalMax | Para_Aux_Ventilation_PrDiff_ER_ScalMin | Para_Aux_Ventilation_Purgecycle_Active | Para_Aux_Ventilation_Scal_CtrInlVentER_Set_Max | Para_Aux_Ventilation_Scal_CtrInlVentER_Set_Min | Para_Aux_Ventilation_Scal_OffSetMax_CtrOutlVent | Para_Aux_Ventilation_Scal_OffSetMax_Pel | Para_Aux_Ventilation_Scal_OffSetMin_CtrOutlVent | Para_Aux_Ventilation_Scal_OffSetMin_Pel | Para_Aux_Ventilation_Scal_PmaxEl | Para_Aux_Ventilation_Scal_PminEl | Para_Aux_Ventilation_Vent_SpeedDif | Para_Aux_Ventilation_VISA | Para_base_tvisversion_xx | Para_base_tvisversion_xxbase_tvisversion_yy | Para_Bearing_ConrodAlarm | Para_Bearing_MainLimit | Para_CtrModule_Ctr1_ActStep_NEx | Para_CtrModule_Ctr1_CycleTime | Para_CtrModule_Ctr1_DComp | Para_CtrModule_Ctr1_DCompTune | Para_CtrModule_Ctr1_DCompWMax | Para_CtrModule_Ctr1_DCompWMin | Para_CtrModule_Ctr1_DeadBand | Para_CtrModule_Ctr1_Format | Para_CtrModule_Ctr1_IComp | Para_CtrModule_Ctr1_ICompTune | Para_CtrModule_Ctr1_ICompWMax | Para_CtrModule_Ctr1_ICompWMin | Para_CtrModule_Ctr1_InvertCtrTune | Para_CtrModule_Ctr1_Name | Para_CtrModule_Ctr1_NameF | Para_CtrModule_Ctr1_OptWorkPoint | Para_CtrModule_Ctr1_PComp | Para_CtrModule_Ctr1_PCompTune | Para_CtrModule_Ctr1_PCompWMax | Para_CtrModule_Ctr1_PCompWMin | Para_CtrModule_Ctr1_RangeBegin | Para_CtrModule_Ctr1_RangeEnd | Para_CtrModule_Ctr1_Unit | Para_CtrModule_Ctr1_UserLevelIntExt | Para_CtrModule_Ctr1_UserLevelManAut | Para_CtrModule_Ctr1_UserLevelSet | Para_CtrModule_Ctr1_UserLevelTune | Para_CtrModule_Ctr1_WMax | Para_CtrModule_Ctr1_WMin | Para_CtrModule_Ctr1_WRampNeg | Para_CtrModule_Ctr1_WRampPos | Para_CtrModule_Ctr1_WStart | Para_CtrModule_Ctr1_YBlock | Para_CtrModule_Ctr1_YHl | Para_CtrModule_Ctr1_YMax | Para_CtrModule_Ctr1_YMin | Para_CtrModule_Ctr1_YRampNeg | Para_CtrModule_Ctr1_YRampPos | Para_CtrModule_Ctr1_YRampTune | Para_CtrModule_Ctr2_ActStep_NEx | Para_CtrModule_Ctr2_CycleTime | Para_CtrModule_Ctr2_DComp | Para_CtrModule_Ctr2_DCompTune | Para_CtrModule_Ctr2_DCompWMax | Para_CtrModule_Ctr2_DCompWMin | Para_CtrModule_Ctr2_DeadBand | Para_CtrModule_Ctr2_Format | Para_CtrModule_Ctr2_IComp | Para_CtrModule_Ctr2_ICompTune | Para_CtrModule_Ctr2_ICompWMax | Para_CtrModule_Ctr2_ICompWMin | Para_CtrModule_Ctr2_InvertCtrTune | Para_CtrModule_Ctr2_Name | Para_CtrModule_Ctr2_NameF | Para_CtrModule_Ctr2_OptWorkPoint | Para_CtrModule_Ctr2_PComp | Para_CtrModule_Ctr2_PCompTune | Para_CtrModule_Ctr2_PCompWMax | Para_CtrModule_Ctr2_PCompWMin | Para_CtrModule_Ctr2_RangeBegin | Para_CtrModule_Ctr2_RangeEnd | Para_CtrModule_Ctr2_Unit | Para_CtrModule_Ctr2_UserLevelIntExt | Para_CtrModule_Ctr2_UserLevelManAut | Para_CtrModule_Ctr2_UserLevelSet | Para_CtrModule_Ctr2_UserLevelTune | Para_CtrModule_Ctr2_WMax | Para_CtrModule_Ctr2_WMin | Para_CtrModule_Ctr2_WRampNeg | Para_CtrModule_Ctr2_WRampPos | Para_CtrModule_Ctr2_WStart | Para_CtrModule_Ctr2_YBlock | Para_CtrModule_Ctr2_YHl | Para_CtrModule_Ctr2_YMax | Para_CtrModule_Ctr2_YMin | Para_CtrModule_Ctr2_YRampNeg | Para_CtrModule_Ctr2_YRampPos | Para_CtrModule_Ctr2_YRampTune | Para_CtrModule_Ctr3_ActStep_NEx | Para_CtrModule_Ctr3_CycleTime | Para_CtrModule_Ctr3_DComp | Para_CtrModule_Ctr3_DCompTune | Para_CtrModule_Ctr3_DCompWMax | Para_CtrModule_Ctr3_DCompWMin | Para_CtrModule_Ctr3_DeadBand | Para_CtrModule_Ctr3_Format | Para_CtrModule_Ctr3_IComp | Para_CtrModule_Ctr3_ICompTune | Para_CtrModule_Ctr3_ICompWMax | Para_CtrModule_Ctr3_ICompWMin | Para_CtrModule_Ctr3_InvertCtrTune | Para_CtrModule_Ctr3_Name | Para_CtrModule_Ctr3_NameF | Para_CtrModule_Ctr3_OptWorkPoint | Para_CtrModule_Ctr3_PComp | Para_CtrModule_Ctr3_PCompTune | Para_CtrModule_Ctr3_PCompWMax | Para_CtrModule_Ctr3_PCompWMin | Para_CtrModule_Ctr3_RangeBegin | Para_CtrModule_Ctr3_RangeEnd | Para_CtrModule_Ctr3_Unit | Para_CtrModule_Ctr3_UserLevelIntExt | Para_CtrModule_Ctr3_UserLevelManAut | Para_CtrModule_Ctr3_UserLevelSet | Para_CtrModule_Ctr3_UserLevelTune | Para_CtrModule_Ctr3_WMax | Para_CtrModule_Ctr3_WMin | Para_CtrModule_Ctr3_WRampNeg | Para_CtrModule_Ctr3_WRampPos | Para_CtrModule_Ctr3_WStart | Para_CtrModule_Ctr3_YBlock | Para_CtrModule_Ctr3_YHl | Para_CtrModule_Ctr3_YMax | Para_CtrModule_Ctr3_YMin | Para_CtrModule_Ctr3_YRampNeg | Para_CtrModule_Ctr3_YRampPos | Para_CtrModule_Ctr3_YRampTune | Para_CtrModule_Ctr4_ActStep_NEx | Para_CtrModule_Ctr4_CycleTime | Para_CtrModule_Ctr4_DComp | Para_CtrModule_Ctr4_DCompTune | Para_CtrModule_Ctr4_DCompWMax | Para_CtrModule_Ctr4_DCompWMin | Para_CtrModule_Ctr4_DeadBand | Para_CtrModule_Ctr4_Format | Para_CtrModule_Ctr4_IComp | Para_CtrModule_Ctr4_ICompTune | Para_CtrModule_Ctr4_ICompWMax | Para_CtrModule_Ctr4_ICompWMin | Para_CtrModule_Ctr4_InvertCtrTune | Para_CtrModule_Ctr4_Name | Para_CtrModule_Ctr4_NameF | Para_CtrModule_Ctr4_OptWorkPoint | Para_CtrModule_Ctr4_PComp | Para_CtrModule_Ctr4_PCompTune | Para_CtrModule_Ctr4_PCompWMax | Para_CtrModule_Ctr4_PCompWMin | Para_CtrModule_Ctr4_RangeBegin | Para_CtrModule_Ctr4_RangeEnd | Para_CtrModule_Ctr4_Unit | Para_CtrModule_Ctr4_UserLevelIntExt | Para_CtrModule_Ctr4_UserLevelManAut | Para_CtrModule_Ctr4_UserLevelSet | Para_CtrModule_Ctr4_UserLevelTune | Para_CtrModule_Ctr4_WMax | Para_CtrModule_Ctr4_WMin | Para_CtrModule_Ctr4_WRampNeg | Para_CtrModule_Ctr4_WRampPos | Para_CtrModule_Ctr4_WStart | Para_CtrModule_Ctr4_YBlock | Para_CtrModule_Ctr4_YHl | Para_CtrModule_Ctr4_YMax | Para_CtrModule_Ctr4_YMin | Para_CtrModule_Ctr4_YRampNeg | Para_CtrModule_Ctr4_YRampPos | Para_CtrModule_Ctr4_YRampTune | Para_CtrModule_Ctr5_CycleTime | Para_CtrModule_Ctr5_DComp | Para_CtrModule_Ctr5_DCompTune | Para_CtrModule_Ctr5_DCompWMax | Para_CtrModule_Ctr5_DCompWMin | Para_CtrModule_Ctr5_DeadBand | Para_CtrModule_Ctr5_Format | Para_CtrModule_Ctr5_IComp | Para_CtrModule_Ctr5_ICompTune | Para_CtrModule_Ctr5_ICompWMax | Para_CtrModule_Ctr5_ICompWMin | Para_CtrModule_Ctr5_InvertCtrTune | Para_CtrModule_Ctr5_Name | Para_CtrModule_Ctr5_NameF | Para_CtrModule_Ctr5_OptWorkPoint | Para_CtrModule_Ctr5_PComp | Para_CtrModule_Ctr5_PCompTune | Para_CtrModule_Ctr5_PCompWMax | Para_CtrModule_Ctr5_PCompWMin | Para_CtrModule_Ctr5_RangeBegin | Para_CtrModule_Ctr5_RangeEnd | Para_CtrModule_Ctr5_Unit | Para_CtrModule_Ctr5_UserLevelIntExt | Para_CtrModule_Ctr5_UserLevelManAut | Para_CtrModule_Ctr5_UserLevelSet | Para_CtrModule_Ctr5_UserLevelTune | Para_CtrModule_Ctr5_WMax | Para_CtrModule_Ctr5_WMin | Para_CtrModule_Ctr5_WRampNeg | Para_CtrModule_Ctr5_WRampPos | Para_CtrModule_Ctr5_WStart | Para_CtrModule_Ctr5_YBlock | Para_CtrModule_Ctr5_YHl | Para_CtrModule_Ctr5_YMax | Para_CtrModule_Ctr5_YMin | Para_CtrModule_Ctr5_YRampNeg | Para_CtrModule_Ctr5_YRampPos | Para_CtrModule_Ctr5_YRampTune | Para_CtrModule_Ctr6_CycleTime | Para_CtrModule_Ctr6_DComp | Para_CtrModule_Ctr6_DCompTune | Para_CtrModule_Ctr6_DCompWMax | Para_CtrModule_Ctr6_DCompWMin | Para_CtrModule_Ctr6_DeadBand | Para_CtrModule_Ctr6_Format | Para_CtrModule_Ctr6_IComp | Para_CtrModule_Ctr6_ICompTune | Para_CtrModule_Ctr6_ICompWMax | Para_CtrModule_Ctr6_ICompWMin | Para_CtrModule_Ctr6_InvertCtrTune | Para_CtrModule_Ctr6_Name | Para_CtrModule_Ctr6_NameF | Para_CtrModule_Ctr6_OptWorkPoint | Para_CtrModule_Ctr6_PComp | Para_CtrModule_Ctr6_PCompTune | Para_CtrModule_Ctr6_PCompWMax | Para_CtrModule_Ctr6_PCompWMin | Para_CtrModule_Ctr6_RangeBegin | Para_CtrModule_Ctr6_RangeEnd | Para_CtrModule_Ctr6_Unit | Para_CtrModule_Ctr6_UserLevelIntExt | Para_CtrModule_Ctr6_UserLevelManAut | Para_CtrModule_Ctr6_UserLevelSet | Para_CtrModule_Ctr6_UserLevelTune | Para_CtrModule_Ctr6_WMax | Para_CtrModule_Ctr6_WMin | Para_CtrModule_Ctr6_WRampNeg | Para_CtrModule_Ctr6_WRampPos | Para_CtrModule_Ctr6_WStart | Para_CtrModule_Ctr6_YBlock | Para_CtrModule_Ctr6_YHl | Para_CtrModule_Ctr6_YMax | Para_CtrModule_Ctr6_YMin | Para_CtrModule_Ctr6_YRampNeg | Para_CtrModule_Ctr6_YRampPos | Para_CtrModule_Ctr6_YRampTune | Para_CtrModule_Ctr7_CycleTime | Para_CtrModule_Ctr7_DComp | Para_CtrModule_Ctr7_DCompTune | Para_CtrModule_Ctr7_DCompWMax | Para_CtrModule_Ctr7_DCompWMin | Para_CtrModule_Ctr7_DeadBand | Para_CtrModule_Ctr7_Format | Para_CtrModule_Ctr7_IComp | Para_CtrModule_Ctr7_ICompTune | Para_CtrModule_Ctr7_ICompWMax | Para_CtrModule_Ctr7_ICompWMin | Para_CtrModule_Ctr7_InvertCtrTune | Para_CtrModule_Ctr7_Name | Para_CtrModule_Ctr7_NameF | Para_CtrModule_Ctr7_OptWorkPoint | Para_CtrModule_Ctr7_PComp | Para_CtrModule_Ctr7_PCompTune | Para_CtrModule_Ctr7_PCompWMax | Para_CtrModule_Ctr7_PCompWMin | Para_CtrModule_Ctr7_RangeBegin | Para_CtrModule_Ctr7_RangeEnd | Para_CtrModule_Ctr7_Unit | Para_CtrModule_Ctr7_UserLevelIntExt | Para_CtrModule_Ctr7_UserLevelManAut | Para_CtrModule_Ctr7_UserLevelSet | Para_CtrModule_Ctr7_UserLevelTune | Para_CtrModule_Ctr7_WMax | Para_CtrModule_Ctr7_WMin | Para_CtrModule_Ctr7_WRampNeg | Para_CtrModule_Ctr7_WRampPos | Para_CtrModule_Ctr7_WStart | Para_CtrModule_Ctr7_YBlock | Para_CtrModule_Ctr7_YHl | Para_CtrModule_Ctr7_YMax | Para_CtrModule_Ctr7_YMin | Para_CtrModule_Ctr7_YRampNeg | Para_CtrModule_Ctr7_YRampPos | Para_CtrModule_Ctr7_YRampTune | Para_CtrModule_Ctr8_CycleTime | Para_CtrModule_Ctr8_DComp | Para_CtrModule_Ctr8_DCompTune | Para_CtrModule_Ctr8_DCompWMax | Para_CtrModule_Ctr8_DCompWMin | Para_CtrModule_Ctr8_DeadBand | Para_CtrModule_Ctr8_Format | Para_CtrModule_Ctr8_IComp | Para_CtrModule_Ctr8_ICompTune | Para_CtrModule_Ctr8_ICompWMax | Para_CtrModule_Ctr8_ICompWMin | Para_CtrModule_Ctr8_InvertCtrTune | Para_CtrModule_Ctr8_Name | Para_CtrModule_Ctr8_NameF | Para_CtrModule_Ctr8_OptWorkPoint | Para_CtrModule_Ctr8_PComp | Para_CtrModule_Ctr8_PCompTune | Para_CtrModule_Ctr8_PCompWMax | Para_CtrModule_Ctr8_PCompWMin | Para_CtrModule_Ctr8_RangeBegin | Para_CtrModule_Ctr8_RangeEnd | Para_CtrModule_Ctr8_Unit | Para_CtrModule_Ctr8_UserLevelIntExt | Para_CtrModule_Ctr8_UserLevelManAut | Para_CtrModule_Ctr8_UserLevelSet | Para_CtrModule_Ctr8_UserLevelTune | Para_CtrModule_Ctr8_WMax | Para_CtrModule_Ctr8_WMin | Para_CtrModule_Ctr8_WRampNeg | Para_CtrModule_Ctr8_WRampPos | Para_CtrModule_Ctr8_WStart | Para_CtrModule_Ctr8_YBlock | Para_CtrModule_Ctr8_YHl | Para_CtrModule_Ctr8_YMax | Para_CtrModule_Ctr8_YMin | Para_CtrModule_Ctr8_YRampNeg | Para_CtrModule_Ctr8_YRampPos | Para_CtrModule_Ctr8_YRampTune | Para_CtrModule_CtrX10_CycleTime | Para_CtrModule_CtrX10_DComp | Para_CtrModule_CtrX10_DCompTune | Para_CtrModule_CtrX10_DeadBand | Para_CtrModule_CtrX10_IComp | Para_CtrModule_CtrX10_ICompTune | Para_CtrModule_CtrX10_InvertCtrTune | Para_CtrModule_CtrX10_PComp | Para_CtrModule_CtrX10_PCompTune | Para_CtrModule_CtrX10_RangeBegin | Para_CtrModule_CtrX10_RangeEnd | Para_CtrModule_CtrX10_UserLevelIntExt | Para_CtrModule_CtrX10_UserLevelManAut | Para_CtrModule_CtrX10_UserLevelSet | Para_CtrModule_CtrX10_UserLevelTune | Para_CtrModule_CtrX10_WMax | Para_CtrModule_CtrX10_WMin | Para_CtrModule_CtrX10_WRampNeg | Para_CtrModule_CtrX10_WRampPos | Para_CtrModule_CtrX10_WStart | Para_CtrModule_CtrX10_YBlock | Para_CtrModule_CtrX10_YHl | Para_CtrModule_CtrX10_YMax | Para_CtrModule_CtrX10_YMin | Para_CtrModule_CtrX10_YRampNeg | Para_CtrModule_CtrX10_YRampPos | Para_CtrModule_CtrX10_YRampTune | Para_CtrModule_CtrX11_CycleTime | Para_CtrModule_CtrX11_DComp | Para_CtrModule_CtrX11_DCompTune | Para_CtrModule_CtrX11_DeadBand | Para_CtrModule_CtrX11_IComp | Para_CtrModule_CtrX11_ICompTune | Para_CtrModule_CtrX11_InvertCtrTune | Para_CtrModule_CtrX11_PComp | Para_CtrModule_CtrX11_PCompTune | Para_CtrModule_CtrX11_RangeBegin | Para_CtrModule_CtrX11_RangeEnd | Para_CtrModule_CtrX11_UserLevelIntExt | Para_CtrModule_CtrX11_UserLevelManAut | Para_CtrModule_CtrX11_UserLevelSet | Para_CtrModule_CtrX11_UserLevelTune | Para_CtrModule_CtrX11_WMax | Para_CtrModule_CtrX11_WMin | Para_CtrModule_CtrX11_WRampNeg | Para_CtrModule_CtrX11_WRampPos | Para_CtrModule_CtrX11_WStart | Para_CtrModule_CtrX11_YBlock | Para_CtrModule_CtrX11_YHl | Para_CtrModule_CtrX11_YMax | Para_CtrModule_CtrX11_YMin | Para_CtrModule_CtrX11_YRampNeg | Para_CtrModule_CtrX11_YRampPos | Para_CtrModule_CtrX11_YRampTune | Para_CtrModule_CtrX12_CycleTime | Para_CtrModule_CtrX12_DComp | Para_CtrModule_CtrX12_DCompTune | Para_CtrModule_CtrX12_DeadBand | Para_CtrModule_CtrX12_IComp | Para_CtrModule_CtrX12_ICompTune | Para_CtrModule_CtrX12_InvertCtrTune | Para_CtrModule_CtrX12_PComp | Para_CtrModule_CtrX12_PCompTune | Para_CtrModule_CtrX12_RangeBegin | Para_CtrModule_CtrX12_RangeEnd | Para_CtrModule_CtrX12_UserLevelIntExt | Para_CtrModule_CtrX12_UserLevelManAut | Para_CtrModule_CtrX12_UserLevelSet | Para_CtrModule_CtrX12_UserLevelTune | Para_CtrModule_CtrX12_WMax | Para_CtrModule_CtrX12_WMin | Para_CtrModule_CtrX12_WRampNeg | Para_CtrModule_CtrX12_WRampPos | Para_CtrModule_CtrX12_WStart | Para_CtrModule_CtrX12_YBlock | Para_CtrModule_CtrX12_YHl | Para_CtrModule_CtrX12_YMax | Para_CtrModule_CtrX12_YMin | Para_CtrModule_CtrX12_YRampNeg | Para_CtrModule_CtrX12_YRampPos | Para_CtrModule_CtrX12_YRampTune | Para_CtrModule_CtrX13_CycleTime | Para_CtrModule_CtrX13_DCompTune | Para_CtrModule_CtrX13_DeadBand | Para_CtrModule_CtrX13_ICompTune | Para_CtrModule_CtrX13_InvertCtrTune | Para_CtrModule_CtrX13_PCompTune | Para_CtrModule_CtrX13_RangeBegin | Para_CtrModule_CtrX13_RangeEnd | Para_CtrModule_CtrX13_UserLevelIntExt | Para_CtrModule_CtrX13_UserLevelManAut | Para_CtrModule_CtrX13_UserLevelSet | Para_CtrModule_CtrX13_UserLevelTune | Para_CtrModule_CtrX13_WMax | Para_CtrModule_CtrX13_WMin | Para_CtrModule_CtrX13_WRampNeg | Para_CtrModule_CtrX13_WRampPos | Para_CtrModule_CtrX13_WStart | Para_CtrModule_CtrX13_YBlock | Para_CtrModule_CtrX13_YHl | Para_CtrModule_CtrX13_YMax | Para_CtrModule_CtrX13_YMin | Para_CtrModule_CtrX13_YRampTune | Para_CtrModule_CtrX14_CycleTime | Para_CtrModule_CtrX14_DCompTune | Para_CtrModule_CtrX14_DeadBand | Para_CtrModule_CtrX14_ICompTune | Para_CtrModule_CtrX14_InvertCtrTune | Para_CtrModule_CtrX14_PCompTune | Para_CtrModule_CtrX14_RangeBegin | Para_CtrModule_CtrX14_RangeEnd | Para_CtrModule_CtrX14_UserLevelIntExt | Para_CtrModule_CtrX14_UserLevelManAut | Para_CtrModule_CtrX14_UserLevelSet | Para_CtrModule_CtrX14_UserLevelTune | Para_CtrModule_CtrX14_WMax | Para_CtrModule_CtrX14_WMin | Para_CtrModule_CtrX14_WRampNeg | Para_CtrModule_CtrX14_WRampPos | Para_CtrModule_CtrX14_WStart | Para_CtrModule_CtrX14_YBlock | Para_CtrModule_CtrX14_YHl | Para_CtrModule_CtrX14_YMax | Para_CtrModule_CtrX14_YMin | Para_CtrModule_CtrX14_YRampTune | Para_CtrModule_CtrX15_CycleTime | Para_CtrModule_CtrX15_DCompTune | Para_CtrModule_CtrX15_DeadBand | Para_CtrModule_CtrX15_ICompTune | Para_CtrModule_CtrX15_InvertCtrTune | Para_CtrModule_CtrX15_PCompTune | Para_CtrModule_CtrX15_RangeBegin | Para_CtrModule_CtrX15_RangeEnd | Para_CtrModule_CtrX15_UserLevelIntExt | Para_CtrModule_CtrX15_UserLevelManAut | Para_CtrModule_CtrX15_UserLevelSet | Para_CtrModule_CtrX15_UserLevelTune | Para_CtrModule_CtrX15_WMax | Para_CtrModule_CtrX15_WMin | Para_CtrModule_CtrX15_WRampNeg | Para_CtrModule_CtrX15_WRampPos | Para_CtrModule_CtrX15_WStart | Para_CtrModule_CtrX15_YBlock | Para_CtrModule_CtrX15_YHl | Para_CtrModule_CtrX15_YMax | Para_CtrModule_CtrX15_YMin | Para_CtrModule_CtrX15_YRampTune | Para_CtrModule_CtrX16_CycleTime | Para_CtrModule_CtrX16_DCompTune | Para_CtrModule_CtrX16_DeadBand | Para_CtrModule_CtrX16_ICompTune | Para_CtrModule_CtrX16_InvertCtrTune | Para_CtrModule_CtrX16_PCompTune | Para_CtrModule_CtrX16_RangeBegin | Para_CtrModule_CtrX16_RangeEnd | Para_CtrModule_CtrX16_UserLevelIntExt | Para_CtrModule_CtrX16_UserLevelManAut | Para_CtrModule_CtrX16_UserLevelSet | Para_CtrModule_CtrX16_UserLevelTune | Para_CtrModule_CtrX16_WMax | Para_CtrModule_CtrX16_WMin | Para_CtrModule_CtrX16_WRampNeg | Para_CtrModule_CtrX16_WRampPos | Para_CtrModule_CtrX16_WStart | Para_CtrModule_CtrX16_YBlock | Para_CtrModule_CtrX16_YHl | Para_CtrModule_CtrX16_YMax | Para_CtrModule_CtrX16_YMin | Para_CtrModule_CtrX16_YRampTune | Para_Custom_AnalogIn_10_CustAnaIn_MinMaxActive10 | Para_Custom_AnalogIn_10_CustAnaIn_Typ10 | Para_Custom_AnalogIn_10_Hystereses | Para_Custom_AnalogIn_10_LimitHi | Para_Custom_AnalogIn_10_LimitHiHi | Para_Custom_AnalogIn_10_LimitLo | Para_Custom_AnalogIn_10_LimitLoLo | Para_Custom_AnalogIn_11_CustAnaIn_MinMaxActive11 | Para_Custom_AnalogIn_11_CustAnaIn_Typ11 | Para_Custom_AnalogIn_11_Hystereses | Para_Custom_AnalogIn_11_LimitHi | Para_Custom_AnalogIn_11_LimitHiHi | Para_Custom_AnalogIn_11_LimitLo | Para_Custom_AnalogIn_11_LimitLoLo | Para_Custom_AnalogIn_12_CustAnaIn_MinMaxActive12 | Para_Custom_AnalogIn_12_CustAnaIn_Typ12 | Para_Custom_AnalogIn_12_Hystereses | Para_Custom_AnalogIn_12_LimitHi | Para_Custom_AnalogIn_12_LimitHiHi | Para_Custom_AnalogIn_12_LimitLo | Para_Custom_AnalogIn_12_LimitLoLo | Para_Custom_AnalogIn_13_CustAnaIn_MinMaxActive13 | Para_Custom_AnalogIn_13_CustAnaIn_Typ13 | Para_Custom_AnalogIn_13_Hystereses | Para_Custom_AnalogIn_13_LimitHi | Para_Custom_AnalogIn_13_LimitHiHi | Para_Custom_AnalogIn_13_LimitLo | Para_Custom_AnalogIn_13_LimitLoLo | Para_Custom_AnalogIn_14_CustAnaIn_MinMaxActive14 | Para_Custom_AnalogIn_14_CustAnaIn_Typ14 | Para_Custom_AnalogIn_14_Hystereses | Para_Custom_AnalogIn_14_LimitHi | Para_Custom_AnalogIn_14_LimitHiHi | Para_Custom_AnalogIn_14_LimitLo | Para_Custom_AnalogIn_14_LimitLoLo | Para_Custom_AnalogIn_15_CustAnaIn_MinMaxActive15 | Para_Custom_AnalogIn_15_CustAnaIn_Typ15 | Para_Custom_AnalogIn_15_Hystereses | Para_Custom_AnalogIn_15_LimitHi | Para_Custom_AnalogIn_15_LimitHiHi | Para_Custom_AnalogIn_15_LimitLo | Para_Custom_AnalogIn_15_LimitLoLo | Para_Custom_AnalogIn_16_CustAnaIn_MinMaxActive16 | Para_Custom_AnalogIn_16_CustAnaIn_Typ16 | Para_Custom_AnalogIn_16_Hystereses | Para_Custom_AnalogIn_16_LimitHi | Para_Custom_AnalogIn_16_LimitHiHi | Para_Custom_AnalogIn_16_LimitLo | Para_Custom_AnalogIn_16_LimitLoLo | Para_Custom_AnalogIn_17_CustAnaIn_Active17 | Para_Custom_AnalogIn_17_CustAnaIn_MinMaxActive17 | Para_Custom_AnalogIn_17_CustAnaIn_Set4mA17 | Para_Custom_AnalogIn_17_CustAnaIn_Typ17 | Para_Custom_AnalogIn_17_Hystereses | Para_Custom_AnalogIn_17_LimitHi | Para_Custom_AnalogIn_17_LimitHiHi | Para_Custom_AnalogIn_17_LimitLo | Para_Custom_AnalogIn_17_LimitLoLo | Para_Custom_AnalogIn_17_ScaleMax | Para_Custom_AnalogIn_17_ScaleMin | Para_Custom_AnalogIn_18_CustAnaIn_Active18 | Para_Custom_AnalogIn_18_CustAnaIn_MinMaxActive18 | Para_Custom_AnalogIn_18_CustAnaIn_Set4mA18 | Para_Custom_AnalogIn_18_CustAnaIn_Typ18 | Para_Custom_AnalogIn_18_Hystereses | Para_Custom_AnalogIn_18_LimitHi | Para_Custom_AnalogIn_18_LimitHiHi | Para_Custom_AnalogIn_18_LimitLo | Para_Custom_AnalogIn_18_LimitLoLo | Para_Custom_AnalogIn_18_ScaleMax | Para_Custom_AnalogIn_18_ScaleMin | Para_Custom_AnalogIn_19_CustAnaIn_Active19 | Para_Custom_AnalogIn_19_CustAnaIn_MinMaxActive19 | Para_Custom_AnalogIn_19_CustAnaIn_Set4mA19 | Para_Custom_AnalogIn_19_CustAnaIn_Typ19 | Para_Custom_AnalogIn_19_Hystereses | Para_Custom_AnalogIn_19_LimitHi | Para_Custom_AnalogIn_19_LimitHiHi | Para_Custom_AnalogIn_19_LimitLo | Para_Custom_AnalogIn_19_LimitLoLo | Para_Custom_AnalogIn_19_ScaleMax | Para_Custom_AnalogIn_19_ScaleMin | Para_Custom_AnalogIn_1_CustAnaIn_MinMaxActive1 | Para_Custom_AnalogIn_1_CustAnaIn_Typ1 | Para_Custom_AnalogIn_1_Hystereses | Para_Custom_AnalogIn_1_LimitHi | Para_Custom_AnalogIn_1_LimitHiHi | Para_Custom_AnalogIn_1_LimitLo | Para_Custom_AnalogIn_1_LimitLoLo | Para_Custom_AnalogIn_20_CustAnaIn_Active20 | Para_Custom_AnalogIn_20_CustAnaIn_MinMaxActive20 | Para_Custom_AnalogIn_20_CustAnaIn_Set4mA20 | Para_Custom_AnalogIn_20_CustAnaIn_Typ20 | Para_Custom_AnalogIn_20_Hystereses | Para_Custom_AnalogIn_20_LimitHi | Para_Custom_AnalogIn_20_LimitHiHi | Para_Custom_AnalogIn_20_LimitLo | Para_Custom_AnalogIn_20_LimitLoLo | Para_Custom_AnalogIn_20_ScaleMax | Para_Custom_AnalogIn_20_ScaleMin | Para_Custom_AnalogIn_21_CustAnaIn_Active21 | Para_Custom_AnalogIn_21_CustAnaIn_MinMaxActive21 | Para_Custom_AnalogIn_21_CustAnaIn_Set4mA21 | Para_Custom_AnalogIn_21_CustAnaIn_Typ21 | Para_Custom_AnalogIn_21_Hystereses | Para_Custom_AnalogIn_21_LimitHi | Para_Custom_AnalogIn_21_LimitHiHi | Para_Custom_AnalogIn_21_LimitLo | Para_Custom_AnalogIn_21_LimitLoLo | Para_Custom_AnalogIn_21_ScaleMax | Para_Custom_AnalogIn_21_ScaleMin | Para_Custom_AnalogIn_22_CustAnaIn_Active22 | Para_Custom_AnalogIn_22_CustAnaIn_MinMaxActive22 | Para_Custom_AnalogIn_22_CustAnaIn_Set4mA22 | Para_Custom_AnalogIn_22_CustAnaIn_Typ22 | Para_Custom_AnalogIn_22_Hystereses | Para_Custom_AnalogIn_22_LimitHi | Para_Custom_AnalogIn_22_LimitHiHi | Para_Custom_AnalogIn_22_LimitLo | Para_Custom_AnalogIn_22_LimitLoLo | Para_Custom_AnalogIn_22_ScaleMax | Para_Custom_AnalogIn_22_ScaleMin | Para_Custom_AnalogIn_23_CustAnaIn_Active23 | Para_Custom_AnalogIn_23_CustAnaIn_MinMaxActive23 | Para_Custom_AnalogIn_23_CustAnaIn_Set4mA23 | Para_Custom_AnalogIn_23_CustAnaIn_Typ23 | Para_Custom_AnalogIn_23_Hystereses | Para_Custom_AnalogIn_23_LimitHi | Para_Custom_AnalogIn_23_LimitHiHi | Para_Custom_AnalogIn_23_LimitLo | Para_Custom_AnalogIn_23_LimitLoLo | Para_Custom_AnalogIn_23_ScaleMax | Para_Custom_AnalogIn_23_ScaleMin | Para_Custom_AnalogIn_24_CustAnaIn_Active24 | Para_Custom_AnalogIn_24_CustAnaIn_MinMaxActive24 | Para_Custom_AnalogIn_24_CustAnaIn_Set4mA24 | Para_Custom_AnalogIn_24_CustAnaIn_Typ24 | Para_Custom_AnalogIn_24_Hystereses | Para_Custom_AnalogIn_24_LimitHi | Para_Custom_AnalogIn_24_LimitHiHi | Para_Custom_AnalogIn_24_LimitLo | Para_Custom_AnalogIn_24_LimitLoLo | Para_Custom_AnalogIn_24_ScaleMax | Para_Custom_AnalogIn_24_ScaleMin | Para_Custom_AnalogIn_25_CustAnaIn_Active25 | Para_Custom_AnalogIn_25_CustAnaIn_MinMaxActive25 | Para_Custom_AnalogIn_25_CustAnaIn_Set4mA25 | Para_Custom_AnalogIn_25_CustAnaIn_Typ25 | Para_Custom_AnalogIn_25_Hystereses | Para_Custom_AnalogIn_25_LimitHi | Para_Custom_AnalogIn_25_LimitHiHi | Para_Custom_AnalogIn_25_LimitLo | Para_Custom_AnalogIn_25_LimitLoLo | Para_Custom_AnalogIn_25_ScaleMax | Para_Custom_AnalogIn_25_ScaleMin | Para_Custom_AnalogIn_26_CustAnaIn_Active26 | Para_Custom_AnalogIn_26_CustAnaIn_MinMaxActive26 | Para_Custom_AnalogIn_26_CustAnaIn_Set4mA26 | Para_Custom_AnalogIn_26_CustAnaIn_Typ26 | Para_Custom_AnalogIn_26_Hystereses | Para_Custom_AnalogIn_26_LimitHi | Para_Custom_AnalogIn_26_LimitHiHi | Para_Custom_AnalogIn_26_LimitLo | Para_Custom_AnalogIn_26_LimitLoLo | Para_Custom_AnalogIn_26_ScaleMax | Para_Custom_AnalogIn_26_ScaleMin | Para_Custom_AnalogIn_27_CustAnaIn_Active27 | Para_Custom_AnalogIn_27_CustAnaIn_MinMaxActive27 | Para_Custom_AnalogIn_27_CustAnaIn_Set4mA27 | Para_Custom_AnalogIn_27_CustAnaIn_Typ27 | Para_Custom_AnalogIn_27_Hystereses | Para_Custom_AnalogIn_27_LimitHi | Para_Custom_AnalogIn_27_LimitHiHi | Para_Custom_AnalogIn_27_LimitLo | Para_Custom_AnalogIn_27_LimitLoLo | Para_Custom_AnalogIn_27_ScaleMax | Para_Custom_AnalogIn_27_ScaleMin | Para_Custom_AnalogIn_28_CustAnaIn_Active28 | Para_Custom_AnalogIn_28_CustAnaIn_MinMaxActive28 | Para_Custom_AnalogIn_28_CustAnaIn_Set4mA28 | Para_Custom_AnalogIn_28_CustAnaIn_Typ28 | Para_Custom_AnalogIn_28_Hystereses | Para_Custom_AnalogIn_28_LimitHi | Para_Custom_AnalogIn_28_LimitHiHi | Para_Custom_AnalogIn_28_LimitLo | Para_Custom_AnalogIn_28_LimitLoLo | Para_Custom_AnalogIn_28_ScaleMax | Para_Custom_AnalogIn_28_ScaleMin | Para_Custom_AnalogIn_29_CustAnaIn_Active29 | Para_Custom_AnalogIn_29_CustAnaIn_MinMaxActive29 | Para_Custom_AnalogIn_29_CustAnaIn_Set4mA29 | Para_Custom_AnalogIn_29_CustAnaIn_Typ29 | Para_Custom_AnalogIn_29_Hystereses | Para_Custom_AnalogIn_29_LimitHi | Para_Custom_AnalogIn_29_LimitHiHi | Para_Custom_AnalogIn_29_LimitLo | Para_Custom_AnalogIn_29_LimitLoLo | Para_Custom_AnalogIn_29_ScaleMax | Para_Custom_AnalogIn_29_ScaleMin | Para_Custom_AnalogIn_2_CustAnaIn_MinMaxActive2 | Para_Custom_AnalogIn_2_CustAnaIn_Typ2 | Para_Custom_AnalogIn_2_Hystereses | Para_Custom_AnalogIn_2_LimitHi | Para_Custom_AnalogIn_2_LimitHiHi | Para_Custom_AnalogIn_2_LimitLo | Para_Custom_AnalogIn_2_LimitLoLo | Para_Custom_AnalogIn_30_CustAnaIn_Active30 | Para_Custom_AnalogIn_30_CustAnaIn_MinMaxActive30 | Para_Custom_AnalogIn_30_CustAnaIn_Set4mA30 | Para_Custom_AnalogIn_30_CustAnaIn_Typ30 | Para_Custom_AnalogIn_30_Hystereses | Para_Custom_AnalogIn_30_LimitHi | Para_Custom_AnalogIn_30_LimitHiHi | Para_Custom_AnalogIn_30_LimitLo | Para_Custom_AnalogIn_30_LimitLoLo | Para_Custom_AnalogIn_30_ScaleMax | Para_Custom_AnalogIn_30_ScaleMin | Para_Custom_AnalogIn_31_CustAnaIn_Active31 | Para_Custom_AnalogIn_31_CustAnaIn_MinMaxActive31 | Para_Custom_AnalogIn_31_CustAnaIn_Set4mA31 | Para_Custom_AnalogIn_31_CustAnaIn_Typ31 | Para_Custom_AnalogIn_31_Hystereses | Para_Custom_AnalogIn_31_LimitHi | Para_Custom_AnalogIn_31_LimitHiHi | Para_Custom_AnalogIn_31_LimitLo | Para_Custom_AnalogIn_31_LimitLoLo | Para_Custom_AnalogIn_31_ScaleMax | Para_Custom_AnalogIn_31_ScaleMin | Para_Custom_AnalogIn_32_CustAnaIn_Active32 | Para_Custom_AnalogIn_32_CustAnaIn_MinMaxActive32 | Para_Custom_AnalogIn_32_CustAnaIn_Set4mA32 | Para_Custom_AnalogIn_32_CustAnaIn_Typ32 | Para_Custom_AnalogIn_32_Hystereses | Para_Custom_AnalogIn_32_LimitHi | Para_Custom_AnalogIn_32_LimitHiHi | Para_Custom_AnalogIn_32_LimitLo | Para_Custom_AnalogIn_32_LimitLoLo | Para_Custom_AnalogIn_32_ScaleMax | Para_Custom_AnalogIn_32_ScaleMin | Para_Custom_AnalogIn_33_CustAnaIn_Active33 | Para_Custom_AnalogIn_33_CustAnaIn_MinMaxActive33 | Para_Custom_AnalogIn_33_CustAnaIn_Set4mA33 | Para_Custom_AnalogIn_33_CustAnaIn_Typ33 | Para_Custom_AnalogIn_33_Hystereses | Para_Custom_AnalogIn_33_LimitHi | Para_Custom_AnalogIn_33_LimitHiHi | Para_Custom_AnalogIn_33_LimitLo | Para_Custom_AnalogIn_33_LimitLoLo | Para_Custom_AnalogIn_33_ScaleMax | Para_Custom_AnalogIn_33_ScaleMin | Para_Custom_AnalogIn_34_CustAnaIn_Active34 | Para_Custom_AnalogIn_34_CustAnaIn_MinMaxActive34 | Para_Custom_AnalogIn_34_CustAnaIn_Set4mA34 | Para_Custom_AnalogIn_34_CustAnaIn_Typ34 | Para_Custom_AnalogIn_34_Hystereses | Para_Custom_AnalogIn_34_LimitHi | Para_Custom_AnalogIn_34_LimitHiHi | Para_Custom_AnalogIn_34_LimitLo | Para_Custom_AnalogIn_34_LimitLoLo | Para_Custom_AnalogIn_34_ScaleMax | Para_Custom_AnalogIn_34_ScaleMin | Para_Custom_AnalogIn_35_CustAnaIn_Active35 | Para_Custom_AnalogIn_35_CustAnaIn_MinMaxActive35 | Para_Custom_AnalogIn_35_CustAnaIn_Set4mA35 | Para_Custom_AnalogIn_35_CustAnaIn_Typ35 | Para_Custom_AnalogIn_35_Hystereses | Para_Custom_AnalogIn_35_LimitHi | Para_Custom_AnalogIn_35_LimitHiHi | Para_Custom_AnalogIn_35_LimitLo | Para_Custom_AnalogIn_35_LimitLoLo | Para_Custom_AnalogIn_35_ScaleMax | Para_Custom_AnalogIn_35_ScaleMin | Para_Custom_AnalogIn_36_CustAnaIn_Active36 | Para_Custom_AnalogIn_36_CustAnaIn_MinMaxActive36 | Para_Custom_AnalogIn_36_CustAnaIn_Set4mA36 | Para_Custom_AnalogIn_36_CustAnaIn_Typ36 | Para_Custom_AnalogIn_36_Hystereses | Para_Custom_AnalogIn_36_LimitHi | Para_Custom_AnalogIn_36_LimitHiHi | Para_Custom_AnalogIn_36_LimitLo | Para_Custom_AnalogIn_36_LimitLoLo | Para_Custom_AnalogIn_36_ScaleMax | Para_Custom_AnalogIn_36_ScaleMin | Para_Custom_AnalogIn_37_CustAnaIn_Active37 | Para_Custom_AnalogIn_37_CustAnaIn_MinMaxActive37 | Para_Custom_AnalogIn_37_CustAnaIn_Set4mA37 | Para_Custom_AnalogIn_37_CustAnaIn_Typ37 | Para_Custom_AnalogIn_37_Hystereses | Para_Custom_AnalogIn_37_LimitHi | Para_Custom_AnalogIn_37_LimitHiHi | Para_Custom_AnalogIn_37_LimitLo | Para_Custom_AnalogIn_37_LimitLoLo | Para_Custom_AnalogIn_37_ScaleMax | Para_Custom_AnalogIn_37_ScaleMin | Para_Custom_AnalogIn_38_CustAnaIn_Active38 | Para_Custom_AnalogIn_38_CustAnaIn_MinMaxActive38 | Para_Custom_AnalogIn_38_CustAnaIn_Set4mA38 | Para_Custom_AnalogIn_38_CustAnaIn_Typ38 | Para_Custom_AnalogIn_38_Hystereses | Para_Custom_AnalogIn_38_LimitHi | Para_Custom_AnalogIn_38_LimitHiHi | Para_Custom_AnalogIn_38_LimitLo | Para_Custom_AnalogIn_38_LimitLoLo | Para_Custom_AnalogIn_38_ScaleMax | Para_Custom_AnalogIn_38_ScaleMin | Para_Custom_AnalogIn_39_CustAnaIn_Active39 | Para_Custom_AnalogIn_39_CustAnaIn_MinMaxActive39 | Para_Custom_AnalogIn_39_CustAnaIn_Set4mA39 | Para_Custom_AnalogIn_39_CustAnaIn_Typ39 | Para_Custom_AnalogIn_39_Hystereses | Para_Custom_AnalogIn_39_LimitHi | Para_Custom_AnalogIn_39_LimitHiHi | Para_Custom_AnalogIn_39_LimitLo | Para_Custom_AnalogIn_39_LimitLoLo | Para_Custom_AnalogIn_39_ScaleMax | Para_Custom_AnalogIn_39_ScaleMin | Para_Custom_AnalogIn_3_CustAnaIn_MinMaxActive3 | Para_Custom_AnalogIn_3_CustAnaIn_Typ3 | Para_Custom_AnalogIn_3_Hystereses | Para_Custom_AnalogIn_3_LimitHi | Para_Custom_AnalogIn_3_LimitHiHi | Para_Custom_AnalogIn_3_LimitLo | Para_Custom_AnalogIn_3_LimitLoLo | Para_Custom_AnalogIn_40_CustAnaIn_Active40 | Para_Custom_AnalogIn_40_CustAnaIn_MinMaxActive40 | Para_Custom_AnalogIn_40_CustAnaIn_Set4mA40 | Para_Custom_AnalogIn_40_CustAnaIn_Typ40 | Para_Custom_AnalogIn_40_Hystereses | Para_Custom_AnalogIn_40_LimitHi | Para_Custom_AnalogIn_40_LimitHiHi | Para_Custom_AnalogIn_40_LimitLo | Para_Custom_AnalogIn_40_LimitLoLo | Para_Custom_AnalogIn_40_ScaleMax | Para_Custom_AnalogIn_40_ScaleMin | Para_Custom_AnalogIn_41_CustAnaIn_Active41 | Para_Custom_AnalogIn_41_CustAnaIn_MinMaxActive41 | Para_Custom_AnalogIn_41_CustAnaIn_Set4mA41 | Para_Custom_AnalogIn_41_CustAnaIn_Typ41 | Para_Custom_AnalogIn_41_Hystereses | Para_Custom_AnalogIn_41_LimitHi | Para_Custom_AnalogIn_41_LimitHiHi | Para_Custom_AnalogIn_41_LimitLo | Para_Custom_AnalogIn_41_LimitLoLo | Para_Custom_AnalogIn_41_ScaleMax | Para_Custom_AnalogIn_41_ScaleMin | Para_Custom_AnalogIn_42_CustAnaIn_Active42 | Para_Custom_AnalogIn_42_CustAnaIn_MinMaxActive42 | Para_Custom_AnalogIn_42_CustAnaIn_Set4mA42 | Para_Custom_AnalogIn_42_CustAnaIn_Typ42 | Para_Custom_AnalogIn_42_Hystereses | Para_Custom_AnalogIn_42_LimitHi | Para_Custom_AnalogIn_42_LimitHiHi | Para_Custom_AnalogIn_42_LimitLo | Para_Custom_AnalogIn_42_LimitLoLo | Para_Custom_AnalogIn_42_ScaleMax | Para_Custom_AnalogIn_42_ScaleMin | Para_Custom_AnalogIn_43_CustAnaIn_Active43 | Para_Custom_AnalogIn_43_CustAnaIn_MinMaxActive43 | Para_Custom_AnalogIn_43_CustAnaIn_Set4mA43 | Para_Custom_AnalogIn_43_CustAnaIn_Typ43 | Para_Custom_AnalogIn_43_Hystereses | Para_Custom_AnalogIn_43_LimitHi | Para_Custom_AnalogIn_43_LimitHiHi | Para_Custom_AnalogIn_43_LimitLo | Para_Custom_AnalogIn_43_LimitLoLo | Para_Custom_AnalogIn_43_ScaleMax | Para_Custom_AnalogIn_43_ScaleMin | Para_Custom_AnalogIn_44_CustAnaIn_Active44 | Para_Custom_AnalogIn_44_CustAnaIn_MinMaxActive44 | Para_Custom_AnalogIn_44_CustAnaIn_Set4mA44 | Para_Custom_AnalogIn_44_CustAnaIn_Typ44 | Para_Custom_AnalogIn_44_Hystereses | Para_Custom_AnalogIn_44_LimitHi | Para_Custom_AnalogIn_44_LimitHiHi | Para_Custom_AnalogIn_44_LimitLo | Para_Custom_AnalogIn_44_LimitLoLo | Para_Custom_AnalogIn_44_ScaleMax | Para_Custom_AnalogIn_44_ScaleMin | Para_Custom_AnalogIn_45_CustAnaIn_Active45 | Para_Custom_AnalogIn_45_CustAnaIn_MinMaxActive45 | Para_Custom_AnalogIn_45_CustAnaIn_Set4mA45 | Para_Custom_AnalogIn_45_CustAnaIn_Typ45 | Para_Custom_AnalogIn_45_Hystereses | Para_Custom_AnalogIn_45_LimitHi | Para_Custom_AnalogIn_45_LimitHiHi | Para_Custom_AnalogIn_45_LimitLo | Para_Custom_AnalogIn_45_LimitLoLo | Para_Custom_AnalogIn_45_ScaleMax | Para_Custom_AnalogIn_45_ScaleMin | Para_Custom_AnalogIn_46_CustAnaIn_Active46 | Para_Custom_AnalogIn_46_CustAnaIn_MinMaxActive46 | Para_Custom_AnalogIn_46_CustAnaIn_Set4mA46 | Para_Custom_AnalogIn_46_CustAnaIn_Typ46 | Para_Custom_AnalogIn_46_Hystereses | Para_Custom_AnalogIn_46_LimitHi | Para_Custom_AnalogIn_46_LimitHiHi | Para_Custom_AnalogIn_46_LimitLo | Para_Custom_AnalogIn_46_LimitLoLo | Para_Custom_AnalogIn_46_ScaleMax | Para_Custom_AnalogIn_46_ScaleMin | Para_Custom_AnalogIn_47_CustAnaIn_Active47 | Para_Custom_AnalogIn_47_CustAnaIn_MinMaxActive47 | Para_Custom_AnalogIn_47_CustAnaIn_Set4mA47 | Para_Custom_AnalogIn_47_CustAnaIn_Typ47 | Para_Custom_AnalogIn_47_Hystereses | Para_Custom_AnalogIn_47_LimitHi | Para_Custom_AnalogIn_47_LimitHiHi | Para_Custom_AnalogIn_47_LimitLo | Para_Custom_AnalogIn_47_LimitLoLo | Para_Custom_AnalogIn_47_ScaleMax | Para_Custom_AnalogIn_47_ScaleMin | Para_Custom_AnalogIn_48_CustAnaIn_Active48 | Para_Custom_AnalogIn_48_CustAnaIn_MinMaxActive48 | Para_Custom_AnalogIn_48_CustAnaIn_Set4mA48 | Para_Custom_AnalogIn_48_CustAnaIn_Typ48 | Para_Custom_AnalogIn_48_Hystereses | Para_Custom_AnalogIn_48_LimitHi | Para_Custom_AnalogIn_48_LimitHiHi | Para_Custom_AnalogIn_48_LimitLo | Para_Custom_AnalogIn_48_LimitLoLo | Para_Custom_AnalogIn_48_ScaleMax | Para_Custom_AnalogIn_48_ScaleMin | Para_Custom_AnalogIn_49_CustAnaIn_Active49 | Para_Custom_AnalogIn_49_CustAnaIn_MinMaxActive49 | Para_Custom_AnalogIn_49_CustAnaIn_Set4mA49 | Para_Custom_AnalogIn_49_CustAnaIn_Typ49 | Para_Custom_AnalogIn_49_Hystereses | Para_Custom_AnalogIn_49_LimitHi | Para_Custom_AnalogIn_49_LimitHiHi | Para_Custom_AnalogIn_49_LimitLo | Para_Custom_AnalogIn_49_LimitLoLo | Para_Custom_AnalogIn_49_ScaleMax | Para_Custom_AnalogIn_49_ScaleMin | Para_Custom_AnalogIn_4_CustAnaIn_MinMaxActive4 | Para_Custom_AnalogIn_4_CustAnaIn_Typ4 | Para_Custom_AnalogIn_4_Hystereses | Para_Custom_AnalogIn_4_LimitHi | Para_Custom_AnalogIn_4_LimitHiHi | Para_Custom_AnalogIn_4_LimitLo | Para_Custom_AnalogIn_4_LimitLoLo | Para_Custom_AnalogIn_50_CustAnaIn_Active50 | Para_Custom_AnalogIn_50_CustAnaIn_MinMaxActive50 | Para_Custom_AnalogIn_50_CustAnaIn_Set4mA50 | Para_Custom_AnalogIn_50_CustAnaIn_Typ50 | Para_Custom_AnalogIn_50_Hystereses | Para_Custom_AnalogIn_50_LimitHi | Para_Custom_AnalogIn_50_LimitHiHi | Para_Custom_AnalogIn_50_LimitLo | Para_Custom_AnalogIn_50_LimitLoLo | Para_Custom_AnalogIn_50_ScaleMax | Para_Custom_AnalogIn_50_ScaleMin | Para_Custom_AnalogIn_51_CustAnaIn_Active51 | Para_Custom_AnalogIn_51_CustAnaIn_MinMaxActive51 | Para_Custom_AnalogIn_51_CustAnaIn_Set4mA51 | Para_Custom_AnalogIn_51_CustAnaIn_Typ51 | Para_Custom_AnalogIn_51_Hystereses | Para_Custom_AnalogIn_51_LimitHi | Para_Custom_AnalogIn_51_LimitHiHi | Para_Custom_AnalogIn_51_LimitLo | Para_Custom_AnalogIn_51_LimitLoLo | Para_Custom_AnalogIn_51_ScaleMax | Para_Custom_AnalogIn_51_ScaleMin | Para_Custom_AnalogIn_52_CustAnaIn_Active52 | Para_Custom_AnalogIn_52_CustAnaIn_MinMaxActive52 | Para_Custom_AnalogIn_52_CustAnaIn_Set4mA52 | Para_Custom_AnalogIn_52_CustAnaIn_Typ52 | Para_Custom_AnalogIn_52_Hystereses | Para_Custom_AnalogIn_52_LimitHi | Para_Custom_AnalogIn_52_LimitHiHi | Para_Custom_AnalogIn_52_LimitLo | Para_Custom_AnalogIn_52_LimitLoLo | Para_Custom_AnalogIn_52_ScaleMax | Para_Custom_AnalogIn_52_ScaleMin | Para_Custom_AnalogIn_53_CustAnaIn_Active53 | Para_Custom_AnalogIn_53_CustAnaIn_MinMaxActive53 | Para_Custom_AnalogIn_53_CustAnaIn_Set4mA53 | Para_Custom_AnalogIn_53_CustAnaIn_Typ53 | Para_Custom_AnalogIn_53_Hystereses | Para_Custom_AnalogIn_53_LimitHi | Para_Custom_AnalogIn_53_LimitHiHi | Para_Custom_AnalogIn_53_LimitLo | Para_Custom_AnalogIn_53_LimitLoLo | Para_Custom_AnalogIn_53_ScaleMax | Para_Custom_AnalogIn_53_ScaleMin | Para_Custom_AnalogIn_54_CustAnaIn_Active54 | Para_Custom_AnalogIn_54_CustAnaIn_MinMaxActive54 | Para_Custom_AnalogIn_54_CustAnaIn_Set4mA54 | Para_Custom_AnalogIn_54_CustAnaIn_Typ54 | Para_Custom_AnalogIn_54_Hystereses | Para_Custom_AnalogIn_54_LimitHi | Para_Custom_AnalogIn_54_LimitHiHi | Para_Custom_AnalogIn_54_LimitLo | Para_Custom_AnalogIn_54_LimitLoLo | Para_Custom_AnalogIn_54_ScaleMax | Para_Custom_AnalogIn_54_ScaleMin | Para_Custom_AnalogIn_55_CustAnaIn_Active55 | Para_Custom_AnalogIn_55_CustAnaIn_MinMaxActive55 | Para_Custom_AnalogIn_55_CustAnaIn_Set4mA55 | Para_Custom_AnalogIn_55_CustAnaIn_Typ55 | Para_Custom_AnalogIn_55_Hystereses | Para_Custom_AnalogIn_55_LimitHi | Para_Custom_AnalogIn_55_LimitHiHi | Para_Custom_AnalogIn_55_LimitLo | Para_Custom_AnalogIn_55_LimitLoLo | Para_Custom_AnalogIn_55_ScaleMax | Para_Custom_AnalogIn_55_ScaleMin | Para_Custom_AnalogIn_56_CustAnaIn_Active56 | Para_Custom_AnalogIn_56_CustAnaIn_MinMaxActive56 | Para_Custom_AnalogIn_56_CustAnaIn_Set4mA56 | Para_Custom_AnalogIn_56_CustAnaIn_Typ56 | Para_Custom_AnalogIn_56_Hystereses | Para_Custom_AnalogIn_56_LimitHi | Para_Custom_AnalogIn_56_LimitHiHi | Para_Custom_AnalogIn_56_LimitLo | Para_Custom_AnalogIn_56_LimitLoLo | Para_Custom_AnalogIn_56_ScaleMax | Para_Custom_AnalogIn_56_ScaleMin | Para_Custom_AnalogIn_57_CustAnaIn_Active57 | Para_Custom_AnalogIn_57_CustAnaIn_MinMaxActive57 | Para_Custom_AnalogIn_57_CustAnaIn_Set4mA57 | Para_Custom_AnalogIn_57_CustAnaIn_Typ57 | Para_Custom_AnalogIn_57_Hystereses | Para_Custom_AnalogIn_57_LimitHi | Para_Custom_AnalogIn_57_LimitHiHi | Para_Custom_AnalogIn_57_LimitLo | Para_Custom_AnalogIn_57_LimitLoLo | Para_Custom_AnalogIn_57_ScaleMax | Para_Custom_AnalogIn_57_ScaleMin | Para_Custom_AnalogIn_58_CustAnaIn_Active58 | Para_Custom_AnalogIn_58_CustAnaIn_MinMaxActive58 | Para_Custom_AnalogIn_58_CustAnaIn_Set4mA58 | Para_Custom_AnalogIn_58_CustAnaIn_Typ58 | Para_Custom_AnalogIn_58_Hystereses | Para_Custom_AnalogIn_58_LimitHi | Para_Custom_AnalogIn_58_LimitHiHi | Para_Custom_AnalogIn_58_LimitLo | Para_Custom_AnalogIn_58_LimitLoLo | Para_Custom_AnalogIn_58_ScaleMax | Para_Custom_AnalogIn_58_ScaleMin | Para_Custom_AnalogIn_59_CustAnaIn_Active59 | Para_Custom_AnalogIn_59_CustAnaIn_MinMaxActive59 | Para_Custom_AnalogIn_59_CustAnaIn_Set4mA59 | Para_Custom_AnalogIn_59_CustAnaIn_Typ59 | Para_Custom_AnalogIn_59_Hystereses | Para_Custom_AnalogIn_59_LimitHi | Para_Custom_AnalogIn_59_LimitHiHi | Para_Custom_AnalogIn_59_LimitLo | Para_Custom_AnalogIn_59_LimitLoLo | Para_Custom_AnalogIn_59_ScaleMax | Para_Custom_AnalogIn_59_ScaleMin | Para_Custom_AnalogIn_5_CustAnaIn_MinMaxActive5 | Para_Custom_AnalogIn_5_CustAnaIn_Typ5 | Para_Custom_AnalogIn_5_Hystereses | Para_Custom_AnalogIn_5_LimitHi | Para_Custom_AnalogIn_5_LimitHiHi | Para_Custom_AnalogIn_5_LimitLo | Para_Custom_AnalogIn_5_LimitLoLo | Para_Custom_AnalogIn_60_CustAnaIn_Active60 | Para_Custom_AnalogIn_60_CustAnaIn_MinMaxActive60 | Para_Custom_AnalogIn_60_CustAnaIn_Set4mA60 | Para_Custom_AnalogIn_60_CustAnaIn_Typ60 | Para_Custom_AnalogIn_60_Hystereses | Para_Custom_AnalogIn_60_LimitHi | Para_Custom_AnalogIn_60_LimitHiHi | Para_Custom_AnalogIn_60_LimitLo | Para_Custom_AnalogIn_60_LimitLoLo | Para_Custom_AnalogIn_60_ScaleMax | Para_Custom_AnalogIn_60_ScaleMin | Para_Custom_AnalogIn_6_CustAnaIn_MinMaxActive6 | Para_Custom_AnalogIn_6_CustAnaIn_Typ6 | Para_Custom_AnalogIn_6_Hystereses | Para_Custom_AnalogIn_6_LimitHi | Para_Custom_AnalogIn_6_LimitHiHi | Para_Custom_AnalogIn_6_LimitLo | Para_Custom_AnalogIn_6_LimitLoLo | Para_Custom_AnalogIn_7_CustAnaIn_MinMaxActive7 | Para_Custom_AnalogIn_7_CustAnaIn_Typ7 | Para_Custom_AnalogIn_7_Hystereses | Para_Custom_AnalogIn_7_LimitHi | Para_Custom_AnalogIn_7_LimitHiHi | Para_Custom_AnalogIn_7_LimitLo | Para_Custom_AnalogIn_7_LimitLoLo | Para_Custom_AnalogIn_8_CustAnaIn_MinMaxActive8 | Para_Custom_AnalogIn_8_CustAnaIn_Typ8 | Para_Custom_AnalogIn_8_Hystereses | Para_Custom_AnalogIn_8_LimitHi | Para_Custom_AnalogIn_8_LimitHiHi | Para_Custom_AnalogIn_8_LimitLo | Para_Custom_AnalogIn_8_LimitLoLo | Para_Custom_AnalogIn_9_CustAnaIn_MinMaxActive9 | Para_Custom_AnalogIn_9_CustAnaIn_Typ9 | Para_Custom_AnalogIn_9_Hystereses | Para_Custom_AnalogIn_9_LimitHi | Para_Custom_AnalogIn_9_LimitHiHi | Para_Custom_AnalogIn_9_LimitLo | Para_Custom_AnalogIn_9_LimitLoLo | Para_Custom_AnalogOut_AO10_HardwareScaleMax | Para_Custom_AnalogOut_AO10_HardwareScaleMin | Para_Custom_AnalogOut_AO10_ScaleMax | Para_Custom_AnalogOut_AO10_ScaleMin | Para_Custom_AnalogOut_AO11_HardwareScaleMax | Para_Custom_AnalogOut_AO11_HardwareScaleMin | Para_Custom_AnalogOut_AO11_ScaleMax | Para_Custom_AnalogOut_AO11_ScaleMin | Para_Custom_AnalogOut_AO12_HardwareScaleMax | Para_Custom_AnalogOut_AO12_HardwareScaleMin | Para_Custom_AnalogOut_AO12_ScaleMax | Para_Custom_AnalogOut_AO12_ScaleMin | Para_Custom_AnalogOut_AO13_HardwareScaleMax | Para_Custom_AnalogOut_AO13_HardwareScaleMin | Para_Custom_AnalogOut_AO13_ScaleMax | Para_Custom_AnalogOut_AO13_ScaleMin | Para_Custom_AnalogOut_AO14_HardwareScaleMax | Para_Custom_AnalogOut_AO14_HardwareScaleMin | Para_Custom_AnalogOut_AO14_ScaleMax | Para_Custom_AnalogOut_AO14_ScaleMin | Para_Custom_AnalogOut_AO15_HardwareScaleMax | Para_Custom_AnalogOut_AO15_HardwareScaleMin | Para_Custom_AnalogOut_AO15_ScaleMax | Para_Custom_AnalogOut_AO15_ScaleMin | Para_Custom_AnalogOut_AO16_HardwareScaleMax | Para_Custom_AnalogOut_AO16_HardwareScaleMin | Para_Custom_AnalogOut_AO16_ScaleMax | Para_Custom_AnalogOut_AO16_ScaleMin | Para_Custom_AnalogOut_AO1_HardwareScaleMax | Para_Custom_AnalogOut_AO1_HardwareScaleMin | Para_Custom_AnalogOut_AO1_ScaleMax | Para_Custom_AnalogOut_AO1_ScaleMin | Para_Custom_AnalogOut_AO2_HardwareScaleMax | Para_Custom_AnalogOut_AO2_HardwareScaleMin | Para_Custom_AnalogOut_AO2_ScaleMax | Para_Custom_AnalogOut_AO2_ScaleMin | Para_Custom_AnalogOut_AO3_HardwareScaleMax | Para_Custom_AnalogOut_AO3_HardwareScaleMin | Para_Custom_AnalogOut_AO3_ScaleMax | Para_Custom_AnalogOut_AO3_ScaleMin | Para_Custom_AnalogOut_AO4_HardwareScaleMax | Para_Custom_AnalogOut_AO4_HardwareScaleMin | Para_Custom_AnalogOut_AO4_ScaleMax | Para_Custom_AnalogOut_AO4_ScaleMin | Para_Custom_AnalogOut_AO5_HardwareScaleMax | Para_Custom_AnalogOut_AO5_HardwareScaleMin | Para_Custom_AnalogOut_AO5_ScaleMax | Para_Custom_AnalogOut_AO5_ScaleMin | Para_Custom_AnalogOut_AO6_HardwareScaleMax | Para_Custom_AnalogOut_AO6_HardwareScaleMin | Para_Custom_AnalogOut_AO6_ScaleMax | Para_Custom_AnalogOut_AO6_ScaleMin | Para_Custom_AnalogOut_AO7_HardwareScaleMax | Para_Custom_AnalogOut_AO7_HardwareScaleMin | Para_Custom_AnalogOut_AO7_ScaleMax | Para_Custom_AnalogOut_AO7_ScaleMin | Para_Custom_AnalogOut_AO8_HardwareScaleMax | Para_Custom_AnalogOut_AO8_HardwareScaleMin | Para_Custom_AnalogOut_AO8_ScaleMax | Para_Custom_AnalogOut_AO8_ScaleMin | Para_Custom_AnalogOut_AO9_HardwareScaleMax | Para_Custom_AnalogOut_AO9_HardwareScaleMin | Para_Custom_AnalogOut_AO9_ScaleMax | Para_Custom_AnalogOut_AO9_ScaleMin | Para_Custom_Status_AuxCust_Active1 | Para_Custom_Status_AuxCust_Active10 | Para_Custom_Status_AuxCust_Active11 | Para_Custom_Status_AuxCust_Active12 | Para_Custom_Status_AuxCust_Active13 | Para_Custom_Status_AuxCust_Active14 | Para_Custom_Status_AuxCust_Active15 | Para_Custom_Status_AuxCust_Active16 | Para_Custom_Status_AuxCust_Active17 | Para_Custom_Status_AuxCust_Active18 | Para_Custom_Status_AuxCust_Active19 | Para_Custom_Status_AuxCust_Active2 | Para_Custom_Status_AuxCust_Active20 | Para_Custom_Status_AuxCust_Active21 | Para_Custom_Status_AuxCust_Active22 | Para_Custom_Status_AuxCust_Active23 | Para_Custom_Status_AuxCust_Active24 | Para_Custom_Status_AuxCust_Active25 | Para_Custom_Status_AuxCust_Active26 | Para_Custom_Status_AuxCust_Active27 | Para_Custom_Status_AuxCust_Active28 | Para_Custom_Status_AuxCust_Active29 | Para_Custom_Status_AuxCust_Active3 | Para_Custom_Status_AuxCust_Active30 | Para_Custom_Status_AuxCust_Active31 | Para_Custom_Status_AuxCust_Active32 | Para_Custom_Status_AuxCust_Active33 | Para_Custom_Status_AuxCust_Active34 | Para_Custom_Status_AuxCust_Active35 | Para_Custom_Status_AuxCust_Active36 | Para_Custom_Status_AuxCust_Active37 | Para_Custom_Status_AuxCust_Active38 | Para_Custom_Status_AuxCust_Active39 | Para_Custom_Status_AuxCust_Active4 | Para_Custom_Status_AuxCust_Active40 | Para_Custom_Status_AuxCust_Active5 | Para_Custom_Status_AuxCust_Active6 | Para_Custom_Status_AuxCust_Active7 | Para_Custom_Status_AuxCust_Active8 | Para_Custom_Status_AuxCust_Active9 | Para_Cylinder_Bearing_Pc_T_CBearing_Sig_Lo | Para_Cylinder_Bearing_T_CBearing_Exist | Para_Cylinder_Bearing_T_CBearing_Hi | Para_Cylinder_Bearing_T_CBearing_Hi_Offset | Para_Cylinder_Bearing_T_CBearing_HiHi | Para_Cylinder_Bearing_T_CBearing_MDev_HiHi | Para_Cylinder_Bearing_T_MBearing_Exist | Para_Cylinder_Bearing_T_MBearing_Hi | Para_Cylinder_Bearing_T_MBearing_HiHi | Para_Cylinder_Bearing_T_MBearing_MDev_HiHi | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset1 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset10 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset11 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset12 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset13 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset14 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset15 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset16 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset17 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset18 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset19 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset2 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset20 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset21 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset22 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset23 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset24 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset3 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset4 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset5 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset6 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset7 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset8 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset9 | Para_Cylinder_Ignition_Balancer_CA_IgnP_CylOffset_Active | Para_Cylinder_Ignition_CA_AdvTimeLim | Para_Cylinder_Ignition_CA_Ign_OP_Power1 | Para_Cylinder_Ignition_CA_Ign_OP_Power2 | Para_Cylinder_Ignition_CA_Ign_OP_Power3 | Para_Cylinder_Ignition_CA_Ign_OP_Power4 | Para_Cylinder_Ignition_CA_Ign_OP_Speed1 | Para_Cylinder_Ignition_CA_Ign_OP_Speed2 | Para_Cylinder_Ignition_CA_Ign_OP_Speed3 | Para_Cylinder_Ignition_CA_Ign_OP_Speed4 | Para_Cylinder_Ignition_CA_RetTimeLim | Para_Cylinder_Ignition_MisfCont | Para_Cylinder_Ignition_MORIS_CoilType0_Current | Para_Cylinder_Ignition_MORIS_CoilType0_Time | Para_Cylinder_Ignition_MORIS_SparkChar1_Current | Para_Cylinder_Ignition_MORIS_SparkChar1_Time | Para_Cylinder_Ignition_MORIS_SparkChar2_Current | Para_Cylinder_Ignition_MORIS_SparkChar2_Time | Para_Cylinder_Ignition_MORIS_SparkChar3_Current | Para_Cylinder_Ignition_MORIS_SparkChar3_Time | Para_Cylinder_Ignition_MORIS_SparkChar4_Current | Para_Cylinder_Ignition_MORIS_SparkChar4_Time | Para_Cylinder_Ignition_MORIS_SparkChar5_Current | Para_Cylinder_Ignition_MORIS_SparkChar5_Time | Para_Cylinder_Ignition_MORIS_SparkChar6_Current | Para_Cylinder_Ignition_MORIS_VarSparkDur_DynSparkDuration | Para_Cylinder_Ignition_MORIS_VarSparkDur_P_Act_DynSpark_Limit_Nom | Para_Cylinder_Ignition_MORIS_VarSparkDur_usDurationIdle | Para_Cylinder_Knock_CA_IP_Knck_Max | Para_Cylinder_Knock_Kno_Int_MinLim | Para_Cylinder_Knock_Kno_IP_Scale_StP | Para_Cylinder_Knock_Kno_P2s_Inc_EnP | Para_Cylinder_Knock_Kno_P2s_Inc_StP | Para_Cylinder_Knock_Kno_Pmax_CylMax | Para_Cylinder_Knock_Kno_Pmax_Red_EnP_dlt | Para_Cylinder_Knock_Kno_Pmax_Red_StP | Para_Cylinder_Knock_PBC_Pr_PBC_Knck_Heavy | Para_Cylinder_Knock_PBC_Pr_PBC_Knck_Lim | Para_Cylinder_Knock_Pmax_Knck_Max | Para_Cylinder_Knock_Pr_P2s_Knck_Max | Para_Cylinder_Monic1_delay | Para_Cylinder_Monic1_limit | Para_Cylinder_Monic2_delay | Para_Cylinder_Monic2_limit | Para_Cylinder_Monic3_delay | Para_Cylinder_Monic3_limit | Para_Cylinder_Monic4_delay | Para_Cylinder_Monic4_limit | Para_Cylinder_Monic_Ign_LimitMonitorActive1 | Para_Cylinder_Monic_Ign_LimitMonitorActive2 | Para_Cylinder_Monic_Ign_LimitMonitorActive3 | Para_Cylinder_Monic_Ign_LimitMonitorActive4 | Para_Cylinder_PBC_CoVControl_CoV_Set100 | Para_Cylinder_PBC_CoVControl_CoV_Set50 | Para_Cylinder_PBC_CoVControl_CoVCtr_Act | Para_Cylinder_PBC_CoVControl_CoVCtr_ki | Para_Cylinder_PBC_CoVControl_CoVCtr_kp | Para_Cylinder_PBC_CoVControl_Pr_CoV_p2s_Range | Para_Cylinder_PBC_MFB50Control_CA_MFB50_ITPOfs_early | Para_Cylinder_PBC_MFB50Control_CA_MFB50_ITPOfs_late | Para_Cylinder_PBC_MFB50Control_CA_MFB50_set100 | Para_Cylinder_PBC_MFB50Control_CA_MFB50_set50 | Para_Cylinder_PBC_MFB50Control_MFB50_ITP_ratio | Para_Cylinder_PBC_MFB50Control_MFB50Contr_Ena | Para_Cylinder_PBC_MFB50Control_MFB50Ctr_ki | Para_Cylinder_PBC_MFB50Control_MFB50Ctr_kp | Para_Cylinder_PBC_Num_IMEP_Misf_Lim | Para_Cylinder_PBC_P_PBC_Act_Hys | Para_Cylinder_PBC_P_PBC_Act_SP | Para_Cylinder_PBC_Pr_CPP_AbsLim_LHE | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_cur_gradient | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_duration | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_set_current | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_set_duration | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time1 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time10 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time11 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time12 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time13 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time14 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time15 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time16 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time17 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time18 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time19 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time2 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time20 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time21 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time22 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time23 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time24 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time3 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time4 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time5 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time6 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time7 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time8 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_st_time9 | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_var_limit_Idle | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_var_limit_Load | Para_Cylinder_PI_CloseDetect_SA_PI_clodet_var_limit_Start | Para_Cylinder_PI_CorrectCurrCtr_SA_PI_currCtr_delay | Para_Cylinder_PI_CorrectCurrCtr_SA_PI_currCtr_duration | Para_Cylinder_PI_CorrectCurrCtr_SA_PI_currCtr_level | Para_Cylinder_PI_CorrectCurrCtr_SA_PI_currCtr_rate | Para_Cylinder_PI_CurrentProfile_SA_PI_curr1_current | Para_Cylinder_PI_CurrentProfile_SA_PI_curr1_duration | Para_Cylinder_PI_CurrentProfile_SA_PI_curr2_current | Para_Cylinder_PI_CurrentProfile_SA_PI_curr2_duration | Para_Cylinder_PI_CurrentProfile_SA_PI_curr3_current | Para_Cylinder_PI_CurrentProfile_SA_PI_curr3_duration | Para_Cylinder_PI_CurrentProfile_SA_PI_curr4_current | Para_Cylinder_PI_CurrentRecovery_SA_PI_recov_current | Para_Cylinder_PI_CurrentRecovery_SA_PI_recov_delay | Para_Cylinder_PI_CurrentRecovery_SA_PI_recov_duration | Para_Cylinder_PI_Demagnet_PIDemagActive | Para_Cylinder_PI_Demagnet_SA_PI_demag_delay | Para_Cylinder_PI_Demagnet_SA_PI_demag_duration | Para_Cylinder_PI_Demagnet_SA_PI_demag_up_limit | Para_Cylinder_PI_MisfCyl_Max_Norm | Para_Cylinder_PI_P_MisfCtr_Hys_Norm | Para_Cylinder_PI_P_MisfCtr_SP_Norm | Para_Cylinder_PI_PullInCurrCheck_SA_PI_pudet_duration | Para_Cylinder_PI_PullInCurrCheck_SA_PI_pudet_level | Para_Cylinder_PI_PullInCurrCheck_SA_PI_pudet_st_time | Para_Cylinder_PI_SA_CyclPIOnDuringMisf | Para_Cylinder_PI_SA_PIValveType | Para_Cylinder_PI_ti_OpTi_MisCyl_Trig | Para_Cylinder_PI_ti_OpTi_MisfCyl | Para_Electrical_GeneratCtr_ChoiceSet_PF_CosPCtr_PF_Set1 | Para_Electrical_GeneratCtr_PF_Customer_Selected | Para_Electrical_GeneratCtr_QLimit_Q_OverExc_Lim | Para_Electrical_GeneratCtr_QLimit_Q_UnderExc_Lim | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h0 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h1 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h2 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h3 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h4 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_h5 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m0 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m1 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m2 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m3 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m4 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_m5 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set0 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set1 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set2 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set3 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set4 | Para_Electrical_GeneratCtr_TimeTable_PF_CosPCtr_Tme_Set5 | Para_Electrical_GeneratCtr_Voltage_F_Gen_Match_Max | Para_Electrical_GeneratCtr_Voltage_F_Gen_Match_Min | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map0 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map10 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map2 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map4 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map6 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_map8 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set0 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set1 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set2 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set3 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set4 | Para_Electrical_GeneratCtr_Voltage_PF_CosPCtr_U_Set5 | Para_Electrical_GeneratCtr_Voltage_U_adj_gcb_ext_hilo_a | Para_Electrical_GeneratCtr_Voltage_U_adj_gcb_mmd_calc_a | Para_Electrical_GeneratCtr_Voltage_U_adj_mcb_ext_hilo_a | Para_Electrical_GeneratCtr_Voltage_U_adj_mcb_mmd_calc_a | Para_Electrical_GeneratCtr_Voltage_U_Gen_match_delta | Para_Electrical_GeneratCtr_Voltage_U_Gen_P_Ena | Para_Electrical_GeneratCtr_Voltage_U_Gen_Rmp_Inc | Para_Electrical_GeneratCtr_Voltage_U_Gen_spd_match | Para_Electrical_Generator_F_GenBear_DE1_Active | Para_Electrical_Generator_F_GenBear_DE2_Active | Para_Electrical_Generator_F_GenBear_NDE1_Active | Para_Electrical_Generator_F_GenBear_NDE2_Active | Para_Electrical_Generator_F_GenBear_ScalMax | Para_Electrical_Generator_F_GenBear_ScalMin | Para_Electrical_Generator_T_GenAirIn2_Active | Para_Electrical_Generator_T_Pred_GenAirIn_Rate | Para_Electrical_Generator_T_Pred_GenAirIn_Start | Para_Electrical_Generator_ti_Gen_VoltReg_Fail | Para_Electrical_Generator_tiF_GenBear_Hi | Para_Electrical_Generator_tiF_GenBear_HiHi | Para_Electrical_Generator_tiP_Gen_Reverse | Para_Electrical_Generator_tiP_Gen_Reverse2 | Para_Electrical_Generator_tiP_Reverse_Mon_Ena | Para_Electrical_Generator_tiPF_CosPCtr_del | Para_Electrical_Generator_U_Gen_Contr_Sel | Para_Electrical_Generator_U_Gen_Nom_2 | Para_Electrical_Grid_GridCodeDyn_GrC_CapStop | Para_Electrical_Grid_GridCodeDyn_GrC_Prof_Active0 | Para_Electrical_Grid_GridCodeDyn_GrC_Prof_Active1 | Para_Electrical_Grid_GridCodeDyn_GrC_Prof_Active2 | Para_Electrical_Grid_GridCodeDyn_GridCode_Active | Para_Electrical_Grid_GridCodeDyn_GridCode_Prof23_Active | Para_Electrical_Grid_GridCodeDyn_GridCodeMonitoringOnly | Para_Electrical_Grid_GridCodeDyn_ti_GrC_Prof0 | Para_Electrical_Grid_GridCodeDyn_ti_GrC_Prof1 | Para_Electrical_Grid_GridCodeDyn_ti_GrC_Prof2 | Para_Electrical_Grid_GridCodeDyn_U_GrC_Prof_Norm0 | Para_Electrical_Grid_GridCodeDyn_U_GrC_Prof_Norm1 | Para_Electrical_Grid_GridCodeDyn_U_GrC_Prof_Norm2 | Para_Electrical_Grid_GridCodeStatic_DEIE_Active | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_Droop_FC_neg | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_Droop_FC_pos | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_F_FC_Deadband_neg | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_F_FC_Deadband_pos | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_F_FC_Dlt_neg | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_F_FC_Dlt_pos | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_Calc_PRamp_FC_active | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_PRamp_FC_DecGrad_Norm | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_PRamp_FC_ExtInp | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_PRamp_FC_IncGrad_Norm | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_PRamp_FC_SetCOn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_PowerRamp_tiSetTime_FC_PRamp | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_Set_FC_COn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_Set_FC_ExtInp | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_Set_FC_Input | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_SetMarg_FC_neg | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_SetMarg_FC_pos | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_SetMarg_FC_StaInp | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TestFunction_FAct_FC_ManualTest | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TestFunction_FNom_FC_ManualTest | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TestFunction_Set_FC_Testmode | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_F_FC_Deadband_TAF_neg | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_F_FC_Deadband_TAF_pos | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_P_SetMarg_FC_TAF | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_HFRCOn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_PORCOn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_RRCOn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_SORCOn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_SRCOn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_TimeActFunctCOn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_TOR2COn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_Set_FC_TORCOn | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_POR | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_RR | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_SOR | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_SR | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_TOR | Para_Electrical_Grid_GridCodeStatic_FrequencyCtr_TimeActivatedFunctions_tiSetTime_FC_TOR2 | Para_Electrical_Grid_GridCodeStatic_PowerLimit_P_DEIE_ScalMax | Para_Electrical_Grid_GridCodeStatic_PowerLimit_P_DEIE_ScalMin | Para_Electrical_Grid_GridCodeStatic_tiDelayDEIE | Para_Electrical_Grid_Synchronization_ADL_Enable | Para_Electrical_Grid_Synchronization_BB_ClosCondLimits_Active | Para_Electrical_Grid_Synchronization_BS_Acc_Active | Para_Electrical_Grid_Synchronization_BS_Enable | Para_Electrical_Grid_Synchronization_BS_OnlyMan | Para_Electrical_Grid_Synchronization_C_CB_Enable | Para_Electrical_Grid_Synchronization_EngOpAfterMIF_Enable | Para_Electrical_Grid_Synchronization_F_BB_ClosCond_Hy | Para_Electrical_Grid_Synchronization_F_BB_ClosCond_LimHi | Para_Electrical_Grid_Synchronization_F_BB_ClosCond_LimLo | Para_Electrical_Grid_Synchronization_GCB_MainsCutOff_Active | Para_Electrical_Grid_Synchronization_GenDeexit_Enable | Para_Electrical_Grid_Synchronization_IslandOp_Enable | Para_Electrical_Grid_Synchronization_MCB_Ctr_Cust | Para_Electrical_Grid_Synchronization_MCB_Enable | Para_Electrical_Grid_Synchronization_MCB_ReSw2Mns_Enable | Para_Electrical_Grid_Synchronization_MCB_SyMMD2 | Para_Electrical_Grid_Synchronization_MIF_Enable | Para_Electrical_Grid_Synchronization_Mns_Enable | Para_Electrical_Grid_Synchronization_MSy | Para_Electrical_Grid_Synchronization_N_BS_Acc_LimHi | Para_Electrical_Grid_Synchronization_OnlyIsland_Enable | Para_Electrical_Grid_Synchronization_SyActive | Para_Electrical_Grid_Synchronization_tiBB_ClosCond_Delay | Para_Electrical_Grid_Synchronization_tiBB_ClosCondAftMnsFail_Delay | Para_Electrical_Grid_Synchronization_tiMainsOkDelay | Para_Electrical_Grid_Synchronization_tiMCB_COf_GCB_OpF | Para_Electrical_Grid_Synchronization_tiMIF | Para_Electrical_Grid_Synchronization_U_BB_ClosCond_Hy_Norm | Para_Electrical_Grid_Synchronization_U_BB_ClosCond_LimHi_Norm | Para_Electrical_Grid_Synchronization_U_BB_ClosCond_LimLo_Norm | Para_Electrical_Grid_Synchronization_U_Gen_DeEx_LimLo | Para_Electrical_MMD_MMD1_Ang_DiffMax1 | Para_Electrical_MMD_MMD1_Ang_PhiSync11 | Para_Electrical_MMD_MMD1_Aron_Act1 | Para_Electrical_MMD_MMD1_Bus3PhaseCircuit_Act1 | Para_Electrical_MMD_MMD1_F_DiffMin1 | Para_Electrical_MMD_MMD1_F_Nom1 | Para_Electrical_MMD_MMD1_F_Over1 | Para_Electrical_MMD_MMD1_F_Under1 | Para_Electrical_MMD_MMD1_Gen3PhaseCircuit_Act1 | Para_Electrical_MMD_MMD1_I_CurrRange1 | Para_Electrical_MMD_MMD1_I_GenNom1 | Para_Electrical_MMD_MMD1_I_Short1 | Para_Electrical_MMD_MMD1_MMDSynch_Act1 | Para_Electrical_MMD_MMD1_Mul_U_Bus1 | Para_Electrical_MMD_MMD1_Ti_F_OverDel1 | Para_Electrical_MMD_MMD1_Ti_F_UnderDel1 | Para_Electrical_MMD_MMD1_Ti_I_ShortDel1 | Para_Electrical_MMD_MMD1_Ti_U_AsymDel1 | Para_Electrical_MMD_MMD1_Ti_V_Over1 | Para_Electrical_MMD_MMD1_Ti_V_Under1 | Para_Electrical_MMD_MMD1_Ti_V_Under21 | Para_Electrical_MMD_MMD1_U_Asym1 | Para_Electrical_MMD_MMD1_U_BusNom1 | Para_Electrical_MMD_MMD1_U_DeadBus1 | Para_Electrical_MMD_MMD1_U_DeadSync1 | Para_Electrical_MMD_MMD1_U_DiffMax1 | Para_Electrical_MMD_MMD1_U_Gen_Nom1 | Para_Electrical_MMD_MMD1_U_Range1 | Para_Electrical_MMD_MMD1_U_RangeBus1 | Para_Electrical_MMD_MMD1_U_RangeSync11 | Para_Electrical_MMD_MMD1_U_RangeSync21 | Para_Electrical_MMD_MMD1_U_SyncNom1 | Para_Electrical_MMD_MMD1_V_Over1 | Para_Electrical_MMD_MMD1_V_Under1 | Para_Electrical_MMD_MMD1_V_Under21 | Para_Electrical_MMD_MMD2_Act | Para_Electrical_MMD_MMD2_Ang_DiffMax2 | Para_Electrical_MMD_MMD2_Ang_PhiSync12 | Para_Electrical_MMD_MMD2_Aron_Act2 | Para_Electrical_MMD_MMD2_Bus3PhaseCircuit_Act2 | Para_Electrical_MMD_MMD2_F_DiffMin2 | Para_Electrical_MMD_MMD2_F_Nom2 | Para_Electrical_MMD_MMD2_F_Over2 | Para_Electrical_MMD_MMD2_F_Under2 | Para_Electrical_MMD_MMD2_Gen3PhaseCircuit_Act2 | Para_Electrical_MMD_MMD2_I_CurrRange2 | Para_Electrical_MMD_MMD2_I_GenNom2 | Para_Electrical_MMD_MMD2_I_Short2 | Para_Electrical_MMD_MMD2_MMDSynch_Act2 | Para_Electrical_MMD_MMD2_Mul_U_Bus2 | Para_Electrical_MMD_MMD2_Mul_U_Sync12 | Para_Electrical_MMD_MMD2_Ti_F_OverDel2 | Para_Electrical_MMD_MMD2_Ti_F_UnderDel2 | Para_Electrical_MMD_MMD2_Ti_I_ShortDel2 | Para_Electrical_MMD_MMD2_Ti_U_AsymDel2 | Para_Electrical_MMD_MMD2_Ti_V_Over2 | Para_Electrical_MMD_MMD2_Ti_V_Under2 | Para_Electrical_MMD_MMD2_Ti_V_Under22 | Para_Electrical_MMD_MMD2_U_Asym2 | Para_Electrical_MMD_MMD2_U_BusNom2 | Para_Electrical_MMD_MMD2_U_DeadBus2 | Para_Electrical_MMD_MMD2_U_DeadSync2 | Para_Electrical_MMD_MMD2_U_DiffMax2 | Para_Electrical_MMD_MMD2_U_Gen_Nom2 | Para_Electrical_MMD_MMD2_U_Range2 | Para_Electrical_MMD_MMD2_U_RangeBus2 | Para_Electrical_MMD_MMD2_U_RangeSync12 | Para_Electrical_MMD_MMD2_U_RangeSync22 | Para_Electrical_MMD_MMD2_U_SyncNom2 | Para_Electrical_MMD_MMD2_V_Over2 | Para_Electrical_MMD_MMD2_V_Under2 | Para_Electrical_MMD_MMD2_V_Under22 | Para_emission_bco_scr_emline1_exist | Para_emission_bem_avgcalc_start | Para_emission_bem_avgcalc_steadystate | Para_emission_bno2_scr_emline1_exist | Para_emission_bno_scr_emline1_exist | Para_emission_bnoxs_heating_active | Para_emission_bscr_active | Para_emission_bt_scr_catin_exist | Para_emission_bt_scr_catout_exist | Para_emission_iidx_em_avgmon_option | Para_emission_iidx_noxs_config | Para_emission_iidx_scr_extemoption | Para_emission_inoxs_lifetime | Para_emission_rco_em_catout_mg_hi | Para_emission_rnox_em_catout_mg_hi | Para_emission_rnox_em_catout_mg_hitol | Para_emission_rnox_em_catout_mg_set | Para_emission_rnox_em_engout_mg_hi | Para_emission_rnox_em_engout_mg_hitol | Para_emission_rnox_em_engout_mg_set | Para_emission_rnox_noxs_catout_offs | Para_emission_rnox_noxs_engout_a_offs | Para_emission_rnox_noxs_engout_b_offs | Para_emission_rnox_noxs_engout_dev_hi | Para_emission_rnox_noxs_engout_offs | Para_emission_ro2_noxs_catout_offs | Para_emission_ro2_noxs_engout_a_offs | Para_emission_ro2_noxs_engout_b_offs | Para_emission_ro2_noxs_engout_dev_hi | Para_emission_ro2_noxs_engout_offs | Para_emission_ro2_reference | Para_emission_rp_scr_ureadosingunit_release | Para_emission_rratio_no2_nox_catout | Para_emission_rratio_no2_nox_engout | Para_emission_rt_scr_catin_hi | Para_emission_rt_scr_catout_hi | Para_emission_rt_scr_ureadosingunit_release | Para_emission_tiem_avgcalc_timebase | Para_emission_tiscr_eac_durationstartup | Para_emission_tiscr_emline_purgingwaiting | Para_EngDat_AccessNr | Para_EngDat_Act2StageTC | Para_EngDat_Act3WayKat | Para_EngDat_ActAutGas | Para_EngDat_ActAuxCool | Para_EngDat_ActAuxVent | Para_EngDat_ActCodinox | Para_EngDat_ActExhReactor | Para_EngDat_ActGasMix_NEx | Para_EngDat_ActHumidity | Para_EngDat_ActIC900 | Para_EngDat_ActIsolatedOp | Para_EngDat_ActKLS90_NEx | Para_EngDat_ActKLS98 | Para_EngDat_ActKLS98Misf_NEx | Para_EngDat_ActLIVC | Para_EngDat_ActMixTempCtr | Para_EngDat_ActMMU2_NEx | Para_EngDat_ActMonic | Para_EngDat_ActNOx | Para_EngDat_ActOilCount | Para_EngDat_ActOutDoorTemp | Para_EngDat_ActOxyKat | Para_EngDat_ActPFCtr | Para_EngDat_ActPlantCtr1 | Para_EngDat_ActPlantCtr10 | Para_EngDat_ActPlantCtr11 | Para_EngDat_ActPlantCtr12 | Para_EngDat_ActPlantCtr13 | Para_EngDat_ActPlantCtr14 | Para_EngDat_ActPlantCtr15 | Para_EngDat_ActPlantCtr16 | Para_EngDat_ActPlantCtr2 | Para_EngDat_ActPlantCtr3 | Para_EngDat_ActPlantCtr4 | Para_EngDat_ActPlantCtr5 | Para_EngDat_ActPlantCtr6 | Para_EngDat_ActPlantCtr7 | Para_EngDat_ActPlantCtr8 | Para_EngDat_ActPreChambGasComp | Para_EngDat_ActPRedTempIntakeAir | Para_EngDat_ActPRedTurboSpeed | Para_EngDat_ActReceiveDataBus1 | Para_EngDat_ActReceiveDataBus2 | Para_EngDat_ActReserveAnalog | Para_EngDat_ActReservePar | Para_EngDat_ActRoomTemp | Para_EngDat_ActSAFI | Para_EngDat_ActSpecGM | Para_EngDat_ActSpecialGas | Para_EngDat_ActTecJet | Para_EngDat_ActTempIntakeAir | Para_EngDat_ActTurboBypass | Para_EngDat_ActTurboSpeedA | Para_EngDat_ActTurboSpeedB | Para_EngDat_ActTurboSpeedLPA | Para_EngDat_ActTurboSpeedLPB | Para_EngDat_ActUniIO | Para_EngDat_ActWasteGate | Para_EngDat_ApplicationName_NEx | Para_EngDat_ApplicationType_NEx | Para_EngDat_BasisUpdateVers_NEx | Para_EngDat_CompRate | Para_EngDat_EngineNr_NEx | Para_EngDat_EngineType_NEx | Para_EngDat_GroupAccessNr | Para_EngDat_GroupAccessNr2 | Para_EngDat_GroupAccessNr3 | Para_EngDat_LanguageID_NEx | Para_EngDat_ModBusSlaveIDLink1 | Para_EngDat_ModBusSlaveIDLink2 | Para_EngDat_ModInertia | Para_EngDat_NumbGasmixer | Para_EngDat_NumbGasTrain | Para_EngDat_NumbGasTyp | Para_EngDat_NumbTecjet | Para_EngDat_NumbTurboBypass | Para_EngDat_Tempc_NEx | Para_EngDat_Tempt_NEx | Para_EngDat_Tempu_NEx | Para_EngDat_TurboBypass4_20mA | Para_EngDat_VersRPS_NEx | Para_EngDat_VersSPS_NEx | Para_EngDat_VersVIS_NEx | Para_EngDat_VisuUpdateVers_NEx | Para_Engine_ChargeTempCtr_DComp | Para_Engine_ChargeTempCtr_deadband | Para_Engine_ChargeTempCtr_dW_down | Para_Engine_ChargeTempCtr_dW_up | Para_Engine_ChargeTempCtr_dY_max | Para_Engine_ChargeTempCtr_IComp | Para_Engine_ChargeTempCtr_Kp_manualAdjust | Para_Engine_ChargeTempCtr_nvert | Para_Engine_ChargeTempCtr_PComp | Para_Engine_ChargeTempCtr_Pos_ChC_Valve_ScalMax | Para_Engine_ChargeTempCtr_Pos_ChC_Valve_ScalMin | Para_Engine_ChargeTempCtr_Pos_ChCValve | Para_Engine_ChargeTempCtr_t_min_pulse_down | Para_Engine_ChargeTempCtr_t_min_pulse_up | Para_Engine_ChargeTempCtr_t_period_down | Para_Engine_ChargeTempCtr_t_period_up | Para_Engine_ChargeTempCtr_Tn_manualAdjust | Para_Engine_ChargeTempCtr_Tv_manualAdjust | Para_Engine_ChargeTempCtr_WMax | Para_Engine_ChargeTempCtr_WMin | Para_Engine_ChargeTempCtr_Y_block | Para_Engine_ChargeTempCtr_YMax | Para_Engine_ChargeTempCtr_YMin | Para_Engine_Charging_AirFilterDiffPress_DPr_AirFilt_Exist | Para_Engine_Charging_AirFilterDiffPress_DPr_AirFilt_Hi_incr | Para_Engine_Charging_AirFilterDiffPress_DPr_AirFilt_Lo | Para_Engine_Charging_Pos_CBV_Ref_WG | Para_Engine_Charging_Pressure_DPr_Ch_FA_Hi | Para_Engine_Charging_Pressure_DPr_Ch_HPCooler_Hi | Para_Engine_Charging_Pressure_DPr_Ch_LPCooler_Hi | Para_Engine_Charging_Pressure_Pr_Ch_P1LP_A_Exist | Para_Engine_Charging_Pressure_Pr_Ch_P1LP_B_Exist | Para_Engine_Charging_Pressure_Pr_Ch_P1LPScalMax | Para_Engine_Charging_Pressure_Pr_Ch_P1LPScalMin | Para_Engine_Charging_Pressure_Pr_Ch_P2bFA_Exist | Para_Engine_Charging_Pressure_Pr_Ch_P2bFAScalMax | Para_Engine_Charging_Pressure_Pr_Ch_P2bFAScalMin | Para_Engine_Charging_Pressure_Pr_Ch_P2HP_A_Exist | Para_Engine_Charging_Pressure_Pr_Ch_P2HP_B_Exist | Para_Engine_Charging_Pressure_Pr_Ch_P2HP_Exist | Para_Engine_Charging_Pressure_Pr_Ch_P2HPScalMax | Para_Engine_Charging_Pressure_Pr_Ch_P2HPScalMin | Para_Engine_Charging_Pressure_Pr_Ch_P2LP_A_Exist | Para_Engine_Charging_Pressure_Pr_Ch_P2LP_B_Exist | Para_Engine_Charging_Pressure_Pr_Ch_P2LP_Exist | Para_Engine_Charging_Pressure_Pr_Ch_P2LPScalMax | Para_Engine_Charging_Pressure_Pr_Ch_P2LPScalMin | Para_Engine_Charging_Temp_T_Ch_T1LP_A_Exist | Para_Engine_Charging_Temp_T_Ch_T1LP_B_Exist | Para_Engine_Charging_Temp_T_Ch_T1LP_Exist | Para_Engine_Charging_Temp_T_Ch_T1LP_Hi | Para_Engine_Charging_tiWG_SS_Del | Para_Engine_Charging_WG_Check_Ena | Para_Engine_Charging_WG_Man | Para_Engine_Coupling_Comm1_Baud | Para_Engine_Coupling_Comm1_Parity | Para_Engine_Coupling_Comm1_PB_SlaveID1 | Para_Engine_Coupling_Comm1_PB_SlaveID2 | Para_Engine_Coupling_Comm1_PN_SlaveID1 | Para_Engine_Coupling_Comm1_Stopbit | Para_Engine_Coupling_Comm2_Baud | Para_Engine_Coupling_Comm2_Parity | Para_Engine_Coupling_Comm2_PB_SlaveID1 | Para_Engine_Coupling_Comm2_PB_SlaveID2 | Para_Engine_Coupling_Comm2_PN_SlaveID1 | Para_Engine_Coupling_Comm2_Stopbit | Para_Engine_Coupling_Comm_IPaddr_first_TCP | Para_Engine_Coupling_Comm_IPaddr_fourth_TCP | Para_Engine_Coupling_Comm_IPaddr_second_TCP | Para_Engine_Coupling_Comm_IPaddr_third_TCP | Para_Engine_Coupling_Comm_PortID_TCP | Para_Engine_Coupling_Comm_SlaveID_TCP | Para_Engine_Coupling_Comm_SubMask_first_TCP | Para_Engine_Coupling_Comm_SubMask_fourth_TCP | Para_Engine_Coupling_Comm_SubMask_second_TCP | Para_Engine_Coupling_Comm_SubMask_third_TCP | Para_Engine_Coupling_Idx_Comm1_Interface | Para_Engine_Coupling_Idx_Comm1_type | Para_Engine_Coupling_Idx_Comm2_Interface | Para_Engine_Coupling_Idx_Comm2_type | Para_Engine_Coupling_OPC_Rcv_Ena | Para_Engine_EngDat__IgnIC_900Active | Para_Engine_EngDat_AvailabilityTrackingOn | Para_Engine_EngDat_Country | Para_Engine_EngDat_IdleFrictionMon | Para_Engine_EngDat_IgnMon_Active | Para_Engine_EngDat_KLS98_Active | Para_Engine_EngDat_SA_Active | Para_Engine_EngDat_SDT_Avg_LoLo | Para_Engine_Island_Greenhouse_Num_Eng_LSL | Para_Engine_Island_Greenhouse_P_drift_GH_Ena | Para_Engine_Island_Greenhouse_P_Drift_Rel_Norm | Para_Engine_Island_Greenhouse_P_max_GH_Ena | Para_Engine_Island_Kp_P_Rot_Lam | Para_Engine_Island_Limit_P_LS_HyLo | Para_Engine_Island_LoadSh_LSL_Enable | Para_Engine_Island_P_el_LockTV_Norm | Para_Engine_Island_P_el_ReleaseTV_Norm | Para_Engine_Island_P_LoadReject_Active | Para_Engine_Island_P_Rot_Norm_Lam_Trig | Para_Engine_Island_Pr_CBV_Lock | Para_Engine_Island_Pr_CBV_Release | Para_Engine_Island_Ramp_P_Island_Split_DecGrad_Norm1 | Para_Engine_Island_Ramp_P_Island_Split_IncGrad_Norm1 | Para_Engine_Leanox_Comp_ZZPKorr | Para_Engine_Leanox_Gas1_Pr_Leanox_Offset_Isand1 | Para_Engine_Leanox_Gas1_Pr_P2_Dev_Lim1 | Para_Engine_Leanox_Gas2_Pr_Leanox_Offset_Isand2 | Para_Engine_Leanox_Gas2_Pr_P2_Dev_Lim2 | Para_Engine_Leanox_Gas3_Pr_Leanox_Offset_Isand3 | Para_Engine_Leanox_Gas3_Pr_P2_Dev_Lim3 | Para_Engine_Leanox_Gas4_Pr_Leanox_Offset_Isand4 | Para_Engine_Leanox_Gas4_Pr_P2_Dev_Lim4 | Para_Engine_Leanox_Gasmixer_Gas1_deadband | Para_Engine_Leanox_Gasmixer_Gas1_I | Para_Engine_Leanox_Gasmixer_Gas1_P | Para_Engine_Leanox_Gasmixer_Gas1_umax | Para_Engine_Leanox_Gasmixer_Gas1_umin | Para_Engine_Leanox_Gasmixer_Gas2_deadband | Para_Engine_Leanox_Gasmixer_Gas2_I | Para_Engine_Leanox_Gasmixer_Gas2_P | Para_Engine_Leanox_Gasmixer_Gas2_umax | Para_Engine_Leanox_Gasmixer_Gas2_umin | Para_Engine_Leanox_Gasmixer_Gas3_deadband | Para_Engine_Leanox_Gasmixer_Gas3_I | Para_Engine_Leanox_Gasmixer_Gas3_P | Para_Engine_Leanox_Gasmixer_Gas3_umax | Para_Engine_Leanox_Gasmixer_Gas3_umin | Para_Engine_Leanox_Gasmixer_Gas4_deadband | Para_Engine_Leanox_Gasmixer_Gas4_I | Para_Engine_Leanox_Gasmixer_Gas4_P | Para_Engine_Leanox_Gasmixer_Gas4_umax | Para_Engine_Leanox_Gasmixer_Gas4_umin | Para_Engine_Leanox_IdleLambdaCtr_Gas1_Pr_p2s_LLCtr1 | Para_Engine_Leanox_IdleLambdaCtr_Gas2_Pr_p2s_LLCtr2 | Para_Engine_Leanox_IdleLambdaCtr_Gas3_Pr_p2s_LLCtr3 | Para_Engine_Leanox_IdleLambdaCtr_Gas4_Pr_p2s_LLCtr4 | Para_Engine_Leanox_IdleLambdaCtr_Gasmixer_Ki_LeanoxC_GM | Para_Engine_Leanox_IdleLambdaCtr_Gasmixer_Kp_LeanoxC_GM | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Gas1_Lam_CR_Speed1 | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Gas2_Lam_CR_Speed2 | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Gas3_Lam_CR_Speed3 | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Gas4_Lam_CR_Speed4 | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Ki_LeanoxC_TJ | Para_Engine_Leanox_IdleLambdaCtr_GasPropValve_Kp_LeanoxC_TJ | Para_Engine_Leanox_IdleLambdaCtr_LLCtr_ki | Para_Engine_Leanox_IdleLambdaCtr_LLCtr_kp | Para_Engine_Leanox_IdleLambdaCtr_LLLCtr_act | Para_Engine_Leanox_IdleLambdaCtr_LLLCtr_delay_Trip | Para_Engine_Leanox_IdleLambdaCtr_Pr_p2s_Win_sy_lfg | Para_Engine_Leanox_LambdaFeedFwdCtr_Gas1_Lam_Start_Offs1 | Para_Engine_Leanox_LambdaFeedFwdCtr_Gas2_Lam_Start_Offs2 | Para_Engine_Leanox_LambdaFeedFwdCtr_Gas3_Lam_Start_Offs3 | Para_Engine_Leanox_LambdaFeedFwdCtr_Gas4_Lam_Start_Offs4 | Para_Engine_Leanox_LambdaFeedFwdCtr_N_LamOffs_x1 | Para_Engine_Leanox_LambdaFeedFwdCtr_N_LamOffs_x2 | Para_Engine_Leanox_LeanoxPRED | Para_Engine_Leanox_LeanoxRamp | Para_Engine_Leanox_Pr_P2s_Set_0kW | Para_Engine_PFPDR_Adv_IP_Ena | Para_Engine_PFPDR_Auto_Ena | Para_Engine_PFPDR_BH_Auto | Para_Engine_PFPDR_CA_IP_EGT | Para_Engine_PFPDR_CA_Offs_Lim | Para_Engine_PFPDR_Ena | Para_Engine_PFPDR_Lam_Lim | Para_Engine_PFPDR_tiSS_Del | Para_Engine_Power_Ctr_CBV_N | Para_Engine_Power_Ctr_GEN2_PowCtrl_Ki | Para_Engine_Power_Ctr_GEN2_PowCtrl_Kp | Para_Engine_Power_Ctr_Pr_P2s_CtrLim | Para_Engine_Power_Ctr_TV_N | Para_Engine_Power_ExtSet_P_Set5_ExtDI_Norm | Para_Engine_Power_FastStart_CA_GEN2_fastSt | Para_Engine_Power_FastStart_FastSpeedUp | Para_Engine_Power_FastStart_FastSync | Para_Engine_Power_FastStart_GEN2_preM_Act | Para_Engine_Power_FastStart_LowTransNOx_Ena | Para_Engine_Power_FastStart_P_Ramp_Norm1 | Para_Engine_Power_FastStart_P_Ramp_Norm2 | Para_Engine_Power_FastStart_P_Ramp_Norm3 | Para_Engine_Power_FastStart_P_Ramp_Norm4 | Para_Engine_Power_FastStart_PrR_GEN2_TV_level | Para_Engine_Power_FastStart_PrR_GEN2_TV_level_Hy | Para_Engine_Power_FastStart_ti_Desired1 | Para_Engine_Power_FastStart_ti_Desired2 | Para_Engine_Power_FastStart_ti_Desired3 | Para_Engine_Power_FastStart_ti_Desired4 | Para_Engine_Power_Limit_P_GhStep_Ena | Para_Engine_Power_Limit_P_GhStep_Lim_Norm0 | Para_Engine_Power_Limit_P_GhStep_Lim_Norm1 | Para_Engine_Power_Limit_P_GhStep_Lim_Norm2 | Para_Engine_Power_Limit_P_GhStep_Lim_Norm3 | Para_Engine_Power_Limit_P_GhStep_Lim_Norm4 | Para_Engine_Power_Limit_P_LimHiHi | Para_Engine_Power_RedCrankCase_P_Red_CC | Para_Engine_Power_RedExhaust_PID_EGT_I | Para_Engine_Power_RedExhaust_PID_EGT_P | Para_Engine_Power_RedGCBTemp_P_Red_TempMax_GenCB_Active | Para_Engine_Power_RedGCBTemp_P_Red_TempMax_GenCB_Rate | Para_Engine_Power_RedTransformer_P_Red_TransformerWarning_Rate | Para_Engine_Power_RedTransformer_P_Red_TransformerWarning_Sel | Para_Engine_Remote_RemoteReqActive | Para_Engine_Remote_ResetRemActive | Para_Engine_Remote_ResetRemRiskClass | Para_Engine_SAFI_SA_Ign_Active | Para_Engine_Speed_Ctr_CBV_IdleOp_D | Para_Engine_Speed_Ctr_CBV_IdleOp_I | Para_Engine_Speed_Ctr_CBV_IdleOp_N | Para_Engine_Speed_Ctr_CBV_IdleOp_P | Para_Engine_Speed_Ctr_CBV_IdleOp_umax | Para_Engine_Speed_Ctr_CBV_IdleOp_umin | Para_Engine_Speed_Ctr_CBV_IsolatedOp_D | Para_Engine_Speed_Ctr_CBV_IsolatedOp_I | Para_Engine_Speed_Ctr_CBV_IsolatedOp_N | Para_Engine_Speed_Ctr_CBV_IsolatedOp_P | Para_Engine_Speed_Ctr_CBV_IsolatedOp_umax | Para_Engine_Speed_Ctr_CBV_IsolatedOp_umin | Para_Engine_Speed_Ctr_TV_IdleOp_a | Para_Engine_Speed_Ctr_TV_IdleOp_D | Para_Engine_Speed_Ctr_TV_IdleOp_I | Para_Engine_Speed_Ctr_TV_IdleOp_N | Para_Engine_Speed_Ctr_TV_IdleOp_P | Para_Engine_Speed_Ctr_TV_IdleOp_umax | Para_Engine_Speed_Ctr_TV_IdleOp_umin | Para_Engine_Speed_Ctr_TV_IsolatedOp_N | Para_Engine_Speed_Limit_N_EngStart_HyHi | Para_Engine_Speed_Limit_N_EngStart_LimHi | Para_Engine_Speed_N_Offs_Sync | Para_Engine_SteadyState_ChargePress_Abs | Para_Engine_SteadyState_ChargePress_Rel | Para_Engine_SteadyState_ChargePress_ti_Filt | Para_Engine_SteadyState_ChargeTemp_Abs | Para_Engine_SteadyState_ChargeTemp_Rel | Para_Engine_SteadyState_ChargeTemp_ti_Filt | Para_Engine_SteadyState_Exhaust_Abs | Para_Engine_SteadyState_Exhaust_Rel | Para_Engine_SteadyState_Exhaust_ti_Filt | Para_Engine_SteadyState_Power_Abs | Para_Engine_SteadyState_Power_Rel | Para_Engine_SteadyState_Power_ti_Filt | Para_enginecontroller_blx2_enable | Para_enginecontroller_bp2s_comp_leanoxdrift | Para_enginecontroller_ioph_nox_measure_mandatory | Para_enginecontroller_ioph_nox_measure_recommend | Para_enginecontroller_ioph_p2s_comp_leanoxdrift_reset | Para_enginecontroller_ioph_p2s_comp_leanoxdrift_sec2 | Para_enginecontroller_p2s_comp_leanoxdrift_x1 | Para_enginecontroller_p2s_comp_leanoxdrift_x2 | Para_enginecontroller_p2s_comp_leanoxdrift_y1 | Para_enginecontroller_p2s_comp_leanoxdrift_y2 | Para_enginecontroller_rcoeff_p2s_comp_sector2 | Para_enginecontroller_rlx2_steadystatefactor | Para_enginecontroller_rp_p2s_comp_leanoxdrift_sp | Para_enginecontroller_rpr_lx2_offsetlimit | Para_enginecontroller_tifilterconst_nox | Para_enginecontroller_tilx2_ctrl_tn | Para_Exhaust_ActBoil | Para_Exhaust_ActExhDevAvg | Para_Exhaust_ActExhGasScav_NEx | Para_Exhaust_ActExhMax | Para_Exhaust_ActExhTemp | Para_Exhaust_ActInHec | Para_Exhaust_ActInKat | Para_Exhaust_ActKat | Para_Exhaust_ActOutHec | Para_Exhaust_ActOutKat | Para_Exhaust_ActTempInTurboCh | Para_Exhaust_ActTempOutHec1 | Para_Exhaust_ActTempOutHec2 | Para_exhaust_boxicat_exist | Para_exhaust_bpr_oxicat_in_exist | Para_exhaust_bpr_oxicat_in_fast_exist | Para_exhaust_bpr_oxicat_out_exist | Para_exhaust_bt_oxicat_in_exist | Para_exhaust_bt_oxicat_out_exist | Para_Exhaust_CODINOX_CO2_PneumVal | Para_Exhaust_CODINOX_tiCO2_ExPSp_StartOffTime | Para_Exhaust_CODINOX_tiCO2_ExPSp_StopOffTime | Para_Exhaust_DiffPressCooler_Pr_Diff_ExGCooler_Active | Para_Exhaust_DiffPressCooler_Pr_Diff_ExGCooler_Hi | Para_Exhaust_DiffPressCooler_Pr_Diff_ExGCooler_HyHi | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_Active | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_Hi | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_Hi1 | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_Hi2 | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_HyHi | Para_Exhaust_DiffPressFilter_Pr_Diff_ExGFilter_Lo | Para_Exhaust_EGValveEnable | Para_Exhaust_HeatExchanger_T_EGaHE1_HyHi_Trip | Para_Exhaust_HeatExchanger_T_EGaHE1_HyHi_Warn | Para_Exhaust_HeatExchanger_T_EGaHE1_LimHi_Trip | Para_Exhaust_HeatExchanger_T_EGaHE1_LimHi_Warn | Para_Exhaust_HeatExchanger_T_EGaHE2_HyHi_Trip | Para_Exhaust_HeatExchanger_T_EGaHE2_HyHi_Warn | Para_Exhaust_HeatExchanger_T_EGaHE2_LimHi_Trip | Para_Exhaust_HeatExchanger_T_EGaHE2_LimHi_Warn | Para_Exhaust_HeatExchanger_T_PlateHE_InpLimMax | Para_Exhaust_HeatExchanger_T_PlateHE_InpLimMin | Para_Exhaust_NOx_ActCtr | Para_Exhaust_NOx_ErrorMax | Para_Exhaust_NOx_O2ref | Para_Exhaust_NOx_Sensor1_ActSensor | Para_Exhaust_NOx_Sensor1_NOxOffset | Para_Exhaust_NOx_Sensor1_O2Offset | Para_Exhaust_NOx_Sensor2_ActSensor | Para_Exhaust_NOx_Sensor2_NOxOffset | Para_Exhaust_NOx_Sensor2_O2Offset | Para_Exhaust_NOx_SetNOx | Para_Exhaust_Pr_EGaHPTC_A_Active | Para_Exhaust_Pr_EGaHPTC_B_Active | Para_Exhaust_Pr_EGaLPTC_A_Active | Para_Exhaust_Pr_EGaLPTC_B_Active | Para_Exhaust_Pr_EGbHPTC_A_Active | Para_Exhaust_Pr_EGbHPTC_B_Active | Para_Exhaust_Reactor_Active | Para_Exhaust_Reactor_ActiveHys | Para_Exhaust_Reactor_AdjustRefTemp | Para_Exhaust_Reactor_FlapTimer1 | Para_Exhaust_Reactor_FlapTimer2 | Para_Exhaust_Reactor_LimitReactChamb00 | Para_Exhaust_Reactor_LimitReactChamb25 | Para_Exhaust_Reactor_LimitReactChamb50 | Para_Exhaust_Reactor_LimitReactChamb75 | Para_Exhaust_Reactor_LimitReactChambStartGasInj | Para_Exhaust_Reactor_RelTemp1 | Para_Exhaust_Reactor_RelTemp2 | Para_Exhaust_Reactor_Sel_Flap5Pos | Para_Exhaust_Reactor_Sel_FlapActEl | Para_Exhaust_Reactor_T_ThR_LimGasHy | Para_Exhaust_Reactor_T_ThR_LimPInc | Para_Exhaust_Reactor_T_ThR_SetwoGas | Para_Exhaust_Reactor_ThR_NatGas | Para_Exhaust_Reactor_ThR_woGas | Para_Exhaust_Reactor_ti_ThR_TimePInc | Para_Exhaust_Reactor_ti_ThR_ValDurationPInc | Para_Exhaust_Reactor_ti_ThR_ValIntervalPInc | Para_exhaust_rpr_eg_deflag_fast_hihi | Para_exhaust_rpr_oxicat_diff_hi | Para_exhaust_rt_oxicat_in_hi | Para_exhaust_rt_oxicat_out_hihi | Para_Exhaust_Scavenging_EGScav_ifAuxV_ok | Para_Exhaust_Scavenging_N2_NoScavGas1 | Para_Exhaust_Scavenging_N2_NoScavGas2 | Para_Exhaust_Scavenging_ScavBeStart_Active | Para_Exhaust_SCR_Active | Para_Exhaust_SCR_Dosing_Flow_Urea100 | Para_Exhaust_SCR_Dosing_Flow_Urea30 | Para_Exhaust_SCR_Dosing_Flow_Urea40 | Para_Exhaust_SCR_Dosing_Flow_Urea50 | Para_Exhaust_SCR_Dosing_Flow_Urea60 | Para_Exhaust_SCR_Dosing_Flow_Urea70 | Para_Exhaust_SCR_Dosing_Flow_Urea80 | Para_Exhaust_SCR_Dosing_Flow_Urea90 | Para_Exhaust_SCR_Dosing_Flow_Urea_Hi | Para_Exhaust_SCR_Dosing_Flow_Urea_Offs | Para_Exhaust_SCR_Dosing_Flow_Urea_ScalMax | Para_Exhaust_SCR_Dosing_Flow_Urea_ScalMin | Para_Exhaust_SCR_Dosing_Flow_Urea_Set_ScalMax | Para_Exhaust_SCR_Dosing_Flow_Urea_Set_ScalMin | Para_Exhaust_SCR_Dosing_Flow_UreaGain | Para_Exhaust_SCR_Dosing_Pr_AirSupply_Hi | Para_Exhaust_SCR_Dosing_Pr_AirSupply_Lo | Para_Exhaust_SCR_Dosing_Pr_AirSupply_ScalMax | Para_Exhaust_SCR_Dosing_Pr_AirSupply_ScalMin | Para_Exhaust_SCR_Dosing_Pr_Urea_Hi | Para_Exhaust_SCR_Dosing_Pr_Urea_Lo | Para_Exhaust_SCR_Dosing_Pr_Urea_ScalMax | Para_Exhaust_SCR_Dosing_Pr_Urea_ScalMin | Para_Exhaust_SCR_Dosing_tiAirCompressed_OfC | Para_Exhaust_SCR_Dosing_tiUreaTank_LevelLow | Para_Exhaust_SCR_Dosing_UreaCirculatePump_Exist | Para_Exhaust_SCR_Dosing_UreaPump_Service | Para_Exhaust_SCR_Emission_CEMS_Shutdown | Para_Exhaust_SCR_Emission_CEMS_SteadyState | Para_Exhaust_SCR_Emission_CO_Eng_Out_Set | Para_Exhaust_SCR_Emission_CO_SCR_Out_Hi | Para_Exhaust_SCR_Emission_CO_SCR_ScalMax | Para_Exhaust_SCR_Emission_CO_SCR_ScalMin | Para_Exhaust_SCR_Emission_Idx_NOxS_Config | Para_Exhaust_SCR_Emission_NH3_Slip_Ctrl_Active | Para_Exhaust_SCR_Emission_NO2_SCR_ScalMax | Para_Exhaust_SCR_Emission_NO2_SCR_ScalMin | Para_Exhaust_SCR_Emission_NO_Ctrl_SCR_ScalMax | Para_Exhaust_SCR_Emission_NO_Ctrl_SCR_ScalMin | Para_Exhaust_SCR_Emission_NO_NH3_Slip_Set | Para_Exhaust_SCR_Emission_NO_SCR_ScalMax | Para_Exhaust_SCR_Emission_NO_SCR_ScalMin | Para_Exhaust_SCR_Emission_NOx_Eng_Out_Set | Para_Exhaust_SCR_Emission_NOx_SCR_Out_Hi | Para_Exhaust_SCR_Emission_NOx_SCR_Out_Set | Para_Exhaust_SCR_Emission_NOxS_Eng_Out_Hi | Para_Exhaust_SCR_Emission_tiGasAnalys_Purge_Duration | Para_Exhaust_SCR_Emission_tiGasAnalys_Purge_Intervall | Para_Exhaust_SCR_Emission_tiGasAnalys_Waiting | Para_Exhaust_SCR_Emission_tiNO_AboveLimit | Para_Exhaust_SCR_Emission_tiReset_SampleGas_Valves | Para_Exhaust_SCR_P_LoadEngine_Dosing | Para_Exhaust_SCR_Pr_SCR_Hi | Para_Exhaust_SCR_Pr_SCR_In_ScalMax | Para_Exhaust_SCR_Pr_SCR_In_ScalMin | Para_Exhaust_SCR_Pr_SCR_Out_ScalMax | Para_Exhaust_SCR_Pr_SCR_Out_ScalMin | Para_Exhaust_SCR_SCR_Release | Para_Exhaust_SCR_T_SCR_Avg | Para_Exhaust_SCR_T_SCR_In_Hi | Para_Exhaust_SCR_T_SCR_In_ScalMax | Para_Exhaust_SCR_T_SCR_In_ScalMin | Para_Exhaust_SCR_T_SCR_Out_Hi | Para_Exhaust_SCR_T_SCR_Out_ScalMax | Para_Exhaust_SCR_T_SCR_Out_ScalMin | Para_Exhaust_T_EGaHPTC_A_Active | Para_Exhaust_T_EGaHPTC_B_Active | Para_Exhaust_T_EGbHPTC_A_Active | Para_Exhaust_T_EGbHPTC_B_Active | Para_Exhaust_TCSpeed2Stage_20mA_A | Para_Exhaust_TCSpeed2Stage_20mA_B | Para_Exhaust_TCSpeed2Stage_4mA_A | Para_Exhaust_TCSpeed2Stage_4mA_B | Para_Exhaust_TCSpeed2Stage_ActTempOutlet_A | Para_Exhaust_TCSpeed2Stage_ActTempOutlet_B | Para_Exhaust_TCSpeed2Stage_IncLimit | Para_Exhaust_TCSpeed2Stage_Limit | Para_Exhaust_TCSpeed2Stage_LimitHys | Para_Exhaust_TCSpeedA_20mA | Para_Exhaust_TCSpeedA_4mA | Para_Exhaust_TCSpeedA_Limit | Para_Exhaust_TCSpeedA_LimitHys | Para_Exhaust_TCSpeedB_20mA | Para_Exhaust_TCSpeedB_4mA | Para_Exhaust_TCSpeedB_Limit | Para_Exhaust_TCSpeedB_LimitHys | Para_Exhaust_TempBoilHys | Para_Exhaust_TempBoilInputMax | Para_Exhaust_TempBoilInputMin | Para_Exhaust_TempBoilTrip | Para_Exhaust_TempBoilWarning | Para_Exhaust_TempExhAvgDevNeg | Para_Exhaust_TempExhAvgDevPos | Para_Exhaust_TempExhAvgPnGr40 | Para_Exhaust_TempExhMaxPnGr40 | Para_Exhaust_TempExhMaxPnSm40 | Para_Exhaust_TempInHexHys | Para_Exhaust_TempInHexMax | Para_Exhaust_TempInKatHys | Para_Exhaust_TempInKatMax | Para_Exhaust_TempInTurboAlarm | Para_Exhaust_TempInTurboAlarmHys | Para_Exhaust_TempInTurboMax | Para_Exhaust_TempInTurboMaxHys | Para_Exhaust_TempKatAlarm | Para_Exhaust_TempKatAlarmHys | Para_Exhaust_TempKatdTMax | Para_Exhaust_TempKatdTRel | Para_Exhaust_TempKatdTRelHys | Para_Exhaust_TempKatHys | Para_Exhaust_TempKatMax | Para_Exhaust_TempOutHexHys | Para_Exhaust_TempOutHexMax | Para_Exhaust_TempOutKatHys | Para_Exhaust_TempOutKatMax | Para_Exhaust_TimeScavening | Para_Exhaust_ValveControl_EGValveRegulation | Para_Exhaust_ValveControl_Sel_EGVa_Combi | Para_Exhaust_ValveControl_Sel_EGVa_ROTORK | Para_Exhaust_ValveControl_Sel_EGVa_Torque | Para_Gas_Cnt_Gas_NormM3 | Para_Gas_Cnt_Gas_OpM3 | Para_Gas_Cnt_GasImp_Active | Para_Gas_GasData_Gas1_HCR1 | Para_Gas_GasData_Gas1_LHV1 | Para_Gas_GasData_Gas1_MinAirReq1 | Para_Gas_GasData_Gas1_StdGD1 | Para_Gas_GasData_Gas2_HCR2 | Para_Gas_GasData_Gas2_LHV2 | Para_Gas_GasData_Gas2_MinAirReq2 | Para_Gas_GasData_Gas2_StdGD2 | Para_Gas_GasData_Gas3_HCR3 | Para_Gas_GasData_Gas3_LHV3 | Para_Gas_GasData_Gas3_MinAirReq3 | Para_Gas_GasData_Gas3_StdGD3 | Para_Gas_GasData_Gas4_HCR4 | Para_Gas_GasData_Gas4_LHV4 | Para_Gas_GasData_Gas4_MinAirReq4 | Para_Gas_GasData_Gas4_StdGD4 | Para_Gas_Gasmixer_Gas1_y1 | Para_Gas_Gasmixer_Gas1_y2 | Para_Gas_Gasmixer_Gas2_y1 | Para_Gas_Gasmixer_Gas2_y2 | Para_Gas_Gasmixer_Gas3_y1 | Para_Gas_Gasmixer_Gas3_y2 | Para_Gas_Gasmixer_Gas4_y1 | Para_Gas_Gasmixer_Gas4_y2 | Para_Gas_GasMixerSpecial_N_Eng_RunUpLim | Para_Gas_GasMixerSpecial_Pos_GM_RunUpOffset | Para_Gas_GasPropValve_Gas1_Lam_TJ_Power_Offs1 | Para_Gas_GasPropValve_Gas1_Lam_TJ_Speed_Offs1 | Para_Gas_GasPropValve_Gas1_x1 | Para_Gas_GasPropValve_Gas1_x2 | Para_Gas_GasPropValve_Gas1_y1 | Para_Gas_GasPropValve_Gas1_y2 | Para_Gas_GasPropValve_Gas2_Lam_TJ_Power_Offs2 | Para_Gas_GasPropValve_Gas2_Lam_TJ_Speed_Offs2 | Para_Gas_GasPropValve_Gas2_x1 | Para_Gas_GasPropValve_Gas2_x2 | Para_Gas_GasPropValve_Gas2_y1 | Para_Gas_GasPropValve_Gas2_y2 | Para_Gas_GasPropValve_Gas3_Lam_TJ_Power_Offs3 | Para_Gas_GasPropValve_Gas3_Lam_TJ_Speed_Offs3 | Para_Gas_GasPropValve_Gas3_x1 | Para_Gas_GasPropValve_Gas3_x2 | Para_Gas_GasPropValve_Gas3_y1 | Para_Gas_GasPropValve_Gas3_y2 | Para_Gas_GasPropValve_Gas4_Lam_TJ_Power_Offs4 | Para_Gas_GasPropValve_Gas4_Lam_TJ_Speed_Offs4 | Para_Gas_GasPropValve_Gas4_x1 | Para_Gas_GasPropValve_Gas4_x2 | Para_Gas_GasPropValve_Gas4_y1 | Para_Gas_GasPropValve_Gas4_y2 | Para_Gas_GasRail_Pr_GR_I_Exist | Para_Gas_GasRail_Pr_GR_II_Exist | Para_Gas_GasRail_Pr_GR_IScalMax | Para_Gas_GasRail_Pr_GR_IScalMin | Para_Gas_GasRail_T_GR_Exist | Para_Gas_GasTrain_DPr_GR_BOV_Open_Hy | Para_Gas_GasTrain_MGT_SetActAdjustActive | Para_Gas_GasTrain_Pr_MGT_PipeLoss_Ch_P1 | Para_Gas_GasTrain_Pr_MGT_PipeLoss_Ch_P2 | Para_Gas_GasTrain_Pr_MGT_PipeLoss_P1 | Para_Gas_GasTrain_Pr_MGT_PipeLoss_P2 | Para_Gas_GasTrain_Pr_MGT_sp_offset | Para_Gas_GasTrain_Pr_MGT_spScalMax | Para_Gas_GasTrain_Pr_MGT_spScalMin | Para_Gas_GasTrain_tiBOV_Open_Max | Para_Gas_GasTrain_tiBOV_Open_Min | Para_Gas_GCActive | Para_Gas_GT_MixActive | Para_Gas_GT_MixActiveEngStop | Para_Gas_Num_GM | Para_Gas_Num_GT1_Lines | Para_Gas_P_GT_SetLim | Para_Gas_Pr_GasPrAbsActive | Para_Gas_PreChambDifPress_Pr_BlowOff_LimHi | Para_Gas_PreChambGasTrain_PCGT_SafeDevice_Exist | Para_Gas_PreChambGasTrain_PCGT_SetActAdjustActive | Para_Gas_PreChambGasTrain_Pr_PCGT_Out_Exist | Para_Gas_PreChambGasTrain_Pr_PCGT_OutScalMax | Para_Gas_PreChambGasTrain_Pr_PCGT_OutScalMin | Para_Gas_PreChambGasTrain_Pr_PCGT_sp_offset | Para_Gas_PreChambGasTrain_Pr_PCGT_spScalMax | Para_Gas_PreChambGasTrain_Pr_PCGT_spScalMin | Para_Gas_PreChambGasTrain_T_PCGAfCo_Active | Para_Gas_PreChambGasTrain_T_PCGAfCo_HyHi | Para_Gas_PreChambGasTrain_T_PCGAfCo_LimHi | Para_Gas_SpecGas_AdvGasPropValveStart_P_TJ_SG_Start_Norm | Para_Gas_SpecGas_AdvGasPropValveStart_TJ_SG_Start1 | Para_Gas_SpecGas_AdvGasPropValveStart_TJ_SG_Start2 | Para_Gas_SpecGas_AdvGasPropValveStart_TJ_SG_Start3 | Para_Gas_SpecGas_AdvGasPropValveStart_TJ_SG_Start4 | Para_Gas_SpecGas_AdvGasPropValveStart_TJ_SG_Start_Ena | Para_Gas_SpecGas_BioGas_BiogasActive | Para_Gas_SpecGas_BioGas_Msg3327Active | Para_Gas_SpecGas_BioGas_Msg3328Active | Para_Gas_SpecGas_BioGas_Msg3567Active | Para_Gas_SpecGas_BioGas_Msg3568Active | Para_Gas_SpecGas_BioGas_Msg3569Active | Para_Gas_SpecGas_BioGas_Msg3570Active | Para_Gas_SpecGas_CBV34Control_CBV34_Fun | Para_Gas_SpecGas_CBV34Control_CBV34_min | Para_Gas_SpecGas_CBV34Control_CBV34_Set | Para_Gas_SpecGas_CBV34Control_CBV34Ctr_ki | Para_Gas_SpecGas_CBV34Control_CBV34Ctr_kp | Para_Gas_SpecGas_GlowIgn_CA_SG_IP_Step | Para_Gas_SpecGas_GlowIgn_FastPowerRed_FPRGasRed | Para_Gas_SpecGas_GlowIgn_FastPowerRed_FPRGasRedOpt | Para_Gas_SpecGas_GlowIgn_FastPowerRed_FPRGasRedTime | Para_Gas_SpecGas_GlowIgn_FastPowerRed_Pos_SG_FPR_CBV | Para_Gas_SpecGas_GlowIgn_FastPowerRed_Pos_SG_FPR_TV | Para_Gas_SpecGas_GlowIgn_Pos_Gm_SG_Offs | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_Num_SG_SCO_Max | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_Num_SG_SCO_Max_DltT | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_Pos_SG_SCO_CBV | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_Pos_SG_SCO_TV | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_SG_SCO_Active | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_ti_SG_SCO_Block | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_ti_SG_SCO_DurMonDis | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_ti_SG_SCO_Max | Para_Gas_SpecGas_GlowIgn_SafetyCutOut_ti_SG_SCO_TV | Para_Gas_SpecGas_GlowIgnPrevActive | Para_Gas_SpecGas_SG_BackFirePrev | Para_Gas_SpecGas_ti_SG_EngBlock | Para_GasData_Gas1_CalorificValue | Para_GasData_Gas1_MinAirRequirement | Para_GasData_Gas1_SpecificHeatRatio | Para_GasData_Gas1_StandGasDens | Para_GasData_Gas2_CalorificValue | Para_GasData_Gas2_MinAirRequirement | Para_GasData_Gas2_SpecificHeatRatio | Para_GasData_Gas2_StandGasDens | Para_GasData_Gas3_CalorificValue | Para_GasData_Gas3_MinAirRequirement | Para_GasData_Gas3_SpecificHeatRatio | Para_GasData_Gas3_StandGasDens | Para_GasData_Gas4_CalorificValue | Para_GasData_Gas4_MinAirRequirement | Para_GasData_Gas4_SpecificHeatRatio | Para_GasData_Gas4_StandGasDens | Para_Gasmixer_Gas1_AirTempPoint1 | Para_Gasmixer_Gas1_AirTempPoint2 | Para_Gasmixer_Gas1_GasMixPosOffsetIsland | Para_Gasmixer_Gas1_GasMixPosOffsetNet | Para_Gasmixer_Gas1_GasMixPosPoint1 | Para_Gasmixer_Gas1_GasMixPosPoint2 | Para_Gasmixer_Gas1_PosOffsetPoint1 | Para_Gasmixer_Gas1_PosOffsetPoint2 | Para_Gasmixer_Gas1_TempOilPoint1 | Para_Gasmixer_Gas1_TempOilPoint2 | Para_Gasmixer_Gas2_AirTempPoint1 | Para_Gasmixer_Gas2_AirTempPoint2 | Para_Gasmixer_Gas2_GasMixPosOffsetIsland | Para_Gasmixer_Gas2_GasMixPosOffsetNet | Para_Gasmixer_Gas2_GasMixPosPoint1 | Para_Gasmixer_Gas2_GasMixPosPoint2 | Para_Gasmixer_Gas2_PosOffsetPoint1 | Para_Gasmixer_Gas2_PosOffsetPoint2 | Para_Gasmixer_Gas2_TempOilPoint1 | Para_Gasmixer_Gas2_TempOilPoint2 | Para_Gasmixer_Gas3_AirTempPoint1 | Para_Gasmixer_Gas3_AirTempPoint2 | Para_Gasmixer_Gas3_GasMixPosOffsetIsland | Para_Gasmixer_Gas3_GasMixPosOffsetNet | Para_Gasmixer_Gas3_GasMixPosPoint1 | Para_Gasmixer_Gas3_GasMixPosPoint2 | Para_Gasmixer_Gas3_PosOffsetPoint1 | Para_Gasmixer_Gas3_PosOffsetPoint2 | Para_Gasmixer_Gas3_TempOilPoint1 | Para_Gasmixer_Gas3_TempOilPoint2 | Para_Gasmixer_Gas4_AirTempPoint1 | Para_Gasmixer_Gas4_AirTempPoint2 | Para_Gasmixer_Gas4_GasMixPosOffsetIsland | Para_Gasmixer_Gas4_GasMixPosOffsetNet | Para_Gasmixer_Gas4_GasMixPosPoint1 | Para_Gasmixer_Gas4_GasMixPosPoint2 | Para_Gasmixer_Gas4_PosOffsetPoint1 | Para_Gasmixer_Gas4_PosOffsetPoint2 | Para_Gasmixer_Gas4_TempOilPoint1 | Para_Gasmixer_Gas4_TempOilPoint2 | Para_Gasmixer_IdleLambdaCtr_Delay1 | Para_Gasmixer_IdleLambdaCtr_Delay2 | Para_Gasmixer_IdleLambdaCtr_Gas1_GasMixPosDP | Para_Gasmixer_IdleLambdaCtr_Gas1_TrPos | Para_Gasmixer_IdleLambdaCtr_Gas2_GasMixPosDP | Para_Gasmixer_IdleLambdaCtr_Gas2_TrPos | Para_Gasmixer_IdleLambdaCtr_Gas3_GasMixPosDP | Para_Gasmixer_IdleLambdaCtr_Gas3_TrPos | Para_Gasmixer_IdleLambdaCtr_Gas4_GasMixPosDP | Para_Gasmixer_IdleLambdaCtr_Gas4_TrPos | Para_Gasmixer_IdleLambdaCtr_IComp | Para_Gasmixer_IdleLambdaCtr_PComp | Para_Gasmixer_LimitAirTempMax | Para_Gasmixer_LimitAirTempMin | Para_Gasmixer_Special_FullStepAirThrot1 | Para_Gasmixer_Special_FullStepAirThrot2 | Para_Gasmixer_Special_FullStepGasThrot | Para_Gasmixer_Special_Gas1_AirThrotFull | Para_Gasmixer_Special_Gas1_OfAirThrotIdle | Para_Gasmixer_Special_Gas1_OfAirThrotNetp | Para_Gasmixer_Special_Gas1_OfAirThrotStart | Para_Gasmixer_Special_Gas2_AirThrotFull | Para_Gasmixer_Special_Gas2_OfAirThrotIdle | Para_Gasmixer_Special_Gas2_OfAirThrotNetp | Para_Gasmixer_Special_Gas2_OfAirThrotStart | Para_Gasmixer_Special_Gas3_AirThrotFull | Para_Gasmixer_Special_Gas3_OfAirThrotIdle | Para_Gasmixer_Special_Gas3_OfAirThrotNetp | Para_Gasmixer_Special_Gas3_OfAirThrotStart | Para_Gasmixer_Special_Gas4_AirThrotFull | Para_Gasmixer_Special_Gas4_OfAirThrotIdle | Para_Gasmixer_Special_Gas4_OfAirThrotNetp | Para_Gasmixer_Special_Gas4_OfAirThrotStart | Para_Gasmixer_Special_SpeedAirThrot1 | Para_Gasmixer_Special_SpeedAirThrot2 | Para_Gasmixer_Special_SpeedGasThrot | Para_Gasmixer_StepFrequency | Para_Gasmixer_StepFrequency1 | Para_Gasmixer_StepsGasmixPos | Para_Gasmixer_StepsGasmixPos1 | Para_Gasmixer_TempOilMax | Para_Gasmixer_TempOilMin | Para_GeneratCtr_ChoiceSet_ExtmAneg | Para_GeneratCtr_ChoiceSet_ExtmApos | Para_GeneratCtr_ChoiceSet_ExtPF1fix | Para_GeneratCtr_ChoiceSet_ExtPF2fix | Para_GeneratCtr_ChoiceSet_ExtPF3fix | Para_GeneratCtr_ChoiceSet_ExtPF4fix | Para_GeneratCtr_ChoiceSet_ExtPF5fix | Para_GeneratCtr_ChoiceSet_ExtSetPF1 | Para_GeneratCtr_ChoiceSet_ExtSetPF2 | Para_GeneratCtr_ChoiceSet_PFIntern | Para_GeneratCtr_ChoiceSet_Type | Para_GeneratCtr_PowerDep_PFPowPoint1 | Para_GeneratCtr_PowerDep_PFPowPoint2 | Para_GeneratCtr_PowerDep_PowPoint1 | Para_GeneratCtr_PowerDep_PowPoint2 | Para_GeneratCtr_QLimit_AppPowNom | Para_GeneratCtr_QLimit_PolarWheelLimit | Para_GeneratCtr_QLimit_PolarWheelTrip | Para_GeneratCtr_QLimit_SyncReakt | Para_GeneratCtr_TimeTable_PFTimePoint1 | Para_GeneratCtr_TimeTable_PFTimePoint2 | Para_GeneratCtr_TimeTable_PFTimePoint3 | Para_GeneratCtr_TimeTable_PFTimePoint4 | Para_GeneratCtr_TimeTable_PFTimePoint5 | Para_GeneratCtr_TimeTable_PFTimePoint6 | Para_GeneratCtr_TimeTable_TimePoint1h | Para_GeneratCtr_TimeTable_TimePoint1m | Para_GeneratCtr_TimeTable_TimePoint2h | Para_GeneratCtr_TimeTable_TimePoint2m | Para_GeneratCtr_TimeTable_TimePoint3h | Para_GeneratCtr_TimeTable_TimePoint3m | Para_GeneratCtr_TimeTable_TimePoint4h | Para_GeneratCtr_TimeTable_TimePoint4m | Para_GeneratCtr_TimeTable_TimePoint5h | Para_GeneratCtr_TimeTable_TimePoint5m | Para_GeneratCtr_TimeTable_TimePoint6h | Para_GeneratCtr_TimeTable_TimePoint6m | Para_GeneratCtr_Type | Para_GeneratCtr_Voltage_ActVoltAdjust | Para_GeneratCtr_Voltage_MaxVoltAdjNeg | Para_GeneratCtr_Voltage_MaxVoltAdjPos | Para_GeneratCtr_Voltage_PFVoltPoint1 | Para_GeneratCtr_Voltage_PFVoltPoint2 | Para_GeneratCtr_Voltage_PFVoltPoint3 | Para_GeneratCtr_Voltage_PFVoltPoint4 | Para_GeneratCtr_Voltage_PFVoltPoint5 | Para_GeneratCtr_Voltage_PFVoltPoint6 | Para_GeneratCtr_Voltage_RampeVoltAdj | Para_GeneratCtr_Voltage_VoltOffsetFullLoad | Para_GeneratCtr_Voltage_VoltOffsetIdle | Para_GeneratCtr_Voltage_VoltPoint1 | Para_GeneratCtr_Voltage_VoltPoint2 | Para_GeneratCtr_Voltage_VoltPoint3 | Para_GeneratCtr_Voltage_VoltPoint4 | Para_GeneratCtr_Voltage_VoltPoint5 | Para_GeneratCtr_Voltage_VoltPoint6 | Para_GeneratCtr_WindTempDep_PFRedWindTemp | Para_GeneratCtr_WindTempDep_TempPowRed | Para_GeneratCtr_WindTempDep_TempStartPFred | Para_Generator_ActBear1 | Para_Generator_ActBear2 | Para_Generator_ActDisplace | Para_Generator_ActInletTemp | Para_Generator_ActOutletTemp | Para_Generator_ActPt100M1_NEx | Para_Generator_ActPt100PTCWindTemp | Para_Generator_ActVoltExcit | Para_Generator_DeActDiffProtect | Para_Generator_Displace20mA | Para_Generator_Displace4mA | Para_Generator_DisplaceDelay1 | Para_Generator_DisplaceDelay2 | Para_Generator_DisplaceLimit1 | Para_Generator_DisplaceLimit2 | Para_Generator_TempBear1Alarm | Para_Generator_TempBear1Trip | Para_Generator_TempBear2Alarm | Para_Generator_TempBear2Trip | Para_Generator_TempBearAlarmHys | Para_Generator_TempBearTripHys | Para_Generator_TempWindPh123AlarmHys | Para_Generator_TempWindPh123TripHys | Para_Generator_TempWindPh1Alarm | Para_Generator_TempWindPh1Trip | Para_Generator_TempWindPh2Alarm | Para_Generator_TempWindPh2Trip | Para_Generator_TempWindPh3Alarm | Para_Generator_TempWindPh3Trip | Para_Generator_TempWindPTCAlarm | Para_Generator_TempWindPTCAlarmHys | Para_Generator_TempWindPTCTrip | Para_Generator_TempWindPTCTripHys | Para_Generator_VoltExitLimit | Para_Generator_VoltExitLimitHys | Para_Generator_VoltExitMax | Para_Generator_VoltExitMaxHys | Para_Grid_DelayStabilGrid | Para_Grid_GridCode_ActDynGridCode | Para_Grid_GridCode_ActDynGridCodeMonOnly | Para_Grid_GridCode_AngleSumLimit | Para_Grid_GridCode_CurrentChangeLimit | Para_Grid_GridCode_PolarWheelAngleLimit | Para_Grid_GridCode_PoleSlipLimit | Para_Grid_GridCode_PowerLimit | Para_Grid_GridCode_SpeedChangeLimit | Para_Grid_GridCode_StopCap | Para_Grid_GridCode_VoltageLimit | Para_Grid_GridCode_XqGen | Para_Grid_GridCodeStatic_010_Ramp_ActPRampMainFailure | Para_Grid_GridCodeStatic_010_Ramp_ActPRampUtility | Para_Grid_GridCodeStatic_010_Ramp_ActSlowRampPFC | Para_Grid_GridCodeStatic_010_Ramp_PowerFacSetpoint | Para_Grid_GridCodeStatic_010_Ramp_PRampMainFailure | Para_Grid_GridCodeStatic_010_Ramp_RampUtility | Para_Grid_GridCodeStatic_010_Ramp_TimeDelMainOk | Para_Grid_GridCodeStatic_020_PowerSet_ActPowerSetUtility | Para_Grid_GridCodeStatic_020_PowerSet_UtilityConst1 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityConst2 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityConst3 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityConst4 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityConst5 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityCurr1 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityCurr2 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityPoint1 | Para_Grid_GridCodeStatic_020_PowerSet_UtilityPoint2 | Para_Grid_GridCodeStatic_030_PowerLimit_ActPowerLimUtility | Para_Grid_GridCodeStatic_030_PowerLimit_IntSetPoint | Para_Grid_GridCodeStatic_030_PowerLimit_LimitDemOff | Para_Grid_GridCodeStatic_030_PowerLimit_LimitDemOffHys | Para_Grid_GridCodeStatic_030_PowerLimit_LimitDemOffTimeDel | Para_Grid_GridCodeStatic_030_PowerLimit_Step1 | Para_Grid_GridCodeStatic_030_PowerLimit_Step2 | Para_Grid_GridCodeStatic_030_PowerLimit_Step3 | Para_Grid_GridCodeStatic_030_PowerLimit_Step4 | Para_Grid_GridCodeStatic_030_PowerLimit_Step5 | Para_Grid_GridCodeStatic_030_PowerLimit_UtilityCurr1 | Para_Grid_GridCodeStatic_030_PowerLimit_UtilityCurr2 | Para_Grid_GridCodeStatic_030_PowerLimit_UtilityPoint1 | Para_Grid_GridCodeStatic_030_PowerLimit_UtilityPoint2 | Para_Grid_GridCodeStatic_040_PFC_RMC_PFCRelative | Para_Grid_GridCodeStatic_040_PFC_RMC_ResponseCurve | Para_Grid_GridCodeStatic_040_PFC_RMC_RMCMargin | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_ActSetPointExt | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_BackupSetPoint | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_ChoiceFunction | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtConst1 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtConst2 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtConst3 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtConst4 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtConst5 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtCurr1 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtCurr2 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtPoint1 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointExtPoint2 | Para_Grid_GridCodeStatic_050_CosPhiSetIntExt_SetPointInt | Para_Grid_GridCodeStatic_060_CosPhiP_ResponseCurve | Para_Grid_GridCodeStatic_070_VoltageSet_ActSetPointExt | Para_Grid_GridCodeStatic_070_VoltageSet_Backup | Para_Grid_GridCodeStatic_070_VoltageSet_ChoiceFunction | Para_Grid_GridCodeStatic_070_VoltageSet_Internal | Para_Grid_GridCodeStatic_070_VoltageSet_SetPointExtCurr1 | Para_Grid_GridCodeStatic_070_VoltageSet_SetPointExtCurr2 | Para_Grid_GridCodeStatic_070_VoltageSet_SetPointExtPoint1 | Para_Grid_GridCodeStatic_070_VoltageSet_SetPointExtPoint2 | Para_Grid_GridCodeStatic_070_VoltageSet_Unom | Para_Grid_GridCodeStatic_080_CosPhiU_ResponseCurve | Para_Grid_GridCodeStatic_090_QVolt_ResponseCurve | Para_Grid_GridCodeStatic_100_QSetIntExt_ActSetPointExt | Para_Grid_GridCodeStatic_100_QSetIntExt_BackupSetPoint | Para_Grid_GridCodeStatic_100_QSetIntExt_ChoiceFunction | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtConst1 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtConst2 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtConst3 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtConst4 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtConst5 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtCurr1 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtCurr2 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtPoint1 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointExtPoint2 | Para_Grid_GridCodeStatic_100_QSetIntExt_SetPointInt | Para_Grid_GridCodeStatic_110_QLimit_ActSetPointExt | Para_Grid_GridCodeStatic_110_QLimit_SetPointExtCurr1 | Para_Grid_GridCodeStatic_110_QLimit_SetPointExtCurr2 | Para_Grid_GridCodeStatic_110_QLimit_SetPointExtPoint1 | Para_Grid_GridCodeStatic_110_QLimit_SetPointExtPoint2 | Para_Grid_GridCodeStatic_110_QLimit_SetPointIntLimit | Para_Grid_GridCodeStatic_120_AnalogOut_ActCosPhi4mA | Para_Grid_GridCodeStatic_120_AnalogOut_ActReactPower4mA | Para_Grid_GridCodeStatic_120_AnalogOut_CosPhiOutPoint1 | Para_Grid_GridCodeStatic_120_AnalogOut_CosPhiOutPoint2 | Para_Grid_GridCodeStatic_120_AnalogOut_ReactPowerOutPoint1 | Para_Grid_GridCodeStatic_120_AnalogOut_ReactPowerOutPoint2 | Para_halio_rpr_oxicat_in_fast_scalmax | Para_halio_rpr_oxicat_in_fast_scalmin | Para_halio_rpr_oxicat_in_scalmax | Para_halio_rpr_oxicat_in_scalmin | Para_halio_rpr_oxicat_out_scalmax | Para_halio_rpr_oxicat_out_scalmin | Para_halio_rt_oxicat_in_scalmax | Para_halio_rt_oxicat_in_scalmin | Para_halio_rt_oxicat_out_scalmax | Para_halio_rt_oxicat_out_scalmin | Para_halio_rt_scr_catscalmax | Para_halio_rt_scr_catscalmin | Para_Hyd_CoolWat_Press_20mA | Para_Hyd_CoolWat_Press_Limit1 | Para_Hyd_CoolWat_Press_Limit1Hys | Para_Hyd_CoolWat_Press_Max | Para_Hyd_CoolWat_Press_MaxHys | Para_Hyd_CoolWat_Press_Min | Para_Hyd_CoolWat_Press_Min1 | Para_Hyd_CoolWat_Press_Min1Hys | Para_Hyd_CoolWat_Press_MinHys | Para_Hyd_CoolWat_Temp_Limit1 | Para_Hyd_CoolWat_Temp_Limit1Hys | Para_Hyd_CoolWat_Temp_Limit2 | Para_Hyd_CoolWat_Temp_Limit2Hys | Para_Hyd_CoolWat_Temp_LoadEnab | Para_Hyd_CoolWat_Temp_LoadEnabHys | Para_Hyd_CoolWat_Temp_Max | Para_Hyd_CoolWat_Temp_MaxHys | Para_Hyd_CoolWat_Temp_Min | Para_Hyd_CoolWat_Temp_MinHys | Para_Hyd_CoolWat_Temp_PreHeatOff | Para_Hyd_CoolWat_Temp_PreHeatOffHys | Para_Hyd_CrankCase_20mA | Para_Hyd_CrankCase_4mA | Para_Hyd_CrankCase_Act | Para_Hyd_CrankCase_ActLimitMon | Para_Hyd_CrankCase_FreqMax | Para_Hyd_CrankCase_FreqMin | Para_Hyd_CrankCase_Limit | Para_Hyd_CrankCase_LimitHys | Para_Hyd_CrankCase_LimitWarn | Para_Hyd_CrankCase_LimitWarnHys | Para_Hyd_Oil_Counter_OilRefillOpH | Para_Hyd_Oil_Counter_PulseValue | Para_Hyd_Oil_Level_LimitClose | Para_Hyd_Oil_Level_LimitCloseHys | Para_Hyd_Oil_Level_LimitOpen | Para_Hyd_Oil_Level_LimitOpenHys | Para_Hyd_Oil_Level_Max | Para_Hyd_Oil_Level_MaxHys | Para_Hyd_Oil_Level_Min | Para_Hyd_Oil_Level_MinHys | Para_Hyd_Oil_Press_20mA | Para_Hyd_Oil_Press_DiffMax | Para_Hyd_Oil_Press_DiffMaxHys | Para_Hyd_Oil_Press_DiffMaxWarn | Para_Hyd_Oil_Press_DiffMaxWarnHys | Para_Hyd_Oil_Press_GrEqSpeed2 | Para_Hyd_Oil_Press_Hys | Para_Hyd_Oil_Press_Limit1 | Para_Hyd_Oil_Press_Limit1Hys | Para_Hyd_Oil_Press_Max | Para_Hyd_Oil_Press_MaxDelay | Para_Hyd_Oil_Press_MaxHys | Para_Hyd_Oil_Press_PreLubrLimit1 | Para_Hyd_Oil_Press_PreLubrLimit1Hys | Para_Hyd_Oil_Press_PreLubrLimit2 | Para_Hyd_Oil_Press_PreLubrLimit2Hys | Para_Hyd_Oil_Press_SmEqSpeed1 | Para_Hyd_Oil_Press_Speed1 | Para_Hyd_Oil_Press_Speed2 | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMax | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMaxHys | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMin | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMinHys | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMinWarn | Para_Hyd_Oil_Press_TCFiltPreLubrOutletMinWarnHys | Para_Hyd_Oil_Press_TCFiltPressOutletMin1 | Para_Hyd_Oil_Press_TCFiltPressOutletMin2 | Para_Hyd_Oil_Press_TCFiltPressOutletMinHys | Para_Hyd_Oil_Press_TCFiltSpeedMin1PressOutlet | Para_Hyd_Oil_Press_TCFiltSpeedMin2PressOutlet | Para_Hyd_Oil_Press_TimeDelFiltDifPress | Para_Hyd_Oil_PressDiffFilter_Limit1 | Para_Hyd_Oil_PressDiffFilter_Limit2 | Para_Hyd_Oil_PressDiffFilter_Limit3 | Para_Hyd_Oil_PressDiffFilter_LimitDelay1 | Para_Hyd_Oil_PressDiffFilter_LimitDelay2 | Para_Hyd_Oil_PressDiffFilter_LimitDelay3 | Para_Hyd_Oil_PressDiffFilter_ReleaseTemp | Para_Hyd_Oil_PressFilterIn_20mA | Para_Hyd_Oil_PressFilterIn_4mA | Para_Hyd_Oil_PressFilterIn_ActMeasure | Para_Hyd_Oil_Temp_Limit1 | Para_Hyd_Oil_Temp_Limit1Hys | Para_Hyd_Oil_Temp_Limit2 | Para_Hyd_Oil_Temp_Limit2Hys | Para_Hyd_Oil_Temp_LimitPreWarm | Para_Hyd_Oil_Temp_LimitPreWarmHys | Para_Hyd_Oil_Temp_LoadEnab | Para_Hyd_Oil_Temp_LoadEnabHys | Para_Hyd_Oil_Temp_Max | Para_Hyd_Oil_Temp_MaxHys | Para_Hyd_Oil_Temp_Min | Para_Hyd_Oil_Temp_MinHys | Para_Hyd_Oil_TurboCh_TCType | Para_Hyd_RetWat_20mA | Para_Hyd_RetWat_Act | Para_Hyd_RetWat_ActSigTrip | Para_Hyd_RetWat_Limit | Para_Hyd_RetWat_Limit1 | Para_Hyd_RetWat_Limit1Hys | Para_Hyd_RetWat_LimitHys | Para_Hyd_RetWatCoolOut_20mA | Para_Hyd_RetWatCoolOut_Act | Para_Hyd_RetWatCoolOut_ActSigTrip | Para_Hyd_RetWatCoolOut_Limit | Para_Hyd_RetWatCoolOut_Limit1 | Para_Hyd_RetWatCoolOut_Limit1Hys | Para_Hyd_RetWatCoolOut_LimitHys | Para_Hyd_RetWatLowTemp_Act | Para_Hyd_RetWatLowTemp_Limit | Para_Hyd_RetWatLowTemp_LimitHys | Para_Hyd_RetWatPreEng_Act | Para_Hyd_RetWatPreEng_ActSigTrip | Para_Hyd_RetWatPreEng_Limit | Para_Hyd_RetWatPreEng_Limit1 | Para_Hyd_RetWatPreEng_Limit1Hys | Para_Hyd_RetWatPreEng_LimitHys | Para_Hyd_SupWat_20mA | Para_Hyd_SupWat_Act | Para_Hyd_SupWat_ActSigTrip | Para_Hyd_SupWat_Limit | Para_Hyd_SupWat_Limit1 | Para_Hyd_SupWat_Limit1Hys | Para_Hyd_SupWat_LimitHys | Para_Hydraulic_Condenser_T_CD_Re_Active | Para_Hydraulic_Condenser_T_CD_Re_HyHi | Para_Hydraulic_Condenser_T_CD_Re_LimHi | Para_Hydraulic_Condenser_T_CD_Su_Active | Para_Hydraulic_Condenser_T_CD_Su_HyHi | Para_Hydraulic_Condenser_T_CD_Su_LimHi | Para_Hydraulic_CoolWat_ECWP_MechDriven | Para_Hydraulic_CoolWat_N_ECWP_Set | Para_Hydraulic_CoolWat_Press_Pr_ECWaEng_Active | Para_Hydraulic_CoolWat_Press_Pr_ECWaEng_ScalMax | Para_Hydraulic_CoolWat_T_ECW_bChC_HT_Active | Para_Hydraulic_CoolWat_T_ECW_bECWC_Active | Para_Hydraulic_CoolWat_T_ECW_bOilC_Active | Para_Hydraulic_CoolWat_Temp_T_ECW_HyBpV | Para_Hydraulic_CoolWat_Temp_T_ECW_LimBpV | Para_Hydraulic_CoolWat_Temp_T_ECWbEng_Active | Para_Hydraulic_CoolWatModule_T_ECW_Mod_In_Active | Para_Hydraulic_CoolWatModule_T_ECW_Mod_Out_Active | Para_Hydraulic_CrankCase_DPr_BbFilt_Hi_P1 | Para_Hydraulic_CrankCase_DPr_BbFilt_Hi_P2 | Para_Hydraulic_CrankCase_DPr_BbFilt_Lo_P1 | Para_Hydraulic_CrankCase_DPr_BbFilt_Lo_P2 | Para_Hydraulic_CrankCase_DPr_BbFilt_Pstart | Para_Hydraulic_CrankCase_Pc_BbBlower_Hi | Para_Hydraulic_CrankCase_Pr_a_BbFilt_A_Exist | Para_Hydraulic_CrankCase_Pr_a_BbFilt_B_Exist | Para_Hydraulic_CrankCase_Pr_a_BbFilt_Exist | Para_Hydraulic_CrankCase_Pr_a_BbFiltScalMax | Para_Hydraulic_CrankCase_Pr_a_BbFiltScalMin | Para_Hydraulic_CrankCase_Pr_CC_Hi | Para_Hydraulic_CrankCase_Pr_CC_Lo | Para_Hydraulic_CrankCase_Pr_CCScalMax | Para_Hydraulic_CrankCase_Pr_CCScalMin | Para_Hydraulic_CrankCase_Pr_f_BbFilt_A_Exist | Para_Hydraulic_CrankCase_Pr_f_BbFilt_B_Exist | Para_Hydraulic_CrankCase_Pr_f_BbFilt_Exist | Para_Hydraulic_CrankCase_Pr_f_BbFiltScalMax | Para_Hydraulic_CrankCase_Pr_f_BbFiltScalMin | Para_Hydraulic_CrankCase_tiPr_CC_Hi | Para_Hydraulic_CrankCase_tiPr_CC_HiHi | Para_Hydraulic_HeatCircuitRetWater_T_HW_HC_Re_Active | Para_Hydraulic_HeatCircuitRetWater_T_HW_HC_Re_HyHi | Para_Hydraulic_HeatCircuitRetWater_T_HW_HC_Re_LimHi | Para_Hydraulic_HeatOutputCounter_Cnt_P_Heat | Para_Hydraulic_HeatOutputCounter_ImpVal_Cnt_P_Heat | Para_Hydraulic_HeatOutputCounter_P_Heat_Active | Para_Hydraulic_HeatOutputCounter_P_Heat_ScalMax | Para_Hydraulic_HeatOutputCounter_P_Heat_ScalMin | Para_Hydraulic_HeatWaterHigh_Pr_HW_Re_HT_Active | Para_Hydraulic_HeatWaterHigh_Pr_HW_Re_HT_ScalMax | Para_Hydraulic_HeatWaterHigh_Pr_HW_Re_HT_ScalMin | Para_Hydraulic_HeatWaterHigh_Pr_HW_Su_HT_Active | Para_Hydraulic_HeatWaterHigh_Pr_HW_Su_HT_ScalMax | Para_Hydraulic_HeatWaterLow_Pr_HW_Re_LT_Active | Para_Hydraulic_HeatWaterLow_Pr_HW_Re_LT_ScalMax | Para_Hydraulic_HeatWaterLow_Pr_HW_Re_LT_ScalMin | Para_Hydraulic_HeatWaterLow_Pr_HW_Su_LT_Active | Para_Hydraulic_HeatWaterLow_Pr_HW_Su_LT_ScalMax | Para_Hydraulic_HeatWaterLow_T_HW_Su_LT_Active | Para_Hydraulic_Oil_EO_Level_Active | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_DE_Exist | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_DE_Hi | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_DE_Lo | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_DEScalMax | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_DEScalMin | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_NDE_Exist | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_NDE_Hi | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_NDE_Lo | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_NDEScalMax | Para_Hydraulic_Oil_GenOilSkid_Flow_OilSkid_NDEScalMin | Para_Hydraulic_Oil_GenOilSkid_Lev_OilSkid_Tank_Exist | Para_Hydraulic_Oil_GenOilSkid_Lev_OilSkid_Tank_Lo | Para_Hydraulic_Oil_GenOilSkid_Lev_OilSkid_Tank_LoLo | Para_Hydraulic_Oil_GenOilSkid_Lev_OilSkid_TankScalMax | Para_Hydraulic_Oil_GenOilSkid_Lev_OilSkid_TankScalMin | Para_Hydraulic_Oil_GenOilSkid_Pr_OilSkid_HP_DE_Exist | Para_Hydraulic_Oil_GenOilSkid_Pr_OilSkid_HP_Lo | Para_Hydraulic_Oil_GenOilSkid_Pr_OilSkid_HP_NDE_Exist | Para_Hydraulic_Oil_GenOilSkid_Pr_OilSkid_HPScalMax | Para_Hydraulic_Oil_GenOilSkid_Pr_OilSkid_HPScalMin | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_Supply_Exist | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_Supply_Hi | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_Supply_Lo | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_SupplyScalMax | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_SupplyScalMin | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_Tank_Exist | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_Tank_Set | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_TankScalMax | Para_Hydraulic_Oil_GenOilSkid_T_OilSkid_TankScalMin | Para_Hydraulic_Oil_GenOilSkid_tiOilSkid_PumpHP_Run | Para_Hydraulic_Oil_OilFilterUnit_DPr_OFU_Filt_LimHi | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUaFilt_Active | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUaFilt_ScalMax | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUaFilt_ScalMin | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbCentrifuge_Active | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbCentrifuge_Hi | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbCentrifuge_ScalMax | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbCentrifuge_ScalMin | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbFilt_Active | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbFilt_Hi | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbFilt_ScalMax | Para_Hydraulic_Oil_OilFilterUnit_Pr_OFUbFilt_ScalMin | Para_Hydraulic_Oil_OilFiltUnit_Exist | Para_Hydraulic_Oil_OilSkid_Exist | Para_Hydraulic_Oil_Press_EngTyp3_Prelub_Active | Para_Hydraulic_Oil_Press_EOP_PreHeat_Set | Para_Hydraulic_Oil_Press_EOP_PreLube_Set | Para_Hydraulic_Oil_Press_Pr_EOaP_Active | Para_Hydraulic_Oil_Press_Pr_EOaP_LimHi | Para_Hydraulic_Oil_Press_Pr_EOaP_LimHiHi | Para_Hydraulic_Oil_Press_Pr_LimHeatRel | Para_Hydraulic_Oil_PressFilterOut_Pr_EOF_After_Active | Para_Hydraulic_Oil_PressFilterOut_Pr_EOF_After_ScalMax | Para_Hydraulic_Oil_PressFilterOut_Pr_EOF_After_ScalMin | Para_Hydraulic_Oil_Quality_OQS_Active | Para_Hydraulic_Oil_Quality_OQS_Conduct_ScalMax | Para_Hydraulic_Oil_Quality_OQS_Conduct_ScalMin | Para_Hydraulic_Oil_Quality_OQS_Dielect_ScalMax | Para_Hydraulic_Oil_Quality_OQS_Dielect_ScalMin | Para_Hydraulic_Oil_Quality_OQS_Temp_ScalMax | Para_Hydraulic_Oil_Quality_OQS_Temp_ScalMin | Para_Hydraulic_Oil_Quality_OQS_Visco_ScalMax | Para_Hydraulic_Oil_Quality_OQS_Visco_ScalMin | Para_Hydraulic_Oil_ServicePrelub | Para_Hydraulic_Oil_Temp_T_EO_Pan_Active | Para_Hydraulic_Oil_Temp_T_EOaPump_Active | Para_Hydraulic_Oil_TurboCh_Pr_Oil_LPTC_In_A | Para_Hydraulic_Oil_TurboCh_Pr_Oil_LPTC_In_B | Para_Hydraulic_Oil_TurboCh_Pr_TCOaF_Active | Para_Hydraulic_Oil_TurboCh_Pr_TCObF_Active | Para_Hydraulic_Oil_TurboCh_Pr_TCObF_ScalMax | Para_Hydraulic_Oil_TurboCh_Pr_TCObF_ScalMin | Para_Hydraulic_Oil_TurboCh_TC_PostLub_Active | Para_Hydraulic_Oil_TurboCh_TC_watercooled | Para_Hydraulic_Oil_TurboCh_tiTC_Postlub | Para_Hydraulic_OilModule_Pr_EO_Mod_Out_Active | Para_Hydraulic_OilModule_Pr_EO_Mod_Out_ScalMax | Para_Hydraulic_OilModule_Pr_EO_Mod_Out_ScalMin | Para_Hydraulic_OilModule_T_EO_Mod_In_Active | Para_Hydraulic_OilModule_T_EO_Mod_Out_Active | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_ECW_Active | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_ECW_ScalMax | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_ECW_ScalMin | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_EO_Active | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_EO_ScalMax | Para_Hydraulic_PreHeat_Pr_HW_Re_PreH_EO_ScalMin | Para_Hydraulic_PreHeat_T_HW_Re_PreH_ECW_Active | Para_Hydraulic_PreHeat_T_HW_Re_PreH_EO_Active | Para_Hydraulic_PreHeat_T_HW_Su_PreH_ECW_Active | Para_Hydraulic_PreHeat_T_HW_Su_PreH_EO_Active | Para_Hydraulic_RetWatPreEng_T_HW_ReBeEng_SF_Trip | Para_Hydraulic_WasteHeatRec_ReturnPrim_T_Re_PriCirc_Active | Para_Hydraulic_WasteHeatRec_ReturnPrim_T_Re_PriCirc_HyLimHi | Para_Hydraulic_WasteHeatRec_ReturnPrim_T_Re_PriCirc_LimHi | Para_Hydraulic_WasteHeatRec_ReturnSec_T_Re_SecCirc_Active | Para_Hydraulic_WasteHeatRec_ReturnSec_T_Re_SecCirc_HyLimHi | Para_Hydraulic_WasteHeatRec_ReturnSec_T_Re_SecCirc_LimHi | Para_Hydraulic_WasteHeatRec_SupplyPrim_T_Su_PriCirc_Active | Para_Hydraulic_WasteHeatRec_SupplyPrim_T_Su_PriCirc_HyLimHi | Para_Hydraulic_WasteHeatRec_SupplyPrim_T_Su_PriCirc_LimHi | Para_Hydraulic_WasteHeatRec_SupplySec_T_Su_SecCirc_Active | Para_Hydraulic_WasteHeatRec_SupplySec_T_Su_SecCirc_HyLimHi | Para_Hydraulic_WasteHeatRec_SupplySec_T_Su_SecCirc_LimHi | Para_Ignition_ActITPTbAdap | Para_Ignition_EnergLev | Para_Ignition_ITPEarl | Para_Ignition_ITPGas1 | Para_Ignition_ITPGas2 | Para_Ignition_ITPGas3 | Para_Ignition_ITPGas4 | Para_Ignition_ITPIslandG1 | Para_Ignition_ITPIslandG2 | Para_Ignition_ITPIslandG3 | Para_Ignition_ITPIslandG4 | Para_Ignition_ITPKnockMonOffG1 | Para_Ignition_ITPKnockMonOffG2 | Para_Ignition_ITPKnockMonOffG3 | Para_Ignition_ITPKnockMonOffG4 | Para_Ignition_ITPLate | Para_Ignition_ITPMinGas1 | Para_Ignition_ITPMinGas2 | Para_Ignition_ITPMinGas3 | Para_Ignition_ITPMinGas4 | Para_Ignition_ITPTbPosAdap | Para_Ignition_mAOutput_Curr1 | Para_Ignition_mAOutput_Curr2 | Para_Ignition_mAOutput_Point1 | Para_Ignition_mAOutput_Point2 | Para_Ignition_MisfControl | Para_Ignition_MORIS_CoilType | Para_Ignition_MORIS_CoilType0_IonTimeEarl | Para_Ignition_MORIS_CoilType0_IonTimeLate | Para_Ignition_MORIS_CoilType0_MagLevelDec | Para_Ignition_MORIS_CoilType0_MagLevelInc | Para_Ignition_MORIS_CoilType0_MagLevelIon | Para_Ignition_MORIS_CoilType0_MagLevelLim | Para_Ignition_MORIS_CoilType0_PowerIgn | Para_Ignition_MORIS_CoilType0_PowerSparkLim | Para_Ignition_MORIS_CoilType0_PowerSparkRate | Para_Ignition_MORIS_CoilType0_SparkCurrIonis | Para_Ignition_MORIS_CoilType0_SparkDelayFailRate | Para_Ignition_MORIS_CoilType0_SparkDelayLim | Para_Ignition_MORIS_CoilType0_SparkDurIonis | Para_Ignition_MORIS_PowerSupplyOut | Para_Ignition_MORIS_SparkChar0_SparkCurr1 | Para_Ignition_MORIS_SparkChar0_SparkCurr2 | Para_Ignition_MORIS_SparkChar0_SparkCurr3 | Para_Ignition_MORIS_SparkChar0_SparkCurr4 | Para_Ignition_MORIS_SparkChar0_SparkCurr5 | Para_Ignition_MORIS_SparkChar0_SparkCurr6 | Para_Ignition_MORIS_SparkChar0_SparkDur1 | Para_Ignition_MORIS_SparkChar0_SparkDur2 | Para_Ignition_MORIS_SparkChar0_SparkDur3 | Para_Ignition_MORIS_SparkChar0_SparkDur4 | Para_Ignition_MORIS_SparkChar0_SparkDur5 | Para_Ignition_MORIS_SparkCurrChar | Para_Ignition_MORIS_SparkCurrDur | Para_Ignition_MORIS_SparkCurrLevel | Para_Ignition_MORIS_SparkDurTol | Para_Ignition_MORIS_SparkDurTolFailRate | Para_Ignition_OutputMon | Para_Ignition_OverSpeed | Para_Ignition_ResetPos | Para_Ignition_SecSpeed | Para_Ignition_Setting_EnergLev | Para_Ignition_Setting_OutputMon | Para_Ignition_Setting_ResetPos | Para_Ignition_Setting_SecSpeed | Para_Ignition_Setting_SpeedRelay1 | Para_Ignition_Setting_SpeedRelay2 | Para_Ignition_Setting_SpeedRelay2InvOut | Para_Ignition_Setting_SpeedRelayHys1 | Para_Ignition_Setting_SpeedRelayHys2 | Para_Ignition_SpeedRelay1 | Para_Ignition_SpeedRelay2 | Para_Ignition_SpeedRelay2InvOut | Para_Ignition_SpeedRelayHys1 | Para_Ignition_SpeedRelayHys2 | Para_Island_Advanced_ActMapVolEff | Para_Island_Advanced_ActSpeedComp | Para_Island_Advanced_CompByTimeCorr | Para_Island_Advanced_CompByValueCorr | Para_Island_Advanced_CompByValueCorrRed | Para_Island_Advanced_ITPShift | Para_Island_Advanced_SpeedCompCorrFact | Para_Island_Advanced_SpeedCompFact | Para_Island_Ctr_TbDComp | Para_Island_Ctr_TbIComp | Para_Island_Ctr_TbPComp | Para_Island_Ctr_TbYMax | Para_Island_Ctr_TbYMin | Para_Island_Ctr_TrDComp | Para_Island_Ctr_TrIComp | Para_Island_Ctr_TrPComp | Para_Island_Ctr_TrYMax | Para_Island_Ctr_TrYMin | Para_Island_LambdaAdap_FactNegPower | Para_Island_LambdaAdap_FactNegSpeed | Para_Island_LambdaAdap_FactPosPower | Para_Island_LambdaAdap_FactPosSpeed | Para_Island_LambdaAdap_TriggerLowPower | Para_Island_LambdaAdap_TriggerLowSpeed | Para_Island_LambdaAdap_TriggerUpPower | Para_Island_LambdaAdap_TriggerUpSpeed | Para_Island_Limit_LSdPowerMax | Para_Island_Limit_LSdPowerMaxDelay | Para_Island_Limit_LSdPowerMaxHys | Para_Island_Limit_LSdPowerMinAlarm | Para_Island_Limit_LSdPowerMinAlarmDelay | Para_Island_Limit_LSdPowerMinHys | Para_Island_Limit_LSdPowerMinTrip | Para_Island_Limit_LSdPowerMinTripDelay | Para_Island_Limit_LSdSpeedLimit | Para_Island_Limit_LSdSpeedLimitDelay | Para_Island_Limit_LSdSpeedLimitHys | Para_Island_LoadSh_ActOffsetCoef | Para_Island_LoadSh_LoadSh | Para_Island_LoadSh_OffsetCoef | Para_Island_OutPowerLimit_Curr1 | Para_Island_OutPowerLimit_Curr2 | Para_Island_OutPowerLimit_Point1 | Para_Island_OutPowerLimit_Point2 | Para_Island_Ramp_Ramp | Para_Knock_ActKnockMon | Para_Knock_ActKnockMonHys | Para_Knock_CylOpt_Active | Para_Knock_CylOpt_IntTimeUp | Para_Knock_CylOpt_IPAdaptIntervall | Para_Knock_CylOpt_LimitKnockInt | Para_Knock_CylOpt_MonIntervall | Para_Knock_CylOpt_PowAdaptIntervall | Para_Knock_CylOpt_ResetTimeOpt | Para_Knock_CylOpt_ResetTimeOptPred | Para_Knock_IPAdapOffsetKnockCtrGas1 | Para_Knock_IPAdapOffsetKnockCtrGas2 | Para_Knock_IPAdapOffsetKnockCtrGas3 | Para_Knock_IPAdapOffsetKnockCtrGas4 | Para_Knock_IPRedMaxKnockCtrGas1 | Para_Knock_IPRedMaxKnockCtrGas2 | Para_Knock_IPRedMaxKnockCtrGas3 | Para_Knock_IPRedMaxKnockCtrGas4 | Para_Knock_ITPMinGas1 | Para_Knock_ITPMinGas2 | Para_Knock_ITPMinGas3 | Para_Knock_ITPMinGas4 | Para_Knock_KLS90_KnockLimit1 | Para_Knock_KLS90_KnockLimit2 | Para_Knock_KLS98_AngleDurWindow1 | Para_Knock_KLS98_AngleDurWindow2 | Para_Knock_KLS98_AngleDurWindow3 | Para_Knock_KLS98_AnglePosCam | Para_Knock_KLS98_AnglePosWindow1 | Para_Knock_KLS98_AnglePosWindow2 | Para_Knock_KLS98_AnglePosWindow3 | Para_Knock_KLS98_EnabCyl1 | Para_Knock_KLS98_EnabCyl10 | Para_Knock_KLS98_EnabCyl11 | Para_Knock_KLS98_EnabCyl12 | Para_Knock_KLS98_EnabCyl13 | Para_Knock_KLS98_EnabCyl14 | Para_Knock_KLS98_EnabCyl15 | Para_Knock_KLS98_EnabCyl16 | Para_Knock_KLS98_EnabCyl17 | Para_Knock_KLS98_EnabCyl18 | Para_Knock_KLS98_EnabCyl19 | Para_Knock_KLS98_EnabCyl2 | Para_Knock_KLS98_EnabCyl20 | Para_Knock_KLS98_EnabCyl21 | Para_Knock_KLS98_EnabCyl22 | Para_Knock_KLS98_EnabCyl23 | Para_Knock_KLS98_EnabCyl24 | Para_Knock_KLS98_EnabCyl3 | Para_Knock_KLS98_EnabCyl4 | Para_Knock_KLS98_EnabCyl5 | Para_Knock_KLS98_EnabCyl6 | Para_Knock_KLS98_EnabCyl7 | Para_Knock_KLS98_EnabCyl8 | Para_Knock_KLS98_EnabCyl9 | Para_Knock_KLS98_ITPAdjustGlobCylsel | Para_Knock_KLS98_KnockFilterFunc | Para_Knock_KLS98_KnockLimit | Para_Knock_KLS98_MeasSigDist | Para_Knock_KLS98_MechNoiseMax | Para_Knock_KLS98_ValveNoiseMax | Para_Knock_PBC_AngleDurGlowI | Para_Knock_PBC_AngleDurKnock | Para_Knock_PBC_AnglePosGlowI | Para_Knock_PBC_AnglePosKnock | Para_Knock_PBC_GlobalIPAdj | Para_Knock_PBC_GlowILimit | Para_Knock_PBC_KnockLimit | Para_Knock_PBC_MeasSigLimit | Para_Knock_RedITPEnd | Para_Knock_RedITPEndNew | Para_Knock_RedITPStart | Para_Knock_RedMixTempEnd | Para_Knock_RedMixTempEndNew | Para_Knock_RedMixTempStart | Para_Knock_RedPowerEnd | Para_Knock_RedPowerEndNew | Para_Knock_RedPowerStart | Para_Knock_TempMixRedMax | Para_Knock_TimeIntDown | Para_Knock_TimeIntUp | Para_Leanox_ActILeanoxCtrIsland | Para_Leanox_ActPRedLeanox | Para_Leanox_Comp_ActITPBoostPress | Para_Leanox_Comp_ActMixtTempBoostPress | Para_Leanox_Comp_ActPowerFriction | Para_Leanox_Comp_ActSpeed | Para_Leanox_Comp_ITPDeltaPress1 | Para_Leanox_Comp_ITPDeltaPress2 | Para_Leanox_Comp_ITPPower1 | Para_Leanox_Comp_ITPPower2 | Para_Leanox_Comp_ITPPowerMin | Para_Leanox_Comp_MixTempPower1 | Para_Leanox_Comp_MixTempPower2 | Para_Leanox_Comp_MixTempPowerMin | Para_Leanox_Comp_MixTempPress1 | Para_Leanox_Comp_MixTempPress2 | Para_Leanox_Gas1_CtrGasmixer_DeadBand | Para_Leanox_Gas1_CtrGasmixer_IComp | Para_Leanox_Gas1_CtrGasmixer_Limit | Para_Leanox_Gas1_CtrGasmixer_PComp | Para_Leanox_Gas1_CtrGasmixer_YMax | Para_Leanox_Gas1_CtrGasmixer_YMin | Para_Leanox_Gas1_CtrTecjet_DeadBand | Para_Leanox_Gas1_CtrTecjet_IComp | Para_Leanox_Gas1_CtrTecjet_Limit | Para_Leanox_Gas1_CtrTecjet_PComp | Para_Leanox_Gas1_CtrTecjet_YMax | Para_Leanox_Gas1_CtrTecjet_YMin | Para_Leanox_Gas1_DeltaPressIsl | Para_Leanox_Gas1_Para_DP | Para_Leanox_Gas1_Para_DPIslandAdap | Para_Leanox_Gas1_Para_P1 | Para_Leanox_Gas1_Para_P2 | Para_Leanox_Gas1_Para_PowerPoint1 | Para_Leanox_Gas1_Para_PowerPoint2 | Para_Leanox_Gas1_Para_PressurePoint1 | Para_Leanox_Gas1_Para_PressurePoint2 | Para_Leanox_Gas1_Para_SpeedPoint1 | Para_Leanox_Gas1_Para_SpeedPoint2 | Para_Leanox_Gas1_Para_T1 | Para_Leanox_Gas1_Para_TempPoint1 | Para_Leanox_Gas1_Para_TempPoint2 | Para_Leanox_Gas1_Para_W1 | Para_Leanox_Gas1_PowerAct | Para_Leanox_Gas1_PowerActHys | Para_Leanox_Gas2_CtrGasmixer_DeadBand | Para_Leanox_Gas2_CtrGasmixer_IComp | Para_Leanox_Gas2_CtrGasmixer_Limit | Para_Leanox_Gas2_CtrGasmixer_PComp | Para_Leanox_Gas2_CtrGasmixer_YMax | Para_Leanox_Gas2_CtrGasmixer_YMin | Para_Leanox_Gas2_CtrTecjet_DeadBand | Para_Leanox_Gas2_CtrTecjet_IComp | Para_Leanox_Gas2_CtrTecjet_Limit | Para_Leanox_Gas2_CtrTecjet_PComp | Para_Leanox_Gas2_CtrTecjet_YMax | Para_Leanox_Gas2_CtrTecjet_YMin | Para_Leanox_Gas2_DeltaPressIsl | Para_Leanox_Gas2_Para_DP | Para_Leanox_Gas2_Para_DPIslandAdap | Para_Leanox_Gas2_Para_P1 | Para_Leanox_Gas2_Para_P2 | Para_Leanox_Gas2_Para_PowerPoint1 | Para_Leanox_Gas2_Para_PowerPoint2 | Para_Leanox_Gas2_Para_PressurePoint1 | Para_Leanox_Gas2_Para_PressurePoint2 | Para_Leanox_Gas2_Para_SpeedPoint1 | Para_Leanox_Gas2_Para_SpeedPoint2 | Para_Leanox_Gas2_Para_T1 | Para_Leanox_Gas2_Para_TempPoint1 | Para_Leanox_Gas2_Para_TempPoint2 | Para_Leanox_Gas2_Para_W1 | Para_Leanox_Gas2_PowerAct | Para_Leanox_Gas2_PowerActHys | Para_Leanox_Gas3_CtrGasmixer_DeadBand | Para_Leanox_Gas3_CtrGasmixer_IComp | Para_Leanox_Gas3_CtrGasmixer_Limit | Para_Leanox_Gas3_CtrGasmixer_PComp | Para_Leanox_Gas3_CtrGasmixer_YMax | Para_Leanox_Gas3_CtrGasmixer_YMin | Para_Leanox_Gas3_CtrTecjet_DeadBand | Para_Leanox_Gas3_CtrTecjet_IComp | Para_Leanox_Gas3_CtrTecjet_Limit | Para_Leanox_Gas3_CtrTecjet_PComp | Para_Leanox_Gas3_CtrTecjet_YMax | Para_Leanox_Gas3_CtrTecjet_YMin | Para_Leanox_Gas3_DeltaPressIsl | Para_Leanox_Gas3_Para_DP | Para_Leanox_Gas3_Para_DPIslandAdap | Para_Leanox_Gas3_Para_P1 | Para_Leanox_Gas3_Para_P2 | Para_Leanox_Gas3_Para_PowerPoint1 | Para_Leanox_Gas3_Para_PowerPoint2 | Para_Leanox_Gas3_Para_PressurePoint1 | Para_Leanox_Gas3_Para_PressurePoint2 | Para_Leanox_Gas3_Para_SpeedPoint1 | Para_Leanox_Gas3_Para_SpeedPoint2 | Para_Leanox_Gas3_Para_T1 | Para_Leanox_Gas3_Para_TempPoint1 | Para_Leanox_Gas3_Para_TempPoint2 | Para_Leanox_Gas3_Para_W1 | Para_Leanox_Gas3_PowerAct | Para_Leanox_Gas3_PowerActHys | Para_Leanox_Gas4_CtrGasmixer_DeadBand | Para_Leanox_Gas4_CtrGasmixer_IComp | Para_Leanox_Gas4_CtrGasmixer_Limit | Para_Leanox_Gas4_CtrGasmixer_PComp | Para_Leanox_Gas4_CtrGasmixer_YMax | Para_Leanox_Gas4_CtrGasmixer_YMin | Para_Leanox_Gas4_CtrTecjet_DeadBand | Para_Leanox_Gas4_CtrTecjet_IComp | Para_Leanox_Gas4_CtrTecjet_Limit | Para_Leanox_Gas4_CtrTecjet_PComp | Para_Leanox_Gas4_CtrTecjet_YMax | Para_Leanox_Gas4_CtrTecjet_YMin | Para_Leanox_Gas4_DeltaPressIsl | Para_Leanox_Gas4_Para_DP | Para_Leanox_Gas4_Para_DPIslandAdap | Para_Leanox_Gas4_Para_P1 | Para_Leanox_Gas4_Para_P2 | Para_Leanox_Gas4_Para_PowerPoint1 | Para_Leanox_Gas4_Para_PowerPoint2 | Para_Leanox_Gas4_Para_PressurePoint1 | Para_Leanox_Gas4_Para_PressurePoint2 | Para_Leanox_Gas4_Para_SpeedPoint1 | Para_Leanox_Gas4_Para_SpeedPoint2 | Para_Leanox_Gas4_Para_T1 | Para_Leanox_Gas4_Para_TempPoint1 | Para_Leanox_Gas4_Para_TempPoint2 | Para_Leanox_Gas4_Para_W1 | Para_Leanox_Gas4_PowerAct | Para_Leanox_Gas4_PowerActHys | Para_Leanox_Humidity_ActBoostTempOffset | Para_Leanox_Humidity_BoostTempDevToICWT | Para_Leanox_Humidity_BoostTempRaiseDevTime | Para_Leanox_Humidity_BosstTempRaiseMax | Para_Leanox_Humidity_CompValKnockMonStart | Para_Leanox_Humidity_CompValPnom | Para_Leanox_Humidity_Offset | Para_Leanox_PressBoost_20mA | Para_Leanox_PressBoost_4mA | Para_Leanox_PressBoost_ActP2 | Para_Leanox_PressBoost_P2_20mA | Para_Leanox_PressBoost_P2_4mA | Para_Leanox_RampPowerRed | Para_Misfire_KLS98_Active | Para_Misfire_KLS98_ActOCA | Para_Misfire_KLS98_AngleWindowDur | Para_Misfire_KLS98_AngleWindowLimit | Para_Misfire_KLS98_Limit | Para_Misfire_Limit | Para_Misfire_PreWarn | Para_Misfire_TimeIntDown | Para_Misfire_TimeIntUp | Para_MixCharge_AirFilterDiffPress_20mA | Para_MixCharge_AirFilterDiffPress_4mA | Para_MixCharge_AirFilterDiffPress_ActPressA | Para_MixCharge_AirFilterDiffPress_ActPressB | Para_MixCharge_AirFilterDiffPress_Limit | Para_MixCharge_AirFilterDiffPress_LimitHys | Para_MixCharge_Press_Act_Pr_Ch_P1HP | Para_MixCharge_Press_Act_Pr_Ch_P1HP_A | Para_MixCharge_Press_Act_Pr_Ch_P1HP_B | Para_MixCharge_Press_Act_Pr_Ch_P2_A | Para_MixCharge_Press_Act_Pr_Ch_P2_B | Para_MixCharge_Press_Act_Pr_Ch_P2s | Para_MixCharge_Press_Act_Pr_Ch_P2s_A | Para_MixCharge_Press_Act_Pr_Ch_P2s_B | Para_MixCharge_Press_Pr_Ch_P1HPScalMax | Para_MixCharge_Press_Pr_Ch_P1HPScalMin | Para_MixCharge_Press_Pr_Ch_P2s_Diff_HiHi | Para_MixCharge_Speed_Act_N_TCHP | Para_MixCharge_Speed_Act_N_TCLP | Para_MixCharge_Speed_TCHPScalMax | Para_MixCharge_Speed_TCHPScalMin | Para_MixCharge_Speed_TCLPScalMax | Para_MixCharge_Speed_TCLPScalMin | Para_MixCharge_SpreadChargePress | Para_MixCharge_SpreadChargeTemp | Para_MixCharge_Temp_Act_T_Ch_T1HP_Exist | Para_MixCharge_Temp_ActTempInletHighpressA | Para_MixCharge_Temp_ActTempInletHighPressB | Para_MixCharge_Temp_MaxDtInletHighPress | Para_MixCharge_Temp_MaxHysDtInletHighPress | Para_MixCharge_Temp_MaxHysInletHighPress | Para_MixCharge_Temp_MaxInletHighPress | Para_MixCharge_Temp_MinHysInletHighPress | Para_MixCharge_Temp_MinInletHighPress | Para_MixTemp_Ctr_CycleTime | Para_MixTemp_Ctr_DComp | Para_MixTemp_Ctr_DCompTune | Para_MixTemp_Ctr_DeadBand | Para_MixTemp_Ctr_IComp | Para_MixTemp_Ctr_ICompTune | Para_MixTemp_Ctr_InvertCtrTune | Para_MixTemp_Ctr_PComp | Para_MixTemp_Ctr_PCompTune | Para_MixTemp_Ctr_RangeEnd | Para_MixTemp_Ctr_UserLevelIntExt | Para_MixTemp_Ctr_UserLevelManAut | Para_MixTemp_Ctr_UserLevelSet | Para_MixTemp_Ctr_UserLevelTune | Para_MixTemp_Ctr_WGas1 | Para_MixTemp_Ctr_WGas2 | Para_MixTemp_Ctr_WGas3 | Para_MixTemp_Ctr_WGas4 | Para_MixTemp_Ctr_WMax | Para_MixTemp_Ctr_WMin | Para_MixTemp_Ctr_WRampNeg | Para_MixTemp_Ctr_WRampPos | Para_MixTemp_Ctr_YBlock | Para_MixTemp_Ctr_YMax | Para_MixTemp_Ctr_YMin | Para_MixTemp_Ctr_YRampNeg | Para_MixTemp_Ctr_YRampPos | Para_MixTemp_Ctr_YRampTune | Para_MixTemp_Limit_Act_T_Ch_T2s_A_Exist | Para_MixTemp_Limit_Act_T_Ch_T2s_B_Exist | Para_MixTemp_Limit_Act_T_Ch_T2s_Exist | Para_MixTemp_Limit_TempdTMax | Para_MixTemp_Limit_TempLimit1 | Para_MixTemp_Limit_TempLimit2 | Para_MixTemp_Limit_TempLimitHys1 | Para_MixTemp_Limit_TempLimitHys2 | Para_MixTemp_Limit_TempMax | Para_MixTemp_Limit_TempMaxHys | Para_MixTemp_Limit_TempMin | Para_MixTemp_Limit_TempMinHys | Para_MMD_Aron | Para_MMD_CurrAsymetry | Para_MMD_CurrAsymetryDelay | Para_MMD_CurrNeuMax | Para_MMD_CurrNeuMaxDelay | Para_MMD_CurrRange | Para_MMD_CurrShortCircuit | Para_MMD_CurrShortCircuitDelay | Para_MMD_CurrThermOverloadProt | Para_MMD_ImpulseValue | Para_MMD_IntValue | Para_MMD_MMD1_ActSynch | Para_MMD_MMD1_Aron | Para_MMD_MMD1_Bus3PhaseCircuit | Para_MMD_MMD1_CurrAsymetryDelay | Para_MMD_MMD1_CurrNeuMax | Para_MMD_MMD1_CurrNeuMaxDelay | Para_MMD_MMD1_CurrNeuNom | Para_MMD_MMD1_CurrRange | Para_MMD_MMD1_CurrShortCircuit | Para_MMD_MMD1_CurrShortCircuitDelay | Para_MMD_MMD1_CurrThermOverloadProt | Para_MMD_MMD1_FreqDiffMax | Para_MMD_MMD1_FreqDiffMin | Para_MMD_MMD1_Gen3PhaseCircuit | Para_MMD_MMD1_ImpulseValue | Para_MMD_MMD1_IntValue | Para_MMD_MMD1_MultiplierBusBar | Para_MMD_MMD1_MultiplierIL1L3 | Para_MMD_MMD1_MultiplierSynch1 | Para_MMD_MMD1_MultiplierSynch2 | Para_MMD_MMD1_MultiplierUL1L3 | Para_MMD_MMD1_NomFreq | Para_MMD_MMD1_NomFreqConv100 | Para_MMD_MMD1_NomVolt | Para_MMD_MMD1_OverFreq | Para_MMD_MMD1_OverFreqDelay | Para_MMD_MMD1_OverVolt | Para_MMD_MMD1_OverVoltDelay | Para_MMD_MMD1_PhaseDiffMax | Para_MMD_MMD1_Power0mA | Para_MMD_MMD1_Power20mA | Para_MMD_MMD1_PowerReactMin | Para_MMD_MMD1_PowerReactMinDelay | Para_MMD_MMD1_SwitchTimePowerCB | Para_MMD_MMD1_TimeRelImpMin | Para_MMD_MMD1_TransPhaseShift | Para_MMD_MMD1_UnderFreq | Para_MMD_MMD1_UnderFreqDelay | Para_MMD_MMD1_UnderVolt | Para_MMD_MMD1_UnderVolt2 | Para_MMD_MMD1_UnderVolt2Delay | Para_MMD_MMD1_UnderVoltDelay | Para_MMD_MMD1_VoltAsymetry | Para_MMD_MMD1_VoltAsymetryDelay | Para_MMD_MMD1_VoltBusBarMin | Para_MMD_MMD1_VoltDeadBus | Para_MMD_MMD1_VoltDiffMax | Para_MMD_MMD1_VoltNomBusBar | Para_MMD_MMD1_VoltNomSynch | Para_MMD_MMD1_VoltRange | Para_MMD_MMD1_VoltRangeBus | Para_MMD_MMD1_VoltRangeSync1 | Para_MMD_MMD1_VoltRangeSync2 | Para_MMD_MMD2_ActSynch | Para_MMD_MMD2_Aron | Para_MMD_MMD2_Bus3PhaseCircuit | Para_MMD_MMD2_CurrAsymetryDelay | Para_MMD_MMD2_CurrNeuMax | Para_MMD_MMD2_CurrNeuMaxDelay | Para_MMD_MMD2_CurrNeuNom | Para_MMD_MMD2_CurrRange | Para_MMD_MMD2_CurrShortCircuit | Para_MMD_MMD2_CurrShortCircuitDelay | Para_MMD_MMD2_CurrThermOverloadProt | Para_MMD_MMD2_FreqDiffMax | Para_MMD_MMD2_FreqDiffMin | Para_MMD_MMD2_Gen3PhaseCircuit | Para_MMD_MMD2_ImpulseValue | Para_MMD_MMD2_IntValue | Para_MMD_MMD2_MultiplierBusBar | Para_MMD_MMD2_MultiplierIL1L3 | Para_MMD_MMD2_MultiplierSynch1 | Para_MMD_MMD2_MultiplierSynch2 | Para_MMD_MMD2_MultiplierUL1L3 | Para_MMD_MMD2_NomFreq | Para_MMD_MMD2_NomFreqConv100 | Para_MMD_MMD2_NomVolt | Para_MMD_MMD2_OverFreq | Para_MMD_MMD2_OverFreqDelay | Para_MMD_MMD2_OverVolt | Para_MMD_MMD2_OverVoltDelay | Para_MMD_MMD2_PhaseDiffMax | Para_MMD_MMD2_Power0mA | Para_MMD_MMD2_Power20mA | Para_MMD_MMD2_PowerReactMin | Para_MMD_MMD2_PowerReactMinDelay | Para_MMD_MMD2_SwitchTimePowerCB | Para_MMD_MMD2_TimeRelImpMin | Para_MMD_MMD2_TransPhaseShift | Para_MMD_MMD2_UnderFreq | Para_MMD_MMD2_UnderFreqDelay | Para_MMD_MMD2_UnderVolt | Para_MMD_MMD2_UnderVolt2 | Para_MMD_MMD2_UnderVolt2Delay | Para_MMD_MMD2_UnderVoltDelay | Para_MMD_MMD2_VoltAsymetry | Para_MMD_MMD2_VoltAsymetryDelay | Para_MMD_MMD2_VoltBusBarMin | Para_MMD_MMD2_VoltDeadBus | Para_MMD_MMD2_VoltDiffMax | Para_MMD_MMD2_VoltNomBusBar | Para_MMD_MMD2_VoltNomSynch | Para_MMD_MMD2_VoltRange | Para_MMD_MMD2_VoltRangeBus | Para_MMD_MMD2_VoltRangeSync1 | Para_MMD_MMD2_VoltRangeSync2 | Para_MMD_MultiplierIL1L3 | Para_MMD_MultiplierUL1L3 | Para_MMD_OverFreq | Para_MMD_OverFreqDelay | Para_MMD_OverVolt | Para_MMD_OverVoltDelay | Para_MMD_Power0mA | Para_MMD_Power20mA | Para_MMD_PowerReactMin | Para_MMD_PowerReactMinDelay | Para_MMD_Relay1 | Para_MMD_Relay2 | Para_MMD_Relay3 | Para_MMD_Relay4 | Para_MMD_Relay5 | Para_MMD_Relay6 | Para_MMD_Relay7 | Para_MMD_Relay8 | Para_MMD_UnderFreq | Para_MMD_UnderFreqDelay | Para_MMD_UnderVolt | Para_MMD_UnderVoltDelay | Para_MMD_VoltAsymetry | Para_MMD_VoltAsymetryDelay | Para_MMD_VoltRange | Para_ModulControler_Ctr10_DComp | Para_ModulControler_Ctr10_deadband | Para_ModulControler_Ctr10_dW_down | Para_ModulControler_Ctr10_dW_up | Para_ModulControler_Ctr10_dY_max | Para_ModulControler_Ctr10_IComp | Para_ModulControler_Ctr10_Kp_manualAdjust | Para_ModulControler_Ctr10_nvert | Para_ModulControler_Ctr10_PComp | Para_ModulControler_Ctr10_Pos_HW_ReValve | Para_ModulControler_Ctr10_Pos_HW_ReValve_ScalMax | Para_ModulControler_Ctr10_Pos_HW_ReValve_ScalMin | Para_ModulControler_Ctr10_t_min_pulse_down | Para_ModulControler_Ctr10_t_min_pulse_up | Para_ModulControler_Ctr10_t_period_down | Para_ModulControler_Ctr10_t_period_up | Para_ModulControler_Ctr10_Tn_manualAdjust | Para_ModulControler_Ctr10_Tv_manualAdjust | Para_ModulControler_Ctr10_WMax | Para_ModulControler_Ctr10_WMin | Para_ModulControler_Ctr10_WStart | Para_ModulControler_Ctr10_Y_block | Para_ModulControler_Ctr10_YMax | Para_ModulControler_Ctr10_YMin | Para_ModulControler_Ctr11_DComp | Para_ModulControler_Ctr11_deadband | Para_ModulControler_Ctr11_dW_down | Para_ModulControler_Ctr11_dW_up | Para_ModulControler_Ctr11_dY_max | Para_ModulControler_Ctr11_IComp | Para_ModulControler_Ctr11_Kp_manualAdjust | Para_ModulControler_Ctr11_nvert | Para_ModulControler_Ctr11_PComp | Para_ModulControler_Ctr11_Pos_HW_EC_ReValve | Para_ModulControler_Ctr11_Pos_HW_EC_ReValve_ScalMax | Para_ModulControler_Ctr11_Pos_HW_EC_ReValve_ScalMin | Para_ModulControler_Ctr11_t_min_pulse_down | Para_ModulControler_Ctr11_t_min_pulse_up | Para_ModulControler_Ctr11_t_period_down | Para_ModulControler_Ctr11_t_period_up | Para_ModulControler_Ctr11_Tn_manualAdjust | Para_ModulControler_Ctr11_Tv_manualAdjust | Para_ModulControler_Ctr11_WMax | Para_ModulControler_Ctr11_WMin | Para_ModulControler_Ctr11_WStart | Para_ModulControler_Ctr11_Y_block | Para_ModulControler_Ctr11_YMax | Para_ModulControler_Ctr11_YMin | Para_ModulControler_Ctr12_DComp | Para_ModulControler_Ctr12_deadband | Para_ModulControler_Ctr12_dW_down | Para_ModulControler_Ctr12_dW_up | Para_ModulControler_Ctr12_dY_max | Para_ModulControler_Ctr12_IComp | Para_ModulControler_Ctr12_Kp_manualAdjust | Para_ModulControler_Ctr12_nvert | Para_ModulControler_Ctr12_PComp | Para_ModulControler_Ctr12_t_min_pulse_down | Para_ModulControler_Ctr12_t_min_pulse_up | Para_ModulControler_Ctr12_t_period_down | Para_ModulControler_Ctr12_t_period_up | Para_ModulControler_Ctr12_Tn_manualAdjust | Para_ModulControler_Ctr12_Tv_manualAdjust | Para_ModulControler_Ctr12_WMax | Para_ModulControler_Ctr12_WMin | Para_ModulControler_Ctr12_WStart | Para_ModulControler_Ctr12_Y_block | Para_ModulControler_Ctr12_YMax | Para_ModulControler_Ctr12_YMin | Para_ModulControler_Ctr13_DComp | Para_ModulControler_Ctr13_deadband | Para_ModulControler_Ctr13_dW_down | Para_ModulControler_Ctr13_dW_up | Para_ModulControler_Ctr13_dY_max | Para_ModulControler_Ctr13_IComp | Para_ModulControler_Ctr13_Kp_manualAdjust | Para_ModulControler_Ctr13_nvert | Para_ModulControler_Ctr13_PComp | Para_ModulControler_Ctr13_t_min_pulse_down | Para_ModulControler_Ctr13_t_min_pulse_up | Para_ModulControler_Ctr13_t_period_down | Para_ModulControler_Ctr13_t_period_up | Para_ModulControler_Ctr13_Tn_manualAdjust | Para_ModulControler_Ctr13_Tv_manualAdjust | Para_ModulControler_Ctr13_WMax | Para_ModulControler_Ctr13_WMin | Para_ModulControler_Ctr13_WStart | Para_ModulControler_Ctr13_Y_block | Para_ModulControler_Ctr13_YMax | Para_ModulControler_Ctr13_YMin | Para_ModulControler_Ctr14_DComp | Para_ModulControler_Ctr14_deadband | Para_ModulControler_Ctr14_dW_down | Para_ModulControler_Ctr14_dW_up | Para_ModulControler_Ctr14_dY_max | Para_ModulControler_Ctr14_IComp | Para_ModulControler_Ctr14_Kp_manualAdjust | Para_ModulControler_Ctr14_nvert | Para_ModulControler_Ctr14_PComp | Para_ModulControler_Ctr14_t_min_pulse_down | Para_ModulControler_Ctr14_t_min_pulse_up | Para_ModulControler_Ctr14_t_period_down | Para_ModulControler_Ctr14_t_period_up | Para_ModulControler_Ctr14_Tn_manualAdjust | Para_ModulControler_Ctr14_Tv_manualAdjust | Para_ModulControler_Ctr14_WMax | Para_ModulControler_Ctr14_WMin | Para_ModulControler_Ctr14_WStart | Para_ModulControler_Ctr14_Y_block | Para_ModulControler_Ctr14_YMax | Para_ModulControler_Ctr14_YMin | Para_ModulControler_Ctr15_DComp | Para_ModulControler_Ctr15_deadband | Para_ModulControler_Ctr15_dW_down | Para_ModulControler_Ctr15_dW_up | Para_ModulControler_Ctr15_dY_max | Para_ModulControler_Ctr15_IComp | Para_ModulControler_Ctr15_Kp_manualAdjust | Para_ModulControler_Ctr15_nvert | Para_ModulControler_Ctr15_PComp | Para_ModulControler_Ctr15_t_min_pulse_down | Para_ModulControler_Ctr15_t_min_pulse_up | Para_ModulControler_Ctr15_t_period_down | Para_ModulControler_Ctr15_t_period_up | Para_ModulControler_Ctr15_Tn_manualAdjust | Para_ModulControler_Ctr15_Tv_manualAdjust | Para_ModulControler_Ctr15_WMax | Para_ModulControler_Ctr15_WMin | Para_ModulControler_Ctr15_WStart | Para_ModulControler_Ctr15_Y_block | Para_ModulControler_Ctr15_YMax | Para_ModulControler_Ctr15_YMin | Para_ModulControler_Ctr16_DComp | Para_ModulControler_Ctr16_deadband | Para_ModulControler_Ctr16_dW_down | Para_ModulControler_Ctr16_dW_up | Para_ModulControler_Ctr16_dY_max | Para_ModulControler_Ctr16_IComp | Para_ModulControler_Ctr16_Kp_manualAdjust | Para_ModulControler_Ctr16_nvert | Para_ModulControler_Ctr16_PComp | Para_ModulControler_Ctr16_t_min_pulse_down | Para_ModulControler_Ctr16_t_min_pulse_up | Para_ModulControler_Ctr16_t_period_down | Para_ModulControler_Ctr16_t_period_up | Para_ModulControler_Ctr16_Tn_manualAdjust | Para_ModulControler_Ctr16_Tv_manualAdjust | Para_ModulControler_Ctr16_WMax | Para_ModulControler_Ctr16_WMin | Para_ModulControler_Ctr16_WStart | Para_ModulControler_Ctr16_Y_block | Para_ModulControler_Ctr16_YMax | Para_ModulControler_Ctr16_YMin | Para_ModulControler_Ctr17_DComp | Para_ModulControler_Ctr17_deadband | Para_ModulControler_Ctr17_dW_down | Para_ModulControler_Ctr17_dW_up | Para_ModulControler_Ctr17_dY_max | Para_ModulControler_Ctr17_IComp | Para_ModulControler_Ctr17_Kp_manualAdjust | Para_ModulControler_Ctr17_nvert | Para_ModulControler_Ctr17_PComp | Para_ModulControler_Ctr17_t_min_pulse_down | Para_ModulControler_Ctr17_t_min_pulse_up | Para_ModulControler_Ctr17_t_period_down | Para_ModulControler_Ctr17_t_period_up | Para_ModulControler_Ctr17_Tn_manualAdjust | Para_ModulControler_Ctr17_Tv_manualAdjust | Para_ModulControler_Ctr17_WMax | Para_ModulControler_Ctr17_WMin | Para_ModulControler_Ctr17_WStart | Para_ModulControler_Ctr17_Y_block | Para_ModulControler_Ctr17_YMax | Para_ModulControler_Ctr17_YMin | Para_ModulControler_Ctr18_DComp | Para_ModulControler_Ctr18_deadband | Para_ModulControler_Ctr18_dW_down | Para_ModulControler_Ctr18_dW_up | Para_ModulControler_Ctr18_dY_max | Para_ModulControler_Ctr18_IComp | Para_ModulControler_Ctr18_Kp_manualAdjust | Para_ModulControler_Ctr18_nvert | Para_ModulControler_Ctr18_PComp | Para_ModulControler_Ctr18_t_min_pulse_down | Para_ModulControler_Ctr18_t_min_pulse_up | Para_ModulControler_Ctr18_t_period_down | Para_ModulControler_Ctr18_t_period_up | Para_ModulControler_Ctr18_Tn_manualAdjust | Para_ModulControler_Ctr18_Tv_manualAdjust | Para_ModulControler_Ctr18_WMax | Para_ModulControler_Ctr18_WMin | Para_ModulControler_Ctr18_WStart | Para_ModulControler_Ctr18_Y_block | Para_ModulControler_Ctr18_YMax | Para_ModulControler_Ctr18_YMin | Para_ModulControler_Ctr19_DComp | Para_ModulControler_Ctr19_deadband | Para_ModulControler_Ctr19_dW_down | Para_ModulControler_Ctr19_dW_up | Para_ModulControler_Ctr19_dY_max | Para_ModulControler_Ctr19_IComp | Para_ModulControler_Ctr19_Kp_manualAdjust | Para_ModulControler_Ctr19_nvert | Para_ModulControler_Ctr19_PComp | Para_ModulControler_Ctr19_t_min_pulse_down | Para_ModulControler_Ctr19_t_min_pulse_up | Para_ModulControler_Ctr19_t_period_down | Para_ModulControler_Ctr19_t_period_up | Para_ModulControler_Ctr19_Tn_manualAdjust | Para_ModulControler_Ctr19_Tv_manualAdjust | Para_ModulControler_Ctr19_WMax | Para_ModulControler_Ctr19_WMin | Para_ModulControler_Ctr19_WStart | Para_ModulControler_Ctr19_Y_block | Para_ModulControler_Ctr19_YMax | Para_ModulControler_Ctr19_YMin | Para_ModulControler_Ctr1_DComp | Para_ModulControler_Ctr1_deadband | Para_ModulControler_Ctr1_dY_max | Para_ModulControler_Ctr1_IComp | Para_ModulControler_Ctr1_Kp_manualAdjust | Para_ModulControler_Ctr1_nvert | Para_ModulControler_Ctr1_PComp | Para_ModulControler_Ctr1_ScaleMax | Para_ModulControler_Ctr1_ScaleMin | Para_ModulControler_Ctr1_t_min_pulse_down | Para_ModulControler_Ctr1_t_min_pulse_up | Para_ModulControler_Ctr1_t_period_down | Para_ModulControler_Ctr1_t_period_up | Para_ModulControler_Ctr1_Tn_manualAdjust | Para_ModulControler_Ctr1_Tv_manualAdjust | Para_ModulControler_Ctr1_WMax | Para_ModulControler_Ctr1_WMin | Para_ModulControler_Ctr1_WRampNeg | Para_ModulControler_Ctr1_WRampPos | Para_ModulControler_Ctr1_WStart | Para_ModulControler_Ctr1_Y_block | Para_ModulControler_Ctr1_YMax | Para_ModulControler_Ctr1_YMin | Para_ModulControler_Ctr20_DComp | Para_ModulControler_Ctr20_deadband | Para_ModulControler_Ctr20_dW_down | Para_ModulControler_Ctr20_dW_up | Para_ModulControler_Ctr20_dY_max | Para_ModulControler_Ctr20_IComp | Para_ModulControler_Ctr20_Kp_manualAdjust | Para_ModulControler_Ctr20_nvert | Para_ModulControler_Ctr20_PComp | Para_ModulControler_Ctr20_t_min_pulse_down | Para_ModulControler_Ctr20_t_min_pulse_up | Para_ModulControler_Ctr20_t_period_down | Para_ModulControler_Ctr20_t_period_up | Para_ModulControler_Ctr20_Tn_manualAdjust | Para_ModulControler_Ctr20_Tv_manualAdjust | Para_ModulControler_Ctr20_WMax | Para_ModulControler_Ctr20_WMin | Para_ModulControler_Ctr20_WStart | Para_ModulControler_Ctr20_Y_block | Para_ModulControler_Ctr20_YMax | Para_ModulControler_Ctr20_YMin | Para_ModulControler_Ctr21_DComp | Para_ModulControler_Ctr21_deadband | Para_ModulControler_Ctr21_dW_down | Para_ModulControler_Ctr21_dW_up | Para_ModulControler_Ctr21_dY_max | Para_ModulControler_Ctr21_IComp | Para_ModulControler_Ctr21_Kp_manualAdjust | Para_ModulControler_Ctr21_nvert | Para_ModulControler_Ctr21_PComp | Para_ModulControler_Ctr21_t_min_pulse_down | Para_ModulControler_Ctr21_t_min_pulse_up | Para_ModulControler_Ctr21_t_period_down | Para_ModulControler_Ctr21_t_period_up | Para_ModulControler_Ctr21_Tn_manualAdjust | Para_ModulControler_Ctr21_Tv_manualAdjust | Para_ModulControler_Ctr21_WMax | Para_ModulControler_Ctr21_WMin | Para_ModulControler_Ctr21_WStart | Para_ModulControler_Ctr21_Y_block | Para_ModulControler_Ctr21_YMax | Para_ModulControler_Ctr21_YMin | Para_ModulControler_Ctr22_DComp | Para_ModulControler_Ctr22_deadband | Para_ModulControler_Ctr22_dW_down | Para_ModulControler_Ctr22_dW_up | Para_ModulControler_Ctr22_dY_max | Para_ModulControler_Ctr22_IComp | Para_ModulControler_Ctr22_Kp_manualAdjust | Para_ModulControler_Ctr22_nvert | Para_ModulControler_Ctr22_PComp | Para_ModulControler_Ctr22_t_min_pulse_down | Para_ModulControler_Ctr22_t_min_pulse_up | Para_ModulControler_Ctr22_t_period_down | Para_ModulControler_Ctr22_t_period_up | Para_ModulControler_Ctr22_Tn_manualAdjust | Para_ModulControler_Ctr22_Tv_manualAdjust | Para_ModulControler_Ctr22_WMax | Para_ModulControler_Ctr22_WMin | Para_ModulControler_Ctr22_WStart | Para_ModulControler_Ctr22_Y_block | Para_ModulControler_Ctr22_YMax | Para_ModulControler_Ctr22_YMin | Para_ModulControler_Ctr23_DComp | Para_ModulControler_Ctr23_deadband | Para_ModulControler_Ctr23_dW_down | Para_ModulControler_Ctr23_dW_up | Para_ModulControler_Ctr23_dY_max | Para_ModulControler_Ctr23_IComp | Para_ModulControler_Ctr23_Kp_manualAdjust | Para_ModulControler_Ctr23_nvert | Para_ModulControler_Ctr23_PComp | Para_ModulControler_Ctr23_t_min_pulse_down | Para_ModulControler_Ctr23_t_min_pulse_up | Para_ModulControler_Ctr23_t_period_down | Para_ModulControler_Ctr23_t_period_up | Para_ModulControler_Ctr23_Tn_manualAdjust | Para_ModulControler_Ctr23_Tv_manualAdjust | Para_ModulControler_Ctr23_WMax | Para_ModulControler_Ctr23_WMin | Para_ModulControler_Ctr23_WStart | Para_ModulControler_Ctr23_Y_block | Para_ModulControler_Ctr23_YMax | Para_ModulControler_Ctr23_YMin | Para_ModulControler_Ctr24_DComp | Para_ModulControler_Ctr24_deadband | Para_ModulControler_Ctr24_dW_down | Para_ModulControler_Ctr24_dW_up | Para_ModulControler_Ctr24_dY_max | Para_ModulControler_Ctr24_IComp | Para_ModulControler_Ctr24_Kp_manualAdjust | Para_ModulControler_Ctr24_nvert | Para_ModulControler_Ctr24_PComp | Para_ModulControler_Ctr24_t_min_pulse_down | Para_ModulControler_Ctr24_t_min_pulse_up | Para_ModulControler_Ctr24_t_period_down | Para_ModulControler_Ctr24_t_period_up | Para_ModulControler_Ctr24_Tn_manualAdjust | Para_ModulControler_Ctr24_Tv_manualAdjust | Para_ModulControler_Ctr24_WMax | Para_ModulControler_Ctr24_WMin | Para_ModulControler_Ctr24_WStart | Para_ModulControler_Ctr24_Y_block | Para_ModulControler_Ctr24_YMax | Para_ModulControler_Ctr24_YMin | Para_ModulControler_Ctr25_DComp | Para_ModulControler_Ctr25_deadband | Para_ModulControler_Ctr25_dW_down | Para_ModulControler_Ctr25_dW_up | Para_ModulControler_Ctr25_dY_max | Para_ModulControler_Ctr25_IComp | Para_ModulControler_Ctr25_Kp_manualAdjust | Para_ModulControler_Ctr25_nvert | Para_ModulControler_Ctr25_PComp | Para_ModulControler_Ctr25_t_min_pulse_down | Para_ModulControler_Ctr25_t_min_pulse_up | Para_ModulControler_Ctr25_t_period_down | Para_ModulControler_Ctr25_t_period_up | Para_ModulControler_Ctr25_Tn_manualAdjust | Para_ModulControler_Ctr25_Tv_manualAdjust | Para_ModulControler_Ctr25_WMax | Para_ModulControler_Ctr25_WMin | Para_ModulControler_Ctr25_WStart | Para_ModulControler_Ctr25_Y_block | Para_ModulControler_Ctr25_YMax | Para_ModulControler_Ctr25_YMin | Para_ModulControler_Ctr26_DComp | Para_ModulControler_Ctr26_deadband | Para_ModulControler_Ctr26_dW_down | Para_ModulControler_Ctr26_dW_up | Para_ModulControler_Ctr26_dY_max | Para_ModulControler_Ctr26_IComp | Para_ModulControler_Ctr26_Kp_manualAdjust | Para_ModulControler_Ctr26_nvert | Para_ModulControler_Ctr26_PComp | Para_ModulControler_Ctr26_t_min_pulse_down | Para_ModulControler_Ctr26_t_min_pulse_up | Para_ModulControler_Ctr26_t_period_down | Para_ModulControler_Ctr26_t_period_up | Para_ModulControler_Ctr26_Tn_manualAdjust | Para_ModulControler_Ctr26_Tv_manualAdjust | Para_ModulControler_Ctr26_WMax | Para_ModulControler_Ctr26_WMin | Para_ModulControler_Ctr26_WStart | Para_ModulControler_Ctr26_Y_block | Para_ModulControler_Ctr26_YMax | Para_ModulControler_Ctr26_YMin | Para_ModulControler_Ctr27_DComp | Para_ModulControler_Ctr27_deadband | Para_ModulControler_Ctr27_dW_down | Para_ModulControler_Ctr27_dW_up | Para_ModulControler_Ctr27_dY_max | Para_ModulControler_Ctr27_IComp | Para_ModulControler_Ctr27_Kp_manualAdjust | Para_ModulControler_Ctr27_nvert | Para_ModulControler_Ctr27_PComp | Para_ModulControler_Ctr27_t_min_pulse_down | Para_ModulControler_Ctr27_t_min_pulse_up | Para_ModulControler_Ctr27_t_period_down | Para_ModulControler_Ctr27_t_period_up | Para_ModulControler_Ctr27_Tn_manualAdjust | Para_ModulControler_Ctr27_Tv_manualAdjust | Para_ModulControler_Ctr27_WMax | Para_ModulControler_Ctr27_WMin | Para_ModulControler_Ctr27_WStart | Para_ModulControler_Ctr27_Y_block | Para_ModulControler_Ctr27_YMax | Para_ModulControler_Ctr27_YMin | Para_ModulControler_Ctr28_DComp | Para_ModulControler_Ctr28_deadband | Para_ModulControler_Ctr28_dW_down | Para_ModulControler_Ctr28_dW_up | Para_ModulControler_Ctr28_dY_max | Para_ModulControler_Ctr28_IComp | Para_ModulControler_Ctr28_Kp_manualAdjust | Para_ModulControler_Ctr28_nvert | Para_ModulControler_Ctr28_PComp | Para_ModulControler_Ctr28_t_min_pulse_down | Para_ModulControler_Ctr28_t_min_pulse_up | Para_ModulControler_Ctr28_t_period_down | Para_ModulControler_Ctr28_t_period_up | Para_ModulControler_Ctr28_Tn_manualAdjust | Para_ModulControler_Ctr28_Tv_manualAdjust | Para_ModulControler_Ctr28_WMax | Para_ModulControler_Ctr28_WMin | Para_ModulControler_Ctr28_WStart | Para_ModulControler_Ctr28_Y_block | Para_ModulControler_Ctr28_YMax | Para_ModulControler_Ctr28_YMin | Para_ModulControler_Ctr29_DComp | Para_ModulControler_Ctr29_deadband | Para_ModulControler_Ctr29_dW_down | Para_ModulControler_Ctr29_dW_up | Para_ModulControler_Ctr29_dY_max | Para_ModulControler_Ctr29_IComp | Para_ModulControler_Ctr29_Kp_manualAdjust | Para_ModulControler_Ctr29_nvert | Para_ModulControler_Ctr29_PComp | Para_ModulControler_Ctr29_t_min_pulse_down | Para_ModulControler_Ctr29_t_min_pulse_up | Para_ModulControler_Ctr29_t_period_down | Para_ModulControler_Ctr29_t_period_up | Para_ModulControler_Ctr29_Tn_manualAdjust | Para_ModulControler_Ctr29_Tv_manualAdjust | Para_ModulControler_Ctr29_WMax | Para_ModulControler_Ctr29_WMin | Para_ModulControler_Ctr29_WStart | Para_ModulControler_Ctr29_Y_block | Para_ModulControler_Ctr29_YMax | Para_ModulControler_Ctr29_YMin | Para_ModulControler_Ctr2_DComp | Para_ModulControler_Ctr2_deadband | Para_ModulControler_Ctr2_dY_max | Para_ModulControler_Ctr2_IComp | Para_ModulControler_Ctr2_Kp_manualAdjust | Para_ModulControler_Ctr2_nvert | Para_ModulControler_Ctr2_PComp | Para_ModulControler_Ctr2_ScaleMax | Para_ModulControler_Ctr2_ScaleMin | Para_ModulControler_Ctr2_t_min_pulse_down | Para_ModulControler_Ctr2_t_min_pulse_up | Para_ModulControler_Ctr2_t_period_down | Para_ModulControler_Ctr2_t_period_up | Para_ModulControler_Ctr2_Tn_manualAdjust | Para_ModulControler_Ctr2_Tv_manualAdjust | Para_ModulControler_Ctr2_WMax | Para_ModulControler_Ctr2_WMin | Para_ModulControler_Ctr2_WRampNeg | Para_ModulControler_Ctr2_WRampPos | Para_ModulControler_Ctr2_WStart | Para_ModulControler_Ctr2_Y_block | Para_ModulControler_Ctr2_YMax | Para_ModulControler_Ctr2_YMin | Para_ModulControler_Ctr30_DComp | Para_ModulControler_Ctr30_deadband | Para_ModulControler_Ctr30_dW_down | Para_ModulControler_Ctr30_dW_up | Para_ModulControler_Ctr30_dY_max | Para_ModulControler_Ctr30_IComp | Para_ModulControler_Ctr30_Kp_manualAdjust | Para_ModulControler_Ctr30_nvert | Para_ModulControler_Ctr30_PComp | Para_ModulControler_Ctr30_t_min_pulse_down | Para_ModulControler_Ctr30_t_min_pulse_up | Para_ModulControler_Ctr30_t_period_down | Para_ModulControler_Ctr30_t_period_up | Para_ModulControler_Ctr30_Tn_manualAdjust | Para_ModulControler_Ctr30_Tv_manualAdjust | Para_ModulControler_Ctr30_WMax | Para_ModulControler_Ctr30_WMin | Para_ModulControler_Ctr30_WStart | Para_ModulControler_Ctr30_Y_block | Para_ModulControler_Ctr30_YMax | Para_ModulControler_Ctr30_YMin | Para_ModulControler_Ctr31_DComp | Para_ModulControler_Ctr31_deadband | Para_ModulControler_Ctr31_dW_down | Para_ModulControler_Ctr31_dW_up | Para_ModulControler_Ctr31_dY_max | Para_ModulControler_Ctr31_IComp | Para_ModulControler_Ctr31_Kp_manualAdjust | Para_ModulControler_Ctr31_nvert | Para_ModulControler_Ctr31_PComp | Para_ModulControler_Ctr31_t_min_pulse_down | Para_ModulControler_Ctr31_t_min_pulse_up | Para_ModulControler_Ctr31_t_period_down | Para_ModulControler_Ctr31_t_period_up | Para_ModulControler_Ctr31_Tn_manualAdjust | Para_ModulControler_Ctr31_Tv_manualAdjust | Para_ModulControler_Ctr31_WMax | Para_ModulControler_Ctr31_WMin | Para_ModulControler_Ctr31_WStart | Para_ModulControler_Ctr31_Y_block | Para_ModulControler_Ctr31_YMax | Para_ModulControler_Ctr31_YMin | Para_ModulControler_Ctr32_Ctr_Mns_AnaIn_Setp_Enable | Para_ModulControler_Ctr32_Ctr_Mns_Setp_ScalMax | Para_ModulControler_Ctr32_Ctr_Mns_Setp_ScalMin | Para_ModulControler_Ctr32_Ctr_Mns_Setp_Set4mA | Para_ModulControler_Ctr32_DComp | Para_ModulControler_Ctr32_deadband | Para_ModulControler_Ctr32_dW_down | Para_ModulControler_Ctr32_dW_up | Para_ModulControler_Ctr32_dY_max | Para_ModulControler_Ctr32_IComp | Para_ModulControler_Ctr32_Kp_manualAdjust | Para_ModulControler_Ctr32_Limit_DemGenerate_Lim_Off | Para_ModulControler_Ctr32_Limit_DemGenerate_Lim_On | Para_ModulControler_Ctr32_Limit_LimOnOff_aktiv | Para_ModulControler_Ctr32_Limit_MainsExport_max | Para_ModulControler_Ctr32_Limit_MainsExport_max_trip | Para_ModulControler_Ctr32_Limit_MainsImport_max | Para_ModulControler_Ctr32_Limit_MainsImport_max_trip | Para_ModulControler_Ctr32_Limit_Time_Dem_Off_delay | Para_ModulControler_Ctr32_Limit_Time_Dem_On_delay | Para_ModulControler_Ctr32_nvert | Para_ModulControler_Ctr32_P_Mns_AnaIn_ScalMax | Para_ModulControler_Ctr32_P_Mns_AnaIn_ScalMin | Para_ModulControler_Ctr32_P_Mns_AnaIn_Set4mA | Para_ModulControler_Ctr32_P_Mns_MMU_Enable | Para_ModulControler_Ctr32_PComp | Para_ModulControler_Ctr32_t_min_pulse_down | Para_ModulControler_Ctr32_t_min_pulse_up | Para_ModulControler_Ctr32_t_period_down | Para_ModulControler_Ctr32_t_period_up | Para_ModulControler_Ctr32_Tn_manualAdjust | Para_ModulControler_Ctr32_Tv_manualAdjust | Para_ModulControler_Ctr32_WMax | Para_ModulControler_Ctr32_WMin | Para_ModulControler_Ctr32_WStart | Para_ModulControler_Ctr32_Y_block | Para_ModulControler_Ctr32_YMax | Para_ModulControler_Ctr32_YMin | Para_ModulControler_Ctr3_DComp | Para_ModulControler_Ctr3_deadband | Para_ModulControler_Ctr3_dY_max | Para_ModulControler_Ctr3_IComp | Para_ModulControler_Ctr3_Kp_manualAdjust | Para_ModulControler_Ctr3_nvert | Para_ModulControler_Ctr3_PComp | Para_ModulControler_Ctr3_ScaleMax | Para_ModulControler_Ctr3_ScaleMin | Para_ModulControler_Ctr3_t_min_pulse_down | Para_ModulControler_Ctr3_t_min_pulse_up | Para_ModulControler_Ctr3_t_period_down | Para_ModulControler_Ctr3_t_period_up | Para_ModulControler_Ctr3_Tn_manualAdjust | Para_ModulControler_Ctr3_Tv_manualAdjust | Para_ModulControler_Ctr3_WMax | Para_ModulControler_Ctr3_WMin | Para_ModulControler_Ctr3_WRampNeg | Para_ModulControler_Ctr3_WRampPos | Para_ModulControler_Ctr3_WStart | Para_ModulControler_Ctr3_Y_block | Para_ModulControler_Ctr3_YMax | Para_ModulControler_Ctr3_YMin | Para_ModulControler_Ctr4_DComp | Para_ModulControler_Ctr4_deadband | Para_ModulControler_Ctr4_dY_max | Para_ModulControler_Ctr4_IComp | Para_ModulControler_Ctr4_Kp_manualAdjust | Para_ModulControler_Ctr4_nvert | Para_ModulControler_Ctr4_PComp | Para_ModulControler_Ctr4_ScaleMax | Para_ModulControler_Ctr4_ScaleMin | Para_ModulControler_Ctr4_t_min_pulse_down | Para_ModulControler_Ctr4_t_min_pulse_up | Para_ModulControler_Ctr4_t_period_down | Para_ModulControler_Ctr4_t_period_up | Para_ModulControler_Ctr4_Tn_manualAdjust | Para_ModulControler_Ctr4_Tv_manualAdjust | Para_ModulControler_Ctr4_WMax | Para_ModulControler_Ctr4_WMin | Para_ModulControler_Ctr4_WRampNeg | Para_ModulControler_Ctr4_WRampPos | Para_ModulControler_Ctr4_WStart | Para_ModulControler_Ctr4_Y_block | Para_ModulControler_Ctr4_YMax | Para_ModulControler_Ctr4_YMin | Para_ModulControler_Ctr5_DComp | Para_ModulControler_Ctr5_deadband | Para_ModulControler_Ctr5_dY_max | Para_ModulControler_Ctr5_IComp | Para_ModulControler_Ctr5_Kp_manualAdjust | Para_ModulControler_Ctr5_nvert | Para_ModulControler_Ctr5_PComp | Para_ModulControler_Ctr5_ScaleMax | Para_ModulControler_Ctr5_ScaleMin | Para_ModulControler_Ctr5_t_min_pulse_down | Para_ModulControler_Ctr5_t_min_pulse_up | Para_ModulControler_Ctr5_t_period_down | Para_ModulControler_Ctr5_t_period_up | Para_ModulControler_Ctr5_Tn_manualAdjust | Para_ModulControler_Ctr5_Tv_manualAdjust | Para_ModulControler_Ctr5_WMax | Para_ModulControler_Ctr5_WMin | Para_ModulControler_Ctr5_WRampNeg | Para_ModulControler_Ctr5_WRampPos | Para_ModulControler_Ctr5_WStart | Para_ModulControler_Ctr5_Y_block | Para_ModulControler_Ctr5_YMax | Para_ModulControler_Ctr5_YMin | Para_ModulControler_Ctr6_DComp | Para_ModulControler_Ctr6_deadband | Para_ModulControler_Ctr6_dY_max | Para_ModulControler_Ctr6_IComp | Para_ModulControler_Ctr6_Kp_manualAdjust | Para_ModulControler_Ctr6_nvert | Para_ModulControler_Ctr6_PComp | Para_ModulControler_Ctr6_ScaleMax | Para_ModulControler_Ctr6_ScaleMin | Para_ModulControler_Ctr6_t_min_pulse_down | Para_ModulControler_Ctr6_t_min_pulse_up | Para_ModulControler_Ctr6_t_period_down | Para_ModulControler_Ctr6_t_period_up | Para_ModulControler_Ctr6_Tn_manualAdjust | Para_ModulControler_Ctr6_Tv_manualAdjust | Para_ModulControler_Ctr6_WMax | Para_ModulControler_Ctr6_WMin | Para_ModulControler_Ctr6_WRampNeg | Para_ModulControler_Ctr6_WRampPos | Para_ModulControler_Ctr6_WStart | Para_ModulControler_Ctr6_Y_block | Para_ModulControler_Ctr6_YMax | Para_ModulControler_Ctr6_YMin | Para_ModulControler_Ctr7_DComp | Para_ModulControler_Ctr7_deadband | Para_ModulControler_Ctr7_dY_max | Para_ModulControler_Ctr7_IComp | Para_ModulControler_Ctr7_Kp_manualAdjust | Para_ModulControler_Ctr7_nvert | Para_ModulControler_Ctr7_PComp | Para_ModulControler_Ctr7_ScaleMax | Para_ModulControler_Ctr7_ScaleMin | Para_ModulControler_Ctr7_t_min_pulse_down | Para_ModulControler_Ctr7_t_min_pulse_up | Para_ModulControler_Ctr7_t_period_down | Para_ModulControler_Ctr7_t_period_up | Para_ModulControler_Ctr7_Tn_manualAdjust | Para_ModulControler_Ctr7_Tv_manualAdjust | Para_ModulControler_Ctr7_WMax | Para_ModulControler_Ctr7_WMin | Para_ModulControler_Ctr7_WRampNeg | Para_ModulControler_Ctr7_WRampPos | Para_ModulControler_Ctr7_WStart | Para_ModulControler_Ctr7_Y_block | Para_ModulControler_Ctr7_YMax | Para_ModulControler_Ctr7_YMin | Para_ModulControler_Ctr8_DComp | Para_ModulControler_Ctr8_deadband | Para_ModulControler_Ctr8_dY_max | Para_ModulControler_Ctr8_IComp | Para_ModulControler_Ctr8_Kp_manualAdjust | Para_ModulControler_Ctr8_nvert | Para_ModulControler_Ctr8_PComp | Para_ModulControler_Ctr8_ScaleMax | Para_ModulControler_Ctr8_ScaleMin | Para_ModulControler_Ctr8_t_min_pulse_down | Para_ModulControler_Ctr8_t_min_pulse_up | Para_ModulControler_Ctr8_t_period_down | Para_ModulControler_Ctr8_t_period_up | Para_ModulControler_Ctr8_Tn_manualAdjust | Para_ModulControler_Ctr8_Tv_manualAdjust | Para_ModulControler_Ctr8_WMax | Para_ModulControler_Ctr8_WMin | Para_ModulControler_Ctr8_WRampNeg | Para_ModulControler_Ctr8_WRampPos | Para_ModulControler_Ctr8_WStart | Para_ModulControler_Ctr8_Y_block | Para_ModulControler_Ctr8_YMax | Para_ModulControler_Ctr8_YMin | Para_ModulControler_Ctr_CC | Para_ModulControler_Ctr_CDSu | Para_ModulControler_Ctr_ChCHP | Para_ModulControler_Ctr_CircLou | Para_ModulControler_Ctr_Cust1 | Para_ModulControler_Ctr_Cust2 | Para_ModulControler_Ctr_Cust3 | Para_ModulControler_Ctr_Cust4 | Para_ModulControler_Ctr_Cust5 | Para_ModulControler_Ctr_Cust6 | Para_ModulControler_Ctr_Cust7 | Para_ModulControler_Ctr_Cust8 | Para_ModulControler_Ctr_ECW | Para_ModulControler_Ctr_EOVal_Active | Para_ModulControler_Ctr_EOVal_LT_Active | Para_ModulControler_Ctr_GC | Para_ModulControler_Ctr_InlLou | Para_ModulControler_Ctr_Mns_Enable | Para_ModulControler_Ctr_OutlLou_RDP | Para_ModulControler_Ctr_OutlLou_RT | Para_ModulControler_Ctr_OutlVE_RDP | Para_ModulControler_Ctr_OutlVE_RT | Para_ModulControler_Ctr_SCR_Flow | Para_ModulControler_Ctr_SCR_NOx | Para_ModulControler_CtrGenPF_Active | Para_ModulControler_CtrThR_Heater_Active | Para_Monic_ActVoltAvgMax | Para_Monic_ActVoltDif | Para_Monic_ActVoltMax | Para_Monic_ActVoltMin | Para_Monic_LimitActive | Para_Monic_LimitActiveHys | Para_Monic_TriggerVolt | Para_Monic_VoltAvgMax | Para_Monic_VoltAvgMaxDelay | Para_Monic_VoltDif | Para_Monic_VoltDifDelay | Para_Monic_VoltMax | Para_Monic_VoltMaxDelay | Para_Monic_VoltMin | Para_Monic_VoltMinDelay | Para_PBC_AI_NEx | Para_PBC_AvgPMaxLimit | Para_PBC_LimitPressMax | Para_PBC_LimitPressMaxAvg | Para_PBC_NumbCycBelowPressMax | Para_PBC_NumbCycBelowPressMean | Para_PBC_NumbCycExcPressMax | Para_PBC_NumbCycExcPressMean | Para_PBC_NumbMisfCycMin | Para_PBC_PowerRed | Para_PBC_PressMeanDevMisf | Para_PBC_PressMeanDevNeg | Para_PBC_PressMeanDevPos | Para_PBC_Sensitivity | Para_PI_20mA | Para_PI_4mA | Para_PI_ActCloseDetection | Para_PI_FailRateValveOpen | Para_PI_FailRateValveOpenTP | Para_PI_LambdaFeedFwdCtr_Gas1_OffsetStartLambda | Para_PI_LambdaFeedFwdCtr_Gas2_OffsetStartLambda | Para_PI_LambdaFeedFwdCtr_Gas3_OffsetStartLambda | Para_PI_LambdaFeedFwdCtr_Gas4_OffsetStartLambda | Para_PI_Limit_GasRailPressDiffMax | Para_PI_Limit_GasRailPressDiffMin | Para_PI_Limit_GasRailPressMax | Para_PI_Limit_GasRailPressMin | Para_PI_Limit_GasRailTempMax | Para_PI_Limit_GasRailTempMin | Para_PI_ReleaseBal | Para_PI_ValveType | Para_Power_Actual_Curr1 | Para_Power_Actual_Curr2 | Para_Power_Actual_Point1 | Para_Power_Actual_Point2 | Para_Power_Ctr_TbDComp | Para_Power_Ctr_TbIComp | Para_Power_Ctr_TbPComp | Para_Power_Ctr_TbYMax | Para_Power_Ctr_TbYMin | Para_Power_Ctr_TrDComp | Para_Power_Ctr_TrIComp | Para_Power_Ctr_TrPComp | Para_Power_Ctr_TrYMax | Para_Power_Ctr_TrYMin | Para_Power_ExtRed_Curr1 | Para_Power_ExtRed_Curr2 | Para_Power_ExtRed_Point1 | Para_Power_ExtRed_Point2 | Para_Power_ExtSet_ConstSetPoint1 | Para_Power_ExtSet_ConstSetPoint2 | Para_Power_ExtSet_ConstSetPoint3 | Para_Power_ExtSet_ConstSetPoint4 | Para_Power_ExtSet_ConstSetPoint5 | Para_Power_ExtSet_Curr1 | Para_Power_ExtSet_Curr2 | Para_Power_ExtSet_Point1 | Para_Power_ExtSet_Point2 | Para_Power_IntakeAirRed_RedFac | Para_Power_IntakeAirRed_RedFac2 | Para_Power_IntakeAirRed_Start | Para_Power_IntakeAirRed_Start2 | Para_Power_IPAdap_ActITPTbAdap | Para_Power_IPAdap_IPRedTBGas1 | Para_Power_IPAdap_IPRedTBGas2 | Para_Power_IPAdap_IPRedTBGas3 | Para_Power_IPAdap_IPRedTBGas4 | Para_Power_IPAdap_ITPTbPosAdap | Para_Power_Limit_Backfire | Para_Power_Limit_BackfireHys | Para_Power_Limit_GasChange | Para_Power_Limit_GasChangeHys | Para_Power_Limit_Perc40Pnom | Para_Power_Limit_Perc40PnomHys | Para_Power_Limit_PowerDiff | Para_Power_Limit_PowerDiffDelay | Para_Power_Limit_PowerDiffRated | Para_Power_Limit_PowerDiffRatedDelay | Para_Power_Limit_PowerLimit1 | Para_Power_Limit_PowerLimit1Hys | Para_Power_Limit_PowerRetLimit | Para_Power_Limit_PowerRetLimitHys | Para_Power_Limit_SigLoss | Para_Power_Limit_SigLossHys | Para_Power_Limit_SigOverload | Para_Power_Limit_SigOverloadHys | Para_Power_Limit_SigTrip | Para_Power_Limit_SwitchCosPhi | Para_Power_Limit_SwitchCosPhiHys | Para_Power_Nominal_Power1 | Para_Power_Nominal_Power2 | Para_Power_Nominal_Power3 | Para_Power_Nominal_Power4 | Para_Power_Nominal_PowerMin | Para_Power_Ramp_DownG1 | Para_Power_Ramp_DownG2 | Para_Power_Ramp_DownG3 | Para_Power_Ramp_DownG4 | Para_Power_Ramp_UpG1 | Para_Power_Ramp_UpG2 | Para_Power_Ramp_UpG3 | Para_Power_Ramp_UpG4 | Para_Power_RedChargeTemp_Active | Para_Power_RedChargeTemp_Fix | Para_Power_RedCoolWatTemp_Rate | Para_Power_RedCoolWatTemp_Start | Para_Power_RedGenerator_ActPowRedFreq | Para_Power_RedGenerator_ActPowRedVolt | Para_Power_RedGenerator_FreqHighStart | Para_Power_RedGenerator_FreqHighStop | Para_Power_RedGenerator_FreqLowStart | Para_Power_RedGenerator_FreqLowStop | Para_Power_RedGenerator_FreqReturn | Para_Power_RedGenerator_PowerMinFreqHigh | Para_Power_RedGenerator_PowerMinFreqLow | Para_Power_RedGenerator_PowerMinVoltHigh | Para_Power_RedGenerator_PowerMinVoltLow | Para_Power_RedGenerator_TempPowRed | Para_Power_RedGenerator_VoltHighStart | Para_Power_RedGenerator_VoltHighStop | Para_Power_RedGenerator_VoltLowStart | Para_Power_RedGenerator_VoltLowStop | Para_Power_RedGenerator_WindTempHighStart | Para_Power_RedHumidity_ActPred | Para_Power_RedHumidity_PRedLimit | Para_Power_RedOilTemp_Rate | Para_Power_RedOilTemp_Start | Para_Power_RedPreChambGasTrain_ActPowerRed | Para_Power_RedPreChambGasTrain_Rate | Para_Power_RedPreChambGasTrain_Start | Para_Power_RedRetWat_PowRedActive | Para_Power_RedRetWat_Rate | Para_Power_RedRetWat_Start | Para_Power_RedUtility_Step1 | Para_Power_RedUtility_Step2 | Para_Power_TCSpeedRed_RedValue | Para_Power_TMixRed_DeltaPG1 | Para_Power_TMixRed_DeltaPG2 | Para_Power_TMixRed_DeltaPG3 | Para_Power_TMixRed_DeltaPG4 | Para_Power_TMixRed_TempRedG1 | Para_Power_TMixRed_TempRedG2 | Para_Power_TMixRed_TempRedG3 | Para_Power_TMixRed_TempRedG4 | Para_Reserve_Analog_Active1 | Para_Reserve_Analog_Active10 | Para_Reserve_Analog_Active11 | Para_Reserve_Analog_Active12 | Para_Reserve_Analog_Active13 | Para_Reserve_Analog_Active14 | Para_Reserve_Analog_Active15 | Para_Reserve_Analog_Active16 | Para_Reserve_Analog_Active2 | Para_Reserve_Analog_Active3 | Para_Reserve_Analog_Active4 | Para_Reserve_Analog_Active5 | Para_Reserve_Analog_Active6 | Para_Reserve_Analog_Active7 | Para_Reserve_Analog_Active8 | Para_Reserve_Analog_Active9 | Para_Reserve_Analog_LiveZero1 | Para_Reserve_Analog_LiveZero10 | Para_Reserve_Analog_LiveZero11 | Para_Reserve_Analog_LiveZero12 | Para_Reserve_Analog_LiveZero13 | Para_Reserve_Analog_LiveZero14 | Para_Reserve_Analog_LiveZero15 | Para_Reserve_Analog_LiveZero16 | Para_Reserve_Analog_LiveZero2 | Para_Reserve_Analog_LiveZero3 | Para_Reserve_Analog_LiveZero4 | Para_Reserve_Analog_LiveZero5 | Para_Reserve_Analog_LiveZero6 | Para_Reserve_Analog_LiveZero7 | Para_Reserve_Analog_LiveZero8 | Para_Reserve_Analog_LiveZero9 | Para_Reserve_Analog_ScaleBegin1 | Para_Reserve_Analog_ScaleBegin10 | Para_Reserve_Analog_ScaleBegin11 | Para_Reserve_Analog_ScaleBegin12 | Para_Reserve_Analog_ScaleBegin13 | Para_Reserve_Analog_ScaleBegin14 | Para_Reserve_Analog_ScaleBegin15 | Para_Reserve_Analog_ScaleBegin16 | Para_Reserve_Analog_ScaleBegin2 | Para_Reserve_Analog_ScaleBegin3 | Para_Reserve_Analog_ScaleBegin4 | Para_Reserve_Analog_ScaleBegin5 | Para_Reserve_Analog_ScaleBegin6 | Para_Reserve_Analog_ScaleBegin7 | Para_Reserve_Analog_ScaleBegin8 | Para_Reserve_Analog_ScaleBegin9 | Para_Reserve_Analog_ScaleEnd1 | Para_Reserve_Analog_ScaleEnd10 | Para_Reserve_Analog_ScaleEnd11 | Para_Reserve_Analog_ScaleEnd12 | Para_Reserve_Analog_ScaleEnd13 | Para_Reserve_Analog_ScaleEnd14 | Para_Reserve_Analog_ScaleEnd15 | Para_Reserve_Analog_ScaleEnd16 | Para_Reserve_Analog_ScaleEnd2 | Para_Reserve_Analog_ScaleEnd3 | Para_Reserve_Analog_ScaleEnd4 | Para_Reserve_Analog_ScaleEnd5 | Para_Reserve_Analog_ScaleEnd6 | Para_Reserve_Analog_ScaleEnd7 | Para_Reserve_Analog_ScaleEnd8 | Para_Reserve_Analog_ScaleEnd9 | Para_Reserve_Para2_Par031 | Para_Reserve_Para2_Par032 | Para_Reserve_Para2_Par033 | Para_Reserve_Para2_Par034 | Para_Reserve_Para2_Par035 | Para_Reserve_Para2_Par036 | Para_Reserve_Para2_Par037 | Para_Reserve_Para2_Par038 | Para_Reserve_Para2_Par039 | Para_Reserve_Para2_Par040 | Para_Reserve_Para2_Par041 | Para_Reserve_Para2_Par042 | Para_Reserve_Para2_Par043 | Para_Reserve_Para2_Par044 | Para_Reserve_Para2_Par045 | Para_Reserve_Para2_Par046 | Para_Reserve_Para2_Par047 | Para_Reserve_Para2_Par048 | Para_Reserve_Para2_Par049 | Para_Reserve_Para2_Par050 | Para_Reserve_Para2_Par051 | Para_Reserve_Para2_Par052 | Para_Reserve_Para2_Par053 | Para_Reserve_Para2_Par054 | Para_Reserve_Para2_Par055 | Para_Reserve_Para2_Par056 | Para_Reserve_Para2_Par057 | Para_Reserve_Para2_Par058 | Para_Reserve_Para2_Par059 | Para_Reserve_Para2_Par060 | Para_Reserve_Para2_ParaName031 | Para_Reserve_Para2_ParaName032 | Para_Reserve_Para2_ParaName033 | Para_Reserve_Para2_ParaName034 | Para_Reserve_Para2_ParaName035 | Para_Reserve_Para2_ParaName036 | Para_Reserve_Para2_ParaName037 | Para_Reserve_Para2_ParaName038 | Para_Reserve_Para2_ParaName039 | Para_Reserve_Para2_ParaName040 | Para_Reserve_Para2_ParaName041 | Para_Reserve_Para2_ParaName042 | Para_Reserve_Para2_ParaName043 | Para_Reserve_Para2_ParaName044 | Para_Reserve_Para2_ParaName045 | Para_Reserve_Para2_ParaName046 | Para_Reserve_Para2_ParaName047 | Para_Reserve_Para2_ParaName048 | Para_Reserve_Para2_ParaName049 | Para_Reserve_Para2_ParaName050 | Para_Reserve_Para2_ParaName051 | Para_Reserve_Para2_ParaName052 | Para_Reserve_Para2_ParaName053 | Para_Reserve_Para2_ParaName054 | Para_Reserve_Para2_ParaName055 | Para_Reserve_Para2_ParaName056 | Para_Reserve_Para2_ParaName057 | Para_Reserve_Para2_ParaName058 | Para_Reserve_Para2_ParaName059 | Para_Reserve_Para2_ParaName060 | Para_Reserve_Para2_ParaNameF031 | Para_Reserve_Para2_ParaNameF032 | Para_Reserve_Para2_ParaNameF033 | Para_Reserve_Para2_ParaNameF034 | Para_Reserve_Para2_ParaNameF035 | Para_Reserve_Para2_ParaNameF036 | Para_Reserve_Para2_ParaNameF037 | Para_Reserve_Para2_ParaNameF038 | Para_Reserve_Para2_ParaNameF039 | Para_Reserve_Para2_ParaNameF040 | Para_Reserve_Para2_ParaNameF041 | Para_Reserve_Para2_ParaNameF042 | Para_Reserve_Para2_ParaNameF043 | Para_Reserve_Para2_ParaNameF044 | Para_Reserve_Para2_ParaNameF045 | Para_Reserve_Para2_ParaNameF046 | Para_Reserve_Para2_ParaNameF047 | Para_Reserve_Para2_ParaNameF048 | Para_Reserve_Para2_ParaNameF049 | Para_Reserve_Para2_ParaNameF050 | Para_Reserve_Para2_ParaNameF051 | Para_Reserve_Para2_ParaNameF052 | Para_Reserve_Para2_ParaNameF053 | Para_Reserve_Para2_ParaNameF054 | Para_Reserve_Para2_ParaNameF055 | Para_Reserve_Para2_ParaNameF056 | Para_Reserve_Para2_ParaNameF057 | Para_Reserve_Para2_ParaNameF058 | Para_Reserve_Para2_ParaNameF059 | Para_Reserve_Para2_ParaNameF060 | Para_Reserve_Para2_ParaUnit031 | Para_Reserve_Para2_ParaUnit032 | Para_Reserve_Para2_ParaUnit033 | Para_Reserve_Para2_ParaUnit034 | Para_Reserve_Para2_ParaUnit035 | Para_Reserve_Para2_ParaUnit036 | Para_Reserve_Para2_ParaUnit037 | Para_Reserve_Para2_ParaUnit038 | Para_Reserve_Para2_ParaUnit039 | Para_Reserve_Para2_ParaUnit040 | Para_Reserve_Para2_ParaUnit041 | Para_Reserve_Para2_ParaUnit042 | Para_Reserve_Para2_ParaUnit043 | Para_Reserve_Para2_ParaUnit044 | Para_Reserve_Para2_ParaUnit045 | Para_Reserve_Para2_ParaUnit046 | Para_Reserve_Para2_ParaUnit047 | Para_Reserve_Para2_ParaUnit048 | Para_Reserve_Para2_ParaUnit049 | Para_Reserve_Para2_ParaUnit050 | Para_Reserve_Para2_ParaUnit051 | Para_Reserve_Para2_ParaUnit052 | Para_Reserve_Para2_ParaUnit053 | Para_Reserve_Para2_ParaUnit054 | Para_Reserve_Para2_ParaUnit055 | Para_Reserve_Para2_ParaUnit056 | Para_Reserve_Para2_ParaUnit057 | Para_Reserve_Para2_ParaUnit058 | Para_Reserve_Para2_ParaUnit059 | Para_Reserve_Para2_ParaUnit060 | Para_Reserve_Para3_Par061 | Para_Reserve_Para3_Par062 | Para_Reserve_Para3_Par063 | Para_Reserve_Para3_Par064 | Para_Reserve_Para3_Par065 | Para_Reserve_Para3_Par066 | Para_Reserve_Para3_Par067 | Para_Reserve_Para3_Par068 | Para_Reserve_Para3_Par069 | Para_Reserve_Para3_Par070 | Para_Reserve_Para3_ParaName061 | Para_Reserve_Para3_ParaName062 | Para_Reserve_Para3_ParaName063 | Para_Reserve_Para3_ParaName064 | Para_Reserve_Para3_ParaName065 | Para_Reserve_Para3_ParaName066 | Para_Reserve_Para3_ParaName067 | Para_Reserve_Para3_ParaName068 | Para_Reserve_Para3_ParaName069 | Para_Reserve_Para3_ParaName070 | Para_Reserve_Para3_ParaNameF061 | Para_Reserve_Para3_ParaNameF062 | Para_Reserve_Para3_ParaNameF063 | Para_Reserve_Para3_ParaNameF064 | Para_Reserve_Para3_ParaNameF065 | Para_Reserve_Para3_ParaNameF066 | Para_Reserve_Para3_ParaNameF067 | Para_Reserve_Para3_ParaNameF068 | Para_Reserve_Para3_ParaNameF069 | Para_Reserve_Para3_ParaNameF070 | Para_Reserve_Para3_ParaUnit061 | Para_Reserve_Para3_ParaUnit062 | Para_Reserve_Para3_ParaUnit063 | Para_Reserve_Para3_ParaUnit064 | Para_Reserve_Para3_ParaUnit065 | Para_Reserve_Para3_ParaUnit066 | Para_Reserve_Para3_ParaUnit067 | Para_Reserve_Para3_ParaUnit068 | Para_Reserve_Para3_ParaUnit069 | Para_Reserve_Para3_ParaUnit070 | Para_Reserve_Para_Par001 | Para_Reserve_Para_Par002 | Para_Reserve_Para_Par003 | Para_Reserve_Para_Par004 | Para_Reserve_Para_Par005 | Para_Reserve_Para_Par006 | Para_Reserve_Para_Par007 | Para_Reserve_Para_Par008 | Para_Reserve_Para_Par009 | Para_Reserve_Para_Par010 | Para_Reserve_Para_Par011 | Para_Reserve_Para_Par012 | Para_Reserve_Para_Par013 | Para_Reserve_Para_Par014 | Para_Reserve_Para_Par015 | Para_Reserve_Para_Par016 | Para_Reserve_Para_Par017 | Para_Reserve_Para_Par018 | Para_Reserve_Para_Par019 | Para_Reserve_Para_Par020 | Para_Reserve_Para_Par021 | Para_Reserve_Para_Par022 | Para_Reserve_Para_Par023 | Para_Reserve_Para_Par024 | Para_Reserve_Para_Par025 | Para_Reserve_Para_Par026 | Para_Reserve_Para_Par027 | Para_Reserve_Para_Par028 | Para_Reserve_Para_Par029 | Para_Reserve_Para_Par030 | Para_Reserve_Para_ParaName001 | Para_Reserve_Para_ParaName002 | Para_Reserve_Para_ParaName003 | Para_Reserve_Para_ParaName004 | Para_Reserve_Para_ParaName005 | Para_Reserve_Para_ParaName006 | Para_Reserve_Para_ParaName007 | Para_Reserve_Para_ParaName008 | Para_Reserve_Para_ParaName009 | Para_Reserve_Para_ParaName010 | Para_Reserve_Para_ParaName011 | Para_Reserve_Para_ParaName012 | Para_Reserve_Para_ParaName013 | Para_Reserve_Para_ParaName014 | Para_Reserve_Para_ParaName015 | Para_Reserve_Para_ParaName016 | Para_Reserve_Para_ParaName017 | Para_Reserve_Para_ParaName018 | Para_Reserve_Para_ParaName019 | Para_Reserve_Para_ParaName020 | Para_Reserve_Para_ParaName021 | Para_Reserve_Para_ParaName022 | Para_Reserve_Para_ParaName023 | Para_Reserve_Para_ParaName024 | Para_Reserve_Para_ParaName025 | Para_Reserve_Para_ParaName026 | Para_Reserve_Para_ParaName027 | Para_Reserve_Para_ParaName028 | Para_Reserve_Para_ParaName029 | Para_Reserve_Para_ParaName030 | Para_Reserve_Para_ParaNameF001 | Para_Reserve_Para_ParaNameF002 | Para_Reserve_Para_ParaNameF003 | Para_Reserve_Para_ParaNameF004 | Para_Reserve_Para_ParaNameF005 | Para_Reserve_Para_ParaNameF006 | Para_Reserve_Para_ParaNameF007 | Para_Reserve_Para_ParaNameF008 | Para_Reserve_Para_ParaNameF009 | Para_Reserve_Para_ParaNameF010 | Para_Reserve_Para_ParaNameF011 | Para_Reserve_Para_ParaNameF012 | Para_Reserve_Para_ParaNameF013 | Para_Reserve_Para_ParaNameF014 | Para_Reserve_Para_ParaNameF015 | Para_Reserve_Para_ParaNameF016 | Para_Reserve_Para_ParaNameF017 | Para_Reserve_Para_ParaNameF018 | Para_Reserve_Para_ParaNameF019 | Para_Reserve_Para_ParaNameF020 | Para_Reserve_Para_ParaNameF021 | Para_Reserve_Para_ParaNameF022 | Para_Reserve_Para_ParaNameF023 | Para_Reserve_Para_ParaNameF024 | Para_Reserve_Para_ParaNameF025 | Para_Reserve_Para_ParaNameF026 | Para_Reserve_Para_ParaNameF027 | Para_Reserve_Para_ParaNameF028 | Para_Reserve_Para_ParaNameF029 | Para_Reserve_Para_ParaNameF030 | Para_Reserve_Para_ParaUnit001 | Para_Reserve_Para_ParaUnit002 | Para_Reserve_Para_ParaUnit003 | Para_Reserve_Para_ParaUnit004 | Para_Reserve_Para_ParaUnit005 | Para_Reserve_Para_ParaUnit006 | Para_Reserve_Para_ParaUnit007 | Para_Reserve_Para_ParaUnit008 | Para_Reserve_Para_ParaUnit009 | Para_Reserve_Para_ParaUnit010 | Para_Reserve_Para_ParaUnit011 | Para_Reserve_Para_ParaUnit012 | Para_Reserve_Para_ParaUnit013 | Para_Reserve_Para_ParaUnit014 | Para_Reserve_Para_ParaUnit015 | Para_Reserve_Para_ParaUnit016 | Para_Reserve_Para_ParaUnit017 | Para_Reserve_Para_ParaUnit018 | Para_Reserve_Para_ParaUnit019 | Para_Reserve_Para_ParaUnit020 | Para_Reserve_Para_ParaUnit021 | Para_Reserve_Para_ParaUnit022 | Para_Reserve_Para_ParaUnit023 | Para_Reserve_Para_ParaUnit024 | Para_Reserve_Para_ParaUnit025 | Para_Reserve_Para_ParaUnit026 | Para_Reserve_Para_ParaUnit027 | Para_Reserve_Para_ParaUnit028 | Para_Reserve_Para_ParaUnit029 | Para_Reserve_Para_ParaUnit030 | Para_SAFI_ActExhTemp | Para_SAFI_ActHighVolt | Para_SAFI_ActIgn | Para_SAFI_ActITPTolCheck | Para_SAFI_ActKnock | Para_SAFI_ActOCA | Para_SAFI_ActPBC | Para_SAFI_ActPI | Para_SAFI_ITPTol | Para_SAFI_ResetPos | Para_SpecGas_ActBackfireIMEP_P | Para_SpecGas_ActScavN2 | Para_SpecGas_BlockEngineRun | Para_SpecGas_CalValue_ActGas1_2 | Para_SpecGas_CalValue_ActMeasure | Para_SpecGas_CalValue_ActMinAlarm | Para_SpecGas_CalValue_ActMinSd | Para_SpecGas_CalValue_ActPowerRed | Para_SpecGas_CalValue_ContentGas1 | Para_SpecGas_CalValue_ContentGas2 | Para_SpecGas_CalValue_DefaultValGas1_2 | Para_SpecGas_CalValue_HalfLoad | Para_SpecGas_CalValue_HysMinAlarm | Para_SpecGas_CalValue_HysMinSD | Para_SpecGas_CalValue_LimitMinSd | Para_SpecGas_CalValue_Range20mA | Para_SpecGas_CalValue_Range4mA | Para_SpecGas_CalValue_StartPRed | Para_SpecGas_CalValue_SwitchPointMinAlarm | Para_SpecGas_CH4_ActGas1_2 | Para_SpecGas_CH4_ActMeasure | Para_SpecGas_CH4_ActMinAlarm | Para_SpecGas_CH4_ActMinSd | Para_SpecGas_CH4_ActPowerRed | Para_SpecGas_CH4_ContentGas1 | Para_SpecGas_CH4_ContentGas2 | Para_SpecGas_CH4_DefaultValGas1_2 | Para_SpecGas_CH4_HalfLoad | Para_SpecGas_CH4_HysMinAlarm | Para_SpecGas_CH4_HysMinSD | Para_SpecGas_CH4_LimitMinSd | Para_SpecGas_CH4_Range20mA | Para_SpecGas_CH4_Range4mA | Para_SpecGas_CH4_StartPRed | Para_SpecGas_CH4_SwitchPointMinAlarm | Para_SpecGas_GasPress_ActMaxAlarm | Para_SpecGas_GasPress_ActMeasure | Para_SpecGas_GasPress_ActMinAlarm | Para_SpecGas_GasPress_ActPowerRed | Para_SpecGas_GasPress_EndPRed | Para_SpecGas_GasPress_HysMaxAlarm | Para_SpecGas_GasPress_HysMinAlarm | Para_SpecGas_GasPress_LimitMaxAlarm | Para_SpecGas_GasPress_LimitMinAlarm | Para_SpecGas_GasPress_LimitMinAlarmDelay | Para_SpecGas_GasPress_Range20mA | Para_SpecGas_GasPress_Range4mA | Para_SpecGas_GasPress_StartPRed | Para_SpecGas_GasTemp_ActMeasure | Para_SpecGas_GasTemp_HysMax | Para_SpecGas_GasTemp_HysMin | Para_SpecGas_GasTemp_LimitMax | Para_SpecGas_GasTemp_LimitMin | Para_SpecGas_GasTemp_Range20mA | Para_SpecGas_GasTemp_Range4mA | Para_SpecGas_GasVol_ActMeasure | Para_SpecGas_GasVol_Range20mA | Para_SpecGas_GasVol_Range4mA | Para_SpecGas_GlowIgn_ActPredIPRedPBC | Para_SpecGas_GlowIgn_EmergShut_ActEmergShut | Para_SpecGas_GlowIgn_EmergShut_ActEmergShutPBC | Para_SpecGas_GlowIgn_EmergShut_BlockTimeNumbMax | Para_SpecGas_GlowIgn_EmergShut_CloseTimeGasValve | Para_SpecGas_GlowIgn_EmergShut_LimitContent | Para_SpecGas_GlowIgn_EmergShut_LimitDeltaCylTemp | Para_SpecGas_GlowIgn_EmergShut_LimitDevCylTempAvg | Para_SpecGas_GlowIgn_EmergShut_NumbMax | Para_SpecGas_GlowIgn_EmergShut_NumbMax30s | Para_SpecGas_GlowIgn_EmergShut_PowerActTempMon | Para_SpecGas_GlowIgn_EmergShut_SelfReset | Para_SpecGas_GlowIgn_EmergShut_TimeDurMonDeact | Para_SpecGas_GlowIgn_EmergShut_TimeNumbMax | Para_SpecGas_GlowIgn_EmergShut_TrPos | Para_SpecGas_GlowIgn_EmergShut_TrPosTimeDur | Para_SpecGas_GlowIgn_FastPowerRed_ActFastPowerRed | Para_SpecGas_GlowIgn_FastPowerRed_ActFastPowerRedPBC | Para_SpecGas_GlowIgn_FastPowerRed_Limitp2s | Para_SpecGas_GlowIgn_FastPowerRed_MaxNumb | Para_SpecGas_GlowIgn_FastPowerRed_PowerActive | Para_SpecGas_GlowIgn_FastPowerRed_PowerDiff | Para_SpecGas_GlowIgn_FastPowerRed_PowerSave | Para_SpecGas_GlowIgn_FastPowerRed_PowerSaveDur | Para_SpecGas_GlowIgn_FastPowerRed_TimeDiff | Para_SpecGas_GlowIgn_FastPowerRed_TimeDur | Para_SpecGas_GlowIgn_FastPowerRed_TrPos | Para_SpecGas_GlowIgn_ITPstep | Para_SpecGas_GlowIgn_LambdaOffset | Para_SpecGas_GlowIgnPrevent | Para_SpecGas_O2_ActMeasure | Para_SpecGas_O2_ActShutdownMax | Para_SpecGas_O2_HysMaxSd | Para_SpecGas_O2_LimitMaxSd | Para_SpecGas_O2_Range20mA | Para_SpecGas_O2_Range4mA | Para_SpecGas_SucPress_ActMeasure | Para_SpecGas_SucPress_ActPowerRed | Para_SpecGas_SucPress_EndPRed | Para_SpecGas_SucPress_HysMaxAlarm | Para_SpecGas_SucPress_HysMinAlarm | Para_SpecGas_SucPress_LimitMaxAlarm | Para_SpecGas_SucPress_LimitMinAlarm | Para_SpecGas_SucPress_Range20mA | Para_SpecGas_SucPress_Range4mA | Para_SpecGas_SucPress_StartPRed | Para_SpecGas_TwoIgnition | Para_SpecGas_TwoN2Valves | Para_Speed_Ctr_Active | Para_Speed_Ctr_ActStartCompBypassOpen | Para_Speed_Ctr_TrDComp | Para_Speed_Ctr_TrIComp | Para_Speed_Ctr_TrPComp | Para_Speed_Ctr_TrYMax | Para_Speed_Ctr_TrYMin | Para_Speed_ExtSet_Curr1 | Para_Speed_ExtSet_Curr2 | Para_Speed_ExtSet_Point1 | Para_Speed_ExtSet_Point2 | Para_Speed_Limit_Gr1495 | Para_Speed_Limit_Gr1495Hys | Para_Speed_Limit_Limit1 | Para_Speed_Limit_Limit1Hys | Para_Speed_Limit_OverSpeed | Para_Speed_Limit_OverSpeedHys | Para_Speed_Limit_RunUp | Para_Speed_Limit_RunUpHys | Para_Speed_Limit_Sm1505 | Para_Speed_Limit_Sm1505Hys | Para_Speed_Limit_Start | Para_Speed_Limit_StartHys | Para_Speed_Limit_StartSpeedMon | Para_Speed_Limit_StartSpeedMonHys | Para_Speed_Nominal | Para_Speed_Ramp_Ramp | Para_System_HA_Pt100InputFilter | Para_System_IPC_T_IPC_Board_LimHi | Para_System_IPC_T_IPC_CFast_LimHi | Para_System_IPC_T_IPC_Chipset_LimHi | Para_System_IPC_T_IPC_CPU_LimHi | Para_System_IPC_T_IPC_PS_LimHi | Para_Tecjet_Gas1_AirDemandMin | Para_Tecjet_Gas1_CalorificValue | Para_Tecjet_Gas1_StandGasDens | Para_Tecjet_Gas1_TecJetOffsetIsland | Para_Tecjet_Gas1_TecJetOffsetNet | Para_Tecjet_Gas1_TecJetPoint1 | Para_Tecjet_Gas1_TecJetPoint2 | Para_Tecjet_Gas1_TempOilPoint1 | Para_Tecjet_Gas1_TempOilPoint2 | Para_Tecjet_Gas2_AirDemandMin | Para_Tecjet_Gas2_CalorificValue | Para_Tecjet_Gas2_StandGasDens | Para_Tecjet_Gas2_TecJetOffsetIsland | Para_Tecjet_Gas2_TecJetOffsetNet | Para_Tecjet_Gas2_TecJetPoint1 | Para_Tecjet_Gas2_TecJetPoint2 | Para_Tecjet_Gas2_TempOilPoint1 | Para_Tecjet_Gas2_TempOilPoint2 | Para_Tecjet_Gas3_AirDemandMin | Para_Tecjet_Gas3_CalorificValue | Para_Tecjet_Gas3_StandGasDens | Para_Tecjet_Gas3_TecJetOffsetIsland | Para_Tecjet_Gas3_TecJetOffsetNet | Para_Tecjet_Gas3_TecJetPoint1 | Para_Tecjet_Gas3_TecJetPoint2 | Para_Tecjet_Gas3_TempOilPoint1 | Para_Tecjet_Gas3_TempOilPoint2 | Para_Tecjet_Gas4_AirDemandMin | Para_Tecjet_Gas4_CalorificValue | Para_Tecjet_Gas4_StandGasDens | Para_Tecjet_Gas4_TecJetOffsetIsland | Para_Tecjet_Gas4_TecJetOffsetNet | Para_Tecjet_Gas4_TecJetPoint1 | Para_Tecjet_Gas4_TecJetPoint2 | Para_Tecjet_Gas4_TempOilPoint1 | Para_Tecjet_Gas4_TempOilPoint2 | Para_Tecjet_IdleLambdaCtr_Delay1 | Para_Tecjet_IdleLambdaCtr_Delay2 | Para_Tecjet_IdleLambdaCtr_Gas1_TecJetDP | Para_Tecjet_IdleLambdaCtr_Gas1_TrPos | Para_Tecjet_IdleLambdaCtr_Gas2_TecJetDP | Para_Tecjet_IdleLambdaCtr_Gas2_TrPos | Para_Tecjet_IdleLambdaCtr_Gas3_TecJetDP | Para_Tecjet_IdleLambdaCtr_Gas3_TrPos | Para_Tecjet_IdleLambdaCtr_Gas4_TecJetDP | Para_Tecjet_IdleLambdaCtr_Gas4_TrPos | Para_Tecjet_IdleLambdaCtr_IComp | Para_Tecjet_IdleLambdaCtr_PComp | Para_Tecjet_LambdaAdapStartup_LambdaOffsetX2 | Para_Tecjet_LambdaAdapStartup_LambdaOffsetX3 | Para_Tecjet_LambdaAdapStartup_LambdaOffsetY1 | Para_Tecjet_LambdaAdapStartup_LambdaOffsetY2 | Para_Tecjet_LambdaAdapStartup_LambdaStartMin | Para_Tecjet_TempOilMax | Para_Tecjet_TempOilMin | Para_Tecjet_VolumEffic | Para_UniversalIO_Ana_InFirst | Para_UniversalIO_Ana_InLast | Para_UniversalIO_Ana_OutFirst | Para_UniversalIO_Ana_OutLast | Para_UniversalIO_Dig_CntFirst | Para_UniversalIO_Dig_CntLast | Para_UniversalIO_Dig_FlagFirst | Para_UniversalIO_Dig_FlagLast | Para_UniversalIO_Dig_InFirst | Para_UniversalIO_Dig_InLast | Para_UniversalIO_Dig_OutFirst | Para_UniversalIO_Dig_OutLast | Para_Visu_ActRemoteRequest | Para_Visu_Aux_ActAirInLou1 | Para_Visu_Aux_ActAirInLou2 | Para_Visu_Aux_ActAirInVent1 | Para_Visu_Aux_ActAirInVent2 | Para_Visu_Aux_ActAirInVentF | Para_Visu_Aux_ActAirOutLou | Para_Visu_Aux_ActCoolRadStage1 | Para_Visu_Aux_ActCoolRadStage2 | Para_Visu_Aux_ActCoolRadStageX | Para_Visu_Aux_ActExhGasValveBypass | Para_Visu_Aux_ActExhGasValveHeatEx | Para_Visu_Aux_ActMixCoolRadStageX | Para_Visu_Aux_ActPreHeat | Para_Visu_Aux_ActPreHeatWatPump | Para_Visu_Counter_MaintCountName1 | Para_Visu_Counter_MaintCountName1_uc_NEx | Para_Visu_Counter_MaintCountName2 | Para_Visu_Counter_MaintCountName2_uc_NEx | Para_Visu_Counter_MaintCountName3 | Para_Visu_Counter_MaintCountName3_uc_NEx | Para_Visu_Counter_MaintCountName4 | Para_Visu_Counter_MaintCountName4_uc_NEx | Para_Visu_Counter_MaintCountNameF1 | Para_Visu_Counter_MaintCountNameF1_uc_NEx | Para_Visu_Counter_MaintCountNameF2 | Para_Visu_Counter_MaintCountNameF2_uc_NEx | Para_Visu_Counter_MaintCountNameF3 | Para_Visu_Counter_MaintCountNameF3_uc_NEx | Para_Visu_Counter_MaintCountNameF4 | Para_Visu_Counter_MaintCountNameF4_uc_NEx | Para_Visu_Counter_ResCountName1 | Para_Visu_Counter_ResCountName2 | Para_Visu_Counter_ResCountName3 | Para_Visu_Counter_ResCountName4 | Para_Visu_Counter_ResCountNameF1 | Para_Visu_Counter_ResCountNameF2 | Para_Visu_Counter_ResCountNameF3 | Para_Visu_Counter_ResCountNameF4 | Para_Visu_Counter_ResCountUnit1 | Para_Visu_Counter_ResCountUnit2 | Para_Visu_Counter_ResCountUnit3 | Para_Visu_Counter_ResCountUnit4 | Para_Visu_Ele_ActGenNetPath | Para_Visu_Ele_ActNetOK_NEx | Para_Visu_Ele_ActTrGenDown | Para_Visu_Ele_ActTrGenUp | Para_Visu_Ele_ActTrNetDown | Para_Visu_Ele_ActTrNetUp | Para_Visu_Hyd_ActCoolWaterCircuit | Para_Visu_Hyd_ActDeskCooler | Para_Visu_Hyd_ActExtHeating | Para_Visu_Hyd_ActIntHeating | Para_Visu_Hyd_ActOil2Stage | Para_Visu_Hyd_ActOilPreLubPumpAC | Para_Visu_Hyd_ActOilPreLubPumpDC | Para_Visu_Hyd_ActTC | Para_Visu_UserLevelAck | PBC_HeatChar10_Cyl01 | PBC_HeatChar10_Cyl02 | PBC_HeatChar10_Cyl03 | PBC_HeatChar10_Cyl04 | PBC_HeatChar10_Cyl05 | PBC_HeatChar10_Cyl06 | PBC_HeatChar10_Cyl07 | PBC_HeatChar10_Cyl08 | PBC_HeatChar10_Cyl09 | PBC_HeatChar10_Cyl10 | PBC_HeatChar10_Cyl11 | PBC_HeatChar10_Cyl12 | PBC_HeatChar10_Cyl13 | PBC_HeatChar10_Cyl14 | PBC_HeatChar10_Cyl15 | PBC_HeatChar10_Cyl16 | PBC_HeatChar10_Cyl17 | PBC_HeatChar10_Cyl18 | PBC_HeatChar10_Cyl19 | PBC_HeatChar10_Cyl20 | PBC_HeatChar10_Cyl21 | PBC_HeatChar10_Cyl22 | PBC_HeatChar10_Cyl23 | PBC_HeatChar10_Cyl24 | PBC_HeatChar90_Cyl01 | PBC_HeatChar90_Cyl02 | PBC_HeatChar90_Cyl03 | PBC_HeatChar90_Cyl04 | PBC_HeatChar90_Cyl05 | PBC_HeatChar90_Cyl06 | PBC_HeatChar90_Cyl07 | PBC_HeatChar90_Cyl08 | PBC_HeatChar90_Cyl09 | PBC_HeatChar90_Cyl10 | PBC_HeatChar90_Cyl11 | PBC_HeatChar90_Cyl12 | PBC_HeatChar90_Cyl13 | PBC_HeatChar90_Cyl14 | PBC_HeatChar90_Cyl15 | PBC_HeatChar90_Cyl16 | PBC_HeatChar90_Cyl17 | PBC_HeatChar90_Cyl18 | PBC_HeatChar90_Cyl19 | PBC_HeatChar90_Cyl20 | PBC_HeatChar90_Cyl21 | PBC_HeatChar90_Cyl22 | PBC_HeatChar90_Cyl23 | PBC_HeatChar90_Cyl24 | PBC_HeatCharVar_Avg | PBC_HeatCharVar_Cyl01 | PBC_HeatCharVar_Cyl02 | PBC_HeatCharVar_Cyl03 | PBC_HeatCharVar_Cyl04 | PBC_HeatCharVar_Cyl05 | PBC_HeatCharVar_Cyl06 | PBC_HeatCharVar_Cyl07 | PBC_HeatCharVar_Cyl08 | PBC_HeatCharVar_Cyl09 | PBC_HeatCharVar_Cyl10 | PBC_HeatCharVar_Cyl11 | PBC_HeatCharVar_Cyl12 | PBC_HeatCharVar_Cyl13 | PBC_HeatCharVar_Cyl14 | PBC_HeatCharVar_Cyl15 | PBC_HeatCharVar_Cyl16 | PBC_HeatCharVar_Cyl17 | PBC_HeatCharVar_Cyl18 | PBC_HeatCharVar_Cyl19 | PBC_HeatCharVar_Cyl20 | PBC_HeatCharVar_Cyl21 | PBC_HeatCharVar_Cyl22 | PBC_HeatCharVar_Cyl23 | PBC_HeatCharVar_Cyl24 | PBC_HeatCharVar_Max | PBC_HeatCharVar_Min | PBC_Press49bfTDC_Avg | PBC_Press49bfTDC_Cyl01 | PBC_Press49bfTDC_Cyl02 | PBC_Press49bfTDC_Cyl03 | PBC_Press49bfTDC_Cyl04 | PBC_Press49bfTDC_Cyl05 | PBC_Press49bfTDC_Cyl06 | PBC_Press49bfTDC_Cyl07 | PBC_Press49bfTDC_Cyl08 | PBC_Press49bfTDC_Cyl09 | PBC_Press49bfTDC_Cyl10 | PBC_Press49bfTDC_Cyl11 | PBC_Press49bfTDC_Cyl12 | PBC_Press49bfTDC_Cyl13 | PBC_Press49bfTDC_Cyl14 | PBC_Press49bfTDC_Cyl15 | PBC_Press49bfTDC_Cyl16 | PBC_Press49bfTDC_Cyl17 | PBC_Press49bfTDC_Cyl18 | PBC_Press49bfTDC_Cyl19 | PBC_Press49bfTDC_Cyl20 | PBC_Press49bfTDC_Cyl21 | PBC_Press49bfTDC_Cyl22 | PBC_Press49bfTDC_Cyl23 | PBC_Press49bfTDC_Cyl24 | PBC_Press49bfTDC_Max | PBC_Press49bfTDC_Min | PBC_PressMean_Avg | PBC_PressMean_Cyl01 | PBC_PressMean_Cyl02 | PBC_PressMean_Cyl03 | PBC_PressMean_Cyl04 | PBC_PressMean_Cyl05 | PBC_PressMean_Cyl06 | PBC_PressMean_Cyl07 | PBC_PressMean_Cyl08 | PBC_PressMean_Cyl09 | PBC_PressMean_Cyl10 | PBC_PressMean_Cyl11 | PBC_PressMean_Cyl12 | PBC_PressMean_Cyl13 | PBC_PressMean_Cyl14 | PBC_PressMean_Cyl15 | PBC_PressMean_Cyl16 | PBC_PressMean_Cyl17 | PBC_PressMean_Cyl18 | PBC_PressMean_Cyl19 | PBC_PressMean_Cyl20 | PBC_PressMean_Cyl21 | PBC_PressMean_Cyl22 | PBC_PressMean_Cyl23 | PBC_PressMean_Cyl24 | PBC_PressMean_Max | PBC_PressMean_Min | PI_Commissioning | PI_Duration_Avg | PI_Duration_Cyl01 | PI_Duration_Cyl02 | PI_Duration_Cyl03 | PI_Duration_Cyl04 | PI_Duration_Cyl05 | PI_Duration_Cyl06 | PI_Duration_Cyl07 | PI_Duration_Cyl08 | PI_Duration_Cyl09 | PI_Duration_Cyl10 | PI_Duration_Cyl11 | PI_Duration_Cyl12 | PI_Duration_Cyl13 | PI_Duration_Cyl14 | PI_Duration_Cyl15 | PI_Duration_Cyl16 | PI_Duration_Cyl17 | PI_Duration_Cyl18 | PI_Duration_Cyl19 | PI_Duration_Cyl20 | PI_Duration_Cyl21 | PI_Duration_Cyl22 | PI_Duration_Cyl23 | PI_Duration_Cyl24 | PI_Duration_Max | PI_Duration_Min | PI_Man_Req | PI_Numb_SkipCyl_Act | PI_Required | PI_ResetMap | PI_SteadyState | pole_slipping_counter | Power_PowerAct | Power_PowerActUnfilt | Power_PowerMax | Power_PowerNominal | Power_RedExt | Power_RedExtBus | Power_RedKnock | Power_RedMisfire | Power_RedMixTemp | Power_RedPowerAct | Power_SetPower | Power_SetPowerExtInt | Power_SetPowerUnred | pr_ch_p1hp_a | pr_ch_p1hp_b | pr_egahptc_a | pr_egahptc_b | pr_egalptc_a | pr_egalptc_b | pr_egbhptc_a | pr_egbhptc_b | rE_SinceStart | rHours_SinceStart | RMD_ListAvgCCP_CCPSensor | RMD_ListAvgOilPress_OilPressureLimit | RMD_ListBuffMAvgOilConsume_OilConsumption | RMD_ListBuffMAvgOilDiffPress_OilDiffPress | rP_Ramp_Act | rP_Ramp_Set | rP_Targ_LastStart | rpr_oil_lptc_in_a | rpr_oil_lptc_in_b | rpr_tc_eof_after | rT_ECW_FS_Perm | rT_EGaHPTC | rT_EO_FS_Perm | rt_eo_pan | rTi_Load_0 | rTi_Load_2 | rTi_Prep_0 | rTi_Prep_1 | rTi_Prep_2 | rTi_Speedup_0 | rTi_Speedup_1 | rTi_Speedup_2 | rTi_Start_0 | rTi_Start_1 | rTi_Start_2 | rTi_SumLoad | rTi_SumSync | rTi_Sync_0 | rTi_Sync_1 | rTi_Sync_2 | rTi_Targ | SAFI_Electronic_Temp_Average | safi_valvelashset_1 | safi_valvelashset_10 | safi_valvelashset_11 | safi_valvelashset_12 | safi_valvelashset_13 | safi_valvelashset_14 | safi_valvelashset_15 | safi_valvelashset_16 | safi_valvelashset_17 | safi_valvelashset_18 | safi_valvelashset_19 | safi_valvelashset_2 | safi_valvelashset_20 | safi_valvelashset_21 | safi_valvelashset_22 | safi_valvelashset_23 | safi_valvelashset_24 | safi_valvelashset_3 | safi_valvelashset_4 | safi_valvelashset_5 | safi_valvelashset_6 | safi_valvelashset_7 | safi_valvelashset_8 | safi_valvelashset_9 | safi_win3_1 | safi_win3_10 | safi_win3_11 | safi_win3_12 | safi_win3_13 | safi_win3_14 | safi_win3_15 | safi_win3_16 | safi_win3_17 | safi_win3_18 | safi_win3_19 | safi_win3_2 | safi_win3_20 | safi_win3_21 | safi_win3_22 | safi_win3_23 | safi_win3_24 | safi_win3_3 | safi_win3_4 | safi_win3_5 | safi_win3_6 | safi_win3_7 | safi_win3_8 | safi_win3_9 | safi_win4_1 | safi_win4_10 | safi_win4_11 | safi_win4_12 | safi_win4_13 | safi_win4_14 | safi_win4_15 | safi_win4_16 | safi_win4_17 | safi_win4_18 | safi_win4_19 | safi_win4_2 | safi_win4_20 | safi_win4_21 | safi_win4_22 | safi_win4_23 | safi_win4_24 | safi_win4_3 | safi_win4_4 | safi_win4_5 | safi_win4_6 | safi_win4_7 | safi_win4_8 | safi_win4_9 | SCR_Catalyst_RUL | SendingDataCondition | SendingDataConditionNumeric | SlowDownTime00 | SlowDownTime01 | SlowDownTime02 | SlowDownTime03 | SlowDownTime04 | SlowDownTime05 | SlowDownTime06 | SlowDownTime07 | SlowDownTime08 | SlowDownTime09 | SlowDownTime10 | SlowDownTime11 | SlowDownTime12 | SlowDownTime13 | SlowDownTime14 | SlowDownTime15 | SlowDownTime16 | SlowDownTime17 | SlowDownTime18 | SlowDownTime19 | spark_plug_maintenance_IV01 | spark_plug_maintenance_IV02 | spark_plug_maintenance_IV03 | spark_plug_maintenance_IV04 | spark_plug_maintenance_IV05 | spark_plug_maintenance_IV06 | spark_plug_maintenance_IV07 | spark_plug_maintenance_IV08 | spark_plug_maintenance_IV09 | spark_plug_maintenance_IV10 | spark_plug_maintenance_IV11 | spark_plug_maintenance_IV12 | spark_plug_maintenance_IV13 | spark_plug_maintenance_IV14 | spark_plug_maintenance_IV15 | spark_plug_maintenance_IV16 | spark_plug_maintenance_IV17 | spark_plug_maintenance_IV18 | spark_plug_maintenance_IV19 | spark_plug_maintenance_IV20 | spark_plug_maintenance_IV21 | spark_plug_maintenance_IV22 | spark_plug_maintenance_IV23 | spark_plug_maintenance_IV24 | Spark_Plug_RUL01 | Spark_Plug_RUL02 | Spark_Plug_RUL03 | Spark_Plug_RUL04 | Spark_Plug_RUL05 | Spark_Plug_RUL06 | Spark_Plug_RUL07 | Spark_Plug_RUL08 | Spark_Plug_RUL09 | Spark_Plug_RUL10 | Spark_Plug_RUL11 | Spark_Plug_RUL12 | Spark_Plug_RUL13 | Spark_Plug_RUL14 | Spark_Plug_RUL15 | Spark_Plug_RUL16 | Spark_Plug_RUL17 | Spark_Plug_RUL18 | Spark_Plug_RUL19 | Spark_Plug_RUL20 | Spark_Plug_RUL21 | Spark_Plug_RUL22 | Spark_Plug_RUL23 | Spark_Plug_RUL24 | SPW_calc_starts_per_week | StartsCnt_Statistic | synchronization_bmcb_on | systeminfo_availablememory | systeminfo_cpuutilization | systeminfo_diskwriteperformance | systeminfo_externaldrive_averageerasecount | systeminfo_externaldrive_lifetimepercentage | systeminfo_externaldrive_poweronhours | systeminfo_freediskspace | systeminfo_internaldrive_averageerasecount | systeminfo_internaldrive_lifetimepercentage | systeminfo_internaldrive_poweronhours | systeminfo_systemuptime | t_ch_t1hp_a | t_ch_t1hp_b | t_egahptc_a | t_egahptc_b | t_egbhptc_a | t_egbhptc_b | TC_SurgeEvents | TecJet_GasDiffPress | TecJet_GasDiffPress2 | TecJet_GasDiffPress3 | TecJet_GasDiffPress4 | TecJet_GasFlow1 | TecJet_GasFlow2 | TecJet_GasFlow3 | TecJet_GasFlow4 | TecJet_GasPress1 | TecJet_GasPress2 | TecJet_GasPress3 | TecJet_GasPress4 | TecJet_GasTemp1 | TecJet_GasTemp2 | TecJet_GasTemp3 | TecJet_GasTemp4 | TecJet_Lambda1 | TecJet_Lambda2 | TecJet_Lambda3 | TecJet_Lambda4 | TecJet_ValvePos1 | TecJet_ValvePos2 | TecJet_ValvePos3 | TecJet_ValvePos4 | thermalreactor_bpos_thr_val_mid | thermalreactor_icnt_ophours_reactor | thermalreactor_rt_thr_chamber | turbocharger_post_cooling_detection | turbocharger_post_cooling_detection_lpa | turbocharger_post_cooling_detection_lpb | turbocharger_post_cooling_v2_cumulative_counter | valverecession_cyl01_deltaOphSinceInit | valverecession_cyl01_new_cyl_head | valverecession_cyl02_deltaOphSinceInit | valverecession_cyl02_new_cyl_head | valverecession_cyl03_deltaOphSinceInit | valverecession_cyl03_new_cyl_head | valverecession_cyl04_deltaOphSinceInit | valverecession_cyl04_new_cyl_head | valverecession_cyl05_deltaOphSinceInit | valverecession_cyl05_new_cyl_head | valverecession_cyl06_deltaOphSinceInit | valverecession_cyl06_new_cyl_head | valverecession_cyl07_deltaOphSinceInit | valverecession_cyl07_new_cyl_head | valverecession_cyl08_deltaOphSinceInit | valverecession_cyl08_new_cyl_head | valverecession_cyl09_deltaOphSinceInit | valverecession_cyl09_new_cyl_head | valverecession_cyl10_deltaOphSinceInit | valverecession_cyl10_new_cyl_head | valverecession_cyl11_deltaOphSinceInit | valverecession_cyl11_new_cyl_head | valverecession_cyl12_deltaOphSinceInit | valverecession_cyl12_new_cyl_head | valverecession_cyl13_deltaOphSinceInit | valverecession_cyl13_new_cyl_head | valverecession_cyl14_deltaOphSinceInit | valverecession_cyl14_new_cyl_head | valverecession_cyl15_deltaOphSinceInit | valverecession_cyl15_new_cyl_head | valverecession_cyl16_deltaOphSinceInit | valverecession_cyl16_new_cyl_head | valverecession_cyl17_deltaOphSinceInit | valverecession_cyl17_new_cyl_head | valverecession_cyl18_deltaOphSinceInit | valverecession_cyl18_new_cyl_head | valverecession_cyl19_deltaOphSinceInit | valverecession_cyl19_new_cyl_head | valverecession_cyl20_deltaOphSinceInit | valverecession_cyl20_new_cyl_head | valverecession_cyl21_deltaOphSinceInit | valverecession_cyl21_new_cyl_head | valverecession_cyl22_deltaOphSinceInit | valverecession_cyl22_new_cyl_head | valverecession_cyl23_deltaOphSinceInit | valverecession_cyl23_new_cyl_head | valverecession_cyl24_deltaOphSinceInit | valverecession_cyl24_new_cyl_head | valverecession_lev_cyl01_deltaVRSinceInit | valverecession_lev_cyl01_init | valverecession_lev_cyl02_deltaVRSinceInit | valverecession_lev_cyl02_init | valverecession_lev_cyl03_deltaVRSinceInit | valverecession_lev_cyl03_init | valverecession_lev_cyl04_deltaVRSinceInit | valverecession_lev_cyl04_init | valverecession_lev_cyl05_deltaVRSinceInit | valverecession_lev_cyl05_init | valverecession_lev_cyl06_deltaVRSinceInit | valverecession_lev_cyl06_init | valverecession_lev_cyl07_deltaVRSinceInit | valverecession_lev_cyl07_init | valverecession_lev_cyl08_deltaVRSinceInit | valverecession_lev_cyl08_init | valverecession_lev_cyl09_deltaVRSinceInit | valverecession_lev_cyl09_init | valverecession_lev_cyl10_deltaVRSinceInit | valverecession_lev_cyl10_init | valverecession_lev_cyl11_deltaVRSinceInit | valverecession_lev_cyl11_init | valverecession_lev_cyl12_deltaVRSinceInit | valverecession_lev_cyl12_init | valverecession_lev_cyl13_deltaVRSinceInit | valverecession_lev_cyl13_init | valverecession_lev_cyl14_deltaVRSinceInit | valverecession_lev_cyl14_init | valverecession_lev_cyl15_deltaVRSinceInit | valverecession_lev_cyl15_init | valverecession_lev_cyl16_deltaVRSinceInit | valverecession_lev_cyl16_init | valverecession_lev_cyl17_deltaVRSinceInit | valverecession_lev_cyl17_init | valverecession_lev_cyl18_deltaVRSinceInit | valverecession_lev_cyl18_init | valverecession_lev_cyl19_deltaVRSinceInit | valverecession_lev_cyl19_init | valverecession_lev_cyl20_deltaVRSinceInit | valverecession_lev_cyl20_init | valverecession_lev_cyl21_deltaVRSinceInit | valverecession_lev_cyl21_init | valverecession_lev_cyl22_deltaVRSinceInit | valverecession_lev_cyl22_init | valverecession_lev_cyl23_deltaVRSinceInit | valverecession_lev_cyl23_init | valverecession_lev_cyl24_deltaVRSinceInit | valverecession_lev_cyl24_init | valverecession_liv_cyl01_deltaVRSinceInit | valverecession_liv_cyl01_init | valverecession_liv_cyl02_deltaVRSinceInit | valverecession_liv_cyl02_init | valverecession_liv_cyl03_deltaVRSinceInit | valverecession_liv_cyl03_init | valverecession_liv_cyl04_deltaVRSinceInit | valverecession_liv_cyl04_init | valverecession_liv_cyl05_deltaVRSinceInit | valverecession_liv_cyl05_init | valverecession_liv_cyl06_deltaVRSinceInit | valverecession_liv_cyl06_init | valverecession_liv_cyl07_deltaVRSinceInit | valverecession_liv_cyl07_init | valverecession_liv_cyl08_deltaVRSinceInit | valverecession_liv_cyl08_init | valverecession_liv_cyl09_deltaVRSinceInit | valverecession_liv_cyl09_init | valverecession_liv_cyl10_deltaVRSinceInit | valverecession_liv_cyl10_init | valverecession_liv_cyl11_deltaVRSinceInit | valverecession_liv_cyl11_init | valverecession_liv_cyl12_deltaVRSinceInit | valverecession_liv_cyl12_init | valverecession_liv_cyl13_deltaVRSinceInit | valverecession_liv_cyl13_init | valverecession_liv_cyl14_deltaVRSinceInit | valverecession_liv_cyl14_init | valverecession_liv_cyl15_deltaVRSinceInit | valverecession_liv_cyl15_init | valverecession_liv_cyl16_deltaVRSinceInit | valverecession_liv_cyl16_init | valverecession_liv_cyl17_deltaVRSinceInit | valverecession_liv_cyl17_init | valverecession_liv_cyl18_deltaVRSinceInit | valverecession_liv_cyl18_init | valverecession_liv_cyl19_deltaVRSinceInit | valverecession_liv_cyl19_init | valverecession_liv_cyl20_deltaVRSinceInit | valverecession_liv_cyl20_init | valverecession_liv_cyl21_deltaVRSinceInit | valverecession_liv_cyl21_init | valverecession_liv_cyl22_deltaVRSinceInit | valverecession_liv_cyl22_init | valverecession_liv_cyl23_deltaVRSinceInit | valverecession_liv_cyl23_init | valverecession_liv_cyl24_deltaVRSinceInit | valverecession_liv_cyl24_init | valverecession_rev_cyl01_deltaVRSinceInit | valverecession_rev_cyl01_init | valverecession_rev_cyl02_deltaVRSinceInit | valverecession_rev_cyl02_init | valverecession_rev_cyl03_deltaVRSinceInit | valverecession_rev_cyl03_init | valverecession_rev_cyl04_deltaVRSinceInit | valverecession_rev_cyl04_init | valverecession_rev_cyl05_deltaVRSinceInit | valverecession_rev_cyl05_init | valverecession_rev_cyl06_deltaVRSinceInit | valverecession_rev_cyl06_init | valverecession_rev_cyl07_deltaVRSinceInit | valverecession_rev_cyl07_init | valverecession_rev_cyl08_deltaVRSinceInit | valverecession_rev_cyl08_init | valverecession_rev_cyl09_deltaVRSinceInit | valverecession_rev_cyl09_init | valverecession_rev_cyl10_deltaVRSinceInit | valverecession_rev_cyl10_init | valverecession_rev_cyl11_deltaVRSinceInit | valverecession_rev_cyl11_init | valverecession_rev_cyl12_deltaVRSinceInit | valverecession_rev_cyl12_init | valverecession_rev_cyl13_deltaVRSinceInit | valverecession_rev_cyl13_init | valverecession_rev_cyl14_deltaVRSinceInit | valverecession_rev_cyl14_init | valverecession_rev_cyl15_deltaVRSinceInit | valverecession_rev_cyl15_init | valverecession_rev_cyl16_deltaVRSinceInit | valverecession_rev_cyl16_init | valverecession_rev_cyl17_deltaVRSinceInit | valverecession_rev_cyl17_init | valverecession_rev_cyl18_deltaVRSinceInit | valverecession_rev_cyl18_init | valverecession_rev_cyl19_deltaVRSinceInit | valverecession_rev_cyl19_init | valverecession_rev_cyl20_deltaVRSinceInit | valverecession_rev_cyl20_init | valverecession_rev_cyl21_deltaVRSinceInit | valverecession_rev_cyl21_init | valverecession_rev_cyl22_deltaVRSinceInit | valverecession_rev_cyl22_init | valverecession_rev_cyl23_deltaVRSinceInit | valverecession_rev_cyl23_init | valverecession_rev_cyl24_deltaVRSinceInit | valverecession_rev_cyl24_init | valverecession_riv_cyl01_deltaVRSinceInit | valverecession_riv_cyl01_init | valverecession_riv_cyl02_deltaVRSinceInit | valverecession_riv_cyl02_init | valverecession_riv_cyl03_deltaVRSinceInit | valverecession_riv_cyl03_init | valverecession_riv_cyl04_deltaVRSinceInit | valverecession_riv_cyl04_init | valverecession_riv_cyl05_deltaVRSinceInit | valverecession_riv_cyl05_init | valverecession_riv_cyl06_deltaVRSinceInit | valverecession_riv_cyl06_init | valverecession_riv_cyl07_deltaVRSinceInit | valverecession_riv_cyl07_init | valverecession_riv_cyl08_deltaVRSinceInit | valverecession_riv_cyl08_init | valverecession_riv_cyl09_deltaVRSinceInit | valverecession_riv_cyl09_init | valverecession_riv_cyl10_deltaVRSinceInit | valverecession_riv_cyl10_init | valverecession_riv_cyl11_deltaVRSinceInit | valverecession_riv_cyl11_init | valverecession_riv_cyl12_deltaVRSinceInit | valverecession_riv_cyl12_init | valverecession_riv_cyl13_deltaVRSinceInit | valverecession_riv_cyl13_init | valverecession_riv_cyl14_deltaVRSinceInit | valverecession_riv_cyl14_init | valverecession_riv_cyl15_deltaVRSinceInit | valverecession_riv_cyl15_init | valverecession_riv_cyl16_deltaVRSinceInit | valverecession_riv_cyl16_init | valverecession_riv_cyl17_deltaVRSinceInit | valverecession_riv_cyl17_init | valverecession_riv_cyl18_deltaVRSinceInit | valverecession_riv_cyl18_init | valverecession_riv_cyl19_deltaVRSinceInit | valverecession_riv_cyl19_init | valverecession_riv_cyl20_deltaVRSinceInit | valverecession_riv_cyl20_init | valverecession_riv_cyl21_deltaVRSinceInit | valverecession_riv_cyl21_init | valverecession_riv_cyl22_deltaVRSinceInit | valverecession_riv_cyl22_init | valverecession_riv_cyl23_deltaVRSinceInit | valverecession_riv_cyl23_init | valverecession_riv_cyl24_deltaVRSinceInit | valverecession_riv_cyl24_init | Various_Bits_ColAlarm | Various_Bits_CollAlarm | Various_Bits_CollWarning | Various_Bits_GenSwitchOn | Various_Bits_OperationOn | Various_EngineStatus | Various_SetValues_SetWasteGate | Various_Values_PosThrottle | Various_Values_PosThrottleA1 | Various_Values_PosThrottleA2 | Various_Values_PosThrottleB1 | Various_Values_PosThrottleB2 | Various_Values_PosTurboBypass | Various_Values_PosTurboBypassA1 | Various_Values_PosTurboBypassA2 | Various_Values_PosTurboBypassB1 | Various_Values_PosTurboBypassB2 | Various_Values_PosWasteGateA | Various_Values_PosWasteGateB | Various_Values_PressBoost | Various_Values_PressBoostP2 | Various_Values_PressBoostP2A | Various_Values_PressBoostP2B | Various_Values_PressBoostP2sA | Various_Values_PressBoostP2sB | Various_Values_PressBoostUnfilt | Various_Values_SetPosThrottleA1 | Various_Values_SetPosThrottleA2 | Various_Values_SetPosThrottleB1 | Various_Values_SetPosThrottleB2 | Various_Values_SetPosTurboBypassA1 | Various_Values_SetPosTurboBypassA2 | Various_Values_SetPosTurboBypassB1 | Various_Values_SetPosTurboBypassB2 | Various_Values_SetPressBoost | Various_Values_SetSpeed | Various_Values_SpeedAct | Various_Values_TempIntakeAir | Various_Values_TempMixture | Various_Values_TempT2A | Various_Values_TempT2B | Various_Values_TempT2sA | Various_Values_TempT2sB | Name
0 | Never Connected | 39 | 1 | 0 | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","agent_conn":"Prim-SSL-NoProxy","mon_conn":"no","rem_conn":"no"} |  |  | 0 | 0 |  |  |  |  | 0 | 0 | 0 | -1535 |  |  |  |  | 5.71 | 0 |  | 0 | 0 | 0 | 0 | 0 | [8 empty] | 3.4 | 7499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [73 empty] | 0.02 | 0.01 |  |  |  |  | 0 |  | 0 | 0 | 0 | [5 empty] | 98260 | 98260 | 98260 | 98260 |  |  |  |  | 33030 | 53849 | 53849 | 11 | 390 | 53 | 52.8 | 0 | 73 | 0 | 0 | 70 | 0 | 0 | 28 | 0 | 0 | 97 | 97.1 | 30.7 | 90 | 91.8 | 100 | 50 | 52.8 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [283 empty] | 0 | 44 | 1 |  |  |  |  | -20.26 | 1 |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 40.44 | 40.51 | 32.84 | 32.46 | 0 | 0 | 0 | 0 | 525.2 | 530.3 | 530.2 | 529 | 529 | 530.9 | 532.1 | 532.1 | 532.8 | 530.2 | 534.1 | 529.4 | 530.2 | 528.8 | 528.3 | 529.2 | 532.8 | 529.5 | 532.9 | 532.6 | 531.7 | 531.8 | 530.7 | 534.5 | 530 | 530 | 535 | 535 | 525 | 526 | 0 | 0 | 0 | 332 | 334 | 9 | 0 | 0 | [42 empty] | 0 | 0 | 0 | 195.6 | 195.6 | 0 |  |  | 0 | 0 |  | 0 | [8 empty] | 54.6 | 46.7 | 0 | 0 | 64.9 | 62.2 | 64.3 | 27.6 | 54.6 | 46.7 | 53.7988 | 45.4117 | 20848 |  |  |  |  | 50 | [7 empty] | 10217 | 5937 | 10199 | 5947 | 10193 | 5927 |  | 14057 | 4685 | 3 | 0.0063314 | 100 | 2.38 | -46 | 3.95 | 0.9 | 0 | 0 | 86.3 | 78 | 0 | 0 | 0 | 74.3 |  | 0 |  | 23 | 2.9 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 52.1 | 43.3 | 54.7 | 52.2 | 53.8 | 49.1 | 47.8 | 66.3 | 61.2 | 46 | 44.2 | 53 | 1.24 | 1.24 | 1.24 |  | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.088 | 1.088 | 1.088 | 1.088 | 1.088 | 1.088 | 1.088 | 1.088 | 1.088 | 1.088 | 1.088 | 1.088 | [12 empty] | 33051.6 | 33051.5 | 33051.7 | 33051.7 | 33051.5 | 33051.3 | 33051.6 | 33051.4 | 33051.8 | 2179 | 33051.6 | 33051.6 | 2015-06-17 | 2015-06-17 |  |  | 2015-06-16 |  |  | 2015-06-17 |  |  |  |  | 2015-06-17 |  |  | 2015-06-16 |  |  | 2015-06-17 |  |  | 2015-06-17 |  |  | 2015-06-16 |  |  | 2015-08-13 |  |  | 2015-06-17 |  |  | 2015-06-17 |  |  | 22779 | 22777 | 22741 | 22808 | 22809 | 22740 | 22778 | 22781 | 22742 | 24583 | 22810 | 22764 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | [20 empty] | 1 | 1 |  | 0 | 0 | -14.5 | -15.2 | -15.2 | -15.2 | -15.2 | -15.2 | -15.2 | -15.2 | -15.2 | -15.2 | -15.2 | -15.2 | -15.2 | -15.2 | -15.2 | -15.2 | -15.2 | -15.2 | -15.2 | -15.2 | -15.2 | -15.2 | -15.2 | -15.2 | 207 | 269 | 176 | 191 | 127 | 176 | 159 | 221 | 143 | 191 | 111 | 159 | 207 | 127 | 191 | 191 | 221 | 176 | 269 | 143 | 143 | 143 | 127 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1423 | 1420 | 866 | 1295 | 927 | 1700 | 1377 | 1422 | 1210 | 1975 | 2201 | 2410 | 1850 | 1341 | 2183 | 1405 | 1239 | 1487 | 1525 | 1768 | 1848 | 1449 | 1534 | 1887 | -5 |  | 0 |  | 0 | 0 | 7.79 | 7.81 | 7.91 | 7.68 | 7.68 | 7.78 | 7.84 | 7.78 | 7.78 | 7.69 | 7.68 | 7.67 | 7.72 | 7.91 | 7.68 | 7.78 | 7.81 | 7.86 | 7.87 | 7.84 | 7.84 | 7.85 | 7.76 | 7.78 | -0.19 | -0.11 | -0.37 | -0.46 | -0.27 | -0.45 | -0.24 | -0.22 | -0.42 | -0.37 | -0.32 | -0.24 | -0.27 | -0.31 | -0.27 | -0.46 | -0.34 | -0.28 | -0.42 | -0.42 | -0.24 | -0.36 | -0.32 | -0.18 | 7.81 | 7.72 | 7.78 | 7.89 | 7.76 | 7.72 | 7.92 | 7.82 | 7.91 | 7.76 | 7.75 | 7.74 | 7.84 | 7.84 | 7.73 | 7.69 | 7.72 | 7.72 | 7.79 | 7.92 | 7.78 | 7.78 | 7.8 | 7.91 | -0.22 | -0.09 | -0.41 | -0.39 | -0.38 | -0.37 | -0.27 | -0.31 | -0.39 | -0.42 | -0.29 | -0.32 | -0.32 | -0.29 | -0.36 | -0.38 | -0.42 | -0.21 | -0.37 | -0.39 | -0.37 | -0.29 | -0.19 | -0.22 | 144546.3 |  | 51190.9 |  | 255 | 0.02 | 0 | 1092 | 1 | 0 | 10198 | [30 empty] | M01 | 18.1 | 20.2 | 18.1 | 18.5 | 17.3 | 18 | 18.8 | 18.7 | 17.3 | 19.7 | 18.3 | 18.7 | 18.4 | 17.8 | 18.6 | 17.4 | 16.4 | 16.8 | 18.8 | 18.3 | 17.5 | 18.6 | 17.7 | 18.1 | 17.6 | 20.2 | 16.4 | 1273 | [82 empty] | Running | 50 | Unknown | 0 | 0 |  | 83.82 | [35 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | [25 empty] | 60 | 30 | 30 |  | 1.4 | 20 | 1.5 | 80 | 0 | 0 | 11 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 2 | 20 | 25 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 | -1000 | 200 | -1000 | -1700 | -200 | -1700 | 10 | 0 | 50 | 1300 | 6.7 | 5.6 | 6.9 | 0.1 | 2.7 | 0.1 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 4.5 | 0 | 0 | 10 | 0 | 0 | 0 | 0 |  | 0 | 5 | 5 | 5 | 5 | 5 | 60 | 28 | 40 | 30 | 50 | 180 | 28 | 40 | [58 empty] | 0 | 0 | 1 | 100 | 0 | 0 | 0 | 0 | 0.1 | 0 | 205 | 205 | 0 | 0 | 0 |  |  | 0 | 1 | 1 | 0 | 0 | 0 | 120 | 1 | 50 | 30 | 30 | 15 | 120 | 0 | 100 | 100 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 100 | 1 | 100 | 0 | 0 | 0 | 0 | 0.1 | 0 | 205 | 205 | 0 | 0 | 0 |  |  | 0 | 1 | 1 | 0 | 0 | 0 | 120 | 1 | 50 | 30 | 30 | 15 | 120 | 0 | 100 | 100 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 100 | 1 | 100 | 0 | 0 | 0 | 0 | 0.1 | 0 | 205 | 205 | 0 | 0 | 0 |  |  | 0 | 1 | 1 | 0 | 0 | 0 | 120 | 1 | 50 | 30 | 30 | 15 | 120 | 0 | 100 | 100 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 100 | 1 | 100 | 0 | 0 | 0 | 0 | 0.1 | 0 | 205 | 205 | 0 | 0 | 0 |  |  | 0 | 1 | 1 | 0 | 0 | 0 | 120 | 1 | 50 | 30 | 30 | 15 | 120 | 0 | 100 | 100 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 0.1 | 0 | 205 | 205 | 0 | 0 | 0 |  |  | 0 | 1 | 1 | 0 | 0 | 0 | 120 | 1 | 50 | 30 | 30 | 15 | 120 | 0 | 100 | 100 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 0.1 | 0 | 205 | 205 | 0 | 0 | 0 |  |  | 0 | 1 | 1 | 0 | 0 | 0 | 120 | 1 | 50 | 30 | 30 | 15 | 120 | 0 | 100 | 100 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 0.1 | 0 | 205 | 205 | 0 | 0 | 0 |  |  | 0 | 1 | 1 | 0 | 0 | 0 | 120 | 1 | 50 | 30 | 30 | 15 | 120 | 0 | 100 | 100 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 0.1 | 0 | 205 | 205 | 0 | 0 | 0 |  |  | 0 | 1 | 1 | 0 | 0 | 0 | 120 | 1 | 50 | 30 | 30 | 15 | 120 | 0 | 100 | 100 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 100 | 100 | 2050 | 2.05 | 0.1 | 24.201 | 24.201 | 1 | 4.078 | 4.078 | 0 | 120 | 50 | 30 | 30 | 15 | 73 | 73 | 100 | 0.1 | 73 | 0 | 0 | 100 | 0 | 0 | 100 | 100 | 100 | 0 | 0 | 0.1 | 0.005 | 0.005 | 1 | 1 | 1 | 0 | 120 | 50 | 30 | 30 | 15 | 70 | 70 | 100 | 100 | 70 | 0 | 0 | 100 | 0 | 0 | 100 | 100 | 100 | 0 | 0 | 0.2 | 205 | 205 | 1 | 1 | 1 | 0 | 120 | 50 | 30 | 30 | 15 | 40 | 20 | 1 | 0.1 | 20 | 0 | 0 | 100 | 0 | 0 | 100 | 100 | 100 | 0 | 0.3 | 3.5 | 1 | 0.2 | 0 | 200 | 50 | 30 | 30 | 30 | 110 | 70 | 1 | 1 | 100 | 0 | 0 | 100 | 0 | 10 | 100 | 0 | 0.1 | 205 | 1 | 1 | 0 | 120 | 50 | 30 | 30 | 15 | 99 | 85 | 100 | 100 | 90 | 0 | 0 | 100 | 0 | 100 | 100 | 0 | 0.1 | 40 | 1 | 1 | 30 | 80 | 50 | 30 | 30 | 15 | 80 | 30 | 0.5 | 0.5 | 50 | 0 | 10 | 100 | 10 | 100 | 100 | 0 | 1 | 205 | 0 | 1 | 0 | 400 | 50 | 30 | 30 | 15 | 400 | 0 | 320 | 320 | 0 | 0 | 0 | 100 | 0 | 100 | [1124 empty] | 84241 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | T241 | AG | 0o | 0 | 1145166 | 624 | 0 | 0 | 12239 | ITA | 11 | 0 | 337 | 0 | 1 | 1 | 1 | 2 | 503220 | 569784 | 115762 | 1 | 3.4 | 0.3 | 3.4 | 0o | [257 empty] | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [29 empty] | 0 | 100 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | [6 empty] | 48 | 20 | 0 | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | [88 empty] | 60 | 60 | 0 | 0 | 1 | 1 | 2 | 38 | 2 | 60 | 0 | 44.8 | 2 | 60 | 0 | 44.8 | 2 | 5 | 250 | 100 | 250 | 250 | 100 | 100 | 1000 | 640 | 680 | 5 | 640 | 5 | 650 | 640 | 5 | 650 | 5 | 1000 | 5 | 15 | 300 | 20 | 50 | 650 | 5 | 1000 | 5 | 1000 | 100 | [129 empty] | 10.043 | 9.71 | 1.316 | 0.735 | 10.043 | 9.71 | 1.316 | 0.735 | 10.043 | 9.71 | 1.316 | 0.735 | 10.043 | 9.71 | 1.316 | 0.735 | 20 | 30 | 0 | 0 | 155 | 170 | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 | 155 | 175 | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 | 155 | 175 | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 | 155 | 175 | 0 | 0 | 30 | 75 | 4 | 4 | 50 | 10 | 0 | 10 | 0 | 10 | 0 | 10 | 15 | -30 | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | 0 | 20 | 0.8 | 0.9 | 1 | -0.98 | -0.95 | 0.8 | -0.97 | 1 | 7 | 0.95 | -0.95 | 20 | 80 | 5468 | 80 | 85 | 2.03 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 5 | 0 | 9 | 0 | 12 | 0 | 14 | 0 | 18 | 0 | 22 | 0 | 7 | 1 | -10 | 10 | 0.85 | 0.9 | 0.95 | 1 | -0.97 | -0.95 | 0.5 | 0 | 0 | 85 | 90 | 95 | 100 | 105 | 110 | 4 | 5 | 135 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 90 | 85 | 90 | 5 | 5 | 10 | 10 | 140 | 155 | 140 | 155 | 140 | 155 | 140 | 5 | 175 | 5 | 5 | 1 | 53.3 | 1 | 300 | 1 | 0 | 150 | 1000 | 80 | 60 | 45 | 3000 | 0 | 75 | 1.5 | 0 | 0 |  | 60 | 0.1 | 1.11 | 30 | 0 | 60 | 75 | 90 | 100 | 100 | 4 | 20 | 312 | 624 | 0 | 5000 | 45 | 5 | 0 | 75 | 50 | 50 | 50 | 0 | 4 | 20 | 5000 | 5000 | 1 | 0 | 10 | 0 | 1 | 3 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 4 | 20 | 0.8 | -0.95 | 1 | 0 | 0 | 100 | 0 | 100 | 4 | 20 | 100 | 100 | 10500 | 0 | 0 | 0 | 0 | 3 | -1445 | -893 | 0 | 893 | 1445 | 4 | 20 | -1445 | 1445 | 0 | 0 | 4 | 20 | -1445 | 1445 | 5000 | 0 | 0 | 0.8 | -0.8 | -10000 | 10000 | [12 empty] | 10 | 3.3 | 0.2 | 3 | 0.05 | 1 | 1.5 | 0.05 | 0.05 | 120 | 5 | 120 | 5 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 | 100 | -100 | 1 | 50 | 0 | 0 | 20 | 2 | 0 | 0 | 3 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 3 | 0.05 | 10 | 0.5 | 5.2 | 600 | 0.01 | 0.3 | 0.1 | 0.4 | 0.1 | 0.5 | 500 | 1500 | 3.5 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1.5 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 120 | 2 | 120 | 2 | 0 | 0 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 120 | 0 | 0 | 120 | 120 | 2 | 2 | 120 | 0 | 0 | 120 | 120 | 2 | 2 | 0 | 73 | 2 | 1 | 0 | 78 | 120 | 2 | 0.5 | 120 | 1 | 0 | 0 | 99 | 2 | 2 | [163 empty] | 1 | 100 | 27 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 10 | 13 | 13 | 13 | 13 | 4 | 4 | 20 | 7.5 | 22.5 | 0 | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 | 10 | 3 | 42 | 48 | 924 | 60 | 100 | 75 | 50 | 30 | 10 | 13 | 33 | 17 | 17 | 13 | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 | 100 | 15 | 50 | 300 | 1800 | 1800 | 0 | 50 | 50 | 1800 | 1800 | 0 | 50 | 50 | 0 | 0 | 990 | -950 | -650 | 0 | 1000 | 10 | 400 | 25 | 500 | 100 | 0 | 700 | 15 | 750 | 95 | 2 | 1000 | 1000 | 1000 | 1000 | -0.05 | -0.02 | 0.02 | 0.02 | 95 | 100 | 100 | 30 | 0 | 100 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 200 | 850 | 30 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 3 | 5 | 5 | 5 | -5 | -5 | -5 | -5 | 13 | 13 | 13 | 13 | 4.5 | 4.5 | 45 | 660 | 660 | -144 | 0 | 60 | 50 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 4 | 500 | 30 | 8000 | 8000 | 8 | 40 | 0 | 0 | 0 | 1200 | 1500 | 10000 | 2 | 50 | 0 | 0 | 100 | 100 | 2 | 100 | 50 | 10 | 25 | 2500 | 1 | 0 | 1 | 0 | 380 | 1 | -30 | -9 | 4300 | 1300 | 10 | 4300 | 2600 | 60 | 0 | 0 | 30 | 10 | 300 | 15 | 230 | 110 | 30 | 10 | 300 | 15 | 2.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 4396 | 2199 | 5930 | 3024 | 1496 | 1498 | 0 | 53.7 | 50.8 | 0 | 660 | 10 | 30 | 10 | 300 | 15 | 230 | 110 | 30 | 10 | 300 | 15 | 2.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 4750 | 2000 | 4900 | 2150 | 1500 | 1500 | 0 | 50 | 50 | 0 | 660 | 10 | 30 | 10 | 300 | 15 | 230 | 110 | 30 | 10 | 300 | 15 | 2.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 4750 | 2000 | 4900 | 2150 | 1500 | 1500 | 0 | 50 | 50 | 0 | 660 | 10 | 30 | 10 | 300 | 15 | 230 | 110 | 30 | 10 | 300 | 15 | 2.3 | 1.1 | 0 | 0 | 0 | 0 | 0 | 4750 | 2000 | 4900 | 2150 | 1500 | 1500 | 0 | 50 | 50 | 0 | 660 | 10 | 0 | 1000 | 300 | 48 | -1.6 | -4 | 100 | 10 | 0 | 1 | 10 | 0 | 0.5 | 45 | 0 | 50 | 0 | 30 | 100 | 50 | 100 | 12000 | 0 | 0 | 0 | 0 | 0 | 0 | [17 empty] | 0 | 0 |  | 1 | 1 | 5 | 0.1 | 0.1 | 80 | 0.1 | 35 | 100 | 2010000 | 2010 | 0.5 | 15 | 15 | 1 | 2 | 2 | 120 | 50 | 30 | 30 | 15 | 53 | 53 | 53 | 53 | 63 | 30 | 0.1 | 0.1 | 0 | 100 | 0 | 0 | 100 | 100 |  |  |  | 3 | 55 | 57 | 2 | 2 | 60 | 0.1 | 30 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14140 | 0 | 1 | 0 | 1 | 20 | 30 | 1 | 301 | 1 | 250 | 0.8 | 110 | 0.2 | -0.2 | 1 | 100 | 0.2 | 150 | 69 | 150 | 150 | 105 | 500 | 50 | 10500 | 110 | 10 | 120 | 4 | 7 | -1225 | 4900 | 0 | 0.2 | 100 | 200 | 0 | 80 | 2 | 85 | 45 | 0.5 | 10 | 4 | 3 | 20 | 10 | 3 | 15000 | 15000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 10500 | 0 | 0 | 0 | 0 | 0 | -5000 | 5000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [716 empty] | 0 | 0 | 1 | 1 | 8 | 2 | 5 | 35 | 30 | 20 | 30 | 32 | 10 | 6 | 30 | 0 | 140 | 250 | 40 | 30 | 10 | 3 | 5 | 40 | 30 | 4 | 6 | 3 | 10 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2 | 70 | 70 | 0 | 5 | 3 | 20 | 99 | 2 | 0 | 20 | 5000 | 5000 | 60 | 75 | 90 | 100 | 100 | 0 | 20 | 2200 | 4401 | 2.5 | 2 | 35 | 45 | 1 | -2 | -2 | -2 | -2 | 4 | 50 | 2 | 20 | 10 | 40 | 10 | 20 | 300 | 0 | 0 | 50 | 10 | -145 | 10 | 10 | 10 | 105 | 10 | 0.5 | 0 | 10 | 4401 | 4401 | 4401 | 4401 | 50 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 24.5 | 1 | 10 | 0 | 150 | 1 | 1 | 100.6 | 103.1 | 98 | 91 | 103.1 | 50 | 65 | 85 | 75 | 5 | 105 | 120 | 95 | 70 | 140 | 0 | 80 | 0 | 120 | 1 | 20 | 5.55 | 0 | 0 | 120 | 75 | 50 | 625 | 4 | 4 | 4 | 4 | 56 | 56 | 56 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 500 | 500 | 800 | 800 | 0 | 0 | 0 | 0 | 0 | 0 | [60 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6500 | 5000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [60 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 50 | 48.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1650 | 10 | 200 | 400 | 2800 | 5 | 10000 | 0 | 3850 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 0 | 1500 | 0 | 0 | 0 | 0 | 5 | 1 | 90 | 3 | 35 | 10 | 3 | 200 | 0 | 40 | 60 | 35 | 10 | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 | 100 | 1 | 0 | 0 | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 800 | 1 | 100 | 7 | 900 | 99 | 2 | 0 | 20 | 0 | 1500 | 1495 | 1 | 0 | 0 | 1740 | 10 | 800 | 10 | 1505 | 1 | 250 | 10 | 100 | 2 | 1500 | 100 | [6 empty] | 9.81 | 10.24 | 755 | 0 | 0 | 1.55 | 1.7 | 30 | 75 | 9.54 | 9.971 | 720 | 0 | 0 | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 | 0 | 0 | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 | 0 | 0 | 1.55 | 1.75 | 30 | 75 | 4 | 4 | 0.5 | 10 | 0 | 10 | 0 | 10 | 0 | 10 | 15 | -30 | 900 | 1300 | 0.3 | 0.2 | 1.2 | 100 | 30 | 0.59 | 1 | 20 | 21 | 24 | 9 | 12 | 25 | 32 | 1 | 8 | 13 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | System.Byte[] |  | System.Byte[] |  | System.Byte[] |  | System.Byte[] |  | System.Byte[] |  | System.Byte[] |  | System.Byte[] |  | System.Byte[] | [8 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | 2 | 1 | 0 | 0 | 2 | 1 | 1 | 1 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [27 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 4400 | 4384 | 4401 | 4401 | 0 | 0 | 0 | 0 | 0 | 0 | 4401 | 0 | 4401 | [10 empty] | -46.1 | 3.967 | 0.027768 | 0.88309 | [27 empty] | 51.59 | [73 empty] | Sending | 30 | [20 empty] | 22.4006 | 22.2006 | 22.3 | 24.0021 | 22.7 | 25.1 | 23.703 | 20.8 | 26 | 21.8024 | 20.5004 | 23.4033 | 26.7014 | 23.0997 | 24.0034 | 26.05 | 26 | 20.4 | 22.1027 | 22.7006 | 18.5008 | 21.2022 | 27.803 | 19.8012 | 965 | 1509 | 1157 | 1638 | 1127 | 1092 | 1139 | 1656 | 1046 | 1145 | 1132 | 1217 | 1336 | 1123 | 1643 | 1891 | 1634 | 1117 | 1379 | 1517 | 1104 | 1488 | 1250 | 1492 | [21 empty] | 112.2 | 0 | 0 | 0 | 258.944 | 0 | 0 | 0 | 1070.4 | 0 | 0 | 0 | 2.1 | 0 | 0 | 0 | 1.956 | 1.956 | 1.956 | 1.956 | 25.7 | 0 | 0 | 0 | [8 empty] | 1 | 14764 | 1 | 14764 | 1 | 14764 | 1 | 14764 | 1 | 14764 | 1 |  | 1 | 14764 | 1 | 14764 | 1 | 14764 | 1 |  | 1 |  | 1 |  | 1 | 14764 | 1 |  | 1 | 14764 | 1 | 14764 | 1 |  | 1 | 14764 | 1 | 14764 | 1 | 14764 | 1 |  | 1 |  | 1 | 14764 | 1 | 0 | 7.79 | 0.4 | 7.7 | 0 | 8.1 | 3.1 | 7.8 | 0.4 | 7.7 | 0.5 | 7.5 | 0 | 7.84 | 0.7 | 7.7 | 1.4 | 7.6 | 0.6 | 7.4 | 0 | 7.68 | 0 | 7.67 | 0 | 7.72 | 2.5 | 7.5 | 0 | 7.68 | 0.2 | 7.5 | 2.7 | 7.7 | 0 | 7.86 | 0.2 | 7.4 | 0.7 | 7.7 | 0.4 | 7.6 | 0 | 7.85 | 0 | 7.76 | 1.15 | 7.65 | 0 | -0.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.32 | 0 | -0.24 | 0 | -0.27 | 0 | 0 | 0 | -0.27 | 0 | 0 | 0 | 0 | 0 | -0.28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.36 | 0 | -0.32 | 0 | 0 | 0 | 7.81 | 0.3 | 7.8 | 0 | 8 | 1 | 8 | 0.3 | 7.7 | 0.4 | 7.5 | 0 | 7.92 | 0.6 | 7.7 | 0.6 | 7.7 | 0.4 | 7.4 | 0 | 7.75 | 0 | 7.74 | 0 | 7.84 | 0.9 | 7.5 | 0 | 7.73 | 0.2 | 7.5 | 0.7 | 7.7 | 0 | 7.72 | 0.4 | 7.4 | 0.6 | 7.7 | 0.35 | 7.75 | 0 | 7.78 | 0 | 7.8 | 0.65 | 7.65 | 0 | -0.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.29 | 0 | -0.32 | 0 | -0.32 | 0 | 0 | 0 | -0.36 | 0 | 0 | 0 | 0 | 0 | -0.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.29 | 0 | -0.19 | 0 | 0 |  | 0 | 0 | 1 | 1 | 17 | 0 | 98.8 | 98.6 | 98.6 | -24.9 | -24.9 | 9.8 | 9.3 | -24.9 | 9.3 | -24.9 | -24.9 | -24.9 | 5.992 | 5.96 | 5.96 | -2.5 | 5.98 | -2.5 | 22337 | 98.8 | 98.8 | 98.8 | 98.8 | 9.8 | 9.8 | 9.8 | 9.8 | 6.003 | 1500 | 1499 | 3.5 | 52.8 | 0 | 0 | 52.8 | -30 | POLYNT - 2 (1145166-T241) --> Sept
1 | No Contact | 37 | 1 | 0 | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","rem_conn":"Prim-NoSSL-NoProxy","dataItems":"0/20","agent_conn":"Prim-SSL-NoProxy","mon_conn":"Prim-SSL-NoProxy"} | 0 | 0 | 0 | 0 | 0 | 0 | -0.92 | 4.19 | 0 | 0 | 0 | -124 | 0 | 4.17 | 0 | 3.12 | 4.24 | 22.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.31 | 0 | 5.31 | 0 | 0 | 0 | 4.8.0.4 | 3305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 |  | 12292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.02 | 3745192 | 65800 | 93347 | 25978 | 84625885 | 0 | 354946 | 1028644 | 74745 | 0 | 0 | 0 | 0 | 0 | 403 | 1031 | 73 | 31 | 27712 | 27712 | 698228 | 798228 | 32288 | 32292 | 32292 | 1257 | 1485 | 49.7 | 45 | 58.1 | 70 | 70 | 70.4 | 0 | 0 | 0 | 30 | 22.3 | 0 | 0 | 0 | 0 | 127.9 | 125 | 35 | 45 | 45 | 0 | 87.6 | 87.6 | 0 | 120 | 594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.9 | 26.8 | 594 | 5.8 | 7.4 | 1993.4 | 7.5 | 7.1 | 1.8 | 2.1 | 22647.3 | 2439.4 | 52.6 | 40 | 29.5 | 93.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.5727 | 40.495 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 4.29 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1608645430944 | 0 | 43 | 1 | 0 | 0 | 0 | 0 | 38.01 | 0 | 0 | 1776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553 | 552 | 550 | 554 | 554 | 552 | 553 | 557 | 550 | 551 | 554 | 553 | 561 | 555 | 551 | 551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 553 | 553 | 561 | 560 | 550 | 550 | 0 | 373 | 126 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 987 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.8 | 30.7 | 0 | 0 | 89.3 | 89.1 | 87.5 | 33.9 | 48.4 | 40.5 | 51.3989 | 44.7928 | 41 |  |  | 2707 | 0.989 | 50.02 | 0 | 10285 | 5949 | 10286 | 5933 | 10319 | 5953 | 10293 | 5948 | 10283 | 5930 | 10309 | 5945 | 0 | 0 | 0 | 0 | 0 | 0 | 2.13 | -28.3 | 4.43 | 0.88 | 0 | 0 | 87.6 | 73.5 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 24 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.6 | 0 | 0 | 0 | 72.2 | 76.2 | 80.6 | 44.8 | 68.8 | 71.6 | 76.3 | 0 | 1.26 | 0 | 0 | 0 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 88 | 0 | 0 | 0 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 0 | 17189.3 | 0 | 0 | 0 | 8965.5 | 32339.8 | 8997.9 | 32340.2 | 32307.3 | 32340 | 32340.1 | 0 | 2018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 1 | 2018 | 11 | 1 | 2016 | 22 | 2 | 2018 | 7 | 1 | 2016 | 22 | 2 | 2016 | 22 | 2 | 2016 | 22 | 2 | 2016 | 23 | 2 | 0 | 0 | 0 | 38623 | 0 | 0 | 0 | 38622 | 28306 | 38409 | 28310 | 28331 | 28314 | 28372 | 0 | 7.73 | 0 | 0 | 0 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 162 | 0 | 0 | -20.1 | -20.1 | -20.1 | -20.1 | -20.1 | -20.1 | -20.1 | -20.1 | -20.1 | -20.1 | -20.1 | -20.1 | -20.1 | -20.1 | -20.1 | -20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 110 | 126 | 110 | 126 | 94 | 174 | 110 | 126 | 205 | 126 | 110 | 141 | 174 | 158 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 305 | 476 | 231 | 586 | 256 | 402 | 378 | 573 | 293 | 500 | 366 | 280 | 329 | 305 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.36 | 0 | 0 | 0 | 0 | 7.78 | 7.75 | 7.62 | 7.5 | 7.8 | 7.89 | 7.98 | 7.85 | 7.74 | 7.83 | 7.81 | 7.7 | 7.64 | 7.67 | 7.85 | 7.5 | [8 empty] | -0.1 | -0.41 | -0.03 | -0.21 | -0.3 | -0.05 | -0.13 | -0.11 | -0.18 | -0.28 | -0.12 | -0.15 | -0.12 | -0.33 | -0.1 | -0.39 | [8 empty] | 7.64 | 7.89 | 7.69 | 7.61 | 7.67 | 7.97 | 7.94 | 7.84 | 7.78 | 7.68 | 7.84 | 7.85 | 7.72 | 7.69 | 7.92 | 7.5 | [8 empty] | -0.47 | -0.1 | -0.22 | -0.39 | -0.21 | -0.27 | -0.08 | -0.22 | -0.1 | -0.36 | -0.04 | -0.35 | -0.19 | -0.18 | -0.32 | -0.19 | [8 empty] | 86021.4 | 0 | 28214.7 | 0 | 152 | 0.02 | 0 | 387 | 1.06 | 0 | 10291 | 4.8.0.0.0 | 4.7.1.1.1 | 4.7.1.0.2 | 4.7.1.0.0 | 4.7.0.0.1 | 4.8.0.3.1 | 4.7.1.0.0 | 4.7.0.0.2 | 4.7.1.0.0 | 4.7.0.0.1 | 4.5.1.0.0 | 4.7.1.0.0 | 4.7.2.0.1 | 4.7.0.0.1 | 4.7.0.1.4 | 4.8.2.1.0 | 4.7.0.1.1 | 4.7.0.0.0 | 4.7.0.0.0 | 4.6.0.0.0 | 4.7.0.0.2 | 4.7.0.0.0 | 0.0.0.0.0 | 4.7.5.1.1 | 4.7.0.0.0 | 4.7.0.0.3 | 4.7.0.0.1 | 4.7.0.0.0 | 4.7.0.1.1 | 4.8.0.0.0 | M05 | 19.9 | 22.7 | 21.4 | 21.1 | 19 | 19.8 | 18.9 | 18.8 | 22.7 | 18.7 | 19.2 | 17.9 | 19 | 18.1 | 18.9 | 18.7 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.1 | 18 | 1268 | [30 empty] | -1 | 2 | 1 | NaN | 0.0001 | 1606389140000 | 1 | 1 | 0.1504 | 1 | NaN | 4252 | 1 | 1605744000000 | NaN | NaN | NaN | 0.02 | 5.65 | 6 | NaN | 2 | 0.0005 | 1 | 1 | 1 | 1 | 0 | 0 | 1255 | 9 | 0.0313 | 1 | 1606388400000 | 2 | 1 | 3 | 2.13 | 3.2 | 1007760 | 1 | 1 | 31574 | 1 | 14.8 | 141 | 0.05 | 0.0367 |  |  |  |  | Running | 50 | MAINS-PARALLEL OPERATION |  |  |  | 21.65 | 2 | 2 | 50.02 | 50.02 | 0 | 50.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 | 0 | 20 | 0 | 0 | 970 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 1 | 0 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 30 | 30 | 0 | 1.4 | 20 | 1.5 | 80 | 4 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 500 | 7000 | 300 | 1150 | 0 | 1800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 33 | 0 | 0 | 0 | 0 | 0 | 1700 | 800 | 1 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 | 214 | 250 | 100 | -159 | -100 | -350 | 6 | 0 | 50 | 1500 | 3 | 3.7 | 3.9 | 0.1 | 2.7 | 0.1 | 0 | 0 | 0 | 500 | 7000 | 70 | -500 | 0 | 0 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 5 | 5 | 60 | 28 | 35 | 30 | 50 | 180 | 30 | 35 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 0 | 0 | 1 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 0 | 0 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 1 | 100 | 1800 | 1.8 | 0 | 0 | 0.1 | 0 | 22 | 22 | 0 | 0 | 1 |  |  | 0 | 1.75 | 1.75 | 0 | 0 | 0 | 140 | 1 | 50 | 30 | 30 | 15 | 128 | 117 | 100 | 0.01 | 117 | 0 | 0 | 100 | 35 | 0 | 100 | 100 | 1 | 100 | 1000 | 1 | 0 | 0 | 0.1 | 0 | 40 | 40 | 0 | 0 | 0 |  |  | 0 | 2 | 2 | 0 | 0 | 0 | 45 | 20 | 50 | 30 | 30 | 15 | 28 | 10 | 100 | 100 | 22 | 0 | 0 | 100 | 48 | 0 | 100 | 100 | 1 | 100 | 0 | 0 | 0 | 0 | 0.1 | 0 | 30 | 30 | 0 | 0 | 1 |  |  | 0 | 2.2 | 2.2 | 0 | 0 | 0 | 120 | 1 | 50 | 30 | 30 | 15 | 105 | 90 | 100 | 0.01 | 105 | 0 | 0 | 100 | 40 | 0 | 100 | 100 | 1 | 100 | 0 | 0 | 0 | 0 | 0.1 | 0 | 205 | 205 | 0 | 0 | 0 |  |  | 0 | 1 | 1 | 0 | 0 | 0 | 120 | 1 | 50 | 30 | 30 | 15 | 120 | 0 | 100 | 100 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 0.1 | 0 | 205 | 205 | 0 | 0 | 0 |  |  | 0 | 1 | 1 | 0 | 0 | 0 | 120 | 1 | 50 | 30 | 30 | 15 | 120 | 0 | 100 | 100 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 0.1 | 0 | 205 | 205 | 0 | 0 | 0 |  |  | 0 | 1 | 1 | 0 | 0 | 0 | 120 | 1 | 50 | 30 | 30 | 15 | 120 | 0 | 100 | 100 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 0.1 | 0 | 205 | 205 | 0 | 0 | 0 |  |  | 0 | 1 | 1 | 0 | 0 | 0 | 120 | 1 | 50 | 30 | 30 | 15 | 120 | 0 | 100 | 100 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 0.1 | 0 | 205 | 205 | 0 | 0 | 0 |  |  | 0 | 1 | 1 | 0 | 0 | 0 | 120 | 1 | 50 | 30 | 30 | 15 | 120 | 0 | 100 | 100 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 100 | 100 | 1000 | 1 | 0.5 | 120 | 120 | 1 | 2 | 2 | 0 | 120 | 50 | 30 | 30 | 15 | 75 | 55 | 100 | 0.01 | 70 | 0 | 30 | 100 | 0 | 0 | 100 | 100 | 100 | 0 | 0 | 0.1 | 205 | 205 | 1 | 1 | 1 | 0 | 120 | 50 | 30 | 30 | 15 | 70 | 70 | 100 | 100 | 70 | 0 | 0 | 100 | 0 | 0 | 100 | 100 | 100 | 0 | 0 | 0.2 | 205 | 205 | 1 | 1 | 1 | 0 | 120 | 50 | 30 | 30 | 15 | 40 | 20 | 100 | 100 | 28 | 0 | 0 | 10 | 0 | 0 | 100 | 100 | 100 | 0.1 | 0.1 | 4 | 1 | 0.15 | 0 | 200 | 50 | 30 | 30 | 30 | 110 | 70 | 1 | 1 | 100 | 0 | 0 | 100 | 0 | 10 | 100 | 0 | 0.1 | 205 | 1 | 1 | 0 | 120 | 50 | 30 | 30 | 15 | 120 | 100 | 100 | 100 | 117 | 0 | 0 | 100 | 0 | 100 | 100 | 0 | 0.1 | 40 | 1 | 1 | 30 | 80 | 50 | 30 | 30 | 15 | 80 | 30 | 0.5 | 0.5 | 50 | 0 | 10 | 100 | 10 | 100 | 100 | 0 | 1 | 205 | 0 | 1 | 0 | 400 | 50 | 30 | 30 | 15 | 400 | 0 | 320 | 320 | 0 | 0 | 0 | 100 | 0 | 100 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.5 | 8 | 9.5 | 4 | 3.5 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 3000 | 0 | 20 | 4 | 1000 | 0 | 20 | 4 | 3000 | 0 | 20 | 4 | 1000 | 0 | 20 | 4 | 2500 | 0 | 20 | 4 | 3000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 5 | 0 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 32 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 |  |  | 60 | -27 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | [12 empty] | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 1 | 40 | 0 | 30 | 30 | 1 | 1 | 10 | 3 | 1 | 10500 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 4 | 4 | 0.01 | 0.01 | 0.2 | 0.2 | 1 | 0.84 | 1 | 0.84 | 1 | 30 | 0 | 0 | 0 | 100 | 100 | 10 | 50 | 50 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 5000 | -5000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 47.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 0 | 110 | 90 | 35 | 7 | 0 | 0 | 1 | -0.2 | 50 | 110 | 80 | 1 | 0 | 183 | 200 | 1 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 90 | 45 | 0 | 10 | 0 | 0 | 0 | -0.4 | 50 | 110 | 80 | 0 | 0 | 400 | 200 | 0 | 100 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 90 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 6000 | 20 | 100 | 50 | 80 | 250 | 100 | 230 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 5 | 30 | 30 | 70 | 490 | 490 | 300 | 30 | 120 | 30 | 73448 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | T966 | AG | 1 | 1 | 1175579 | 616 | 0 | 0 | 0 | DEU | 11 | 0 | 166 | 0 | 1 | 1 | 1 | 2 | 801465 | 569784 | 668441 | 1 | 3.5 | 1.3 | 3.5 | 1 | 0 | 0.5 | 0.1 | 0.1 | 100 | 35 | 0 | 1 | 2 | 100 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 45 | 35 | 0 | 100 | 20 | 0 | 0 | -5 | 15 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 33 | 30 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 200 | 168 | 75 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 65 | 1 | 0 | 0 | 0 | -4.5 | 10 |  | 60 | 55 | 0 | 2 | 1.65 | 1.82 | 0.6 | 0.6 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0.1 | 0 | 0 | 0 | 15 | 30 | 0.01 | 0.4 | 0 | 60 | 30 | 0.15 | 0 | 0 | 0 | 1200 | 1400 | 0 | 0.5 |  | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 1 | 0.1 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 1 | 0 | [10 empty] | 0 | 50 | 50 | 50 | 50 | 50 |  | 1 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.3 | 1 | 25 | 6.5 | 100 | 0 | 20 | 0 | 0.5 | 0 | 4 | 35 | 0 | 25 | 10 | 250 | 3 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 | 0 | 1 | 4000 | 2000 | 20000 | 10000 | 2425 | 1212 | 0 | 0 | 2 | 1 | 30 | 150 | 20 | 120 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 1 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | 0 | 100 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 | 0 | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 | 1.5 | 1 | 650 | 700 | 0 | 0 | 0 | 0 | [66 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 1000 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 5 | 250 | 250 | 250 | 250 | 100 | 50 | 1000 | 680 | 640 | 5 | 650 | 5 | 1000 | 640 | 5 | 680 | 5 | 1000 | 5 | 15 | 300 | 20 | 50 | 650 | 5 | 1000 | 5 | 1000 | 100 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 20 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | 10.043 | 9.71 | 1.316 | 0.735 | 10.043 | 9.71 | 1.316 | 0.735 | 10.043 | 9.71 | 1.316 | 0.735 | 10.043 | 9.71 | 1.316 | 0.735 | 20 | 30 | 0 | 0 | 160 | 170 | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 | 155 | 175 | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 | 155 | 175 | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 | 155 | 175 | 0 | 0 | 30 | 75 | 20 | 20 | 5 | 5 | 5 | 0 | 5 | 0 | 5 | 0 | 15 | -30 | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | 0 | 20 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 0.8 | -0.95 | 0.95 | 5 | 0.95 | -0.95 | 20 | 80 | 3328 | 88 | 90 | 3 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 5 | 0 | 9 | 0 | 12 | 0 | 14 | 0 | 18 | 0 | 22 | 0 | 5 | 1 | -10 | 10 | 0.85 | 0.9 | 0.95 | 1 | -0.97 | -0.95 | 0.5 | 0 | 0 | 85 | 90 | 95 | 100 | 105 | 110 | 4 | 5 | 135 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 150 | 200 | 75 | 90 | 75 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 50 | 1 | 300 | 1 | 0 | 150 | 1000 | 80 | 60 | 45 | 300 | 0 | 75 | 1.5 | 0 | 0 | 0 | 60 | 0.1 | 0.84 | 60 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 930 | 0 | 5000 | 50 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 500 | 1000 | 1 | 1 | 0 | 0 | 1 | 1 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 0 | 20 | 0.8 | -0.95 | 0.99 | 1 | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 400 | 0 | 0 | 0 | 0 | 1 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -100 | 100 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 0 | 0 | 1 | -0.9 | -100 | 100 | 10 | 0 | 100 | 0 | 100 | 0 | 800 | -20 | 800 | -20 | 600 | 0 | 10 | 2.5 | 0.2 | 3.1 | 0.05 | 1.5 | 1.9 | 0.05 | 0.05 | 120 | 5 | 120 | 5 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 | 100 | -100 | 1 | 30 | 0 | 0 | 20 | 2 | 0 | 2 | 3 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 | 600 | 0.01 | 0.3 | 0.1 | 0.5 | 0.1 | 0.5 | 500 | 1500 | 4.6 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 120 | 2 | 120 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 0 | 0 | 75 | 120 | 2 | 2 | 0 | 0 | 0 | 120 | 120 | 2 | 2 | 0 | 62 | 2 | 1 | 0 | 120 | 120 | 2 | 0.5 | 0 | 1 | 0 | 200 | 200 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 82 | 0 | 0 | 0 | 5 | 20 | 0 | 2 | 30 | 90 | 0 | 0 | 0 | 200 | -200 | 0 | -50 | 100 | -100 | 0 | 0 | 0 | 200 | -200 | 20 | 30 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 9.5 | 10 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 90 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | 25 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 10 | 12 | 12 | 12 | 12 | 15 | 4 | 20 | 7.5 | 22.5 | 0 | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 | 10 | 3 | 42 | 48 | 462 | 60 | 100 | 75 | 50 | 30 | 10 | 13 | 33 | 17 | 17 | 13 | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 | 100 | 15 | 50 | 300 | 1800 | 1800 | 0 | 50 | 50 | 1800 | 1800 | 0 | 50 | 50 | 1 | 0 | 990 | -950 | -650 | 0 | 1000 | 10 | 650 | 80 | 1400 | 100 | 0 | 500 | 40 | 1000 | 80 | 0 | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 4 | 0 | 20 | 4000 | 4000 | 100 | 550 | 25 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 4 | 4 | 4 | 4 | -5 | -5 | -5 | -5 | 8 | 8 | 8 | 8 | 4.5 | 4.5 | 45 | 270 | 90 | -144 | 0 | 80 | 350 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 4 | 500 | 30 | 8000 | 4000 | 8 | 40 | 10 | 0 | 0 | 25 | 1500 | 1.2 | 2 | 50 | 0 | 0 | 100 | 100 | 2 | 100 | 50 | 10 | 25 | 2500 | 1 | 0 | 1 | 0 | 250 | 0 | -24 | -13 | 2175 | 1280 | 10 | 2175 | 1280 | 60 | 0 | 0 | 5 | 5 | 300 | 1 | 220 | 120 | 0 | 0.19531 | 300 | 0.0039 | 2.5 | 1.1 | 50 | 0 | 50 | 0 | 0 | 2669 | 1339 | 4320 | 2190 | 1500 | 1500 | 0 | 50 | 50 | 0 | 400 | 100 | 15 | 5 | 300 | 1 | 220 | 120 | 0 | 0.19531 | 300 | 0.0039 | 2.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 2190 | 1100 | 2950 | 1550 | 1500 | 1500 | 0 | 47 | 44 | 0 | 400 | 100 | 15 | 5 | 300 | 1 | 220 | 120 | 0 | 0.19531 | 300 | 0.0039 | 2.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 2190 | 1100 | 2950 | 1550 | 1500 | 1500 | 0 | 47 | 44 | 0 | 400 | 100 | 15 | 5 | 300 | 1 | 220 | 120 | 0 | 0.19531 | 300 | 0.0039 | 2.5 | 1.1 | 0 | 0 | 0 | 0 | 0 | 2190 | 1100 | 2950 | 1550 | 1500 | 1500 | 0 | 47 | 44 | 0 | 400 | 100 | 0 | 1000 | 600 | 50 | -0.5 | -5 | 120 | 6 | 0 | 1 | 6 | 0 | 0.5 | 45 | 0 | 50 | 0 | 30 | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6 | 0 | 0.5 | 0 | 0 | 120000 | 0 | 120000 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 40 | 100 | 0 | 0 | 0.1 | 100 | 100 | 1 | 6 | 6 | 120 | 50 | 30 | 30 | 15 | 55 | 50 | 50 | 50 | 60 | 35 | 0.1 | 0.01 | 0 | 100 | 0 | 0 | 100 | 100 | 0 | 0 | 1 | 3 | 47 | 49 | 2 | 2 | 62 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14140 | 0 | 1 | 0 | 1 | 20 | 30 | 1 | 183 | 0 | 200 | 0.8 | 110 | 0.2 | -0.2 | 1 | 100 | 0.2 | 100 | 250 | 100 | 100 | 100 | 500 | 50 | 10500 | 110 | 10 | 120 | 4 | 7 | -750 | 3000 | 0 | 0.2 | 100 | 200 | 0 | 80 | 2 | 88 | 45 | 0.5 | 10 | 4 | 3 | 20 | 10 | 5 | 10500 | 10500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 30 | 1 | 0 | 0 | 0 | 0 | 110 | 0.4 | 0 | 0 | 100 | 0.2 | 0 | 100 | 0 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 100 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001 | 0.5 | 100 | 0.1 | 100 | 200 | 0 | 1 | 1.25 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 55 | 70 | 0 | 100 | 35 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 70 | 70 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 150 | 0 | 1 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 30 | 35 | 0 | 100 | 35 | 1.5 | 0.003 | 1 | 1 | 10 | 0.6 | 0 | 1 | 12 | 1 | 1 | 1 | 1 | 0 | 0 | 1.1 | 0.7 | 1 | 0 | 100 | 0 | 0.001 | 0.1 | 0.1 | 0.05 | 100 | 50 | 0 | 1 | 2 | 1 | 1 | 1 | 1 | 0 | 0 | 130 | 110 | 115 | 0 | 100 | 35 | 0 | 0.1 | 0.5 | 0.5 | 100 | 40 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 50 | 0 | 100 | 10 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | [42 empty] | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 1 | 0 | 10 | 10 | 10 | 2 | 5 | 0 | 48 | 50 | 1 | 5000 | 8000 | 5000 | 8000 | 6 | 6 | 0 | 5000 | -5000 | 0 | 0 | 0.02 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 50 | 47 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 1 | 1 | 12 | 2 | 5 | 30 | 30 | 25 | 30 | 35 | 10 | 8 | 30 | 0 | 235 | 235 | 40 | 25 | 232 | 1 | 100 | 40 | 70 | 327 | 327 | 1 | 10 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.3 | 0.3 | 3 | 0.1 | 10 | 0.5 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09478 | 0.44428 | 1.1848 | 100 | 0 | 0.02843 | 0.74047 | 0.4739 | 100 | 0 | 4 | 20 | 818 | 2678 | 100 | 60 | 30 | 0 | 100 | 4 | 20 | 1213 | 2679 | 2 | 2 | 35 | 45 | 1 | -6 | -6 | -6 | -6 | 10 | 50 | 0.1 | 20 | 8 | 40 | 8 | 20 | 300 | 100 | 300 | 50 | 0.3 | -130 | 8 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 2679 | 2679 | 2679 | 2679 | 50 | 0.63 | 0.63 | 0.63 | 0.63 | 0.55 | 0.63 | 0.63 | 0.63 | 0 | 10 | 5 | 95 | 1 | 1 | 102 | 112 | 98 | 91 | 112 | 50 | 65 | 85 | 75 | 5 | 105 | 120 | 95 | 70 | 140 | 1 | 70 | 10 | 85 | 0 | 25 | 3.45 | 1 | 10 | 80 | 100 | 60 | 10 | 4 | 4 | 4 | 4 | 58 | 51 | 51 | 51 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 16 | 32767 | 3300 | 120 | 120 | 120 | 130 | 35 | 1000 | 125 | 16 | 3700 | 10 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [60 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [20 empty] | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [60 empty] | 22 | 22 | 25 | 25 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 50 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1450 | 10 | 200 | 400 | 2800 | 5 | 400 | 0 | 3450 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 0 | 1500 | 0 | 0 | 0 | 0 | 5 | 1 | 90 | 3 | 35 | 10 | 3 | 200 | 0 | 40 | 60 | 35 | 10 | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 | 100 | 1 | 0 | 0 | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 800 | 0 | 0.15 | 0.64 | 7.7 | 100 | 0 | 0 | 20 | 0 | 1500 | 1495 | 1 | 0 | 0 | 1740 | 10 | 800 | 10 | 1505 | 1 | 250 | 10 | 100 | 2 | 1500 | 6.7 | 0 | 85 | 85 | 85 | 95 | 95 | 9.54 | 9.971 | 720 | 0 | 0 | 1.4 | 1.5 | 30 | 75 | 9.54 | 9.971 | 720 | 0 | 0 | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 | 0 | 0 | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 | 0 | 0 | 1.55 | 1.75 | 30 | 75 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | -30 | 1200 | 1400 | 0.4 | 0.4 | 1.25 | 100 | 30 | 0.74 | 1 | 20 | 21 | 24 | 9 | 12 | 25 | 32 | 1 | 8 | 13 | 24 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1 |  | System.Byte[] |  | System.Byte[] |  | System.Byte[] |  | System.Byte[] |  | System.Byte[] |  | System.Byte[] |  | System.Byte[] |  | System.Byte[] | [8 empty] | 18 | 18 | 10 | 11 | 1 | 1 | 0 | 2 | 0 | 2 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2681 | 2676 | 2679 | 2679 | 0 | 0 | 0 | 0 | 0 | 2679 | 2679 | 0 | 2676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.2 | 11.6 | -28.33 | 4.449 |  | 0.86909 | 0 | 0.55 | 2679 | 0 | 0 | 0 | 55 | 561 | 0 | 0 | 158 | 164 | 121 | 99 | 61 | 36 | 41 | 33 | 367 | 347 | 298 | 298 | 134 | 52 | 43 | 40 | 0 | 73.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 369 | 366 | 380 | 379 | 381 | 378 | 378 | 380 | 0 | 0 | 0 | 378 | 0 | 0 | 0 | 0 | 0 | 376 | 380 | 378 | 379 | 380 | 376 | 383 | 526 | 524 | 0 | 529 | 525 | 527 | 528 | 526 | 0 | 0 | 0 | 523 | 0 | 0 | 0 | 0 | 0 | 0 | 524 | 523 | 0 | 521 | 523 | 528 |  | Sending | 30 | 41 | 42 | 41 | 42 | 41 | 42 | 40 | 42 | 40 | 41 | 41 | 41 | 41 | 42 | 41 | 41 | 41 | 41 | 42 | 41 | [24 empty] | 1176 | 1516 | 1302 | 1100 | 3150 | 1089 | 1117 | 1391 | 1105 | 3151 | 1185 | 1045 | 1258 | 1116 | 1145 | 3008 | [8 empty] | 14 | 47 | 1 | 4332 | 17.4714 | 22.656 | 7 | 100 | 5 | 74.4343 | 7 | 100 | 77 | 266.7006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 162.3 | 0 | 0 | 0 | 1119 | 0 | 0 | 0 | 8.3 | 0 | 0 | 0 | 1.848 | 1.872 | 1.872 | 1.872 | 67.2 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 1 | 5601 | 1 |  | 1 | 5601 | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 | [16 empty] | 0 | 7.78 | 0.05 | 8.35 | 0 | 7.62 | 0.2 | 8.2 | 0 | 7.8 | 0 | 7.89 | 0 | 7.98 | 0 | 7.85 | 0 | 7.74 | 0 | 7.83 | 0 | 7.81 | 0 | 7.7 | 0 | 7.64 | 0 | 7.67 | 0 | 7.85 | 0 | 7.5 | [16 empty] | 0 | -0.1 | 0.2 | 0.1 | 0 | -0.03 | 0.2 | 0 | 0 | -0.3 | 0 | -0.05 | 0 | -0.13 | 0 | -0.11 | 0 | -0.18 | 0 | -0.28 | 0 | -0.12 | 0 | -0.15 | 0 | -0.12 | 0 | -0.33 | 0 | -0.1 | 0 | -0.39 | [16 empty] | 0 | 7.64 | 0.3 | 8.4 | 0 | 7.69 | 0.1 | 8.2 | 0 | 7.67 | 0 | 7.97 | 0 | 7.94 | 0 | 7.84 | 0 | 7.78 | 0 | 7.68 | 0 | 7.84 | 0 | 7.85 | 0 | 7.72 | 0 | 7.69 | 0 | 7.92 | 0 | 7.5 | [16 empty] | 0 | -0.47 | 0.1 | 0.1 | 0 | -0.22 | 0 | 0 | 0 | -0.21 | 0 | -0.27 | 0 | -0.08 | 0 | -0.22 | 0 | -0.1 | 0 | -0.36 | 0 | -0.04 | 0 | -0.35 | 0 | -0.19 | 0 | -0.18 | 0 | -0.32 | 0 | -0.19 | [16 empty] | 0 | 0 | 1 | 1 | 1 | 17 | 0 | 100 | 0 | 0 | 0 | 0 | 37.8 | 0 | 0 | 0 | 0 | 0 | 0 | 4.36 | 4.33 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 100 | 100 | 37.8 | 37.8 | 37.8 | 37.8 | 4.301 | 1500 | 1499 | 23.8 | 45 | 0 |  | 0 | 0 | REGENSBURG
2 | No Contact | 54 | 1.014 | 0 | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","rem_conn":"Prim-SSL-NoProxy","dataItems":"4849/9200","agent_conn":"Prim-SSL-NoProxy","mon_conn":"Back-SSL-NoProxy"} | 0 | 0 | 0 | 0 | 0 | 0 | -0.92 | 5.95 | 0 | 0 | 0 | -1282 | 0 | 6.2 | 0 | 4.54 | 4.61 | -3270 | 0 |  |  |  | 0 | 0 |  | 0 | 5.32 |  | 5.31 |  |  |  | 4.3.0.17 | 941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 1 | 1 | 1 | 0 |  |  | 0 | 0 |  | 0 |  |  |  | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0.11 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1771 | 4686 | 29686 | 1771 | 21 | 21 | 1771 | 794894 | 30314 | 30277 | 30277 | 43 | 811 |  | 51.9 | 0 | 65 | 65.4 | 4 | 72 | 65.5 | 0 | 28 | -3270 | 0 | 0.999 | 1.002 | 25 | 90 | 89.7 | 100 | 50 | 51.9 | 0 | 75 | 82.2 | 0 | 72 | 65.4 | 0 | 6.3 | 6.3 | 81.5 | 20 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.5 | 0 | 0 | 0 | [53 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 4.2 | 22.5 | 8.5 | 12.7 | 17 | 21.2 | 24.9 | 19.7 | 21.3 | 10.1 | 0 | 0 | 4.2 | 22.5 | 1 | 0 | 8.5 | 0 | 12.7 | 0 | 17 | 0 | 21.2 | 1 | 24.9 | 1 | 19.7 | 1 | 21.3 | 1 | 10.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 30257 | 0 | 0 | 0 | 0 | 0 | 5110 | -0.4 | 20.1 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 400 | 400 | 399 | 124.3 | 500 | 600 | 0 | 0 | 0 | 120.8 | 0 | 0 | 0 | 118.7 | 0 | 0 | 0 | 382 | 388 | 0 | 0 | 0 | 0 | 10.7 | 0 | 0 | 0 | 10.7 | 0 | 0 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1608894235474 | 0 | 60 | 1 | 1 | 0 | 0 | 22 | 16.49 | 0.8 |  | 5106 |  |  |  |  | 28 | 58 | 0 | 0 | 38026 | 38047 | 35973 | 36234 | 0 | 0 | 328 | 324 | 556 | 556 | 560 | 558 | 555 | 561 | 558 | 561 | 561 | 560 | 557 | 558 | 552 | 552 | 559 | 559 | 557 | 557 | 561 | 556 | 557 | 555 | 556 | 555 | 557 | 557 | 561 | 561 | 553 | 552 | 0 | 0 | 0 | 335 | 333 | 9 | [42 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.9 | 40.9 |  |  | 52.4 | 51.4 | 60.7 | 28.8 | 54.1 | 41.1 | 52.6071 | 39.888 | 1 | 1606606418777 |  | 4441 | -0.998 | 50.01 | 0 | 21031 | 12090 | 21050 | 12088 | 21079 | 12289 | 10965 | 6327 | 10982 | 6359 | 10962 | 6302 | 0 | 11025 | 3675 | 3 | 0.016 | 200 | 2.3 | -52.7 | 4.5 | 0.82 |  | 0 | 82.2 | 71.8 | 0 | 65.4 | 65.5 | 65.4 | 0 | 0 | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 60.5 | 58.8 | 59.1 | 61.8 | 51.7 | 51.2 | 59.7 | 58.5 | 61.7 | 52.7 | 59.7 | 60.6 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 9113.9 | 30358.1 | 14045.6 | 30358.1 | 30358.3 | 30358.4 | 30348.6 | 30350.8 | 30358.1 | 30358.1 | 30358.1 | 30358.1 | 2019 | 2016 | 4 | 2 | 2015 | 7 | 7 | 2016 | 4 | 2 | 22 | 4 | 2016 | 4 | 2 | 2016 | 4 | 2 | 2015 | 2 | 10 | 2016 | 24 | 3 | 2016 | 4 | 2 | 2016 | 2 | 2 | 2016 | 3 | 2 | 2016 | 4 | 2 | 46141 | 27977 | 23295 | 27917 | 27936 | 27953 | 25653 | 29204 | 27938 | 27787 | 27828 | 27978 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | 253 | 174 | 110 | 205 | 174 | 126 | 189 | 269 | 189 | 220 | 174 | 174 | 158 | 220 | 126 | 174 | 158 | 141 | 220 | 110 | 174 | 237 | 189 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415 | 317 | 378 | 402 | 402 | 305 | 305 | 390 | 231 | 317 | 366 | 293 | 549 | 341 | 305 | 329 | 329 | 366 | 268 | 366 | 231 | 244 | 402 | 329 | -0.038 | 5.94 | 0 | 0 | 0 | 0 | 8 | 7.69 | 7.71 | 7.82 | 7.63 | 7.78 | 7.76 | 7.65 | 7.72 | 7.75 | 7.88 | 7.68 | 7.8 | 7.92 | 7.87 | 7.71 | 7.77 | 7.88 | 7.86 | 7.79 | 7.76 | 7.89 | 7.91 | 7.73 | -0.13 | -0.19 | -0.35 | 0.4 | -0.31 | -0.5 | -0.33 | -0.06 | -0.32 | -0.49 | -0.22 | -0.48 | 0.32 | 0.34 | 0.3 | -0.11 | -0.27 | -0.3 | 0 | -0.5 | 0.26 | -0.28 | 0.36 | -0.14 | 7.9 | 7.77 | 7.84 | 7.86 | 7.81 | 7.69 | 7.86 | 7.75 | 7.63 | 7.83 | 7.83 | 7.68 | 7.82 | 7.95 | 7.8 | 7.81 | 7.77 | 7.84 | 7.85 | 7.68 | 7.71 | 7.76 | 7.77 | 7.79 | -0.18 | -0.34 | -0.27 | -0.31 | -0.34 | -0.23 | -0.32 | -0.25 | -0.45 | -0.42 | -0.27 | -0.16 | 0.32 | 0.19 | 0.43 | 0.31 | 0.45 | -0.01 | -0.16 | 0.48 | 0.17 | -0.28 | -0.17 | 0.41 | 132648.5 | 0 | 5168.1 | 0 | 235 | 0.02 | 0 | -245 | 1.02 | 0 | 10968 | 4.3.0.0.5 | 4.3.0.1.0 | 4.3.0.0.0 | 4.3.0.0.1 | 4.3.0.0.2 | 4.3.0.14.12 | 4.7.1.0.0 | 4.3.0.0.16 | 4.3.0.0.12 | 4.3.0.0.16 | 4.3.0.0.5 | 4.3.0.0.11 | 4.3.0.0.5 | 4.3.0.1.5 | 4.3.0.0.13 | 4.3.1.9.14 | 4.3.0.0.1 | 4.3.0.0.8 | 4.3.0.0.0 | 4.3.0.0.8 | 4.3.0.0.16 | 4.3.0.0.0 | 0.0.0.0.0 | 4.3.0.6.15 | 4.3.0.0.0 | 4.3.0.0.17 | 4.3.0.0.13 | 4.3.0.0.0 | 4.3.0.0.6 | 4.3.0.0.0 | M01 | 24.9 | 29.5 | 17.8 | 25.7 | 28.5 | 31.6 | 29.9 | 25.5 | 28 | 27.3 | 13.7 | 11.1 | 28.8 | 28.4 | 30.2 | 13.9 | 24.5 | 19.8 | 30.5 | 27.6 | 28.3 | 29.5 | 25 | 17.6 | 25.4 | 31.6 | 11.1 | 1419 | [82 empty] | Running | 50 | SERVICE SELECTOR SWITCH MAN - NOT READY TO START |  |  |  | 37.46 | 2 | 2 |  | 50.01 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 0 | 0 | 970 | 40 | 0 | [6 empty] | 0 | 9 | 0 | 0 | 1 | 0 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 30 | 30 | 0 | 1.4 | 20 | 1.5 | 80 | 4 | 0 | 11 | 0 |  |  |  |  | 7 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 30 | [5 empty] | 0 | 0 | 1 | 120 |  | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 200 | -1000 |  | -200 | -1950 | 10 | 0 | 50 | 1300 | 5.9 | 6.7 | 7 | 0.1 | 0 | 0.1 | 1 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 0 |  | 0 | 0 | 0.2 | 0 |  | 10 | 0 |  |  |  | 0 |  | 5 | 5 | 5 | 5 | 5 | 60 | 28 | 40 | 30 | 50 | 180 | 28 | 40 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 |  |  | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 |  |  | 10 | 2 |  |  | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 |  |  | 10 | 2 |  |  | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | [9 empty] | 0 | 2 | 10 | [479 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 3 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 |  | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 20 | 20 | 20 | 20 | 17 | 18 | 18 | 18 | 10 | 0 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 0 | 0 | 0 | [9 empty] | 4000 |  |  | 30 | 8 | 10 | 35 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | [11 empty] | 0 |  |  | 235 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 5 | 30 | 0 | 0 | 0 | 0 | 0 | 15 | 60 | 0.95 | 0 |  |  | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | 85 | 110 | 90 | 95 | 100 | 105 | 0.85 | 0.9 | 0.95 | 1 | -0.97 | -0.95 | 0 | 1 | 1 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  |  |  | 0 | 30 | 30 | 10 | 10 | 10 | 3 | 1 | 10500 | 0 | 0 | 0 | 0 | 1 |  | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 51.5 | 47.5 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1400 | 0 | 1 | 0 | 0 | 60 | 30 | 8 | 1 | 115 | 85 | 35 | 10 | 0 | 0 | 1 | -0.4 | 50 | 110 | 80 | 1 | 0 | 301 | 200 | 1 | 200 | 10 | 2 | 0.8 | 3 | 4 | 10 | 0.5 | 4 | 20000 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 20000 | 120 | 88 | 45 | 0 | 10 | 0 | 0 | 0 | -0.4 | 50 | 110 | 80 | 0 | 1 | 400 | 200 | 0 | 100 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 90 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 6000 | 250 | 100 | 50 | 80 | 500 | 100 | 400 | 0 | 0 | 0 | 50 | 10 | 0 | 0 | 0 | 1 | 0 | 5 | 0 | 30 | 60 | 0 | 0 | 0 | 30 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  |  |  | 1 | 1 |  |  | 0 | 1 | 0 | 1 | 1 |  | 1 | 1 | 0 |  | 1 | 0 | [8 empty] | 1 | 1 |  | 1 | 0 |  |  | 0 |  | 0 | 0 | 1 | 1 |  | 1 | 1 | 1 | 1 |  | 0 |  |  |  | 1 |  | 624 |  |  |  |  | 11 | 0 | 527 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.3 | 10 | 1 | 100 | 90 | 0 | 0 | 9 | 100 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 55 | 40 | 100 | 100 | 0 | 0 |  |  | 15 | [25 empty] | 0 | 0 | 9600 | 2 | 16 | 116 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 200 | 168 | 75 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 4 | 1 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1 | 65 | 1 | 0 | 0 | 0 | -2.5 | 10 | 0 | 20 | 15 | 0 | 2 | 1 | 1.82 | 0.7 | 0.7 | 1 | -150 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | [6 empty] | 0 | 0 | 0 | 0 | [7 empty] | 0.5 | 0.45 | 0.45 | 0.45 |  |  | 0 | 0.5 | 700 | [8 empty] | 12.5 |  |  | 2.2 | 12.5 | 0 | [15 empty] | 0 | 50 | 50 | 50 | 50 | 50 | 120 | 1 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 0 | 1 | 4 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.09375 | 3.6621 | 25 | 2.9297 | 100 | 0 | 10 | 0.1 | 0.5 | 1 | 7 | 100 | 0 | 25 | 10 | 250 | 6 | [12 empty] | 1 | 1 | 4000 | 2000 | 20000 | 10000 | 4404 | 2202 | 8 | 4 | 2 | 1 | 30 | 150 | 20 | 120 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 0 | 5 | 5 | 1000 | 160 | 5 | 5 | 1000 | 130 | 250 | 100 | 0 | 100 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 | 1.5 | 1 | 650 | 700 | 0 | 0 | 0 | 0 | 0 | 17 | 5 | 7 | 8.5 | 10 | 12 | 13.5 | 15.3 | 25 | 25 | 60 | 0 | 30 | 0 | 1 | 6 | 0.8 | 6 | 0 | 3.5 | 1 | 6 | 0 | 10 | 92 | 0 | 8000 | 0 | 0 | 540 | 27 | 1000 | 0 | 0 | 1 | 300 | 0 | 300 | 0 | 3 | 300 | 0 | 150 | 8.2 | 7.5 | 180 | 90 | 900 | 30 | 200 | 300 | 40 | 20 | 100 | 0 | 100 | 0 | 0 | 300 | 500 | 600 | 0 | 500 | 600 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 1 | 1 | 1200 | 38000 |  |  |  | 44800 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 100 | 600 | 680 | 640 | 5 | 650 | 5 | 380 | 640 | 5 | 650 | 5 | 1000 | 5 | 15 | 300 | 20 | 50 | 650 | 5 | 160 | 5 | 300 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.6 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 |  |  |  |  | 100 |  | 10 | 3 |  | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 10 | 20 | 5 | 12 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | 0 | 20 |  | 0.98 | 1 | -0.98 | -0.95 | 0.8 | -0.8 | 0.99 | 5 | 0.95 | -0.95 | 20 | 80 | 5467 | 90 | 90 | 2.17 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 0 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 85 | 90 | 85 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 145 | 5 | 5 | 1 | 50 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 45 | 300 |  | 75 | 1.91 | 1 | 0 | 0 | 60 | 0.1 | 1.11 | 60 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 930 | 1 | 5000 | 50 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 3.85 | 19.95 | 0 | 4410 | 1 | 1 | 0 | 1 | 1 | 2 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 4 | 20 | 0.8 | -0.95 | 1 | 0 | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 400 | 0 | 0 | 0 | 0 | 1 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -100 | 100 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 0 | 0 | 1 | -0.9 | 3300 | -3300 | 10 | 0 | 100 | 0 | 100 | 0 | 800 | -20 | 800 | -20 | 0 | 0 | 10 | 3.3 | 0.2 | 3.1 | 0.05 | 1.5 | 1.5 | 0.05 | 0.05 | 120 | 5 | 120 | 5 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 30 |  |  | 20 |  |  |  | 3 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.6 | 0.2 | 0.5 | 500 | 1500 | 3.5 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1.5 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 120 | 2 | 120 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 1 | 0 | 80 | 120 | 2 | 2 | 0 | 1 | 0 | 80 | 120 | 2 | 2 | 1 | 50 | 2 | 1 |  | 80 | 120 | 0.5 | 0.5 | 0 | 1 | 0 | 99 | 200 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 |  |  |  | 2 | 82 | 0 | 0 | 0 | 5 | 20 | 1 | 4 | 30 | 90 | 0 | 0 | 0 | 200 | -200 | -1 | -70 | 100 | -100 | 0 | 0 | 0 | 200 | -200 | 20 | 8 | 0 | 2 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | [13 empty] | 0 | 0 | 50 | 100 |  |  |  | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 |  | 0 | 0 | 0 | 0 | 1 | 0 | 10 | 0 | 0 | 1 | 60 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 18 | 18 | 18 | 18 | [5 empty] | 1 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 924 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 0 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 0 | 0 | 20 | 0 | 4404 |  | 850 | 30 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 2 | 2 | 5 | 5 | -5 | -5 | -5 | -5 | 13 | 13 | 13 | 13 | 4.5 |  | 45 | 270 | 70 | -144 | 0 | 80 | 350 | [24 empty] | 0 | 4 | 500 | 30 |  | 2000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 380 | 1 | -30 | -9 | 4300 | 1300 | 10 | 4300 | 2600 | 60 | 0 | 0 | [6 empty] | 0.0007 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4408 | 2198 | 5876 | 2981 | 1499 | 1499 |  | 51.5 | 49.8 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4900 | 2150 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4900 | 2150 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4900 | 2150 | 1500 | 1500 |  | 50 | 50 |  | 660 |  | 0 | 1000 | 300 | 48 | -1.6 | -4 | 100 | 10 | 0 | 1 | 10 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 0 | 0 | 0 | 0 | 0 |  | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 10 | 0 | 0.5 | 0 | 0 | 60000 | 0 | 60000 | 0 |  | 4 | 0 | 1 | 1 |  |  |  | 85 |  | 48 | [14 empty] | 50 | 50 | 50 | 50 | [10 empty] | 0 | 0 | 1 | 3 | 57 | 59 | 2 | 2 | 65 |  | 40 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.4 |  |  | 100 | 0.2 |  | 345 | 200 | 200 | 100 | [8 empty] | -1225 | 4900 |  | 0.2 | 100 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.4 |  |  | 100 | 0.2 |  | 100 |  | 100 | 100 | [11 empty] | 0.2 | 100 | 200 | [43 empty] | 0 | 0.3 | 100 | 0.01 | 100 | 44 | 0 | 0 | 4 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 60 | 65 | 0 | 100 | 0 | 0 | 0.1 | 100 | 0.02 | 100 | 80 | 0 | 1 | 4 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 75 | 67 | 72 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 1.5 | 0 | 1 | 1 | 10 | 0.6 | 0 | 1 | 12 | 1 | 1 | 1 | 1 | 0 | 0 | 1.1 | 0.7 | 1 | 0 | 100 | 0 | 0 | 0.5 | 100 | 0.01 | 100 | 120 | 0 | 1 | 4 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 80 | 90 | 0 | 100 | 20 | 0 | 0.1 | 0.5 | 0.5 | 100 | 40 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 50 | 0 | 100 | 10 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 10000 | 10000 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0 | 0.1 | 100 | 80 | 0 | 1 | 2.5 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 50 | 100 | 0.1 | 72 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 10000 | 10000 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | 0 | 0.2 | 1 | 1 | 5 | 50 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 7 | 0 | 100 | -100 | 0 | 0.1 | 5 | 5 | 10 | 10 | 0 | 0 | 2 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 0 | 15 | 0 | 100 | -100 | 0 | 0.1 | 100 | 20 | 0 | 0 | 15 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 6.3 | 0 | 100 | 0 | [80 empty] | 0 | 0.2 | 100 | 10 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 2 | 2 | 0 | 0 | 21 | 19 | 100 | 100 | 20 | 0 | 0.5 | -0.5 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 1 | 0 |  |  |  |  | 12 | 2 | 5 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 70 | 0 | [6 empty] | 0.01421 | 0.29619 | 0.53314 | 100 | 0 | 0 | 0.44428 | 0.23695 | 100 | 2 | 0 | 20 | 5000 | 5000 | 60 | 75 | 90 | 100 |  | 0 | 20 | 2202 | 4404 | 2.5 | 2 | 30 | 45 |  | -2 | -2 | -2 | -2 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -145 | 10 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 4404 | 4404 | 4404 | 4404 | 50 | 0.58 | 0.72 | 0.72 | 0.72 | 0.58 | 0.72 | 0.72 | 0.72 |  | 10 | 17 | 95 | 1 | 1 | 100.4 | 102.9 | 98 | 91 | 100.1 | 50 | 65 | 85 | 80 |  | 110 | 125 | 90 | 70 | 140 | 0 | 80 | 18 | 81 | 1 | 20 | 5.55 | 0 | 0 | 120 |  |  | 10 | 8 | 4 | 4 | 4 | 56 | 56 | 56 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3300 | 0 | 0 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3300 | 10 | 120 | 5000 | 5000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [30 empty] | 5 | 5 | 5 | 10 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1650 | 10 | 200 | 400 | 2800 | 5 | 10000 | 0 | 3850 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 0 | 1500 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 800 |  | 0.16406 | 2.1973 | 4.3945 | 95 | 2 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1500 | 6.7 | 0 | [5 empty] | 9.54 | 9.971 | 720 |  |  | 1.4 | 1.6 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.1 |  |  | 0.6 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [28 empty] | 1 | 1 | 1 | 2 | 2 | 0 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4435 |  |  | 4404 | 0 | 0 | 0 | 0 | 0 | 4404 | 4404 |  |  | 3.14 | 3.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | -52.36 | 4.5 | 0.027 | 0.81373 | 0 | 0.58 | 4404 | 0 | 0 | 2.25 |  | 0 |  | 0 | 169 | 76 | 162 | 145 | 126 | 256 | 241 | 188 | 405 | 372 | 259 | 259 | 210 | -200 | -184 | -132 |  | 58.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 369 | 370 | 377 | 381 | 370 | 369 | 369 | 367 | 367 | 0 | 374 | 383 | 373 | 369 | 368 | 0 | 370 | 370 | 373 | 367 | 370 | 368 | 369 | 495 | 495 | 496 | 495 | 489 | 0 | 505 | 503 | 0 | 491 | 502 | 0 | 497 | 508 | 507 | 501 | 508 | 496 | 498 | 0 | 488 | 488 | 492 | 495 |  | Sending | 30 | 59 | 60 | 58 | 59 | 59 | 59 | 59 | 58 | 59 | 58 | 58 | 58 | 58 | 59 | 59 | 59 | 58 | 59 | 59 | 59 | 24.301 | 32.5977 | 30.5 | 32.7 | 31.4 | 29.2 | 29.2 | 29.001 | 29.2011 | 29.6022 | 27.3 | 29.6022 | 28.601 | 29.401 | 30.6008 | 30.701 | 33.5478 | 31.3012 | 29.5008 | 24.9986 | 28.3 | 30.7 | 31.0011 | 29.8 | 467 | 1297 | 848 | 595 | 55 | 469 | 887 | 631 | 719 | 2132 | 2277 | 330 | 593 | 379 | 1898 | 976 | 3224 | 452 | 631 | 596 | 483 | 1013 | 1565 | 887 |  | 21 | 1 | [11 empty] | 68 | 69.6 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 299.5 | 0 | 0 | 0 | 1017 | 0 | 0 | 0 | 10.4 | 0 | 0 | 0 | 1.883 |  |  |  | 31.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 17167 | 1 | 17167 | 1 | 17167 | 1 | 17167 | 1 | 30182 | 1 | 30182 | 1 | 30182 | 1 | 6829 | 1 | 30182 | 1 | 30182 | 1 | 30182 | 1 | 6829 | 1 | 6829 | 1 | 30182 | 1 | 30182 | 1 | 6829 | 1 | 6829 | 1 | 30182 | 1 | 30182 | 1 | 30182 | 1 | 30182 | 1 | 30182 | 1 | 30182 | 1 | 30182 | 1 | 0.2 | 7.4 | 0.4 | 7.3 | 0.4 | 7.3 | 0.3 | 7.4 | 0 | 7.63 | 0 | 7.78 | 0 | 7.76 | 0 | 7.3 | 0 | 7.72 | 0 | 7.75 | 0 | 7.88 | 0 | 7.3 | 0 | 7.3 | 0 | 7.92 | 0 | 7.87 | 0 | 7.3 | 0 | 7.2 | 0 | 7.88 | 0 | 7.86 | 0 | 7.79 | 0 | 7.76 | 0 | 7.89 | 0 | 7.91 | 0 | 7.73 | -0.01 | 0.01 | -0.01 | 0.01 | -0.01 | 0.01 | -0.01 | 0.01 | 0 | -0.31 | 0 | -0.5 | 0 | -0.33 | 0 | 0 | 0 | -0.32 | 0 | -0.49 | 0 | -0.22 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | -0.3 | 0 | 0 | 0 | -0.5 | 0 | 0.26 | 0 | -0.28 | 0 | 0.36 | 0 | -0.14 | 0.3 | 7.4 | 0.4 | 7.3 | 0.2 | 7.4 | 0.8 | 7.5 | 0 | 7.81 | 0 | 7.69 | 0 | 7.86 | 0 | 7.3 | 0 | 7.63 | 0 | 7.83 | 0 | 7.83 | 0 | 7.3 | 0 | 7.3 | 0 | 7.95 | 0 | 7.8 | 0 | 7.2 | 0 | 7.3 | 0 | 7.84 | 0 | 7.85 | 0 | 7.68 | 0 | 7.71 | 0 | 7.76 | 0 | 7.77 | 0 | 7.79 | -0.01 | 0.01 | -0.01 | 0.01 | -0.01 | 0.01 | 0.19 | 0.01 | 0 | -0.34 | 0 | -0.23 | 0 | -0.32 | 0 | 0 | 0 | -0.45 | 0 | -0.42 | 0 | -0.27 | 0 | 0 | 0 | 0 | 0 | 0.19 | 0 | 0.43 | 0 | 0 | 0 | 0 | 0 | -0.01 | 0 | -0.16 | 0 | 0.48 | 0 | 0.17 | 0 | -0.28 | 0 | -0.17 | 0 | 0.41 |  | 0 | 0 | 1 | 1 | 17 | 0 | 100 | 95.6 | 99.1 | 0 | 0 | 16.7 | 16.9 | 0 | 16.9 | 0 | 0 | 0 | 5.9 |  | 0 | 0 | 0 | 0 |  | 100 | 100 | 100 | 100 | 16.7 | 16.7 | 16.7 | 16.7 |  | 1500 | 1499 | 15.1 | 51.9 |  |  | 0 | 0 | ROCHE PENZBERG KWKK
3 | No Contact |  |  |  | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","rem_conn":"Prim-NoSSL-NoProxy","dataItems":"4393/8388","agent_conn":"Prim-SSL-NoProxy","mon_conn":"Prim-SSL-NoProxy"} | 0 | 0 | 0 | 0 | 0 | 0 | -0.92 | 4.05 | 0 | 0 | 0 | -374 | 0 | 6.96 | 0 | 3.01 | 3.86 | 26.6 | 0 |  |  |  | 0 | 0 |  | 0 | 5.52 |  | 5.52 |  |  |  | 4.3.0.13 | 4909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | NL South | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.06 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31454 | -112 | 788 | 9759 | 5759 | 856741 | 698260 | 798260 | 30241 | 30241 | 30241 | 6808 | 771 |  | 51.2 | 0 | 73 | 72.6 | 7.5 | 70 | 0 | 0 | 28 | 26.6 | 48.5 | 1 | 1.001 | 25 | 95 | 95 | 75.8 | 50 | 51.2 | 0 | 75 | 88.6 | 0 | 75 | 75.9 | 24.7 | 20 | 0 | 40 | 0 | 0 | 0 | 95 | 95.2 | 72.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153.1 | 393.2 | 150 | 87.1 | 42.8 | 0 | 36.9 | 36.8 | 38.7 | [53 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [99 empty] | 40.2994 | 40.167 | [30 empty] | 0 |  | 0 | [10 empty] | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | [7 empty] | 0 |  |  | 0 | 0 |  |  |  | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1608901006835 | 0 | 43 | 1 |  | 0 | 0 |  | 39.89 | 1.1 |  | 8464 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 407 | 548 | 544 | 551 | 557 | 557 | 554 | 555 | 554 | 549 | 545 | 548 | 548 | 548 | 545 | 551 | 547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 550 | 557 | 557 | 544 | 544 | 0 | 401 | 0 | 0 | 0 | 13 | [42 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.1 | 34.3 |  |  | 79 | 76.4 | 75.9 | 29.5 | 35.1 | 35.6 | 34.6643 | 22.9745 | 1 |  |  | 2697 | -0.999 | 50 | 0 | 15553 | 8991 | 15559 | 8974 | 15574 | 8989 | 10407 | 6014 | 10415 | 6012 | 10398 | 6004 | 0 | 8330 | 2776 | 3 | 0.074 | 700 | 2.13 | -25.7 | 4.03 | 0.7 |  | 0 | 88.6 | 78.4 | 0 | 72.6 | 0 | 73.1 | 2 | 0 | 0 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.7 | 0 | 0 | 0 | 65.7 | 65.1 | 69.2 | 53.2 | 67.8 | 73.6 | 83.2 | 0 | 1.26 | 0 | 0 | 0 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 88 | 0 | 0 | 0 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 0 | 11689.4 | 0 | 0 | 0 | 30357.9 | 30312 | 30358.1 | 30357.4 | 30357.7 | 30358 | 30357.6 | 0 | 2018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 2016 | 16 | 8 | 2016 | 16 | 8 | 2016 | 17 | 8 | 2016 | 16 | 8 | 2016 | 12 | 1 | 2016 | 15 | 8 | 2016 | 16 | 8 | 0 | 0 | 0 | 38660 | 0 | 0 | 0 | 31524 | 31548 | 31596 | 31561 | 31549 | 31478 | 31537 | 0 | 7.73 | 0 | 0 | 0 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 166 | 0 | 0 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | -5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 126 | 174 | 141 | 110 | 158 | 141 | 126 | 94 | 94 | 141 | 141 | 94 | 126 | 174 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1587 | 1391 | 732 | 1123 | 1355 | 1050 | 1880 | 1465 | 1575 | 439 | 695 | 1111 | 1196 | 757 | 1037 | 1013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.003 | 4.24 | 0 | 0 | 0 | 0 | 7.62 | 7.5 | 7.72 | 7.71 | 7.66 | 7.55 | 7.5 | 7.56 | 7.64 | 7.52 | 7.58 | 7.72 | 7.53 | 7.71 | 7.58 | 7.6 | [8 empty] | -0.29 | -0.38 | -0.14 | -0.38 | -0.19 | -0.02 | -0.31 | -0.22 | -0.3 | -0.28 | -0.27 | -0.22 | -0.18 | -0.13 | -0.49 | -0.17 | [8 empty] | 7.72 | 7.63 | 7.67 | 7.73 | 7.89 | 7.87 | 7.73 | 7.74 | 7.64 | 7.65 | 7.66 | 7.69 | 7.69 | 7.51 | 7.65 | 7.77 | [8 empty] | -0.13 | -0.33 | -0.45 | -0.13 | -0.26 | -0.11 | -0.36 | -0.24 | -0.37 | -0.21 | -0.39 | -0.19 | -0.25 | -0.13 | 0.31 | -0.1 | [8 empty] | 79646.2 | 0 | 3787.7 | 0 | 149 | 0.02 | 0 | -102 | 1.02 | 0 | 10398 | 4.3.0.0.5 | 4.3.0.2.0 | 4.3.0.0.0 | 4.3.0.1.1 | 4.3.0.0.2 | 4.3.0.5.12 | 4.3.1.0.0 | 4.3.0.0.12 | 4.3.0.0.12 | 4.3.0.1.11 | 4.3.0.0.5 | 4.3.0.0.11 | 4.3.0.0.5 | 4.3.0.0.5 | 4.3.0.0.13 | 4.3.1.2.13 | 4.3.0.1.1 | 4.3.0.0.8 | 4.3.0.0.0 | 4.3.0.0.8 | 4.3.0.0.12 | 4.3.0.0.0 | 0.0.0.0.0 | 4.3.0.0.10 | 4.3.0.0.0 | 4.3.0.0.12 | 4.3.0.0.13 | 4.3.0.0.0 | 4.3.0.0.1 | 4.3.0.0.0 | M02 | 22.4 | 18.2 | 19.5 | 27.9 | 28 | 26 | 15.5 | 24.5 | 23.5 | 20.6 | 26.8 | 23.7 | 15.2 | 27.3 | 14.7 | 22.1 | 26.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.3 | 14.4 | 1653 | [30 empty] | -1 | 3 | 1 | NaN | 0.0001 | 1606755251000 | 1 | 1 | 0.2025 | 1 | NaN | 2875 | 7 | 1606176000000 | NaN | NaN | NaN | 0.05 | 6.05 | 6 | 1198718 | 1 | 0.0006 | 1 | 1 | 1 | 2 | 181 | 0 | 2614 | 5 | 0.0315 | 1 | 1606749000000 | 2 | 1 | 2 | 1.87 | 4.7 | 1021398 | 1 | 1 | 29485 | 1 | 14.5 | 134 | 0.05 | 0.0386 |  |  |  |  | Running | 50 |  | 0 | 0 | 21086 | 39.01 | 2 | 2 | 0 | 50 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 0 | 0 | 970 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 9 | 0 | 0 | 1 | 0 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 30 | 30 | 0 | 1.4 | 20 | 1.5 | 80 | 4 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 15 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 35 | [5 empty] | 0 | 0 | 1 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 0 | 0 |  | -600 | -600 | 6 | 0 | 50 | 1300 | 3 | 3.7 | 3.9 | 0.1 | 2.7 | 0.1 | 0 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 3.8 |  | 9 | 8 | 0 | 3 |  | 10 | 0 |  |  |  | 0 |  | 5 | 5 | 5 | 5 | 5 | 60 | 26 | 38 | 28 | 50 | 180 | 28 | 38 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 10 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 10 | 2 | 0 | 0 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | [479 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 490 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 490 | 500 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 200 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 150 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 10 | 400 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 0 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 10 | 0 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4000 | 0 | 0 | 30 | 8 | 10 | 35 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 5 | 30 | 0 | 0 | 0 | 0 | 0 | 15 | 60 | 0.95 | 0 | 0 | 0 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | 85 | 110 | 90 | 95 | 100 | 105 | 0.85 | 0.9 | 0.95 | 1 | -0.97 | -0.95 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 10 | 10 | 10 | 3 | 1 | 10500 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 51.5 | 47.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 1 | 115 | 85 | 35 | 7 | 0 | 0 | 1 | -0.1 | 50 | 110 | 80 | 1 | 0 | 183 | 200 | 1 | 140 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 15400 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 15400 | 120 | 90 | 45 | 0 | 10 | 0 | 0 | 0 | -0.4 | 50 | 110 | 80 | 0 | 0 | 400 | 200 | 0 | 100 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 90 | 45 | [6 empty] | 0 | [34 empty] | 0 | 0 | 1 | 0 | 1 | 0 | 0 |  | 0 |  | 0 |  |  |  | 1 | 1 |  |  | 0 | 1 | 0 | 1 | 1 |  | 1 | 0 | 1 |  | 1 | 0 | [8 empty] | 0 | 1 |  | 0 | 0 |  |  | 1 |  | 0 | 0 | 1 | 1 |  | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 11.5 |  | 616 |  |  |  |  | 11 | 0 | 217 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.5 | 1 | 1 | 100 | 41 | 0 | 0 | 6 | 100 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 20 | 100 | 85 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 200 | 168 | 75 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 65 | 1 | 0 | 0 | 0 | -4.5 | 10 | 0 | 60 | 55 | 0 | 2 | 1.65 | 1.82 | 6.6 | 6.7 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.5 | 0 | 0 | 2.2 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 50 | 50 | 50 | 50 | 50 | 120 | 1 | 0.0005 | 0.0005 | 0 | 80 | 80 | 1 | 0 | 1 | 4 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 2.3203 | 4.3945 | 25 | 20.5078 | 100 | 0 | 10 | 0 | 0.5 | 0 | 4 | 50 | 0 | 25 | 10 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | [6 empty] | 0 | 60 | 60 | 0 | 0.2 | 0 | 0 | 0.2 | 0.2 | 0.2 | 0 | 0.2 | 1 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | 0 | 100 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 17 | 5 | 7 | 8.5 | 10 | 12 | 13.5 | 15.3 | 25 | 25 | 60 | 0 | 30 | 0 | 1 | 6 | 0.8 | 6 | 0 | 3.5 | 1 | 6 | 0 | 10 | 92 | 0 | 8000 | 0 | 0 | 540 | 27 | 1000 | 0 | 0 | 1 | 300 | 0 | 300 | 0 | 3 | 300 | 0 | 150 | 8.2 | 7.5 | 180 | 90 | 900 | 30 | 200 | 300 | 40 | 20 | 100 | 0 | 100 | 0 | 0 | 300 | 500 | 600 | 0 | 500 | 600 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 1200 | 1000 |  |  |  | 1000 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 50 | 1000 | 680 | 640 | 5 | 650 | 5 | 1000 | 640 | 5 | 680 | 5 | 1000 | 5 | 15 | 300 | 20 | 50 | 650 | 5 | 1000 | 5 | 1000 | 180 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.6 | 0 | 0 | 1 | 6 | 0 | -10 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 10 | 3 | 0 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 6 | 6 | 5 | 8 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | 0 | 20 |  | 0.98 | 1 | -0.98 | -0.95 | 0.8 | -0.95 | 1 | 7 | 0.95 | -0.95 | 20 | 80 | 3328 | 88 | 90 | 1.98 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 0 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 75 | 90 | 75 | 80 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 52 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 45 | 300 |  | 75 | 1.01 | 1 | 0 | 1 | 60 | 0.1 | 1.11 | 60 | 0 | 50 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 930 | 0 | 5000 | 50 | 5 | 0 | 50 | 80 | 70 | 60 | 55 | 4 | 20 | 500 | 1000 | 1 | 2 | 0 | 0 | 1 | 2 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 4 | 20 | 0.8 | -0.95 | 1 | 0 | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 400 | 0 | 0 | 0 | 0 | 1 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -100 | 100 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 0 | 0 | 1 | -0.9 | -100 | 100 | [12 empty] | 10 | 2.5 | 0.2 | 3 | 0.05 | 1.5 | 1.9 | 0.05 | 0.05 | 98 | 3 | 99 | 3 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 30 |  |  | 20 | 0 |  |  | 3 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.5 | 0.1 | 0.5 | 500 | 1500 | 4.6 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 2 | 2.5 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 85 | 2 | 86 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 1 | 0 | 75 | 80 | 2 | 0.5 | 0 | 0 | 0 | 120 | 120 | 2 | 2 | 0 | 62 | 2 | 1 |  | 75 | 80 | 2 | 0.5 | 0 | 1 | 0 | 100 | 101 | 2 | 2 | 1 | 2 | 70 | 1 | 2 | 70 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 82 | 0 | 0 | 0 | 10 | 28 | 3 | 8 | 30 | 90 | 0 | 0 | 0 | 200 | -200 | 0 | -50 | 100 | -100 | 0 | 0 | 0 | 200 | -200 | 20 | 8 | 1 | 2 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 0 | 0 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 1 | 1 | 90 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 18 | 18 | 18 | 18 | [5 empty] | 15 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 462 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 0 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 4 | 0 | 20 | 4000 | 4000 |  | 550 | 25 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 1 | 3 | 3 | 3 | -5 | -5 | -5 | -5 | 12 | 12 | 12 | 12 | 4.5 |  | 45 | 660 | 660 | -144 | 0 | 60 | 50 | [24 empty] | 0 | 4 | 500 | 30 |  | 8000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 250 | 0 | -24 | -13 | 2175 | 1280 | 10 | 2175 | 1280 | 60 | 0 | 0 | [6 empty] | 0 | 0.19531 |  | 0.05 | 2.5 | 1.2 | [5 empty] | 2680 | 1326 | 4245 | 2140 | 1499 | 1499 |  | 51.1 | 47.9 |  | 400 | [7 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2190 | 1100 | 2950 | 1550 | 1500 | 1500 |  | 47 | 44 |  | 400 | [7 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2681 | 1326 | 4213 | 2065 | 1497 | 1499 |  | 51.8 | 44.1 |  | 400 | [7 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2190 | 1100 | 2950 | 1550 | 1500 | 1500 |  | 47 | 44 |  | 400 |  | 0 | 1000 | 300 | 48 | -1.6 | -4 | 100 | 6 | 0 | 1 | 6 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6 | 0 | 0.5 | 0 | 0 | 120000 | 0 | 120000 | 0 |  | 4 | 0 | 0 | 0 |  |  |  | 75 |  | 39 | [14 empty] | 50 | 50 | 50 | 50 | [10 empty] | 0 | 0 | 1 | 3 | 47 | 49 | 2 | 2 | 55 |  | 39 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.1 |  |  | 100 | 0.2 |  | 250 | 140 | 140 | 100 | [8 empty] | -750 | 3000 |  | 0.2 | 100 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.4 |  |  | 100 | 0.2 |  | 100 |  | 100 | 100 | [11 empty] | 0.2 | 100 | 200 | [43 empty] | 0 | 0.1 | 0.01 | 0.01 | 100 | 30 | 0 | 0 | 2.9 | 0 | 0 | 100 | 1 | 1 | 1 | 1 | 0 | 0 | 75 | 60 | 73 | 100 | 80 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 70 | 70 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 250 | 0 | 1 | 1.5 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 30 | 20 | 100 | 20 | 1.5 | 0.003 | 1 | 1 | 10 | 0.6 | 0 | 1 | 12 | 1 | 1 | 1 | 1 | 0 | 0 | 1.1 | 0.7 | 1 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 150 | 0 | 1 | 4.9 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 95 | 25 | 100 | 50 | 0 | 0.1 | 0.5 | 0.5 | 100 | 40 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 50 | 0 | 100 | 10 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 10000 | 10000 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0 | 0.1 | 100 | 0 | 0 | 0 | 0 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 60 | 0.1 | 0.1 | 75 | 90 | 90 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 10000 | 10000 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 0.01 | 0.01 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 40 | 50 | 100 | 50 | 0 | 0.2 | 1 | 1 | 5 | 50 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 7 | 0 | 100 | -100 | 0 | 0.1 | 5 | 5 | 10 | 10 | 0 | 0 | 2 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 0 | 15 | 0 | 100 | -100 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 50 | 20 | 100 | 100 | 20 | 95 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 10 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0 | 0.001 | 0.001 | 0 | 0 | 88888 | 0 | 123 | 100 | 3 | -3 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 150 | 0 | 1 | 3 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 70 | 0.1 | 0.1 | 95 | 0 | 100 | 55 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  |  |  |  | 12 | 2 | 5 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 70 | 0 | [6 empty] | 0.09478 | 0.44428 | 0.85 | 100 | 0 | 0.02843 | 0.74047 | 0.4739 | 100 | 0 | 4 | 20 | 818 | 1635 | 50 | 75 | 90 | 100 |  | 3.95 | 20 | 1340 | 2679 | 2 | 2 | 40 | 40 |  | -6 | -6 | -6 | -6 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -130 | 8 | 10 | 0.5 | 105 | 0.5 | 0.5 | 30 | 2 | 2679 | 2679 | 2679 | 2679 | 50 | 0.56 | 0.56 | 0.56 | 0.56 | 0.35 | 0.56 | 0.56 | 0.56 |  | 10 | 10 | 95 | 1 | 1 | 100.4 | 102.9 | 98 | 91 | 102.9 | 50 | 65 | 85 | 75 |  | 105 | 120 | 95 | 70 | 140 | 0 | 80 | 10 | 81 | 1 | 22.7 | 3.85 | 0 | 20 | 74 |  |  | 10 | 4 | 4 | 4 | 4 | 52 | 52 | 52 | 52 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 120 | 120 | 120 | 120 | 120 | 0 | 0 | 1000 | 1000 | 1000 | 1000 | 1000 | 120 | 120 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [30 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1450 | 10 | 200 | 400 | 2800 | 5 | 400 | 0 | 3450 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 0 | 1500 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 900 |  | 0.30468 | 5.8594 | 20.5078 | 80 | 0 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1500 | 6.7 | 0 | 0 | 0 | 0 | 0 | 0 | 11.19 | 10.1 | 735 |  |  | 1.2 | 1.3 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.2 |  |  | 0.74 | [13 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | [28 empty] | 1 | 1 | 2 | 1 | 0 | 2 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2675 |  |  | 2679 | 0 | 0 | 0 | 0 | 0 | 2679 | 2679 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135.6 | 1.8 | -25.64 | 4.032 | 0.0795 | 0.70418 | 0 | 0.35 | 2679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 270 | 79 | 88 | 31 | 436 | 444 | 387 | 506 | 522 | 408 | 408 | 130 | -363 | -367 | -280 | -2 | 67.12 | [73 empty] | Sending | 30 | 43 | 44 | 44 | 43 | 44 | 44 | 44 | 44 | 43 | 42 | 43 | 43 | 43 | 42 | 44 | 44 | 43 | 42 | 42 | 42 | [24 empty] | 1201 | 1013 | 593 | 549 | 760 | 2135 | 927 | 1098 | 1557 | 760 | 1229 | 2133 | 720 | 2094 | 1351 | 761 | [9 empty] | 17 | 1 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 170.6 | 0 | 0 | 0 | 1088 | 0 | 0 | 0 | 9.3 | 0 | 0 | 0 | 1.555 |  |  |  | 80.7 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 30132 | 1 | 30132 | 1 | 30132 | 1 | 30132 | 1 | 30132 | 1 | 30132 | 1 | 30132 | 1 | 30132 | 1 | 30132 | 1 | 30132 | 1 | 30132 | 1 | 30132 | 1 | 30132 | 1 | 30132 | 1 | 30132 | 1 | 30132 | 1 | [16 empty] | 0 | 7.62 | 0 | 7.5 | 0 | 7.72 | 0 | 7.71 | 0 | 7.66 | 0 | 7.55 | 0 | 7.5 | 0 | 7.56 | 0 | 7.64 | 0 | 7.52 | 0 | 7.58 | 0 | 7.72 | 0 | 7.53 | 0 | 7.71 | 0 | 7.58 | 0 | 7.6 | [16 empty] | 0 | -0.29 | 0 | -0.38 | 0 | -0.14 | 0 | -0.38 | 0 | -0.19 | 0 | -0.02 | 0 | -0.31 | 0 | -0.22 | 0 | -0.3 | 0 | -0.28 | 0 | -0.27 | 0 | -0.22 | 0 | -0.18 | 0 | -0.13 | 0 | -0.49 | 0 | -0.17 | [16 empty] | 0 | 7.72 | 0 | 7.63 | 0 | 7.67 | 0 | 7.73 | 0 | 7.89 | 0 | 7.87 | 0 | 7.73 | 0 | 7.74 | 0 | 7.64 | 0 | 7.65 | 0 | 7.66 | 0 | 7.69 | 0 | 7.69 | 0 | 7.51 | 0 | 7.65 | 0 | 7.77 | [16 empty] | 0 | -0.13 | 0 | -0.33 | 0 | -0.45 | 0 | -0.13 | 0 | -0.26 | 0 | -0.11 | 0 | -0.36 | 0 | -0.24 | 0 | -0.37 | 0 | -0.21 | 0 | -0.39 | 0 | -0.19 | 0 | -0.25 | 0 | -0.13 | 0 | 0.31 | 0 | -0.1 | [17 empty] | 0 | 1 | 1 | 1 | 17 | 0 | 100 | 0 | 0 | 0 | 0 | 36.1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.23 |  | 0 | 0 | 0 | 0 |  | 100 | 100 | 100 | 100 | 36.1 | 36.1 | 36.1 | 36.1 |  | 1500 | 1499 | 12.7 | 51.2 |  |  | 0 | 0 | ECOGEN ENERGY SYSTEMS BVBA
4 |  |  |  |  | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","rem_conn":"Prim-NoSSL-NoProxy","dataItems":"0/20","agent_conn":"Prim-SSL-NoProxy","mon_conn":"Prim-NoSSL-NoProxy"} | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 4.19 | 0 | 0 | 0.97 | 34.8 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0.06 | 0 | 0.05 | 0 | 0 | 0 | 4.8.0.4 | 7833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -150 | 0 | 0 | 0 | 0 | 0 | -150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.01 |  |  |  |  | 3541599 | 0 | 40297 | 1940149 | 156102 | 0 | 0 | 0 | 0 | 0 | 141 | 423 | 330 | 1662 | 27423 | 57423 | 697423 | 797423 | 66470 | 66469 | 66469 |  | 2183 |  | 40.3 | 0 | 65 | 29.9 | 0 | 0 | 0 | 0 | 34.8 | 34.8 | 0 | 0 | 0 | 0 | 115 | 34.3 | 0 | 40.3 | 40.3 | 0 | 75 | 56.4 | 0 | 3.4 | 3.4 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.6 | 3.4 | 1.9 | 0 | 6.9 | 4.3 | 7.7 | 7.4 | 1.8 | 2.2 | 20.1 | 40.6 | 21.3 | 20.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.3368 | 40.3499 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1608799645609 | 0 | 46 | 1 | 0 | 0 | 0 | 0 | 30.39 | 0 | 0 | 2577 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 52 | 51 | 53 | 54 | 52 | 52 | 52 | 52 | 51 | 52 | 53 | 53 | 53 | 54 | 52 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 536 | 54 | 542 | 51 | 533 | 0 | 33 | 21 | 0 | 0 | 9 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.7 | 37.2 |  |  | 38.8 | 39.8 | 38.9 | 0 |  |  |  |  | 63893 | 1605459590857 |  | 0 | 0 | 0 | 0 | 10258 | 5934 | 10290 | 5926 | 10289 | 5944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.19 | 0.1 | 0.13 | -0.07 |  | 0 | 56.4 | 32.6 | 0 | 29.9 | 0 | 32.2 | 3 | 0 | 0 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.7 | 0 | 0 | 0 | 57.2 | 57.5 | 56.7 | 56.3 | 57.2 | 58.2 | 57.5 | 0 | 1.26 | 0 | 0 | 0 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 72 | 0 | 0 | 0 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 0 | 2588.4 | 0 | 0 | 0 | 2588.4 | 2588.4 | 2588.4 | 2588.4 | 2588.4 | 2588.4 | 2588.4 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 4 | 2020 | 30 | 4 | 2020 | 4 | 5 | 2020 | 26 | 4 | 2020 | 30 | 4 | 2020 | 26 | 4 | 2020 | 30 | 4 | 2020 | 4 | 5 | 0 | 0 | 0 | 3611 | 0 | 0 | 0 | 3612 | 3683 | 3549 | 3619 | 3563 | 3627 | 3690 | 0 | 7.73 | 0 | 0 | 0 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.657 | 0.31 | 0 | 0 | 0 | 0 | 8.13 | 8.2 | 8.43 | 8.4 | 8.39 | 8.33 | 8.29 | 8.28 | 8.34 | 8.19 | 8.2 | 8.21 | 8.54 | 8.11 | 8.28 | 8.41 | [8 empty] | 0.22 | -0.14 | 0.05 | 0.32 | 0.13 | 0.01 | 0.18 | 0.07 | 0.29 | 0.19 | -0.01 | -0.02 | 0.05 | 0.14 | 0.15 | 0.47 | [8 empty] | 8.26 | 8.04 | 8.45 | 8.36 | 8.13 | 8.23 | 8.57 | 8.29 | 8.28 | 8.31 | 8.22 | 8.27 | 8.46 | 8.08 | 8.1 | 8.33 | [8 empty] | 0.17 | 0.17 | 0.44 | 0.27 | 0.04 | 0.04 | 0.26 | 0.15 | 0.23 | 0.17 | -0.03 | 0.01 | 0.26 | 0.11 | 0.04 | 0.13 | [8 empty] | 176872.2 | 0 | 43897.3 | 0 | 0 | 0.02 | 0 | 0 | 1.06 | 0 | 0 | 4.8.0.0.0 | 4.7.1.1.1 | 4.7.1.0.2 | 4.7.1.0.0 | 4.7.0.0.1 | 4.8.0.5.1 | 4.7.1.0.0 | 4.7.0.0.2 | 4.7.1.0.0 | 4.7.0.0.1 | 4.5.1.0.0 | 4.7.1.0.0 | 4.7.2.0.1 | 4.7.0.0.1 | 4.7.0.0.4 | 4.8.2.1.0 | 4.7.0.0.1 | 4.7.0.0.0 | 4.7.0.0.0 | 4.6.0.0.0 | 4.7.0.0.2 | 4.7.0.0.0 | 0.0.0.0.0 | 4.7.5.1.1 | 4.7.0.0.0 | 4.7.0.0.3 | 4.7.0.0.1 | 4.7.0.1.0 | 4.7.0.1.1 | 4.8.0.0.0 | M03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1715 | [82 empty] | Not Available | 60 |  |  |  |  | 30.36 | 2 | 2 | 50.02 | 0 | 0 | 50.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 0 | 0 | 970 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 1 | 0 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 30 | 30 | 0 | 1.4 | 20 | 1.5 | 80 | 4 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 7 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 33 | [5 empty] | 1700 | 800 | 1 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 250 | -300 |  | -100 | -800 | 6 | 0 | 50 | 1500 | 3 | 3.7 | 3.9 | 0.1 | 2.7 | 0.1 | 0 | 0 | 0 | 500 | 7000 | 70 | -500 |  |  | 2.8 |  | 0 | 0 | 0 | 0 |  | 10 | 0 |  |  |  | 0 |  | 5 | 5 | 5 | 5 | 5 | 60 | 28 | 35 | 30 | 50 | 180 | 28 | 35 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 0 | 0 | 1 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 0 | 0 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | [479 empty] | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.5 | 8 | 9.5 | 4 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 3000 | 0 | 20 | 4 | 1000 | 0 | 20 | 4 | 3000 | 0 | 20 | 4 | 1000 | 0 | 20 | 4 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 5 | 0 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 32 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 |  |  | 60 | -27 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | [12 empty] | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 1 | 40 | 0 | 30 | 30 | 1 | 1 | 10 | 3 | 1 | 10500 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 4 | 4 | 0.01 | 0.01 | 0.2 | 0.2 | 1 | 0.84 | 1 | 0.84 | 1 | 30 | 0 | 0 | 0 | 100 | 100 | 10 | 50 | 50 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 5000 | -5000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 47.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 0 | 110 | 90 | 35 | 7 | 0 | 0 | 1 | -0.2 | 50 | 110 | 80 | 1 | 0 | 183 | 200 | 1 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 3 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 90 | 45 | 0 | 10 | 0 | 0 | 0 | -0.4 | 50 | 110 | 80 | 0 | 0 | 400 | 200 | 0 | 100 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 90 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 6000 | 20 | 100 | 50 | 80 | 250 | 100 | 230 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 5 | 30 | 30 | 70 | 490 | 490 | 300 | 30 | 120 | 30 |  | 0 |  | 0 | 0 | 1 | 0 | 0 |  | 0 |  | 0 |  |  |  | 1 | 1 |  |  |  | 0 | 0 |  | 1 |  | 1 | 0 | 1 |  | 1 | 0 | [8 empty] | 0 | 1 |  | 0 | 0 |  |  | 1 |  | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 1 |  | 616 |  |  |  |  | 11 | 0 | 166 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.5 | 0.1 | 0.1 | 100 | 35 | 0 | 1 | 2 | 100 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 45 | 35 | 0 | 100 | 20 | 0 | 0 | -5 | 15 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 33 | 30 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 200 | 168 | 75 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 65 | 1 | 0 | 0 | 0 | -4.5 | 10 |  | 60 | 55 | 0 | 2 | 1.65 | 1.82 | 0.6 | 0.6 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0.1 | 0 | 0 | 0 | 15 | 30 | 0.01 | 0.4 | 0 | 60 | 30 | 0 | 0 | 0 | 0 | 1200 | 1400 | 0 | 0.5 |  | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 1 | 0.1 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 1 | 0 | [10 empty] | 0 | 50 | 50 | 50 | 50 | 50 |  | 1 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.3 | 1 | 25 | 6.5 | 100 | 0 | 20 | 0 | 0.5 | 0 | 4 | 50 | 0 | 25 | 10 | 250 | 3 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 | 0 | 1 | 4000 | 2000 | 20000 | 10000 | 2425 | 1212 | 0 | 0 | 2 | 1 | 30 | 150 | 20 | 120 | 0 | 1 | 1 | 1 | 1 | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 1 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 | 1.5 | 1 | 650 | 700 | 0 | 0 | 0 | 0 | [66 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 1200 | 1000 |  |  |  | 1000 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 50 | 1000 | 680 | 640 |  | 650 |  |  | 640 | 5 | 680 | 5 | [7 empty] | 5 | 1000 |  |  | 100 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 20 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 20 | 5 | 5 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | [15 empty] | 3326 | 88 | 90 | 3 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 0 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 75 | 90 | 75 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 40 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 45 | 300 |  | 75 | 1.5 | 0 | 0 | 0 |  | 0.1 | 0.84 | 60 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 930 | 0 | 5000 | 50 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 500 | 1000 |  |  |  | 0 | 1 | 1 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 0 | 20 | 0.8 | -0.95 | 0.99 |  | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 400 |  |  | 0 | 0 | 1 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -100 | 100 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 0 | 0 | 1 | -0.9 | -100 | 100 | 10 | 0 | 100 | 0 | 100 | 0 | 800 | -20 | 800 | -20 | 600 | 0 | 10 | 2.5 | 0.3 | 2.5 | 0.3 | 0.6 | 0.8 | 0.05 | 0.05 | 120 | 5 | 120 | 5 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 30 |  |  | 20 |  |  |  | 3 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.5 | 0.1 | 0.5 | 500 | 1500 | 4.6 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 120 | 2 | 120 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 1 | 0 | 75 | 120 | 2 | 2 | 0 | 0 | 0 | 120 | 120 | 2 | 2 | 0 | 62 | 2 | 1 |  | 120 | 120 | 2 | 0.5 | 0 | 1 | 0 | 200 | 200 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 82 | 0 | 0 | 0 | 5 | 20 | 0 | 2 | 30 | 90 | 0 | 0 | 1 | 100 | -100 | 0 | -50 | 100 | -100 | 0 | 0 | 1 | 100 | -100 | 20 | 30 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 9.5 | 10 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 90 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 18 | 18 | 18 | 18 | [5 empty] | 15 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 462 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 1 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 |  | 100 | 4 | 0 | 20 | 4000 | 4000 |  | 550 | 25 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 4 | 4 | 4 | 4 | -5 | -5 | -5 | -5 | 8 | 8 | 8 | 8 | 4.5 |  | 45 | 270 | 90 | -144 | 0 | 80 | 350 | [24 empty] | 0 | 4 | 500 | 30 |  | 4000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 250 | 0 | -24 | -13 | 2175 | 1280 | 10 | 2175 | 1280 | 60 | 0 | 0 | [6 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2674 | 1339 | 4310 | 2176 | 1500 | 1498 |  | 47.8 | 45.5 |  | 400 | [7 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2190 | 1100 | 2950 | 1550 | 1500 | 1500 |  | 47 | 44 |  | 400 | [7 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2190 | 1100 | 2950 | 1550 | 1500 | 1500 |  | 47 | 44 |  | 400 | [7 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2190 | 1100 | 2950 | 1550 | 1500 | 1500 |  | 47 | 44 |  | 400 |  | 0 | 1000 | 600 | 50 | -0.5 | -5 | 120 | 6 | 0 | 1 | 6 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6 | 0 | 0.5 | 0 | 0 | 120000 | 0 | 120000 | 0 |  | 4 | 0 | 0 | 0 |  |  |  | 75 |  | 40 | [14 empty] | 55 | 50 | 50 | 50 | [10 empty] | 0 | 0 | 1 | 3 | 47 | 49 | 2 | 2 | 62 |  | 35 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 250 | 100 | 100 | 100 | [8 empty] | -750 | 3000 |  | 0.2 | 100 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.4 |  |  | 100 | 0.2 |  | 100 |  | 100 | 100 | [11 empty] | 0.2 | 100 | 200 | [43 empty] | 0.001 | 0.3 | 100 | 2.5 | 100 | 50 | 0 | 1 | 2 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 65 | 70 | 0 | 100 | 35 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 70 | 70 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 150 | 0 | 1 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 30 | 35 | 0 | 100 | 35 | 1.5 | 0.003 | 1 | 1 | 10 | 0.6 | 0 | 1 | 12 | 1 | 1 | 1 | 1 | 0 | 0 | 1.1 | 0.7 | 1 | 0 | 100 | 0 | 0 | 0.1 | 0.1 | 0.01 | 100 | 35 | 0 | 1 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 130 | 115 | 115 | 0 | 100 | 75 | 0 | 0.1 | 0.5 | 0.5 | 100 | 40 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 50 | 0 | 100 | 10 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | [42 empty] | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 1 | 0 | 10 | 10 | 10 | 2 | 5 | 0 | 48 | 50 | 1 | 5000 | 8000 | 5000 | 8000 | 6 | 6 | 0 | 5000 | -5000 | 0 | 0 | 0.02 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 50 | 47 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 12 | 2 | 5 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 80 | 0 | [6 empty] | 0.09478 | 0.44428 | 1.1848 | 100 | 0 | 0.02843 | 0.74047 | 0.4739 | 100 | 0 | 4 | 20 | 818 | 1635 | 60 | 75 | 90 | 100 |  | 4 | 20 | 1213 | 2679 | 2 | 2 | 35 | 45 |  | -6 | -6 | -6 | -6 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -130 | 8 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 2679 | 2679 | 2679 | 2679 | 50 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 |  | 10 | 5 | 95 | 1 | 1 | 102 | 112 | 98 | 91 | 112 | 50 | 65 | 85 | 75 |  | 105 | 120 | 95 | 70 | 140 | 1 | 70 | 10 | 85 | 0 | 25 | 3.45 | 1 | 10 | 80 |  |  | 10 | 4 | 4 | 4 | 4 | 58 | 51 | 51 | 51 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 16 | 120 | 120 | 120 | 120 | 120 | 0 | 35 | 1000 | 100 | 16 | 5000 | 16 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [30 empty] | 20 | 20 | 70 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1450 | 10 | 200 | 400 | 2800 | 5 | 400 | 0 | 3450 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 0 | 1500 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 900 |  | 0.15 | 0.64 | 7.7 | 100 | 0 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1500 | 6.7 | 0 | 85 | 85 | 85 | 95 | 95 | 9.54 | 9.971 | 720 |  |  | 1.375 | 1.475 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.1 |  |  | 0.74 | [13 empty] | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | [28 empty] | 1 | 1 | 0 | 2 | 0 | 2 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2679 | 0 | 0 | 0 | 0 | 0 | 2679 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208 | 5 | -28.46 | 4.108 |  | 0.67655 | 0 | 0.63 | 2676 | 0 | 0 | 0 | 55 | 54 | 0 | 0 | 148 | 144 | 91 | 83 | 88 | 38 | 52 | 225 | 309 | 338 | 498 | 498 | 354 | 33 | 45 | 41 | 238 | 38.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 389 | 402 | 391 | 392 | 401 | 392 | 397 | 394 | 0 | 0 | 0 | 391 | 0 | 0 | 0 | 0 | 0 | 386 | 389 | 394 | 393 | 390 | 385 | 390 | 527 | 527 | 526 | 530 | 528 | 528 | 531 | 532 | 0 | 0 | 0 | 527 | 0 | 0 | 0 | 0 | 0 | 522 | 521 | 523 | 526 | 523 | 524 | 524 |  | Sending | 30 | 44 | 46 | 39 | 44 | 44 | 44 | 46 | 42 | 40 | 40 | 40 | 40 | 40 | 40 | 46 | 46 | 45 | 44 | 45 | 46 | [24 empty] | 1629 | 1242 | 1298 | 1761 | 1884 | 1635 | 1912 | 1251 | 1842 | 1654 | 1245 | 1754 | 2143 | 2004 | 1390 | 1701 | [9 empty] | 57 | 1 | 4261 | 12.6592 | 149.5738 | 9 | 100 | 20 | 72.8898 | 30 | 99 | 326 | 505.2056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 967 | 0 | 0 | 0 | 32.5 | 0 | 0 | 0 | 1.38 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 | [16 empty] | 0 | 8.13 | 0 | 8.2 | 0 | 8.43 | 0 | 8.4 | 0 | 8.39 | 0 | 8.33 | 0 | 8.29 | 0 | 8.28 | 0 | 8.34 | 0 | 8.19 | 0 | 8.2 | 0 | 8.21 | 0 | 8.54 | 0 | 8.11 | 0 | 8.28 | 0 | 8.41 | [16 empty] | 0 | 0.22 | 0 | -0.14 | 0 | 0.05 | 0 | 0.32 | 0 | 0.13 | 0 | 0.01 | 0 | 0.18 | 0 | 0.07 | 0 | 0.29 | 0 | 0.19 | 0 | -0.01 | 0 | -0.02 | 0 | 0.05 | 0 | 0.14 | 0 | 0.15 | 0 | 0.47 | [16 empty] | 0 | 8.26 | 0 | 8.04 | 0 | 8.45 | 0 | 8.36 | 0 | 8.13 | 0 | 8.23 | 0 | 8.57 | 0 | 8.29 | 0 | 8.28 | 0 | 8.31 | 0 | 8.22 | 0 | 8.27 | 0 | 8.46 | 0 | 8.08 | 0 | 8.1 | 0 | 8.33 | [16 empty] | 0 | 0.17 | 0 | 0.17 | 0 | 0.44 | 0 | 0.27 | 0 | 0.04 | 0 | 0.04 | 0 | 0.26 | 0 | 0.15 | 0 | 0.23 | 0 | 0.17 | 0 | -0.03 | 0 | 0.01 | 0 | 0.26 | 0 | 0.11 | 0 | 0.04 | 0 | 0.13 | [17 empty] | 0 | 1 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1500 | 0 |  | 40.3 |  |  | 0 | 0 | BMW REGENSBURG M3
5 |  |  |  |  | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","rem_conn":"Prim-NoSSL-NoProxy","dataItems":"0/20","agent_conn":"Prim-SSL-NoProxy","mon_conn":"Back-NoSSL-NoProxy"} | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 4.19 | 0 | 0 | 0.99 | 34.9 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0.05 | 0 | 0.05 | 0 | 0 | 0 | 4.8.0.4 | 8438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 |  | 0 | 0 | 0 | 0.9 | 0 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0 |  |  |  |  | 3250160 | 0 | 34630 | 1836769 | 149675 | 0 | 0 | 0 | 0 | 0 | 110 | 1039 | 32 | 1651 | 28039 | 58039 | 698039 | 798039 | 64726 | 81236 | 81236 |  | 1476 |  | 40.5 | 0 | 65 | 36.5 | 0 | 0 | 0 | 0 | 34.9 | 34.9 | 0 | 0 | 0 | 0 | 115 | 38 | 0 | 40.5 | 40.5 | 0 | 75 | 53.6 | 0 | 8.1 | 8.1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 127.8 | 8.1 | 1.4 | 0 | 7 | 12.7 | 7.8 | 7.1 | 1.8 | 2.2 | 21.3 | 47 | 20.9 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.0577 | 40.9482 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 47 | 1 | 0 | 0 | 0 | 0 | 36.59 | 0 | 0 | 1961 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 49 | 49 | 51 | 49 | 49 | 49 | 49 | 49 | 48 | 49 | 50 | 51 | 49 | 50 | 50 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 533 | 50 | 537 | 48 | 529 | 0 | 32 | 23 | 0 | 0 | 8 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.8 | 36.4 |  |  | 38 | 39.1 | 37.8 | 0 |  |  |  |  | 62796 | 1602534182914 |  | 0 | 0 | 0 | 0 | 10252 | 5933 | 10283 | 5923 | 10292 | 5942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.19 | 0.2 | 0.13 | -0.07 |  | 0 | 53.6 | 32.6 | 0 | 36.5 | 0 | 33.5 | 5 | 0 | 0 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.3 | 0 | 0 | 0 | 57.2 | 55.8 | 55.8 | 56.2 | 56.8 | 56.8 | 56.2 | 0 | 1.26 | 0 | 0 | 0 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 72 | 0 | 0 | 0 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 0 | 1969.2 | 0 | 0 | 0 | 1969 | 1969.2 | 1969.2 | 1969.2 | 1969.2 | 1969.2 | 1969.2 | 0 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 4 | 2020 | 20 | 4 | 2020 | 13 | 4 | 2020 | 14 | 4 | 2020 | 14 | 4 | 2020 | 14 | 4 | 2020 | 14 | 4 | 2020 | 13 | 4 | 0 | 0 | 0 | 3406 | 0 | 0 | 0 | 3447 | 3368 | 3395 | 3396 | 3385 | 3386 | 3369 | 0 | 7.73 | 0 | 0 | 0 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.668 | 0.3 | 0 | 0 | 0 | 0 | 8.08 | 8.35 | 8.14 | 8.42 | 8.1 | 8.33 | 8.5 | 8.32 | 8.51 | 8.32 | 8.27 | 8.38 | 8.29 | 8.1 | 8.44 | 8.24 | [8 empty] | 0.18 | 0.22 | 0.19 | 0 | 0.09 | 0.33 | 0.11 | 0.12 | 0.07 | 0.08 | 0.28 | 0.01 | -0.12 | 0.39 | 0.3 | 0.25 | [8 empty] | 8.32 | 8.22 | 8.5 | 8.42 | 8.33 | 8.56 | 8.47 | 8.44 | 8.58 | 8.41 | 8.2 | 8.38 | 8.19 | 8.28 | 8.4 | 8.16 | [8 empty] | -0.23 | 0.04 | 0.15 | 0.02 | 0.05 | 0.3 | 0.02 | 0.23 | -0.23 | 0.04 | 0.27 | 0 | 0.15 | 0.34 | 0.3 | 0.03 | [8 empty] | 172324.2 | 0 | 41506.4 | 0 | 0 | 0.02 | 0 | 0 | 1.06 | 0 | 0 | 4.8.0.0.0 | 4.7.1.1.1 | 4.7.1.0.2 | 4.7.1.0.0 | 4.7.0.0.1 | 4.8.0.5.1 | 4.7.1.0.0 | 4.7.0.0.2 | 4.7.1.0.0 | 4.7.0.0.1 | 4.5.1.0.0 | 4.7.1.0.0 | 4.7.2.0.1 | 4.7.0.0.1 | 4.7.0.0.4 | 4.8.2.1.0 | 4.7.0.0.1 | 4.7.0.0.0 | 4.7.0.0.0 | 4.6.0.0.0 | 4.7.0.0.2 | 4.7.0.0.0 | 0.0.0.0.0 | 4.7.5.1.1 | 4.7.0.0.0 | 4.7.0.0.3 | 4.7.0.0.1 | 4.7.0.1.0 | 4.7.0.1.1 | 4.8.0.0.0 | M02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1066 | [30 empty] | -1 | 1 |  | NaN |  | 1608293688000 | 479 |  | 0.0006 |  | NaN | 3691 | 1 | 1607472000000 | NaN | NaN | NaN |  |  | 9 |  | 1 | 0.0002 |  | 1 |  |  |  | 2 |  |  | 0.0012 | 116 | 1608289200000 | 38 |  | 3288 |  |  | 1006827 |  |  | 64377 |  |  |  |  | 0.0001 |  |  |  |  | Not Available | 60 |  |  |  |  | 43.73 | 2 | 2 | 50 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 0 | 0 | 970 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 1 | 0 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 30 | 30 | 0 | 1.4 | 20 | 1.5 | 80 | 4 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 7 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 33 | [5 empty] | 1700 | 800 | 1 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 250 | -300 |  | -100 | -800 | 6 | 0 | 50 | 1500 | 3 | 3.7 | 3.9 | 0.1 | 2.7 | 0.1 | 0 | 0 | 0 | 500 | 7000 | 70 | -500 |  |  | 2.8 |  | 0 | 0 | 0 | 0 |  | 10 | 0 |  |  |  | 0 |  | 5 | 5 | 5 | 5 | 5 | 60 | 28 | 35 | 30 | 50 | 180 | 28 | 35 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 0 | 0 | 1 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 0 | 0 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | [479 empty] | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.5 | 8 | 9.5 | 4 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 3000 | 0 | 20 | 4 | 2500 | 0 | 20 | 4 | 3000 | 0 | 20 | 4 | 1000 | 0 | 20 | 4 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 5 | 0 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 32 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 |  |  | 60 | -27 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | [12 empty] | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 1 | 40 | 0 | 30 | 30 | 1 | 1 | 10 | 3 | 1 | 10500 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 4 | 4 | 0.01 | 0.01 | 0.2 | 0.2 | 1 | 0.84 | 1 | 0.84 | 1 | 30 | 0 | 0 | 0 | 100 | 100 | 10 | 50 | 50 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 5000 | -5000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 47.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 0 | 110 | 90 | 35 | 7 | 0 | 0 | 1 | -0.2 | 50 | 110 | 80 | 1 | 0 | 183 | 200 | 1 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 3 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 90 | 45 | 0 | 10 | 0 | 0 | 0 | -0.4 | 50 | 110 | 80 | 0 | 0 | 400 | 200 | 0 | 100 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 90 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 6000 | 20 | 100 | 50 | 80 | 250 | 100 | 230 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 5 | 30 | 30 | 70 | 490 | 490 | 300 | 30 | 120 | 30 |  | 0 |  | 0 | 0 | 1 | 0 | 0 |  | 0 |  | 0 |  |  |  | 1 | 1 |  |  |  | 0 | 0 |  | 1 |  | 1 | 0 | 1 |  | 1 | 0 | [8 empty] | 0 | 1 |  | 0 | 0 |  |  | 1 |  | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 1 |  | 616 |  |  |  |  | 11 | 0 | 166 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.5 | 0.1 | 0.1 | 100 | 35 | 0 | 1 | 2 | 100 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 45 | 35 | 0 | 100 | 20 | 0 | 0 | -5 | 15 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 33 | 30 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 200 | 168 | 75 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 65 | 1 | 0 | 0 | 0 | -4.5 | 10 |  | 60 | 55 | 0 | 2 | 1.65 | 1.82 | 0.6 | 0.6 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0.1 | 0 | 0 | 0 | 15 | 30 | 0.01 | 0.4 | 0 | 60 | 30 | 0 | 0 | 0 | 0 | 1200 | 1400 | 0 | 0.5 |  | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 1 | 0.1 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 1 | 0 | [10 empty] | 0 | 50 | 50 | 50 | 50 | 50 |  | 1 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.3 | 1 | 25 | 6.5 | 100 | 0 | 20 | 0 | 0.5 | 0 | 4 | 50 | 0 | 25 | 10 | 250 | 3 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 | 0 | 1 | 4000 | 2000 | 20000 | 10000 | 2425 | 1212 | 0 | 0 | 2 | 1 | 30 | 150 | 20 | 120 | 0 | 1 | 1 | 1 | 1 | 1 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 1 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 | 1.5 | 1 | 650 | 700 | 0 | 0 | 0 | 0 | [66 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 1200 | 1000 |  |  |  | 1000 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 50 | 1000 | 680 | 640 |  | 650 |  |  | 640 | 5 | 680 | 5 | [7 empty] | 5 | 1000 |  |  | 100 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 20 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 20 | 5 | 5 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | [15 empty] | 3326 | 88 | 90 | 3 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 0 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 75 | 90 | 75 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 40 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 45 | 300 |  | 75 | 1.5 | 0 | 0 | 0 |  | 0.1 | 0.84 | 60 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 930 | 0 | 5000 | 50 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 500 | 1000 |  |  |  | 0 | 1 | 1 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 0 | 20 | 0.8 | -0.95 | 0.98 |  | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 400 |  |  | 0 | 0 | 1 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -100 | 100 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 0 | 0 | 1 | -0.9 | -100 | 100 | 10 | 0 | 100 | 0 | 100 | 0 | 800 | -20 | 800 | -20 | 600 | 0 | 10 | 2.5 | 0.3 | 2.5 | 0.3 | 0.6 | 0.8 | 0.05 | 0.05 | 120 | 5 | 120 | 5 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 30 |  |  | 20 |  |  |  | 3 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.5 | 0.1 | 0.5 | 500 | 1500 | 4.6 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 120 | 2 | 120 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 1 | 0 | 75 | 120 | 2 | 2 | 0 | 0 | 0 | 120 | 120 | 2 | 2 | 0 | 62 | 2 | 1 |  | 120 | 120 | 2 | 0.5 | 0 | 1 | 0 | 200 | 200 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 82 | 0 | 0 | 0 | 5 | 20 | 0 | 2 | 30 | 90 | 0 | 0 | 1 | 100 | -100 | 0 | -50 | 100 | -100 | 0 | 0 | 1 | 100 | -100 | 20 | 30 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 9.5 | 10 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 90 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 18 | 18 | 18 | 18 | [5 empty] | 15 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 462 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 1 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 |  | 100 | 4 | 0 | 20 | 4000 | 4000 |  | 550 | 25 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 4 | 4 | 4 | 4 | -5 | -5 | -5 | -5 | 8 | 8 | 8 | 8 | 4.5 |  | 45 | 270 | 90 | -144 | 0 | 80 | 350 | [24 empty] | 0 | 4 | 500 | 30 |  | 4000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 250 | 0 | -24 | -13 | 2175 | 1280 | 10 | 2175 | 1280 | 60 | 0 | 0 | [6 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2681 | 1339 | 4335 | 2150 | 1499 | 1499 |  | 45.4 | 45.1 |  | 400 | [7 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2190 | 1100 | 2950 | 1550 | 1500 | 1500 |  | 47 | 44 |  | 400 | [7 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2190 | 1100 | 2950 | 1550 | 1500 | 1500 |  | 47 | 44 |  | 400 | [7 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2190 | 1100 | 2950 | 1550 | 1500 | 1500 |  | 47 | 44 |  | 400 |  | 0 | 1000 | 600 | 50 | -0.5 | -5 | 120 | 6 | 0 | 1 | 6 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6 | 0 | 0.5 | 0 | 0 | 120000 | 0 | 120000 | 0 |  | 4 | 0 | 0 | 0 |  |  |  | 75 |  | 40 | [14 empty] | 55 | 50 | 50 | 50 | [10 empty] | 0 | 0 | 1 | 3 | 47 | 49 | 2 | 2 | 62 |  | 35 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 250 | 100 | 100 | 100 | [8 empty] | -750 | 3000 |  | 0.2 | 100 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.4 |  |  | 100 | 0.2 |  | 100 |  | 100 | 100 | [11 empty] | 0.2 | 100 | 200 | [43 empty] | 0.001 | 0.3 | 100 | 2.5 | 100 | 90 | 0 | 1 | 3.5 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 65 | 70 | 0 | 100 | 35 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 70 | 70 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 150 | 0 | 1 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 30 | 35 | 0 | 100 | 35 | 1.5 | 0.003 | 1 | 1 | 10 | 0.6 | 0 | 1 | 12 | 1 | 1 | 1 | 1 | 0 | 0 | 1.1 | 0.7 | 1 | 0 | 100 | 0 | 0.001 | 0.1 | 0.1 | 0.01 | 100 | 75 | 0 | 1 | 2 | 1 | 1 | 1 | 1 | 0 | 0 | 130 | 115 | 115 | 0 | 100 | 70 | 0 | 0.1 | 0.5 | 0.5 | 100 | 40 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 50 | 0 | 100 | 10 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | [42 empty] | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 1 | 0 | 10 | 10 | 10 | 2 | 5 | 0 | 48 | 50 | 1 | 5000 | 8000 | 5000 | 8000 | 6 | 6 | 0 | 5000 | -5000 | 0 | 0 | 0.02 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 50 | 47 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 12 | 2 | 5 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 80 | 0 | [6 empty] | 0.09478 | 0.44428 | 1.1848 | 100 | 0 | 0.02843 | 0.74047 | 0.4739 | 100 | 0 | 4 | 20 | 818 | 1635 | 60 | 75 | 90 | 100 |  | 4 | 20 | 1213 | 2679 | 2 | 2 | 35 | 45 |  | -6 | -6 | -6 | -6 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -130 | 8 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 2679 | 2679 | 2679 | 2679 | 50 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 |  | 10 | 5 | 95 | 1 | 1 | 102 | 112 | 98 | 91 | 112 | 50 | 65 | 85 | 75 |  | 105 | 120 | 95 | 70 | 140 | 1 | 70 | 10 | 85 | 0 | 25 | 3.45 | 1 | 10 | 80 |  |  | 10 | 4 | 4 | 4 | 4 | 58 | 51 | 51 | 51 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 16 | 120 | 120 | 120 | 120 | 120 | 0 | 35 | 1000 | 100 | 16 | 5000 | 16 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [30 empty] | 10 | 10 | 70 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1450 | 10 | 200 | 400 | 2800 | 5 | 400 | 0 | 3450 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 0 | 1500 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 900 |  | 0.15 | 0.64 | 7.7 | 100 | 0 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1500 | 6.7 | 0 | 85 | 85 | 85 | 95 | 95 | 9.54 | 9.971 | 720 |  |  | 1.28 | 1.4 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.1 |  |  | 0.74 | [13 empty] | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | [28 empty] | 1 | 1 | 0 | 2 | 0 | 2 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2679 | 0 | 0 | 0 | 0 | 0 | 2679 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 347.8 | 13.8 | -23.9 | 4.054 |  | 0.97091 | 0 | 0.63 | 2677 | 0 | 0 | 0 | 55 | 50 | 0 | 0 | 144 | 144 | 83 | 84 | 134 | 31 | 29 | 27 | 294 | 291 | 322 | 322 | 178 | 36 | 35 | 18 | 238 | 39.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 391 | 393 | 392 | 399 | 396 | 389 | 391 | 394 | 0 | 0 | 0 | 394 | 0 | 0 | 0 | 0 | 0 | 393 | 396 | 389 | 392 | 394 | 396 | 393 | 529 | 526 | 526 | 527 | 527 | 527 | 529 | 529 | 0 | 0 | 0 | 525 | 0 | 0 | 0 | 0 | 0 | 527 | 527 | 525 | 527 | 525 | 527 | 523 |  | Sending | 30 | 45 | 45 | 45 | 46 | 45 | 46 | 45 | 46 | 46 | 47 | 45 | 42 | 46 | 43 | 46 | 46 | 36 | 36 | 46 | 46 | [24 empty] | 2030 | 2096 | 1345 | 1886 | 1968 | 1752 | 1829 | 1761 | 1494 | 1895 | 1750 | 1658 | 1714 | 1895 | 1757 | 1172 | [9 empty] | 47 | 1 | 4053 | 40.6347 | 316.224 | 7 | 100 | 9 | 74.3389 | 16 | 100 | 156 | 506.4277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 964 | 0 | 0 | 0 | 36.1 | 0 | 0 | 0 | 1.287 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 | [16 empty] | 0 | 8.08 | 0 | 8.35 | 0 | 8.14 | 0 | 8.42 | 0 | 8.1 | 0 | 8.33 | 0 | 8.5 | 0 | 8.32 | 0 | 8.51 | 0 | 8.32 | 0 | 8.27 | 0 | 8.38 | 0 | 8.29 | 0 | 8.1 | 0 | 8.44 | 0 | 8.24 | [16 empty] | 0 | 0.18 | 0 | 0.22 | 0 | 0.19 | 0 | 0 | 0 | 0.09 | 0 | 0.33 | 0 | 0.11 | 0 | 0.12 | 0 | 0.07 | 0 | 0.08 | 0 | 0.28 | 0 | 0.01 | 0 | -0.12 | 0 | 0.39 | 0 | 0.3 | 0 | 0.25 | [16 empty] | 0 | 8.32 | 0 | 8.22 | 0 | 8.5 | 0 | 8.42 | 0 | 8.33 | 0 | 8.56 | 0 | 8.47 | 0 | 8.44 | 0 | 8.58 | 0 | 8.41 | 0 | 8.2 | 0 | 8.38 | 0 | 8.19 | 0 | 8.28 | 0 | 8.4 | 0 | 8.16 | [16 empty] | 0 | -0.23 | 0 | 0.04 | 0 | 0.15 | 0 | 0.02 | 0 | 0.05 | 0 | 0.3 | 0 | 0.02 | 0 | 0.23 | 0 | -0.23 | 0 | 0.04 | 0 | 0.27 | 0 | 0 | 0 | 0.15 | 0 | 0.34 | 0 | 0.3 | 0 | 0.03 | [17 empty] | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1500 | 0 |  | 40.5 |  |  | 0 | 0 | REGENSBURG
6 |  |  |  |  | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","agent_conn":"Back-SSL-NoProxy","mon_conn":"Prim-NoSSL-NoProxy","rem_conn":"Prim-SSL-NoProxy"} | 0 | 0 | 0 | 0 | 0 | 0 | -0.92 | 5.23 | 0 | 0 | 0 | -1258 | 0 | 6.45 | 0 | 3.95 | 4.02 | -3270 | 0 |  |  |  | 0 | 0 | 0 | 0 | 4.85 | 6.27 | 4.85 | 0 | 0 | 0 | 4.5.1.9 | 7855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 |  | 17660 | 0 | 0 | 0 | 0 | -5295 | 0 | -1316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.01 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -56 | 1865 | 5865 | 15865 | 495866 | 595866 | 695866 | 795866 | 4134 | 9398 | 9398 |  | 147 |  | 52.6 | 28.1 | 70 | 66 | 100 | 67 | 65.9 | 73.3 | 20 | -3270 | 0 | 0 | 0 | 0 | 85 | 0 | 100 | 50 | 52.6 | 100 | 83.2 | 83.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 6.6 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1609049392586 | 0 | 45 | 1 | 0 | 0 | 0 | 0 | 18.16 | 0 |  | 4134 |  |  |  |  | 0 | 0 | 0 | 0 | 40132 | 39866 | 0 | 0 | 0 |  | 0 | 0 | 565 | 571 | 563 | 571 | 568 | 568 | 570 | 568 | 570 | 568 | 570 | 570 | 566 | 565 | 566 | 567 | 562 | 566 | 567 | 567 | 569 | 569 | 567 | 564 | 567 | 567 | 571 | 571 | 562 | 563 | 0 | 0 | 185 | 374 | 374 | 8 | [42 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.6 | 39 |  |  | 87.7 | 88 | 87.8 | 28.9 |  |  |  |  | 758 | 1606207384071 |  | 4414 | 0.949 | 50.02 | 0 | 10147 | 5865 | 10128 | 5848 | 10155 | 5856 | 10158 | 5863 | 10140 | 5864 | 10143 | 5851 | 0 | 0 | 0 | 0 | 0 | 0 | 2.15 | -44.4 | 4 | 0.85 |  | 0 | 83.2 | 71.2 | 0 | 66 | 65.9 | 66.3 | 1 | 0 | 0 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 62.5 | 72.8 | 76.6 | 65.5 | 52.7 | 67.7 | 69.6 | 73.7 | 75.6 | 65.7 | 65.7 | 72.2 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 9422.5 | 9422.9 | 9476.2 | 9423 | 9422.5 | 9422.5 | 3985.4 | 9422.9 | 9422.9 | 9422.9 | 9422.8 | 9422.9 | 2018 | 2018 | 9 | 7 | 2018 | 8 | 10 | 2018 | 11 | 7 | 10 | 7 | 2018 | 10 | 7 | 2018 | 10 | 7 | 2013 | 27 | 12 | 2018 | 11 | 7 | 2018 | 10 | 7 | 2018 | 9 | 7 | 2018 | 11 | 7 | 2018 | 21 | 6 | 42104 | 41987 | 43214 | 42110 | 42064 | 42105 | 12658 | 42111 | 42033 | 41988 | 42108 | 41985 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | -14.2 | -14.2 | -14.2 | -14.2 | -14.2 | -14.2 | -14.2 | -14.2 | -14.2 | -14.2 | -14.2 | -14.2 | -14.2 | -14.2 | -14.2 | -14.2 | -14.2 | -14.2 | -14.2 | -14.2 | -14.2 | -14.2 | -14.2 | -14.2 | 220 | 205 | 220 | 79 | 141 | 189 | 174 | 205 | 189 | 126 | 189 | 205 | 174 | 205 | 158 | 253 | 253 | 141 | 110 | 174 | 237 | 110 | 189 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 305 | 402 | 537 | 378 | 378 | 317 | 268 | 476 | 305 | 317 | 378 | 451 | 329 | 378 | 341 | 317 | 390 | 390 | 378 | 293 | 317 | 256 | 329 | 549 | 0.008 | 5.27 | 0 | 3 | [98 empty] | 37954.7 | 0 | 12086 | 0 | 252 | 0.02 | 0 | 1376 | 1.1 | 0 | 10139 | 4.5.1.0.1 | 4.5.2.0.3 | 4.5.1.0.6 | 4.5.4.0.2 | 4.5.0.0.0 | 4.5.6.7.3 | 4.9.0.0.9 | 4.5.2.0.9 | 4.5.3.0.2 | 4.5.1.0.8 | 4.5.1.0.0 | 4.5.1.0.0 | 4.5.4.0.3 | 4.5.4.0.0 | 4.5.0.2.4 | 4.5.3.2.0 | 4.5.0.0.3 | 4.5.0.0.0 | 4.5.0.0.0 | 4.5.1.0.0 | 4.5.1.0.6 | 4.5.0.0.0 | 0.0.0.0.0 | 4.5.2.2.5 | 4.5.0.0.0 | 4.5.2.0.9 | 4.5.1.0.2 | 4.5.0.0.0 | 4.5.1.0.0 | 4.4.0.0.0 |  | 20.1 | 22.5 | 18.5 | 18.9 | 18.4 | 19.7 | 20.8 | 17.9 | 19.2 | 20.8 | 20.9 | 22.1 | 20.3 | 20.5 | 20.3 | 20.3 | 20.2 | 19.9 | 21 | 21.6 | 18.7 | 20.6 | 19.2 | 21.1 | 20.2 | 22.5 | 17.9 | 1348 | [31 empty] | 0 |  |  | 0 |  | 0 |  | 1789 | 0 |  |  | 1 | 1606694400000 |  | 0 | 385957 |  | 5.2 | 4 |  | 1 | 11 |  | 1 | 0 | 6 |  | 1 | 1000 | 15 | 279 | 2 |  | 2 |  | 2 | 3.22 | 3.29 |  | 0 |  | 3500 |  | 13.98 | 129.5 | 0 | 351 |  |  |  |  | Running | 50 |  |  |  |  | 27.51 | 2 | 2 | 50.03 | 50.03 | 0 | 50.03 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 1 | 0 | 970 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 1 | 0 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 300 | 30 | 1 | 1.4 | 60 | 1.5 | 80 | 14 | 6 | 11 | 1 | 0 | 0 | 0 | 0 | 7 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 30 | [5 empty] | 0 | 0 | 1 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 100 | -900 |  | -200 | -1400 | 10 | 0 | 50 | 1500 | 5.6 | 6.7 | 6.9 | 0.1 | 2.7 | 0.1 | 0 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 5.4 |  | 0 | 0 | 0.2 | 0 |  | 10 | 0 |  |  |  | 0 |  | 5 | 5 | 5 | 5 | 5 | 60 | 28 | 40 | 30 | 50 | 180 | 28 | 40 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 0 | 0 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | [479 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 5 | 0 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 35 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 |  |  | 60 | -27 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | [12 empty] | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 1 | 1 | 40 | 0 | 30 | 30 | 10 | 10 | 10 | 3 | 1 | 10500 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 5 | 5 | 0.05 | 0.05 | 0.2 | 0.2 | 1 | 0.56 | 0 | 0.56 | 1 | 30 | 1 | 0 | 0 | 439.7 | 439.7 | 4.5 | 50 | 50 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 5000 | -5000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 47.5 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 0 | 110 | 90 | 35 | 8 | 0 | 0 | 1 | -0.2 | 50 | 110 | 80 | 0 | 0 | 301 | 200 | 1 | 105 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10000 | 0 | 0 | 0 | 0 | 10500 | 120 | 95 | 45 | 0 | 10 | 0 | 0 | 0 | -0.4 | 50 | 110 | 80 | 0 | 1 | 400 | 200 | 0 | 100 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 90 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30 | 30 | 70 | 490 | 490 | 300 | 0 | 120 | 30 |  | 1 |  | 0 | 1 | 0 | 0 | 0 |  | 0 |  | 0 |  |  |  | 1 | 1 |  |  |  | 0 | 0 |  | 1 |  | 1 | 1 | 0 |  | 0 | 1 | [8 empty] | 0 | 1 |  | 0 | 0 |  |  | 0 |  | 0 | 0 | 1 | 0 |  | 1 | 1 | 0 | 0 |  | 0 |  |  |  | 12.5 |  | 624 |  |  |  |  | 11 | 0 | 336 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.8 | 100 | 0.02 | 100 | 41 | 0 | 1 | 8 | 100 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 30 | 0 | 100 | 5 | 0 | 0 | -5 | 15 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 35 | 30 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 202 | 168 | 75 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 65 | 3 | 0 | 0 | 0 | -2.5 | 10 | 1 | 20 | 15 | 1 | 2 | 1 | 1.82 | 0.6 | 0.6 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0.05 | 0 | 0 | 0 | 15 | 30 | 0.01 | 0.4 | 0 | 60 | 30 | 0 | 0 | 0 | 0 | 1200 | 1400 | 0 | 0.5 | 450 | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 0.2 | 0.05 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1.2 | 0.1 | 280 | 280 | 280 | 280 | 0 | 50 | 50 | 50 | 50 | 50 | 120 | 0 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.3 | 1 | 25 | 5 | 100 | 0 | 10 | 0.01 | 0.5 | 1 | 3 | 60 | 2 | 25 | 10 | 250 | 3 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 | 0 | 1 | 4000 | 2000 | 20000 | 10000 | 4397 | 2198 | 0 | 0 | 2 | 0 | 30 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 0 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 |  | 1 | 650 | 700 | 1 | 0 | 0 | 0 | [66 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 1 | 1 | 1200 | 38000 |  |  |  | 44800 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 100 | 1000 | 680 | 640 |  | 650 |  |  | 640 | 5 | 650 | 5 | [7 empty] | 5 | 450 |  |  | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 20 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 10 | 20 | 5 | 0 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | [15 empty] | 5468 | 88 | 90 | 2.16 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 1 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 75 | 90 | 75 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 44.2 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 45 | 300 |  | 75 | 1.2 | 0 | 0 | 0 |  | 0.1 | 0.84 | 60 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 930 | 0 | 5000 | 50 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 500 | 1000 |  |  |  | 0 | 1 | 1 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 0 | 20 | 0.9 | -0.95 | 0.95 |  | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 10500 |  |  | 1 | 0 | 2 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -1476 | 3280 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 0 | 1 | 1 | -0.9 | -3400 | 3400 | 10 | 0 | 100 | 0 | 100 | 0 | 800 | -20 | 800 | -20 | 600 | 0 | 10 | 3.3 | 0.2 | 3.1 | 0.05 | 1.5 | 1.7 | 0.05 | 0.05 | 120 | 5 | 120 | 5 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 30 |  |  | 20 |  |  |  | 3 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.6 | 0.2 | 0.5 | 500 | 1500 | 3.5 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1.5 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 120 | 2 | 120 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 1 | 0 | 75 | 120 | 2 | 2 | 0 | 1 | 0 | 75 | 120 | 2 | 2 | 1 | 62 | 2 | 1 |  | 75 | 120 | 0.5 | 0.5 | 0 | 0 | 0 | 99 | 200 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 200 | -200 | 0 | -70 | 100 | -100 | 0 | 0 | 0 | 200 | -200 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 9.5 | 10 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 10 | 0 | 0 | 1 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 18 | 18 | 18 | 18 | [5 empty] | 4 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 924 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 1 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 0 | 0 | 20 | 4000 | 4000 |  | 850 | 30 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 3 | 3 | 3 | 3 | -5 | -5 | -5 | -5 | 13 | 13 | 13 | 13 | 4.5 |  | 45 | 270 | 70 | -144 | 0 | 80 | 350 | [24 empty] | 0 | 4 | 500 | 30 |  | 4000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 380 | 1 | -30 | -9 | 4300 | 1300 | 10 | 4300 | 2600 | 60 | 0 | 0 | [6 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4398 | 2200 | 5454 | 2797 | 1499 | 1499 |  | 53.1 | 53 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4900 | 2150 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4900 | 2150 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4900 | 2150 | 1500 | 1500 |  | 50 | 50 |  | 660 |  | 0 | 1000 | 300 | 48 | -1.6 | -4 | 100 | 10 | 0 | 1 | 10 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 |  | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 10 | 0 | 0.5 | 0 | 0 | 60000 | 0 | 60000 | 0 |  | 4 | 0 | 1 | 0 |  |  |  | 80 |  | 48 | [14 empty] | 53 | 53 | 53 | 53 | [10 empty] | 0 | 0 | 1 | 3 | 57 | 59 | 2 | 2 | 60 |  | 48 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 350 | 105 | 105 | 105 | [8 empty] | -1225 | 4900 |  | 0.2 | 100 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.4 |  |  | 100 | 0.2 |  | 100 |  | 100 | 100 | [11 empty] | 0.2 | 100 | 200 | [43 empty] | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 65 | 70 | 100 | 100 | 0 | 0 | 1 | 100 | 0.02 | 100 | 49 | 0 | 1 | 7 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 50 | 67 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 1.5 | 0.003 | 1 | 1 | 10 | 0.6 | 0 | 1 | 12 | 1 | 1 | 1 | 1 | 0 | 0 | 1.1 | 0.7 | 1 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | 0 | 0.1 | 0.5 | 0.5 | 100 | 40 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 50 | 0 | 100 | 10 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | [42 empty] | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 1 | 0 | 10 | 10 | 10 | 2 | 5 | 0 | 48 | 50 | 1 | 5000 | 8000 | 5000 | 8000 | 6 | 6 | 0 | 5000 | -5000 | 0 | 0 | 0.02 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 98.2 | 92.2 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 12 | 2 | 5 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 80 | 0 | [6 empty] | 0.01 | 0.03157 | 0.5936 | 100 | 0 | 0 | 0.44428 | 0.23695 | 99 | 2 | 0 | 20 | 5000 | 5000 | 60 | 75 | 90 | 100 |  | 0 | 20 | 2198 | 4397 | 2.5 | 1.25 | 35 | 45 |  | -2 | -2 | -2 | -2 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -145 | 10 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 4397 | 4397 | 4397 | 4397 | 50 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 |  | 10 | 0 | 150 | 1 | 1 | 102 | 112 | 98 | 91 | 112 | 50 | 65 | 85 | 75 |  | 105 | 120 | 95 | 70 | 140 | 0 | 80 | 0 | 120 | 1 | 20 | 5.55 | 0 | 0 | 120 |  |  | 5 | 4 | 4 | 4 | 4 | 56 | 56 | 56 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [30 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1650 | 10 | 200 | 400 | 2800 | 5 | 10000 | 0 | 3850 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 0 | 1500 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 800 |  | 0.2 | 0.7 | 4 | 98 | 8 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1500 | 6.7 | 0 | 95 | 85 | 85 | 95 | 95 | 9.54 | 9.971 | 720 |  |  | 1.28 | 1.52 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.1 |  |  | 0.6 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | [28 empty] | 1 | 1 | 0 | 2 | 0 | 2 | 1 | 1 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4188 |  |  | 4397 | 0 | 0 | 0 | 0 | 0 | 4397 | 4199 |  |  | 2.63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 21.2 | -44.52 | 4.012 |  | 0.841 | 0 | 0.56 | 4199 | 0 | 0 | 2.24 | 1 | 0 | 1 | 0 | 166 | 162 | 153 | 203 | 259 | 27 | 25 | 26 | 373 | 420 | 478 | 478 | 316 | 32 | 26 | 30 | 0 | 66.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 370 | 0 | 372 | 386 | 0 | 0 | 0 | 383 | 385 | 0 | 384 | 0 | 369 | 367 | 382 | 0 | 383 | 369 | 384 | 384 | 374 | 369 | 363 | 0 | 501 | 493 | 0 | 493 | 493 | 497 | 500 | 492 | 0 | 495 | 493 | 492 | 496 | 496 | 492 | 497 | 504 | 504 | 0 | 488 | 0 | 495 | 497 |  | Sending | 30 | 42 | 41 | 42 | 42 | 42 | 43 | 45 | 43 | 43 | 43 | 43 | 45 | 43 | 42 | 43 | 46 | 44 | 43 | 44 | 44 | [20 empty] | 19.0012 |  |  |  | 1334 | 1211 | 1139 | 1218 | 1045 | 1478 | 1283 | 1052 | 1513 | 1514 | 1300 | 1516 | 3008 | 3008 | 3007 | 3007 | 3150 | 1477 | 1431 | 3198 | 3008 | 1090 | 1427 | 3008 |  | 49 | 1 | [11 empty] | 66.6 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 240.4 | 0 | 0 | 0 | 1091 | 0 | 0 | 0 | 10.4 | 0 | 0 | 0 | 1.949 |  |  |  | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [244 empty] | 0 | 1 | 1 | 1 | 17 | 0 | 98.8 | 98.1 | 98.2 | 0 | 0 | 17.4 | 17.6 | 0 | 17.5 | 0 | 0 | 0 | 5.28 |  | 0 | 0 | 0 | 0 |  | 98.8 | 98.8 | 98.8 | 98.8 | 17.4 | 17.4 | 17.4 | 17.4 |  | 1500 | 1499 |  | 52.6 |  |  | 0 | 0 | ABINSK
7 |  |  |  |  | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","rem_conn":"Back-NoSSL-NoProxy","dataItems":"3157/7533","agent_conn":"Prim-SSL-NoProxy","mon_conn":"Back-NoSSL-NoProxy"} | 0 | 0 | 0 | 755 | 0 | 0 | -0.92 | 4.99 | 12.7 | 546 | 0 | -1127 | 0 | 6.29 | 0 | 3.76 | 3.94 | -3270 | 0 |  |  |  | 0 | 0 | 0 | 0 | 5.06 | 6.57 | 5.07 | 0 | 0 | 0 | 4.4.0.13 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 |  | 15950 | 0 | 0 |  | 0 | -5075 | 0 | -1358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257 | 2257 | 4257 | 6257 | 498536 | 598536 | 698536 | 798536 | 1723 | 18001 | 18001 |  | 391 |  | 72.3 | 0 | 70 | 70.4 | 90.5 | 67 | 66.8 | 57.7 | 20 | -3270 | 0 | 0.94 | 0.939 | 53.1 | 90 | 90.2 | 40.1 | 72.3 | 72.3 | 0 | 84.5 | 84.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [53 empty] | 2 | 2 | 2 | 2 | 2 | 51 | 51 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 51 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 44 | 1 | 0 | 46.6 | 50.7 | 0 | 21.37 | 0 |  | 1464 |  |  |  |  | 0 | 0 | 0 | 0 | 38467 | 38620 | 0 | 0 | 0 | 0 | 0 | 0 | 575 | 577 | 575 | 579 | 577 | 577 | 580 | 583 | 584 | 582 | 580 | 578 | 577 | 580 | 577 | 579 | 579 | 580 | 581 | 584 | 582 | 581 | 579 | 579 | 579 | 580 | 584 | 585 | 575 | 576 | 0 | 0 | 0 | 389 | 386 | 9 | [42 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 16967837 | 9209279 |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.7 | 49 |  |  | 68.9 | 68.8 | 71.4 | 28.2 |  |  |  |  | 262 |  |  | 4227 | 0.939 | 49.94 | 0 | 11107 | 6393 | 11100 | 6398 | 11091 | 6434 | 11122 | 6408 | 11087 | 6406 | 11112 | 6436 | 0 | 0 | 0 | 0 | 0 | 0 | 2.27 | -33.7 | 4.12 | 0.94 |  | 0 | 84.5 | 75.6 | 0 | 0 | 66.8 | 70.4 | 15 | 0 | 0 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 20.8 | 44.8 | 51.2 | 53.3 | 55.8 | 45.6 | 44.2 | 46 | 52 | 52.2 | 47.1 | 45.3 | 49.5 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 17771.7 | 17771.7 | 17771.7 | 17771.5 | 17771.8 | 17771.7 | 17771.8 | 17771.7 | 17771.7 | 17771.8 | 17771.8 | 17771.7 | 2017 | 2017 | 16 | 12 | 2017 | 13 | 12 | 2017 | 13 | 12 | 13 | 12 | 2017 | 13 | 12 | 2017 | 13 | 12 | 2017 | 16 | 12 | 2017 | 17 | 12 | 2017 | 13 | 12 | 2017 | 13 | 12 | 2017 | 14 | 12 | 2017 | 13 | 12 | 38107 | 38187 | 38114 | 38088 | 38110 | 38115 | 38188 | 38229 | 38111 | 38112 | 38135 | 38113 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  | 0 | 0 | -9.6 | -9.6 | -9.6 | -9.6 | -9.6 | -9.6 | -9.6 | -9.6 | -9.6 | -9.6 | -9.6 | -9.6 | -9.6 | -9.6 | -9.4 | -9.6 | -9.6 | -9.6 | -9.6 | -9.6 | -9.6 | -9.6 | -9.6 | -9.6 | 237 | 220 | 110 | 110 | 110 | 189 | 110 | 126 | 94 | 126 | 158 | 94 | 126 | 174 | 284 | 174 | 189 | 94 | 94 | 62 | 253 | 141 | 110 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 329 | 219 | 219 | 317 | 305 | 207 | 244 | 219 | 256 | 231 | 439 | 451 | 354 | 219 | 317 | 268 | 268 | 305 | 293 | 341 | 219 | 415 | 293 | 0.011 | 5.05 | 0 | 0 | [98 empty] | 66952.2 | 0 | 23885.8 | 0 | 218 | 0.02 | 0 | 1438 | 1.04 | 0 | 11117 | 4.4.0.0.0 | 4.4.0.0.1 | 4.4.0.0.0 | 4.4.1.0.10 | 4.4.0.0.10 | 4.4.4.5.8 | 4.7.1.0.0 | 4.4.0.0.12 | 4.4.2.0.8 | 4.4.0.0.12 | 4.4.0.0.0 | 4.4.0.0.8 | 4.4.0.0.0 | 4.4.0.0.0 | 4.4.0.0.9 | 4.4.0.1.10 | 4.4.0.0.0 | 4.4.0.0.2 | 4.4.0.0.0 | 4.4.0.0.2 | 4.4.0.0.12 | 4.3.0.0.0 | 0.0.0.0.0 | 4.4.0.0.11 | 4.4.1.0.0 | 4.4.0.0.13 | 4.4.0.0.9 | 4.3.0.0.0 | 4.4.0.0.6 | 4.4.0.0.0 |  | 15.7 | 15.7 | 14.9 | 16.4 | 17.1 | 14.9 | 15.5 | 15.3 | 15.2 | 16.2 | 14.6 | 16.3 | 16.6 | 14.9 | 15.2 | 15.5 | 16.3 | 17.7 | 15.6 | 16.7 | 14.4 | 16.4 | 15.5 | 15.7 | 16 | 17.7 | 14.4 | 1134 | [82 empty] | Running | 50 |  |  |  |  | 3.44 | 2 | 1 |  | 49.95 | 0 | 49.95 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 0 | 0 | 970 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 1 | 0 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 30 | 30 | 0 | 1.4 | 20 | 1.5 | 80 | 1 | 1 | 11 | 3 | 0 | 0 | 0 | 0 | 7 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 45 | [5 empty] | 0 | 0 | 1 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 100 | -900 |  | -200 | -1400 | 10 | 0 | 50 | 1500 | 6 | 6.7 | 6.9 | 0.1 | 4.7 | 0.1 | 1 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 4.7 |  | 0 | 0 | 0.2 | 0 |  | 10 | 0 |  |  |  | 0 |  | 5 | 5 | 5 | 5 | 5 | 60 | 28 | 40 | 30 | 45 | 180 | 28 | 40 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 1 | 10 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 1 | 10 | 2 | 0 | 0 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 2 | 10 | [479 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 19 | 20 | 20 | 20 | 19 | 18 | 18 | 18 | 10 | 0 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 32 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 | 0.95 | 0 | 60 | -27 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | 85 | 110 | 90 | 95 | 100 | 105 | 0.85 | 0.9 | 0.95 | 1 | -0.97 | -0.95 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 1 | 45 | 0 | 30 | 30 | 10 | 10 | 10 | 3 | 1 | 11000 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 4 | 4 | 0.01 | 0.01 | 0.2 | 0.2 | 1 | 1.11 | 1 | 1.11 | 1 | 30 | 0 | 0 | 0 | 100 | 100 | 10 | 50 | 50 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 5000 | -5000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 51.5 | 47.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 1 | 115 | 85 | 35 | 10 | 0 | 0 | 1 | -0.2 | 50 | 110 | 80 | 1 | 0 | 275 | 200 | 1 | 110 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 11000 | 20 | 10 | 5 | 11000 | 0 | 0 | 0 | 0 | 11000 | 120 | 90 | 45 | 0 | 10 | 0 | 0 | 0 | -0.4 | 50 | 110 | 80 | 0 | 1 | 400 | 200 | 0 | 100 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 90 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 250 | 100 | 50 | 80 | 500 | 100 | 460 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 5 | 0 | 30 | 50 | 0 | 0 | 0 | 30 | 0 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 |  | 1 |  |  |  | 1 | 0 |  |  |  | 0 | 0 | 1 | 1 |  | 1 | 1 | 0 |  | 1 | 0 | [8 empty] | 1 | 1 |  | 0 | 0 |  |  | 0 |  | 0 | 1 | 1 | 1 |  | 1 | 1 | 0 | 0 |  | 0 |  |  |  | 11.5 |  | 624 |  |  |  |  | 11 | 0 | 362 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.5 | 0.1 | 0.1 | 100 | 41 | 0 | 0 | 1 | 100 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 30 | 0 | 100 | 0 | 0 | 0 | -5 | 15 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 55 | 30 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 200 | 168 | 75 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 92 | 1 | 0 | 0 | 1 | 65 | 1 | 0 | 0 | 0 | -2.5 | 10 | 1 | 20 | 15 | 1 | 2 | 1 | 1.82 | 0.6 | 0.6 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0.15 | 0 | 0 | 0 | 15 | 30 | 0.01 | 0.4 | 0 | 60 | 30 | 0 | 0 | 0 | 0 | 1200 | 1400 | 0 | 0.5 | 450 | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 0.2 | 0.05 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1.2 | 0.1 | 300 | 300 | 300 | 300 | 0 | 50 | 50 | 50 | 50 | 50 | 120 | 1 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.15 | 3.6621 | 25 | 2.9297 | 100 | 0 | 6.5 | 0.1 | 0.5 | 1 | 7 | 100 | 2 | 25 | 10 | 250 | 6 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 | 0 | 0 | 4000 | 2000 | 20000 | 10000 | 0 | 0 | 0 | 0 | 2 | 1 | 30 | 150 | 20 | 120 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 0 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 | 1.5 | 1 | 650 | 700 | 1 | 0 | 0 | 1 | [66 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 1 | 1 | 1200 | 38000 |  |  |  | 44800 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 100 | 1000 | 680 | 640 | 5 | 650 | 5 | 650 | 640 | 5 | 650 | 5 | 1000 | 5 | 15 | 300 | 20 | 50 | 650 | 5 | 1000 | 5 | 1000 | 100 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | 0 | -0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 5 | 55 | 20 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 30 | 20 | 5 | 10 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | 0 | 20 |  | 0.98 | 1 | -0.98 | -0.95 | 0.8 | -0.95 | 0.94 | 5 | 0.95 | -0.95 | 20 | 80 | 5250 | 88 | 90 | 1.68 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 0 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 85 | 90 | 85 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 145 | 5 | 5 | 1 | 43.2 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 45 | 300 |  | 75 | 0.857 | 0 | 0 | 0 | 180 | 0.1 | 1.11 | 60 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 930 | 0 | 5000 | 50 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 500 | 1000 | 1 | 0 | 0 | 0 | 1 | 2 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 0 | 20 | 0.8 | -0.95 | 1 | 0 | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 400 | 0 | 0 | 0 | 0 | 1 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -100 | 100 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 0 | 0 | 1 | -0.9 | -100 | 100 | 10 | 0 | 100 | 0 | 100 | 0 | 800 | -20 | 800 | -20 | 0 | 0 | 10 | 3.3 | 0.2 | 3.1 | 0.05 | 1.5 | 1.7 | 0.05 | 0.05 | 120 | 5 | 120 | 5 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 5 |  |  | 1 | 30 |  |  | 20 |  |  |  | 3 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.4 | 0.1 | 0.5 | 500 | 1500 | 3.5 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1.5 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 120 | 2 | 120 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 3 | 0 | 0 | 0 | 68 | 120 | 2 | 2 | 0 | 1 | 0 | 75 | 120 | 2 | 2 | 0 | 62 | 2 | 1 |  | 72 | 120 | 0.5 | 0.5 | 0 | 1 | 0 | 95 | 200 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 82 | 0 | 0 | 0 | 5 | 20 | 0 | 2 | 30 | 90 | 0 | 0 | 0 | 200 | -200 | 0 | -70 | 100 | -100 | 0 | 0 | 0 | 200 | -200 | 20 | 30 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 50 | 100 | 1 | 8.5 | 9 | 0.3 | 0 | 16 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 10 | 0 | 0 | 1 | 90 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 18 | 18 | 18 | 18 | [5 empty] | 4 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 924 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 1 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 100 | 10 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 0 | 0 | 20 | 4000 | 4000 |  | 850 | 30 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 2 | 3 | 3 | 3 | -5 | -5 | -5 | -5 | 13 | 13 | 13 | 13 | 4.5 |  | 45 | 270 | 70 | -144 | 0 | 80 | 350 | [24 empty] | 0 | 4 | 500 | 30 |  | 4000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 380 | 1 | -30 | -9 | 4000 | 2000 | 10 | 4000 | 2000 | 60 | 0 | 0 | [6 empty] | 0 | 0.39062 |  | 0.06 | 2.5 | 1.1 | [5 empty] | 4200 | 2100 | 5530 | 2850 | 1500 | 1500 |  | 71.4 | 70 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4900 | 2150 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4900 | 2150 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4900 | 2150 | 1500 | 1500 |  | 50 | 50 |  | 660 |  | 0 | 1000 | 300 | 48 | -1.6 | -4 | 100 | 10 | 0 | 1 | 10 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 |  | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 10 | 0 | 0.5 | 0 | 0 | 60000 | 0 | 60000 | 0 |  | 5 | 0 | 1 | 0 |  |  |  | 80 |  | 67 | [14 empty] | 75 | 75 | 75 | 75 | [10 empty] | 0 | 0 | 1 | 3 | 57 | 59 | 2 | 2 | 82 |  | 67 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 350 | 110 | 110 | 110 | [8 empty] | -1100 | 4400 |  | 0.2 | 100 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.4 |  |  | 100 | 0.2 |  | 100 |  | 100 | 100 | [11 empty] | 0.2 | 100 | 200 | [43 empty] | 0 | 0.5 | 100 | 100 | 100 | 45 | 0 | 1 | 2 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 75 | 65 | 70 | 100 | 100 | 60 | 0 | 0.1 | 100 | 100 | 100 | 50 | 0 | 1 | 1.8 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 75 | 63 | 67 | 0 | 100 | 45 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 10 | 0.6 | 0 | 1 | 12 | 1 | 1 | 1 | 1 | 0 | 0 | 1.1 | 0.7 | 1 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 40 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 85 | 90 | 0 | 100 | 0 | 0 | 0.1 | 0.5 | 0.5 | 100 | 40 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 50 | 0 | 100 | 10 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | [42 empty] | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 0 | 0 | 10 | 150 | 150 | 100 | 205 | 0 | 48 | 50 | 0 | 3000 | 6000 | 3000 | 6000 | 6 | 6 | 0 | 5000 | -5000 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 100 | 50 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 |  |  |  |  | 12 | 2 | 5 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 80 | 0 | [6 empty] | 0.01121 | 0.28619 | 0.87857 | 100 | 0 | 0 | 0.44428 | 0.23695 | 100 | 2 | 0 | 20 | 5000 | 5000 | 60 | 75 | 90 | 100 |  | 0 | 20 | 2100 | 4200 | 2.5 | 2 | 55 | 55 |  | -2 | -2 | -2 | -2 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -145 | 10 | 5 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 4200 | 4000 | 4000 | 4000 | 50 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 |  | 10 | 0 | 150 | 1 | 1 | 102 | 112 | 98 | 91 | 112 | 50 | 65 | 85 | 75 |  | 105 | 120 | 95 | 70 | 140 | 0 | 80 | 0 | 120 | 1 | 20 | 5.55 | 0 | 0 | 120 |  |  | 10 | 4 | 4 | 4 | 4 | 78 | 78 | 78 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [30 empty] | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 1 | 0 | 0 | 1650 | 10 | 200 | 400 | 2800 | 5 | 5000 | 0 | 3850 | 1 | 5 | 5 | 55 | 10 | 100 | 0 | 1 | 999 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 800 |  | 0.16406 | 2.1973 | 4.3945 | 100 | 2 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1500 | 6.7 | 0 | 95 | 85 | 85 | 95 | 95 | 9.53 | 9.95 | 817 |  |  | 1.4 | 1.6 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.1 |  |  | 0.6 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [28 empty] | 1 | 1 | 0 | 2 | 0 | 2 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3972 |  |  | 4200 | 0 | 0 | 0 | 0 | 0 | 4200 | 4000 |  |  | 2.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1593.3 | 5.4 | -33.78 | 4.127 |  | 0.939 | 0 | 0.72 | 0 | 0 | 0 | 2.23 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 370 | 371 | 376 | 384 | 377 | 376 | 372 | 382 | 385 | 386 | 379 | 380 | 375 | 373 | 371 | 370 | 384 | 382 | 384 | 382 | 373 | 370 | 381 | 507 | 504 | 493 | 493 | 502 | 500 | 505 | 504 | 501 | 506 | 502 | 507 | 495 | 496 | 498 | 493 | 497 | 503 | 503 | 506 | 504 | 505 | 494 | 505 |  | Sending | 30 | 43 | 42 | 43 | 44 | 43 | 43 | 42 | 43 | 43 | 43 | 41 | 38 | 41 | 43 | 44 | 43 | 43 | 43 | 0 | 0 | [24 empty] | 1911 | 2141 | 1768 | 1705 | 1969 | 1966 | 2021 | 1877 | 1830 | 1987 | 1797 | 1747 | 2146 | 1840 | 2021 | 1845 | 1241 | 2068 | 1734 | 2004 | 1761 | 2001 | 1908 | 1952 |  | 0 | 0 | [11 empty] | 71.6 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | 230.9 | 0 | 0 | 0 | 1078 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 1.88 |  |  |  | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [244 empty] | 0 | 0 | 1 | 1 | 27 | 0 | 100 | 99.8 | 99.2 | 0 | 0 | 21.1 | 21.3 | 0 | 21.3 | 0 | 0 | 0 | 5.06 |  | 0 | 0 | 0 | 0 |  | 100 | 100 | 100 | 100 | 21.1 | 21.1 | 21.1 | 21.1 |  | 1500 | 1497 |  | 72.3 |  |  | 0 | 0 | PROSPERITY WEAVING MILLS LTD - 1 (1351388-X243)
8 | No Contact | 33.949 | 1.089 | 0 | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","agent_conn":"Prim-SSL-NoProxy","mon_conn":"Prim-SSL-NoProxy","rem_conn":"Back-NoSSL-NoProxy"} | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 4.14 | 0 | 0 | 0.96 | -3270 | 0 |  |  |  | 0 | 0 |  | 0 | 0.05 |  | 0.05 |  |  |  | 4.3.0.5 | 7217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1 | 0 | 1 | 0 |  |  | 0 | 0 |  | 0 |  |  |  | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.02 |  |  |  |  | 9794 | 18447 | 9805 | 9891 | 9880 | 9891 | 9881 | 0 | 0 | 19097 | 679 | 227 | 18686 | 8686 | 480863 | 580863 | 690676 | 790676 | 19731 | 19731 | 19731 | 3368 | 1280 |  | 28 | 0 | 70 | 28.7 | 100 | 69 | 16.5 | 0 | 40 | -3270 | 0 | 0.986 | 1 | 25 | 90 | 19.5 | 0 | 50 | 28 | 0 | 75 | 57.8 | 0 | 25 | 7 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 21.2 | 15.1 | 10.4 | 15.1 | 0 | 0 | 0 | 0 | [53 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [99 empty] | 41.7192 | 41.724 | [30 empty] | 0 | [12 empty] | 0 | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 | [20 empty] | 0 | [16 empty] | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 1608787288779 | 0 | 38 | 1 |  | 0 | 0 |  | 23.3 | 0.7 |  | 9324 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 49 | 49 | 50 | 49 | 51 | 50 | 51 | 50 | 49 | 53 | 52 | 53 | 49 | 50 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 535 | 54 | 543 | 49 | 524 | 0 | 20 | 0 | 0 | 0 | 19 | [42 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18.7 | 25.6 |  |  | 19.9 | 20.4 | 20.9 | 0 | 37.4 | 21.8 | 38.6572 | 29.5154 | 1 | 1606540156493 | 17105 | 0 | 0.999 | 45.53 | 0 | 15758 | 9077 | 15724 | 9105 | 15687 | 9051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.01 | -0.1 | 0.1 | -0.05 |  | 0 | 57.8 | 17.9 | 0 | 0 | 16.5 | 28.7 | 3 | 0 | 0 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45.8 | 0 | 0 | 0 | 56.2 | 52.8 | 56.1 | 57 | 57.5 | 53.8 | 49.1 | 0 | 1.24 | 0 | 0 | 0 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 88 | 0 | 0 | 0 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 0 | 19796.6 | 0 | 0 | 0 | 19796.6 | 19796.7 | 19796.7 | 19796.7 | 19796.7 | 19796.7 | 19796.6 | 0 | 2016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8 | 2016 | 11 | 8 | 2016 | 11 | 8 | 2016 | 9 | 8 | 2016 | 9 | 8 | 2016 | 10 | 8 | 2016 | 10 | 8 | 2016 | 10 | 8 | 0 | 0 | 0 | 31390 | 0 | 0 | 0 | 31445 | 31414 | 31348 | 31333 | 31365 | 31403 | 31360 | 0 | 7.7 | 0 | 0 | 0 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.647 | 0.3 | 0 | 0 | 18441 | 1228 | 7.9 | 7.68 | 7.71 | 7.8 | 7.56 | 7.66 | 7.78 | 7.67 | 7.81 | 7.95 | 7.59 | 7.71 | 7.67 | 7.56 | 7.66 | 7.58 | [8 empty] | 0.48 | 0.33 | -0.34 | 0.43 | -0.47 | -0.45 | 0.48 | -0.42 | 0.48 | -0.41 | 0.48 | 0.5 | 0.5 | -0.19 | 0.33 | -0.49 | [8 empty] | 7.69 | 7.57 | 7.69 | 7.66 | 7.66 | 7.77 | 7.73 | 7.56 | 7.69 | 7.9 | 7.74 | 7.75 | 7.7 | 7.81 | 7.85 | 7.67 | [8 empty] | 0.44 | 0.49 | 0.5 | 0.5 | 0.37 | 0.47 | -0.29 | 0.45 | -0.33 | -0.42 | 0.44 | 0.38 | 0.48 | 0.5 | 0.36 | 0.44 | [8 empty] | 52635.3 | 0 | 17546.4 | 0 | 0 | 0.02 | 0 | 0 | 1.02 | 0 | 0 | 4.3.0.0.5 | 4.3.0.2.0 | 4.3.0.0.0 | 4.3.0.0.1 | 4.3.0.0.2 | 4.3.0.6.0 | 4.3.1.0.0 | 4.3.0.0.5 | 4.3.0.0.0 | 4.3.0.0.4 | 4.3.0.0.5 | 4.3.0.0.0 | 4.3.0.0.5 | 4.3.0.0.1 | 4.3.0.0.2 | 4.3.1.3.2 | 4.3.0.2.1 | 4.3.0.0.4 | 4.3.0.0.0 | 4.3.0.0.0 | 4.3.0.0.5 | 4.3.0.0.0 | 0.0.0.0.0 | 4.3.0.0.5 | 4.3.0.0.0 | 4.3.0.0.1 | 4.3.0.0.0 | 4.3.0.0.0 | 4.3.0.0.1 | 4.3.0.0.0 | M01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1575 | [82 empty] | Available | 40 | Unknown |  |  |  | 15.25 | 2 | 2 |  | 0 | 0 | 49.99 | 0 | 100 | 100 | 100 | 100 | 0 |  | 0 |  | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 100 |  | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 0 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 0 | 0 | 970 | 40 | 0 | [6 empty] | 0 | 9 | 0 | 0 | 1 | 0 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 30 | 30 | 0 | 1.4 | 20 | 1.5 | 80 | 4 | 0 | 11 | 0 |  |  |  |  | 7 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 30 | [5 empty] | 0 | 0 | 1 | 120 |  | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 220 | -400 |  | -80 | -700 | 6 | 0 | 50 | 1300 | 3 | 3.7 | 3.9 | 0.1 | 2.7 | 0.1 | 0 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 3.6 |  | 0 | 0 | 0 | 0 |  | 10 | 0 |  |  |  | 0 |  | 5 | 5 | 5 | 5 | 5 | 60 | 28 | 40 | 30 | 50 | 180 | 28 | 40 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 |  |  | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 |  |  | 10 | 2 |  |  | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 |  |  | 10 | 2 |  |  | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | [9 empty] | 0 | 4 | 0 | [479 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 |  | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 10 | 0 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | [12 empty] | 4000 |  |  | 30 | 8 | 10 | 35 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | [11 empty] | 0 |  |  | 235 | [52 empty] | 7 | 5 | 30 |  |  |  |  | 0 | 15 | 60 | 0.95 | 0 |  |  | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | 85 | 110 | 90 | 95 | 100 | 105 | 0.85 | 0.9 | 0.95 | 1 | -0.97 | -0.95 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 |  |  |  | 0 | 30 | 30 | 10 | 10 | 10 | 3 | 1 | 6300 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | [42 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 51.5 | 47.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 1 | 115 | 85 | 35 | 5 | 0 | 0 | 1 | -0.1 | 50 | 110 | 80 | 1 | 1 | 305 | 200 | 1 | 136.36 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 15000 | 20 | 10 | 5 | 6300 | 0 | 0 | 0 | 0 | 15000 | 120 | 90 | 45 | 0 | 10 | 0 | 0 | 0 | -0.4 | 50 | 110 | 80 | 0 | 0 | 400 | 200 | 0 | 100 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 90 | 45 | [6 empty] | 0 | [34 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  |  |  | 1 | 1 |  |  | 0 | 0 | 0 | 1 | 1 |  | 1 | 1 | 0 |  | 0 | 0 | [8 empty] | 0 | 1 |  | 0 | 0 |  |  | 0 |  | 0 | 0 | 1 | 1 |  | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 11.5 |  | 616 |  |  |  |  | 11 | 0 | 198 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.5 | 0.1 | 0.1 | 100 | 150 | 0 | 0 | 2.5 | 100 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 45 | 45 | 0 | 70 | 0 | 0 |  |  | 15 | [25 empty] | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 200 | 168 | 75 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 4 | 1 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 1 | 65 | 1 | 0 | 0 | 0 | -4.5 | 10 | 0 | 60 | 55 | 0 | 2 | 1.65 | 1.82 | 6.6 | 6.7 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | [6 empty] | 0 | 0 | 0 | 0 | [7 empty] | 0.5 | 0 | 0 | 0 |  |  | 0 | 0.5 | 700 | [8 empty] | 12.5 |  |  | 2.2 | 12.5 | 0 | [15 empty] | 0 | 50 | 50 | 50 | 50 | 50 | 120 | 1 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 2.3203 | 4.3945 | 25 | 20.5078 | 100 | 0 | 20 | 0 | 0.5 | 0 | 4 | 50 | 0 | 25 | 10 | 250 | 6 | [28 empty] | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 0 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | 0 | 100 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 17 | 5 | 7 | 8.5 | 10 | 12 | 13.5 | 15.3 | 25 | 25 | 60 | 0 | 30 | 0 | 1 | 6 | 0.8 | 6 | 0 | 3.5 | 1 | 6 | 0 | 10 | 92 | 0 | 8000 | 0 | 0 | 540 | 27 | 1000 | 0 | 0 | 1 | 300 | 0 | 300 | 0 | 3 | 300 | 0 | 150 | 8.2 | 7.5 | 180 | 90 | 900 | 30 | 200 | 300 | 40 | 20 | 100 | 0 | 100 | 0 | 0 | 300 | 500 | 600 | 0 | 500 | 600 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 1200 | 1000 |  |  |  | 1000 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 50 | 1000 | 680 | 640 | 5 | 650 | 5 | 1000 | 640 | 5 | 680 | 5 | 1000 | 5 | 15 | 300 | 20 | 50 | 650 | 5 | 1000 | 5 | 1000 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.6 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 |  |  |  |  | 100 |  | 10 | 3 |  | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 20 | 5 | 10 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | 4 | 20 |  | 0.98 | 1 | -0.98 | -0.95 | 0.8 | -0.95 | 0.98 | 4 | 0.95 | -0.95 | 20 | 80 | 3325 | 88 | 90 | 2.01 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 0 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 75 | 90 | 75 | 80 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 58 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 45 | 300 |  | 75 | 1.03 | 0 | 0 | 0 | 60 | 0.1 | 0.56 | 60 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 930 | 0 | 5000 | 50 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 500 | 1000 | 1 | 0 | 0 | 0 | 1 | 2 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 0 | 20 | 0.8 | -0.95 | 1 | 0 | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 400 | 0 | 0 | 0 | 0 | 1 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -100 | 100 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 0 | 0 | 1 | -0.9 | -100 | 100 | [12 empty] | 10 | 2.5 | 0.2 | 3 | 0.05 | 1.5 | 1.9 | 0.05 | 0.05 | 120 | 5 | 120 | 5 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 30 |  |  | 10 |  |  |  | 3 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.5 | 0.1 | 0.5 | 500 | 1500 | 4.6 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1.5 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 80 | 2 | 82 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 0 | 0 | 20 | 80 | 2 | 2 | 0 | 1 | 0 | 120 | 120 | 2 | 2 | 0 | 62 | 2 | 1 |  | 79 | 120 | 2 | 0.5 | 0 | 0 | 0 | 200 | 200 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 |  |  |  | 2 | 82 | 0 | 0 | 0 | 10 | 28 | 3 | 8 | 30 | 90 | 0 | 0 | 0 | 200 | -200 | 0 | -50 | 100 | -100 | 0 | 0 | 0 | 200 | -200 | 20 | 8 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | [13 empty] | 0 | 0 | 50 | 100 |  |  |  | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 1 | 1 | 90 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 18 | 18 | 18 | 18 | [5 empty] | 15 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 462 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 0 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 4 | 0 | 20 | 4000 | 4000 |  | 550 | 25 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 3 | 3 | 3 | 3 | -5 | -5 | -5 | -5 | 12 | 12 | 12 | 12 | 4.5 |  | 45 | 660 | 660 | -144 | 0 | 60 | 50 | [24 empty] | 0 | 4 | 500 | 30 |  | 8000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 250 | 0 | -24 | -13 | 2175 | 1280 | 10 | 2175 | 1280 | 60 | 0 | 0 | [6 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2673 | 1335 | 4164 | 2127 | 1499 | 1499 |  | 47 | 40.6 |  | 400 | [7 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2190 | 1100 | 2950 | 1550 | 1500 | 1500 |  | 47 | 44 |  | 400 | [7 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2190 | 1100 | 2950 | 1550 | 1500 | 1500 |  | 47 | 44 |  | 400 | [7 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2190 | 1100 | 2950 | 1550 | 1500 | 1500 |  | 47 | 44 |  | 400 |  | 0 | 1000 | 300 | 48 | -1.6 | -4 | 100 | 6 | 0 | 1 | 6 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6 | 0 | 0.5 | 0 | 0 | 120000 | 0 | 120000 | 0 |  | 4 | 0 | 0 | 0 |  |  |  | 75 |  | 40 | [14 empty] | 50 | 40 | 40 | 40 | [10 empty] | 0 | 0 | 1 | 3 | 47 | 49 | 2 | 2 | 60 |  | 40 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.1 |  |  | 100 | 0.2 |  | 80 | 136.36 | 136.36 | 63 | [8 empty] | -825 | 3300 |  | 0.2 | 100 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.4 |  |  | 100 | 0.2 |  | 100 |  | 100 | 100 | [11 empty] | 0.2 | 100 | 200 | [43 empty] | 0 | 0.1 | 100 | 100 | 100 | 160 | 0 | 0 | 4.5 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 70 | 70 | 100 | 70 | 0 | 0 | 0.1 | 100 | 100 | 100 | 154 | 0 | 0 | 2.5 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 0 | 69 | 0 | 70 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 1.5 | 0.003 | 1 | 1 | 10 | 0.6 | 0 | 1 | 12 | 1 | 1 | 1 | 1 | 0 | 0 | 1.1 | 0.7 | 1 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | 0 | 0.1 | 0.5 | 0.5 | 100 | 40 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 50 | 0 | 100 | 10 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 10000 | 10000 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0 | 0.1 | 100 | 155 | 0 | 1 | 3.5 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 25 | 100 | 100 | 10 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 10000 | 10000 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | 0 | 0.2 | 1 | 1 | 5 | 50 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 7 | 0 | 100 | -100 | 0 | 0.1 | 5 | 5 | 10 | 10 | 0 | 0 | 2 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 0 | 15 | 0 | 100 | -100 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | [80 empty] | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 1 | 0 |  |  |  |  | 12 | 2 | 5 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 70 | 0 | [6 empty] | 0.09478 | 0.4 | 1 | 100 | 0 | 0.02843 | 0.74047 | 0.4739 | 100 | 0 | 4 | 20 | 1340 | 2700 | 60 | 75 | 90 | 100 |  | 4 | 20 | 0 | 2700 | 2 | 2 | 45 | 45 |  | -6 | -6 | -6 | -6 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -130 | 8 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 2683 | 2679 | 2679 | 2679 | 50 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 |  | 10 | 0 | 75 | 1 | 1 | 102 | 112 | 98 | 91 | 112 | 50 | 65 | 85 | 75 |  | 105 | 120 | 95 | 70 | 140 | 0 | 80 | 4 | 81.5 | 0 | 22.7 | 3.6 | 1 | 4 | 78 |  |  | 10 | 4 | 4 | 4 | 4 | 57 | 57 | 57 | 57 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 120 | 120 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [30 empty] | 32767 | 32767 | 32767 | 180000 | 32767 | 32767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1450 | 10 | 200 | 400 | 2800 | 5 | 400 | 0 | 3450 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 0 | 1500 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 900 |  | 0.30468 | 5.8594 | 20.5078 | 80 | 0 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1500 | 6.7 | 0 | [5 empty] | 9.54 | 9.971 | 720 |  |  | 1.45 | 1.55 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.1 |  |  | 0.72 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [28 empty] | 1 | 1 | 2 | 1 | 0 | 2 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2683 | 0 | 100 | 100 | 0 | 100 | 2683 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197.6 | 0.2 | -26.23 | 4.11 |  | 0.74636 | 0 | 0.56 | 2683 | 0 | 0 | 0 |  | 0 |  | 0 | 176 | 169 | 100 | 101 | 96 | 379 | 377 | 395 | 464 | 464 | 481 | 481 | 311 | -192 | -191 | -179 |  | 73.2 | [73 empty] | Sending | 30 | 40 | 38 | 39 | 37 | 38 | 38 | 40 | 40 | 37 | 37 | 38 | 40 | 37 | 38 | 38 | 38 | 38 | 39 | 37 | 37 | [24 empty] | 3150 | 1780 | 1908 | 1116 | 3151 | 1138 | 1138 | 1241 | 1248 | 1260 | 672 | 676 | 1555 | 3150 | 1132 | 549 | [9 empty] | 74 | 1 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1020 | 0 | 0 | 0 | 17.7 | 0 | 0 | 0 | 1.1 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 1 |  | 1 | 9270 | 1 | 1267 | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 | 1236 | 1 |  | 1 |  | 1 | 4021 | 1 |  | 1 |  | 1 |  | 1 | [16 empty] | 0.52 | 7.9 | 0.03 | 7.68 | 0.74 | 7.62 | 0 | 8.2 | 0.66 | 7.56 | 0.18 | 7.66 | -0.11 | 7.78 | 0.71 | 7.67 | 0.64 | 7.81 | 0 | 7.84 | 0.2 | 7.59 | 0.73 | 7.71 | 0.2 | 8.25 | 0.64 | 7.56 | 0.19 | 7.66 | 0.37 | 7.58 | [16 empty] | -0.54 | 0.48 | -0.86 | 0.33 | 0.25 | -0.38 | 0 | -0.15 | 0.43 | -0.47 | 0 | -0.45 | -0.96 | 0.48 | 0.1 | -0.42 | -0.77 | 0.48 | 0 | 0.29 | -0.89 | 0.48 | -0.64 | 0.5 | -0.2 | -0.01 | 0.4 | -0.19 | -0.79 | 0.33 | 0.2 | -0.49 | [16 empty] | 0.37 | 7.69 | 0.32 | 7.57 | 0.81 | 7.56 | 0 | 8.3 | 1.16 | 7.66 | -0.05 | 7.77 | -0.2 | 7.73 | 0.39 | 7.56 | 0.66 | 7.69 | 0 | 7.67 | -0.02 | 7.74 | 0.48 | 7.75 | 0.11 | 8.1 | 0.29 | 7.81 | -0.19 | 7.85 | 0.52 | 7.67 | [16 empty] | -0.59 | 0.44 | -0.86 | 0.49 | 0.17 | -0.35 | 0 | 0 | -0.07 | 0.37 | -0.72 | 0.47 | -0.09 | -0.29 | -0.81 | 0.45 | -0.09 | -0.33 | 0 | 0.49 | -0.93 | 0.44 | -0.57 | 0.38 | -0.16 | -0.28 | 0.22 | 0.5 | -1.01 | 0.36 | -0.77 | 0.44 | [17 empty] | 0 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1500 | 0 | 13.8 | 28 |  |  | 0 | 0 | SOTERNIX RENOVE
9 |  |  |  |  | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","agent_conn":"Prim-SSL-NoProxy","mon_conn":"Back-NoSSL-NoProxy","rem_conn":"Prim-NoSSL-NoProxy"} | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12 | 0 | 3.51 | 0 | 0 | 0.93 | 24.1 | 0 |  |  |  | 0 | 19.6 | 0 | 0 | 0.06 | 0 | 0.05 | 0 | 0 | 0 | 4.4.0.13 | 5278 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 |  | 0 | 0 | 0 |  | 0 | -942 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 |  |  |  |  | 17899335 | 0 | 285292 | 208322 | 486 | 0 | 0 | 0 | 0 | 0 | 297 | 4071 | -92 | 3572 | 1572 | 3572 | 484 | 897462 | 6428 | 6429 | 6429 |  | 719 |  | 33.4 | 0 | 60 | 19.3 | 5 | 60 | 22.2 | 0 | 24.1 | 24.1 | 40 | 1 | 1 | 52.3 | 120 | 39 | 60 | 30 | 0 | 0 | 75 | 56.3 | 0 | 0 | 0 | 0 | 40 | 2.3 | 0 | 40 | 5.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 25.5 | 12.2 | 20.9 | 0 | 2.3 | 0 | 5.9 | 5.9 | 0 | 120 | 0 | 0.1 | 0 | 2 | 6.79 | 3.5 | 183 | 26.77 | 26.73 | 26.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 2.3 | 21.9 | 4.7 | 7.1 | 9.5 | 11.9 | 7.4 | -6.4 | -6.4 | 6.9 | 0 | 0 | 2.3 | 21.9 | 1 | 0 | 4.7 | 0 | 7.1 | 0 | 9.5 | 0 | 11.9 | 0 | 7.4 | 1 | -6.4 | 1 | -6.4 | 1 | 6.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.8318 | 41.7372 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 6428 | 20 | 0 | 2453 | 0 | 0 | 2452 | -1.3 | 20.2 | 115.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224 | 100 | 150 | 0 | -0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.7 | 0 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.6 | 0 | 0 | 0.3 | 0.2 | 0.01 | 2.31 | 1.06 | 30 | 34 | 28 | 23.53 | 1608763274730 | 0 | 46 | 1.044 | 0 | 0 | 0 | 0 | 43.41 | 0 |  | 694 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 53 | 52 | 52 | 51 | 51 | 52 | 51 | 52 | 52 | 52 | 54 | 52 | 50 | 52 | 53 | 51 | 52 | 51 | 50 | 0 | 0 | 0 | 0 | 51 | 521 | 54 | 528 | 50 | 518 | 0 | 25 | 26 | 0 | 0 | 10 | [42 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 4265545 | 0 |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 24.9 |  |  | 24.9 | 25.7 | 26.2 | 0 |  |  |  |  | 7 | 1606659591673 |  | 0 | 0 | 0 | 0 | 10086 | 5834 | 10081 | 5813 | 10103 | 5829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76174 | 3046 | 25 | 0.099 | 8547 | 2.1 | 0.5 | 0.1 | -0.04 |  | 0 | 56.3 | 23.3 | 0 | 19.3 | 22.2 | 24 | 0 | 0 | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 0 | 0 | 66.1 | 64.1 | 0 | 0 | 63.7 | 65.7 | 64.7 | 64.7 | 64.2 | 65 | 63.5 | 62.2 | 1.26 | 1.26 | 0 | 0 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 88 | 88 | 0 | 0 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 6442.2 | 6442.3 | 0 | 0 | 6442.2 | 6442.3 | 6442.2 | 6442.2 | 6442.3 | 6442.2 | 6442.3 | 6442.3 | 2018 | 2018 | 8 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 3 | 2018 | 8 | 3 | 2018 | 8 | 3 | 2018 | 8 | 3 | 2018 | 8 | 3 | 2018 | 8 | 3 | 2018 | 8 | 3 | 2018 | 9 | 3 | 2018 | 8 | 3 | 39505 | 39522 | 0 | 0 | 39466 | 39467 | 39503 | 39504 | 39520 | 39526 | 39531 | 39529 | 7.73 | 7.73 | 0 | 0 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.65 | 0.29 | 0 | 0 | 0 | 0 | 7.73 | 7.62 | 7.78 | 7.76 | 7.85 | 7.78 | 7.67 | 7.89 | 7.75 | 7.74 | 7.51 | 7.53 | 7.77 | 7.54 | 7.6 | 7.61 | 7.66 | 7.68 | 7.67 | 7.62 |  |  |  |  | -0.17 | -0.25 | -0.15 | 0.05 | -0.19 | -0.16 | -0.17 | -0.24 | -0.32 | -0.26 | -0.18 | -0.34 | -0.24 | -0.05 | -0.1 | -0.34 | -0.17 | -0.4 | -0.22 | -0.29 |  |  |  |  | 7.76 | 7.8 | 7.74 | 8.07 | 7.82 | 7.85 | 7.63 | 7.78 | 7.76 | 7.58 | 7.87 | 7.65 | 7.87 | 7.75 | 7.8 | 7.58 | 7.54 | 7.7 | 7.78 | 7.59 |  |  |  |  | -0.43 | -0.23 | -0.42 | -0.19 | -0.26 | -0.18 | -0.28 | -0.3 | -0.27 | -0.27 | -0.19 | -0.08 | -0.2 | -0.17 | -0.37 | -0.25 | -0.19 | -0.35 | -0.26 | -0.28 |  |  |  |  | 19111 | 0 | 3886.1 | 0 | 0 | 0.02 | 0.02 | 0 | 1.04 | 1.04 | 0 | 4.4.0.0.0 | 4.4.0.4.1 | 4.4.0.0.0 | 4.4.0.2.0 | 4.4.0.1.0 | 4.4.4.23.5 | 4.7.1.2.0 | 4.4.0.4.12 | 4.4.0.0.0 | 4.4.0.5.12 | 4.4.0.0.0 | 4.4.0.0.0 | 4.4.0.7.0 | 4.4.0.1.0 | 4.4.0.0.4 | 4.4.0.6.6 | 4.4.0.6.0 | 4.4.0.0.2 | 4.4.0.0.0 | 4.4.0.0.2 | 4.4.0.1.12 | 0.0.0.0.0 | 0.0.0.0.0 | 4.4.0.4.11 | 4.4.1.1.0 | 4.4.0.2.13 | 4.4.0.3.0 | 4.3.0.0.0 | 4.4.0.3.3 | 4.9.0.0.0 | M04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1025 | [30 empty] | -1 | 3 | 1 | NaN | 0.0001 | 1607949584000 | 1 | 1 | 0.17 | 1 | NaN | 3233 | 1 | 1607472000000 | NaN | NaN | NaN | 0.04 | 5.91 | 14 | NaN | 2 | 0.001 | 1 | 1 | 1 | 1 | 0 | 0 | 1705 | 13 | 0.0336 | 1 | 1607943600000 | 2 | 1 | 4 | 2.68 | 3.2 | 1015633 | 1 | 1 | 6224 | 1 | 15.2 | 145 | 0.05 | 0.0407 |  |  |  |  | Available | 40 |  |  |  | 3997 | 8.81 | 2 | 2 |  | 0 | 0 | 50.01 | 50.01 | 100 | 100 | 100 | 100 | 100 |  | 0 |  | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 100 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 100 | 1 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 1 | 0 | 970 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 1 | 1 | 1 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 30 | 30 | 0 | 2 | 20 | 15 | 80 | 1 | 0 | 11 | 1 | 0 | 0 | 0 | 0 | 7 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 35 | [5 empty] | 0 | 0 | 0 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 0 | 0 |  | -600 | -600 | 6 | 0 | 50 | 1500 | 5.6 | 6.7 | 6.9 | 0.1 | 3 | 0.1 | 0 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 2.5 |  | 0 | 0 | 0.2 | 4.2 |  | 10 | 0 |  |  |  | 0 |  | 5 | 5 | 5 | 5 | 5 | 60 | 28 | 40 | 30 | 50 | 180 | 28 | 40 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 2 | 10 | 2 | 1 | 1 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 2 | 10 | 2 | 1 | 1 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 4 | 0 | [479 empty] | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 12000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 10 | 1 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 32 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 | 0.95 | 0 | 60 | -33 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | 85 | 110 | 90 | 95 | 100 | 105 | 0.85 | 0.9 | 0.95 | 1 | -0.97 | -0.95 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 1 | 40 | 0 | 30 | 30 | 10 | 10 | 10 | 3 | 1 | 10000 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 4 | 4 | 0.01 | 0.01 | 0.2 | 0.2 | 1 | 1.11 | 1 | 1.11 | 1 | 30 | 1 | 2 | 1 | 100 | 100 | 10 | 50 | 50 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 5000 | -5000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 51.5 | 47.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 1 | 115 | 85 | 35 | 10 | 0 | 0 | 1 | -0.2 | 50 | 110 | 80 | 1 | 0 | 241 | 200 | 1 | 99.36 | 10 | 2 | 0.8 | 3 | 4 | 10 | 0.5 | 4 | 10000 | 40 | 40 | 5 | 10000 | 0 | 0 | 0 | 0 | 10000 | 120 | 88 | 45 | 1 | 10 | 0 | 0 | 0 | -0.2 | 50 | 110 | 60 | 1 | 0 | 241 | 200 | 1 | 100 | 100 | 10 | 2 | 0.8 | 3 | 4 | 10 | 0.5 | 4 | 10000 | 40 | 40 | 5 | 10000 | 0 | 0 | 0 | 0 | 10000 | 120 | 88 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 6 | 0 | 6000 | 0 | 100 | 50 | 75 | 500 | 100 | 460 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 1 | 5 | 40 | 20 | 50 | 505 | 505 | 300 | 30 | 120 | 0 |  | 0 | 0 | 0 | 1 | 1 | 0 | 0 |  | 0 |  | 0 |  |  |  | 1 | 1 |  |  |  | 1 | 1 | 0 | 1 |  | 1 | 1 | 1 |  | 1 | 1 | [8 empty] | 0 | 1 |  | 0 | 0 |  |  | 1 |  | 0 | 1 | 1 | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 12.5 |  | 620 |  |  |  |  | 11 | 0 | 300 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.2 | 0.1 | 0.01 | 3.3 | 80 | 0 | 1 | 7 | 100 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 55 | 40 | 0 | 100 | 10 | 0 | 0 | -5 | 15 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 45 | 30 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 200 | 168 | 75 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 65 | 4 | 0 | 0 | 0 | -4.5 | 10 | 1 | 20 | 15 | 0 | 2 | 1 | 1.82 | 0.6 | 0.6 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0 | 0 | 0 | 0 | 15 | 30 | 0.01 | 0.4 | 0 | 60 | 30 | 0 | 0 | 0 | 0 | 1200 | 1400 | 0 | 0.5 | 320 | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 0.2 | 0.05 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1.2 | 0.1 | 300 | 300 | 300 | 300 | 0 | 50 | 50 | 50 | 50 | 50 | 120 | 0 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.15 | 1 | 25 | 3 | 100 | 0 | 7.5 | 0 | 0.5 | 1 | 4 | 50 | 0 | 25 | 10 | 250 | 1 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 | 1 | 1 | 4000 | 2000 | 20000 | 10000 | 3356 | 1678 | 8 | 4 | 2 | 1 | 30 | 150 | 20 | 120 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 1 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [66 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 1200 | 1000 |  |  |  | 1000 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 50 | 1000 | 680 | 640 | 5 | 650 | 5 | 650 | 640 | 5 | 650 | 5 | 1000 | 5 | 15 | 300 | 20 | 50 | 650 | 5 | 200 | 5 | 1000 | 225 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 20 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 20 | 5 | 10 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | 0 | 20 |  | 0.98 | 1 | -0.98 | -0.95 | 0.8 | -0.92 | 1 | 7 | 0.95 | -0.95 | 20 | 80 | 4169 | 88 | 90 | 2.05 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 0 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 85 | 90 | 85 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 43.4 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 35 | 300 |  | 75 | 1.05 | 1 | 1 | 1 | 180 | 0.3 | 1.11 | 60 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 3356 | 0 | 5000 | 40 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 3356 | 1 | 2 | 0 | 1 | 1 | 2 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 4 | 20 | 0.9 | -0.95 | 1 | 0 | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 10000 | 0 | 0 | 0 | 0 | 1 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -100 | 100 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 1 | 1 | 0.8 | -0.92 | 2720 | -2720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 10 | 3.3 | 0.2 | 3.5 | 0.05 | 1.4 | 1.7 | 0.05 | 0.05 | 87 | 5 | 94 | 2 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 35 |  |  | 20 |  |  |  | 3 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.5 | 0.1 | 0.5 | 500 | 1500 | 3.5 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1.5 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 75 | 2 | 79 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 1 | 0 | 120 | 120 | 2 | 2 | 0 | 1 | 0 | 120 | 120 | 2 | 2 | 0 | 62 | 2 | 1 |  | 80 | 120 | 0.5 | 0.5 | 0 | 1 | 0 | 138 | 138 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 82 | 0 | 0 | 0 | 5 | 20 | 0 | 2 | 30 | 90 | 0 | 0 | 0 | 200 | -200 | 0 | -50 | 100 | -100 | 0 | 0 | 0 | 200 | -200 | 20 | 30 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 9.5 | 10 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 1 | 1 | 90 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 16 | 18 | 18 | 18 | [5 empty] | 15 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 462 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 1 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 0 | 0 | 20 | 4000 | 4000 |  | 700 | 30 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 5 | 5 | 5 | 5 | -5 | -5 | -5 | -5 | 12 | 12 | 12 | 12 | 4.5 |  | 45 | 270 | 70 | -144 | 0 | 80 | 350 | [24 empty] | 0 | 4 | 500 | 30 |  | 2000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 320 | 0 | -24 | -13 | 3335 | 1668 | 10 | 3335 | 1668 | 40 | 0 | 0 | [6 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 3358 | 1676 | 4321 | 2200 | 1500 | 1501 |  | 49.8 | 50.1 |  | 500 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4915 | 2158 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4915 | 2158 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4915 | 2158 | 1500 | 1500 |  | 50 | 50 |  | 660 |  | 0 | 1000 | 300 | 48 | -1.6 | -4 | 100 | 6 | 0 | 1 | 6 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6 | 0 | 0.5 | 0 | 0 | 120000 | 0 | 120000 | 0 |  | 4 | 0 | 0 | 0 |  |  |  | 75 |  | 40 | [14 empty] | 50 | 50 | 50 | 50 | [10 empty] | 0 | 0 | 1 | 3 | 55 | 57 | 2 | 2 | 58 |  | 40 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 300 | 100 | 99.36 | 100 | [8 empty] | -925 | 3700 |  | 0.2 | 80 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 300 |  | 100 | 100 | [11 empty] | 0.2 | 80 | 200 | [43 empty] | 0 | 0.1 | 0.03 | 0.01 | 100 | 100 | 0 | 1 | 2.5 | 1 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 60 | 60 | 5 | 100 | 0 | 0 | 0.1 | 0.1 | 0.01 | 100 | 40 | 0 | 1 | 6 | 1 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 60 | 72 | 0 | 100 | 5 | 0 | 0.2 | 100 | 100 | 100 | 80 | 0 | 1 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 20 | 40 | 100 | 40 | 0.15 | 0.003 | 1 | 1 | 10 | 0.4 | 0 | 1 | 3.5 | 0.01 | 0.01 | 0.1 | 0.1 | 0 | 0 | 1.1 | 0.7 | 1 | 25 | 100 | 0 | 0 | 0.1 | 0.03 | 0.02 | 100 | 80 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 130 | 120 | 120 | 60 | 100 | 30 | 0 | 0.3 | 0.01 | 0.01 | 100 | 80 | 0 | 1 | 7 | 1 | 1 | 1 | 1 | 0 | 0 | 47 | 30 | 35 | 0 | 100 | 10 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0 | 0.1 | 100 | 205 | 0 | 1 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 28 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | [42 empty] | 0 | 0.1 | 100 | 80 | 0 | 1 | 4 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 40 | 0.1 | 0.01 | 55 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 0 | 0 | 10 | 150 | 150 | 100 | 205 | 0 | 48 | 50 | 0 | 3000 | 6000 | 3000 | 6000 | 6 | 6 | 0 | 5000 | -5000 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 100 | 50 | 0 | 0.1 | 100 | 80 | 0 | 1 | 4 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 40 | 0.1 | 0.01 | 55 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 |  |  |  |  | 12 | 0 | 0 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 80 | 0 | [6 empty] | 0.01421 | 0.29619 | 0.88857 | 100 | 0 | 0 | 0.44428 | 0.23695 | 100 | 2 | 0 | 20 | 5000 | 5000 | 60 | 75 | 90 | 100 |  | 4 | 20 | 1668 | 3356 | 2 | 2 | 37 | 45 |  | -6 | -6 | -6 | -6 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -145 | 10 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 3356 | 3356 | 3356 | 3356 | 70 | 0.65 | 0.56 | 0.56 | 0.56 | 0.45 | 0.56 | 0.56 | 0.56 |  | 10 | 20 | 93 | 1 | 1 | 100.4 | 103.4 | 98 | 91 | 103.4 | 40 | 65 | 85 | 80 |  | 110 | 125 | 90 | 70 | 140 | 0 | 80 | 20 | 80 | 1 | 22.7 | 3 | 3 | 10 | 75 |  |  | 10 | 4 | 4 | 4 | 4 | 54 | 54 | 54 | 54 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 130 | 1000 | 1000 | 4000 | 3000 | 16 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 300 | 3300 | 50 | 100 | 50 | 300 | 650 | 93 | 98 | 1 | 100 | 2 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [30 empty] | 1 | 1 | 1 | 33 | 1 | 0 | 60 | 60 | 30 | 15 | 15 | 1 | 0 | 1 | 100 | 70 | 200 | 50 | 100 | 90 | 24 | 25 | 24 | 20 | 25 | 10 | 3000 | 50 | 100 | 50 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1650 | 10 | 200 | 400 | 2800 | 5 | 10000 | 0 | 3850 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 1 | 1200 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 900 |  | 0.15 | 0.7 | 4 | 95 | 2 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1500 | 6.7 | 0 | 95 | 85 | 85 | 95 | 95 | 9.54 | 9.971 | 720 |  |  | 1.35 | 1.5 | 40 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.1 |  |  | 0.74 | [13 empty] | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | [28 empty] | 1 | 1 | 0 | 2 | 0 | 2 | 1 | 1 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 3356 | 0 | 100 | 100 | 0 | 100 | 3356 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -18.4 | 4.059 | 0.1 | 0.98909 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 71.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 363 | 365 | 364 | 365 | 361 | 360 | 363 | 360 | 362 | 367 | 360 | 364 | 0 | 0 | 0 | 0 | 363 | 362 | 361 | 360 | 362 | 362 | 359 | 518 | 515 | 519 | 520 | 520 | 519 | 518 | 516 | 517 | 521 | 522 | 516 | 521 | 0 | 0 | 0 | 0 | 515 | 516 | 516 | 515 | 517 | 515 | 516 | 6790 | Sending | 30 | 47 | 47 | 46 | 48 | 47 | 47 | 47 | 47 | 47 | 47 | 49 | 46 | 49 | 47 | 46 | 46 | 47 | 47 | 47 | 47 | 19.2869 | 20.6805 | 19.1737 | 20.9672 | 21.0943 | 20.2697 | 20.3876 | 20.3976 | 20.7511 | 21.847 | 17.3465 | 17.3398 | 23.2121 | 18.6983 | 17.5565 | 19.12 | 22.4155 | 17.0251 | 19.7082 | 20.1319 |  |  |  |  | 1454 | 1217 | 1879 | 1391 | 1788 | 1482 | 1894 | 1143 | 1402 | 1388 | 1780 | 1123 | 1890 | 1210 | 1635 | 1046 | 1643 | 1532 | 1533 | 3151 | [5 empty] | 0 | 1 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 946 | 0 | 0 | 0 | 25.7 | 0 | 0 | 0 | 1.307 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 | [8 empty] | 0 | 7.73 | 0 | 7.62 | 0 | 7.78 | 0 | 7.76 | 0 | 7.85 | 0 | 7.78 | 0 | 7.67 | 0 | 7.89 | 0 | 7.75 | 0 | 7.74 | 0 | 7.51 | 0 | 7.53 | 0 | 7.77 | 0 | 7.54 | 0 | 7.6 | 0 | 7.61 | 0 | 7.66 | 0 | 7.68 | 0 | 7.67 | 0 | 7.62 | [8 empty] | 0 | -0.17 | 0 | -0.25 | 0 | -0.15 | 0 | 0.05 | 0 | -0.19 | 0 | -0.16 | 0 | -0.17 | 0 | -0.24 | 0 | -0.32 | 0 | -0.26 | 0 | -0.18 | 0 | -0.34 | 0 | -0.24 | 0 | -0.05 | 0 | -0.1 | 0 | -0.34 | 0 | -0.17 | 0 | -0.4 | 0 | -0.22 | 0 | -0.29 | [8 empty] | 0 | 7.76 | 0 | 7.8 | 0 | 7.74 | 0 | 8.07 | 0 | 7.82 | 0 | 7.85 | 0 | 7.63 | 0 | 7.78 | 0 | 7.76 | 0 | 7.58 | 0 | 7.87 | 0 | 7.65 | 0 | 7.87 | 0 | 7.75 | 0 | 7.8 | 0 | 7.58 | 0 | 7.54 | 0 | 7.7 | 0 | 7.78 | 0 | 7.59 | [8 empty] | 0 | -0.43 | 0 | -0.23 | 0 | -0.42 | 0 | -0.19 | 0 | -0.26 | 0 | -0.18 | 0 | -0.28 | 0 | -0.3 | 0 | -0.27 | 0 | -0.27 | 0 | -0.19 | 0 | -0.08 | 0 | -0.2 | 0 | -0.17 | 0 | -0.37 | 0 | -0.25 | 0 | -0.19 | 0 | -0.35 | 0 | -0.26 | 0 | -0.28 | [9 empty] | 0 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1500 | 0 |  | 33.4 |  |  | 0 | 0 | BMW MÜNCHEN
10 |  |  |  |  | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","rem_conn":"Back-SSL-NoProxy","dataItems":"0/15","agent_conn":"Back-SSL-NoProxy","mon_conn":"Prim-SSL-NoProxy"} | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6 | 0 | 5.98 | 0 | 0 | 0.93 | 26.1 | 0 |  |  |  | 0 | 21.7 | 0 | 0 | 0.05 | 0 | 0.04 | 0 | 0 | 0 | 4.4.0.13 | 727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 |  | 0 | 0 | 0 |  | 0 | -949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 |  |  |  |  | 18084212 | 0 | 291534 | 213099 | 507 | 0 | 0 | 0 | 0 | 0 | 265 | 4070 | 1592 | 3573 | 1573 | 3583 | 543 | 1592 | 6427 | 6431 | 6431 |  | 734 |  | 33.7 | 0 | 60 | 17.6 | 5 | 60 | 22 | 0 | 26.1 | 26.1 | 40 | 1 | 1 | 52.4 | 105 | 33.3 | 35 | 30 | 0 | 0 | 75 | 55.9 | 0 | 0 | 0 | 0 | 40 | 1.2 | 10 | 40 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.4 | 24 | 12.4 | 21.5 | 0 | 1.2 | 0 | 6.2 | 6.4 | 0 | 120 | 0 | 0 | 0 | 0.6 | 6.76 | 3.5 | 177.8 | 26.77 | 26.77 | 26.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 8.2 | 59.8 | 16.5 | 24.7 | 33 | 41.3 | 44.4 | 47.5 | 47.8 | 54 | 0 | 0 | 8.2 | 59.8 | 1 | 0 | 16.5 | 0 | 24.7 | 0 | 33 | 0 | 41.3 | 0 | 44.4 | 1 | 47.5 | 1 | 47.8 | 1 | 54 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.6267 | 41.5311 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 6348 | 20 | 0 | 2418 | 0 | 0 | 2418 | 1.7 | 20.3 | 117.6 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224 | 100 | 150 | 0 | -1.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 19.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.4 | 0 | 0 | 0 | -0.3 | 0 | 2.43 | -0.24 | 25 | 28 | 24 | 27.73 | 1608664694863 | 0 | 46 | 1.033 | 0 | 0 | 0 | 0 | 46.77 | 0 |  | 731 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 50 | 52 | 53 | 51 | 52 | 52 | 52 | 53 | 53 | 51 | 51 | 53 | 53 | 53 | 53 | 52 | 52 | 52 | 50 | 0 | 0 | 0 | 0 | 51 | 543 | 53 | 549 | 49 | 537 | 0 | 27 | 23 | 0 | 0 | 12 | [42 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 4276154 | 0 |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26.6 |  |  | 26 | 26.5 | 27.3 | 0 |  |  |  |  | 6 | 1606493385106 |  | 0 | 0 | 0 | 0 | 10081 | 5830 | 10080 | 5812 | 10099 | 5827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44499 | 2966 | 15 | 0.171 | 8580 | 1.94 | 0.3 | 0.05 | -0.01 |  | 0 | 55.9 | 25.2 | 0 | 17.6 | 22 | 30 | 0 | 0 | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 0 | 0 | 62.5 | 57.5 | 0 | 0 | 65.7 | 63.2 | 64.6 | 61.7 | 64.3 | 65.1 | 64.5 | 63.1 | 1.26 | 1.26 | 0 | 0 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 88 | 88 | 0 | 0 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 6480.4 | 6480.3 | 0 | 0 | 6480.4 | 6480.4 | 6480.4 | 6480.4 | 6480.3 | 6480.3 | 6480.3 | 6480.3 | 2018 | 2018 | 11 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 3 | 2018 | 11 | 3 | 2018 | 10 | 3 | 2018 | 11 | 3 | 2018 | 10 | 3 | 2018 | 10 | 3 | 2018 | 11 | 3 | 2018 | 10 | 3 | 2018 | 10 | 3 | 39660 | 39693 | 0 | 0 | 39691 | 39671 | 39682 | 39661 | 39628 | 39681 | 39662 | 39659 | 7.73 | 7.73 | 0 | 0 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.659 | 0.28 | 0 | 0 | 0 | 0 | 7.76 | 7.8 | 7.67 | 7.71 | 7.99 | 7.74 | 7.88 | 8.04 | 7.78 | 7.7 | 7.73 | 7.82 | 7.64 | 7.58 | 7.64 | 7.7 | 7.63 | 7.66 | 7.54 | 7.57 |  |  |  |  | -0.12 | -0.38 | -0.04 | -0.13 | -0.26 | 0.11 | -0.3 | -0.09 | -0.04 | 0.28 | -0.06 | -0.23 | -0.16 | -0.15 | -0.46 | -0.19 | -0.12 | -0.27 | 0.18 | -0.2 |  |  |  |  | 7.86 | 8.07 | 7.97 | 7.9 | 7.6 | 7.97 | 7.97 | 7.82 | 8.04 | 7.94 | 7.71 | 7.67 | 7.58 | 7.81 | 7.88 | 7.69 | 7.63 | 7.74 | 7.53 | 7.81 |  |  |  |  | -0.11 | -0.04 | -0.24 | -0.1 | -0.08 | -0.15 | -0.41 | -0.03 | -0.14 | -0.33 | -0.17 | -0.25 | -0.29 | -0.15 | -0.19 | -0.11 | -0.21 | -0.25 | -0.27 | -0.18 |  |  |  |  | 18860.6 | 0 | 3839.6 | 0 | 0 | 0.02 | 0.02 | 0 | 1.04 | 1.04 | 0 | 4.4.0.0.0 | ....1 | ....0 | ....0 | ....0 | ....5 | ....0 | ....12 | ....0 | ....12 | ....0 | ....0 | ....0 | ....0 | ....4 | ....6 | ....0 | ....2 | ....0 | ....2 | ....12 | ....0 | ....0 | ....11 | ....0 | ....13 | ....0 | ....0 | ....3 | ....0 | M02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | [30 empty] | -1 | 3 | 1 | NaN | 0.0001 | 1607949956000 | 1 | 1 | 0.1637 | 1 | NaN | 3190 | 1 | 1607472000000 | NaN | NaN | NaN | 0.03 | 5.72 | 15 |  | 2 | 0.0007 | 1 | 1 | 1 | 2 |  | 0 | 1894 | 13 | 0.0323 | 1 | 1607943600000 | 2 | 1 | 2 | 3.03 | 3 | 1015635 | 1 | 1 | 6192 | 1 | 15.2 | 145 | 0.05 | 0.0386 |  |  |  |  | Not Available | 60 |  | 0 | 0 | 4026 | 8.58 | 2 | 2 |  | 0 | 0 | 50 | 49.99 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 1 | 0 | 970 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 1 | 1 | 1 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 30 | 30 | 0 | 2 | 20 | 15 | 80 | 1 | 0 | 11 | 1 | 0 | 0 | 0 | 0 | 7 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 35 | [5 empty] | 0 | 0 | 0 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 0 | 0 |  | -600 | -600 | 6 | 0 | 50 | 1500 | 5.6 | 6.7 | 6.9 | 0.1 | 3 | 0.1 | 0 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 2.5 |  | 0 | 0 | 0.2 | 4.2 |  | 10 | 0 |  |  |  | 0 |  | 5 | 5 | 5 | 5 | 5 | 60 | 28 | 40 | 30 | 50 | 180 | 28 | 40 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 2 | 10 | 2 | 1 | 1 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 2 | 10 | 2 | 1 | 1 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 4 | 0 | [479 empty] | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 12000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 10 | 1 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 32 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 | 0.95 | 0 | 60 | -33 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | 85 | 110 | 90 | 95 | 100 | 105 | 0.85 | 0.9 | 0.95 | 1 | -0.97 | -0.95 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 1 | 40 | 0 | 30 | 30 | 10 | 10 | 10 | 3 | 1 | 10000 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 4 | 4 | 0.01 | 0.01 | 0.2 | 0.2 | 1 | 1.11 | 1 | 1.11 | 1 | 30 | 1 | 2 | 1 | 100 | 100 | 10 | 50 | 50 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 5000 | -5000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 51.5 | 47.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 1 | 115 | 85 | 35 | 10 | 0 | 0 | 1 | -0.2 | 50 | 110 | 80 | 1 | 0 | 241 | 200 | 1 | 99.36 | 10 | 2 | 0.8 | 3 | 4 | 10 | 0.5 | 4 | 10000 | 40 | 40 | 5 | 10000 | 0 | 0 | 0 | 0 | 10000 | 120 | 88 | 45 | 1 | 10 | 0 | 0 | 0 | -0.2 | 50 | 110 | 60 | 1 | 0 | 241 | 200 | 1 | 100 | 100 | 10 | 2 | 0.8 | 3 | 4 | 10 | 0.5 | 4 | 10000 | 40 | 40 | 5 | 10000 | 0 | 0 | 0 | 0 | 10000 | 120 | 88 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 6 | 0 | 6000 | 0 | 100 | 50 | 75 | 500 | 100 | 460 | 0 | 0 | 0 | 0 | -10 | 0 | 0 | 0 | 0 | 0 | 5 | 40 | 20 | 40 | 505 | 505 | 300 | 30 | 120 | 0 |  | 0 | 0 | 0 | 1 | 1 | 0 | 0 |  | 0 |  | 0 |  |  |  | 1 | 1 |  |  |  | 1 | 1 | 0 | 1 |  | 1 | 1 | 1 |  | 1 | 1 | [8 empty] | 0 | 1 |  | 0 | 0 |  |  | 1 |  | 0 | 1 | 1 | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 12.5 |  | 620 |  |  |  |  | 11 | 0 | 300 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.2 | 0.1 | 0.01 | 3.3 | 80 | 0 | 1 | 7 | 100 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 40 | 0 | 100 | 10 | 0 | 0 | -5 | 15 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 45 | 30 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 200 | 168 | 75 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 65 | 4 | 0 | 0 | 0 | -4.5 | 10 | 1 | 20 | 15 | 0 | 2 | 1 | 1.82 | 0.6 | 0.6 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0 | 0 | 0 | 0 | 15 | 30 | 0.01 | 0.4 | 0 | 60 | 30 | 0 | 0 | 0 | 0 | 1200 | 1400 | 0 | 0.5 | 375 | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 0.2 | 0.05 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1.2 | 0.1 | 300 | 300 | 300 | 300 | 0 | 50 | 50 | 50 | 50 | 50 | 120 | 0 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.15 | 1 | 25 | 3 | 100 | 0 | 8 | 0 | 0.5 | 1 | 4 | 50 | 0 | 25 | 10 | 250 | 1 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 | 1 | 1 | 4000 | 2000 | 20000 | 10000 | 3356 | 1678 | 8 | 4 | 2 | 1 | 30 | 150 | 20 | 120 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 1 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [66 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 1200 | 1000 |  |  |  | 1000 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 50 | 1000 | 680 | 640 | 5 | 650 | 5 | 650 | 640 | 5 | 650 | 5 | 1000 | 5 | 15 | 300 | 20 | 50 | 650 | 5 | 200 | 5 | 1000 | 225 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 20 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 20 | 5 | 10 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | 0 | 20 |  | 0.98 | 1 | -0.98 | -0.95 | 0.8 | -0.92 | 1 | 7 | 0.95 | -0.95 | 20 | 80 | 4169 | 88 | 90 | 2.05 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 0 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 85 | 90 | 85 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 43.4 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 35 | 300 |  | 75 | 1.05 | 1 | 1 | 1 | 180 | 0.3 | 1.11 | 60 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 3356 | 0 | 5000 | 40 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 3356 | 1 | 2 | 0 | 1 | 1 | 2 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 4 | 20 | 0.9 | -0.95 | 1 | 0 | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 10000 | 0 | 0 | 0 | 0 | 1 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -100 | 100 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 1 | 1 | 0.8 | -0.92 | 2720 | -2720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 10 | 3.3 | 0.2 | 3.5 | 0.05 | 1.4 | 1.7 | 0.05 | 0.05 | 87 | 5 | 94 | 2 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 35 |  |  | 20 |  |  |  | 3 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.5 | 0.1 | 0.5 | 500 | 1500 | 3.5 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1.5 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 75 | 2 | 79 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 1 | 0 | 120 | 120 | 2 | 2 | 0 | 1 | 0 | 120 | 120 | 2 | 2 | 0 | 62 | 2 | 1 |  | 80 | 120 | 0.5 | 0.5 | 0 | 1 | 0 | 138 | 138 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 82 | 0 | 0 | 0 | 5 | 20 | 0 | 2 | 30 | 90 | 0 | 0 | 0 | 200 | -200 | 0 | -50 | 100 | -100 | 0 | 0 | 0 | 200 | -200 | 20 | 30 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 9.5 | 10 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 1 | 1 | 90 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 16 | 18 | 18 | 18 | [5 empty] | 15 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 462 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 1 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 0 | 0 | 20 | 4000 | 4000 |  | 700 | 30 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 5 | 5 | 5 | 5 | -5 | -5 | -5 | -5 | 12 | 12 | 12 | 12 | 4.5 |  | 45 | 270 | 70 | -144 | 0 | 80 | 350 | [24 empty] | 0 | 4 | 500 | 30 |  | 2000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 320 | 0 | -24 | -13 | 3335 | 1668 | 10 | 3335 | 1668 | 40 | 0 | 0 | [6 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 3296 | 1676 | 4062 | 2107 | 1500 | 1500 |  | 50 | 49.7 |  | 500 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4915 | 2158 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4915 | 2158 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4915 | 2158 | 1500 | 1500 |  | 50 | 50 |  | 660 |  | 0 | 1000 | 300 | 48 | -1.6 | -4 | 100 | 6 | 0 | 1 | 6 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6 | 0 | 0.5 | 0 | 0 | 120000 | 0 | 120000 | 0 |  | 4 | 0 | 0 | 0 |  |  |  | 75 |  | 40 | [14 empty] | 50 | 50 | 50 | 50 | [10 empty] | 0 | 0 | 1 | 3 | 55 | 57 | 2 | 2 | 58 |  | 40 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 300 | 100 | 99.36 | 100 | [8 empty] | -925 | 3700 |  | 0.2 | 80 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 300 |  | 100 | 100 | [11 empty] | 0.2 | 80 | 200 | [43 empty] | 0 | 0.1 | 0.03 | 0.02 | 100 | 50 | 0 | 1 | 2.3 | 1 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 60 | 60 | 5 | 100 | 0 | 0 | 0.1 | 0.1 | 0.01 | 100 | 40 | 0 | 1 | 6 | 1 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 60 | 71 | 0 | 100 | 5 | 0 | 0.2 | 100 | 100 | 100 | 80 | 0 | 1 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 40 | 100 | 40 | 0.15 | 0.003 | 1 | 1 | 10 | 0.4 | 0 | 1 | 3.5 | 0.01 | 0.01 | 0.1 | 0.1 | 0 | 0 | 1.1 | 0.7 | 1 | 25 | 100 | 0 | 0 | 0.1 | 0.05 | 0.02 | 100 | 50 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 130 | 105 | 105 | 35 | 100 | 30 | 0 | 0.3 | 0.01 | 0.01 | 100 | 80 | 0 | 1 | 7 | 1 | 1 | 1 | 1 | 0 | 0 | 47 | 30 | 35 | 0 | 100 | 10 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0 | 0.1 | 100 | 205 | 0 | 1 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 28 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | [42 empty] | 0 | 0.1 | 100 | 80 | 0 | 1 | 4 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 40 | 0.1 | 0.01 | 55 | 10 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 0 | 0 | 10 | 150 | 150 | 100 | 205 | 0 | 48 | 50 | 0 | 3000 | 6000 | 3000 | 6000 | 6 | 6 | 0 | 5000 | -5000 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 100 | 50 | 0 | 0.1 | 100 | 80 | 0 | 1 | 4 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 40 | 0.1 | 0.01 | 55 | 0 | 100 | 60 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 |  |  |  |  | 12 | 0 | 0 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 80 | 0 | [6 empty] | 0.01421 | 0.29619 | 0.88857 | 100 | 0 | 0 | 0.44428 | 0.23695 | 100 | 2 | 0 | 20 | 5000 | 5000 | 60 | 75 | 90 | 100 |  | 4 | 20 | 1668 | 3356 | 2 | 2 | 37 | 45 |  | -6 | -6 | -6 | -6 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -145 | 10 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 3356 | 3356 | 3356 | 3356 | 70 | 0.65 | 0.56 | 0.56 | 0.56 | 0.45 | 0.56 | 0.56 | 0.56 |  | 10 | 20 | 93 | 1 | 1 | 100.4 | 103.4 | 98 | 91 | 103.4 | 40 | 65 | 85 | 80 |  | 110 | 125 | 90 | 70 | 140 | 0 | 80 | 20 | 80 | 1 | 22.7 | 3 | 3 | 10 | 75 |  |  | 10 | 4 | 4 | 4 | 4 | 54 | 54 | 54 | 54 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 130 | 1000 | 1000 | 4000 | 3000 | 16 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 300 | 3300 | 50 | 100 | 50 | 300 | 650 | 93 | 98 | 1 | 100 | 2 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [30 empty] | 1 | 1 | 1 | 33 | 1 | 0 | 60 | 60 | 30 | 15 | 15 | 1 | 0 | 1 | 100 | 70 | 200 | 50 | 100 | 90 | 24 | 25 | 24 | 20 | 25 | 10 | 3000 | 50 | 100 | 50 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1650 | 10 | 200 | 400 | 2800 | 5 | 10000 | 0 | 3850 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 1 | 1200 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 900 |  | 0.15 | 0.7 | 4 | 95 | 2 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1500 | 6.7 | 0 | 95 | 85 | 85 | 95 | 95 | 9.54 | 9.971 | 720 |  |  | 1.35 | 1.5 | 40 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.1 |  |  | 0.74 | [13 empty] | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | [28 empty] | 1 | 1 | 0 | 2 | 0 | 2 | 1 | 1 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 3356 | 0 | 0 | 0 | 0 | 0 | 3356 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -14.75 | 4.043 | 0.0925 | 1.2295 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 73.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 364 | 362 | 378 | 371 | 367 | 366 | 376 | 366 | 375 | 368 | 366 | 374 | 0 | 0 | 0 | 0 | 365 | 370 | 366 | 368 | 366 | 369 | 363 | 518 | 517 | 517 | 518 | 516 | 519 | 520 | 524 | 521 | 522 | 521 | 517 | 520 | 0 | 0 | 0 | 0 | 517 | 522 | 517 | 517 | 517 | 517 | 516 | 7637 | Sending | 30 | 48 | 47 | 48 | 47 | 48 | 47 | 48 | 48 | 49 | 46 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 48 | 45 | 46 | 20.0752 | 19.5825 | 20.8954 | 19.0431 | 19.6393 | 21.1574 | 21.8418 | 20.4512 | 19.7852 | 21.4437 | 19.6386 | 20.1407 | 23.8809 | 19.61 | 21.5493 | 20.3113 | 20.1553 | 19.468 | 18.7636 | 19.3299 |  |  |  |  | 1627 | 2187 | 3294 | 1251 | 1369 | 1261 | 1372 | 1701 | 1383 | 2562 | 1712 | 1643 | 2112 | 1112 | 1171 | 1615 | 1754 | 1912 | 2061 | 2521 | [5 empty] | 0 | 1 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 943 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 1.307 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 | [8 empty] | 0 | 7.76 | 0 | 7.8 | 0 | 7.67 | 0 | 7.71 | 0 | 7.99 | 0 | 7.74 | 0 | 7.88 | 0 | 8.04 | 0 | 7.78 | 0 | 7.7 | 0 | 7.73 | 0 | 7.82 | 0 | 7.64 | 0 | 7.58 | 0 | 7.64 | 0 | 7.7 | 0 | 7.63 | 0 | 7.66 | 0 | 7.54 | 0 | 7.57 | [8 empty] | 0 | -0.12 | 0 | -0.38 | 0 | -0.04 | 0 | -0.13 | 0 | -0.26 | 0 | 0.11 | 0 | -0.3 | 0 | -0.09 | 0 | -0.04 | 0 | 0.28 | 0 | -0.06 | 0 | -0.23 | 0 | -0.16 | 0 | -0.15 | 0 | -0.46 | 0 | -0.19 | 0 | -0.12 | 0 | -0.27 | 0 | 0.18 | 0 | -0.2 | [8 empty] | 0 | 7.86 | 0 | 8.07 | 0 | 7.97 | 0 | 7.9 | 0 | 7.6 | 0 | 7.97 | 0 | 7.97 | 0 | 7.82 | 0 | 8.04 | 0 | 7.94 | 0 | 7.71 | 0 | 7.67 | 0 | 7.58 | 0 | 7.81 | 0 | 7.88 | 0 | 7.69 | 0 | 7.63 | 0 | 7.74 | 0 | 7.53 | 0 | 7.81 | [8 empty] | 0 | -0.11 | 0 | -0.04 | 0 | -0.24 | 0 | -0.1 | 0 | -0.08 | 0 | -0.15 | 0 | -0.41 | 0 | -0.03 | 0 | -0.14 | 0 | -0.33 | 0 | -0.17 | 0 | -0.25 | 0 | -0.29 | 0 | -0.15 | 0 | -0.19 | 0 | -0.11 | 0 | -0.21 | 0 | -0.25 | 0 | -0.27 | 0 | -0.18 | [9 empty] | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1500 | 0 |  | 33.7 |  |  | 0 | 0 | BMW MÜNCHEN
11 |  |  |  |  | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","rem_conn":"Prim-NoSSL-NoProxy","dataItems":"0/15","agent_conn":"Prim-SSL-NoProxy","mon_conn":"Back-SSL-NoProxy"} | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 3.51 | 0 | 0 | 0.94 | 22.9 | 0 |  |  |  | 0 | 20.5 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0 | 0 | 4.4.0.13 | 502 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 |  | 0 | 0 | 0 |  | 0 | -943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 |  |  |  |  | 18381160 | 0 | 306809 | 216022 | 1472 | 0 | 0 | 0 | 0 | 0 | 295 | 4070 | -310 | 3573 | -427 | 3573 | 475 | -399 | 6427 | 6427 | 6427 |  | 913 |  | 25.6 | 0 | 60 | 17.6 | 5 | 60 | 22 | 0 | 22.9 | 22.9 | 40 | 1 | 1 | 52.6 | 100 | 35.8 | 60 | 30 | 0 | 0 | 75 | 59.6 | 0 | 0 | 0 | 0 | 40 | 2.1 | 0 | 50 | 5.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.4 | 25.4 | 12.4 | 21.2 | 0 | 2.1 | 0 | 5.6 | 5.7 | 0 | 120 | 0 | 0 | 0 | 0 | 6.77 | 3.5 | 169.3 | 26.76 | 26.78 | 26.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 1.5 | 19.2 | 3 | 4.5 | 6 | 7.6 | 3.1 | -3.8 | -3.8 | 6.1 | 0 | 0 | 1.5 | 19.2 | 1 | 0 | 3 | 0 | 4.5 | 0 | 6 | 0 | 7.6 | 0 | 3.1 | 1 | -3.8 | 1 | -3.8 | 1 | 6.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.5901 | 41.5439 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 6412 | 20 | 0 | 2353 | 0 | 0 | 2353 | -1.2 | 20.3 | 114.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224 | 100 | 150 | 0 | -1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.5 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.8 | 0 | 0 | 0.3 | 0.3 | 0.01 | 2.34 | 0.84 | 26 | 29 | 24 | 26.38 | 1608714078903 | 0 | 47 | 1 | 0 | 0 | 0 | 0 | 42.12 | 0 |  | 699 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 54 | 54 | 55 | 53 | 53 | 53 | 54 | 54 | 54 | 52 | 52 | 53 | 54 | 52 | 53 | 53 | 54 | 54 | 53 | 0 | 0 | 0 | 0 | 53 | 543 | 55 | 549 | 52 | 538 | 0 | 26 | 26 | 0 | 0 | 11 | [42 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 4332920 | 0 |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.7 | 25.4 |  |  | 24.3 | 25.1 | 25.7 | 0 |  |  |  |  | 6 | 1606661689513 |  | 0 | 0 | 0 | 0 | 10082 | 5831 | 10078 | 5813 | 10103 | 5828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26331 | 2925 | 9 | 0.161 | 4785 | 2.02 | 0.4 | 0.1 | -0.1 |  | 0 | 59.6 | 23 | 0 | 17.6 | 22 | 22.5 | 0 | 0 | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 0 | 0 | 62.7 | 62.2 | 0 | 0 | 65.8 | 62.8 | 62.2 | 60.2 | 63.7 | 62.2 | 61.8 | 58.1 | 1.26 | 1.26 | 0 | 0 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 88 | 88 | 0 | 0 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 6475.7 | 6475.8 | 0 | 0 | 6475.7 | 6475.8 | 6475.7 | 6475.7 | 6475.8 | 6475.8 | 6475.8 | 6475.8 | 2018 | 2018 | 10 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 3 | 2018 | 11 | 3 | 2018 | 9 | 3 | 2018 | 11 | 3 | 2018 | 11 | 3 | 2018 | 9 | 3 | 2018 | 9 | 3 | 2018 | 11 | 3 | 2018 | 9 | 3 | 39702 | 39641 | 0 | 0 | 39703 | 39594 | 39709 | 39697 | 39592 | 39595 | 39696 | 39596 | 7.73 | 7.73 | 0 | 0 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.652 | 0.28 | 0 | 0 | 0 | 0 | 7.79 | 7.74 | 7.75 | 7.79 | 7.78 | 7.75 | 7.68 | 7.91 | 7.69 | 7.5 | 7.69 | 7.56 | 8.05 | 7.58 | 7.92 | 7.62 | 7.72 | 8.03 | 7.65 | 7.96 |  |  |  |  | -0.14 | -0.21 | -0.12 | 0.12 | -0.21 | -0.26 | -0.46 | -0.4 | -0.12 | -0.17 | 0.14 | -0.35 | 0.09 | -0.23 | 0.14 | -0.21 | -0.35 | 0.02 | 0.02 | -0.05 |  |  |  |  | 7.63 | 7.78 | 7.6 | 7.85 | 7.83 | 8.02 | 7.7 | 7.58 | 7.94 | 7.86 | 7.85 | 7.71 | 8.08 | 7.77 | 7.87 | 7.78 | 7.94 | 7.61 | 7.88 | 7.67 |  |  |  |  | -0.23 | -0.34 | -0.15 | 0.12 | -0.27 | 0.24 | -0.4 | -0.33 | -0.15 | -0.16 | -0.33 | -0.31 | -0.03 | -0.28 | -0.48 | -0.46 | -0.08 | -0.29 | -0.32 | -0.37 |  |  |  |  | 19076.7 | 0 | 3955.8 | 0 | 0 | 0.02 | 0.02 | 0 | 1.04 | 1.04 | 0 | 4.4.0.0.0 | 4.4.0.4.1 | 4.4.0.0.0 | 4.4.0.2.0 | 4.4.0.1.0 | 4.4.4.23.5 | 4.7.1.2.0 | 4.4.0.4.12 | 4.4.0.0.0 | 4.4.0.5.12 | 4.4.0.0.0 | 4.4.0.0.0 | 4.4.0.7.0 | 4.4.0.1.0 | 4.4.0.0.4 | 4.4.0.6.6 | 4.4.0.6.0 | 4.4.0.0.2 | 4.4.0.0.0 | 4.4.0.0.2 | 4.4.0.1.12 | 0.0.0.0.0 | 0.0.0.0.0 | 4.4.0.4.11 | 4.4.1.1.0 | 4.4.0.2.13 | 4.4.0.3.0 | 4.3.0.0.0 | 4.4.0.3.3 | 4.9.0.0.0 | M01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 722 | [30 empty] | -1 | 3 | 1 | NaN | 0.0001 | 1607949461000 | 1 | 1 | 0.1724 | 1 | NaN | 3222 | 1 | 1607472000000 | NaN | NaN | NaN | 0.06 | 5.54 | 17 |  | 2 | 0.0008 | 1 | 1 | 1 | 2 |  | 0 | 2105 | 15 | 0.0336 | 1 | 1607943600000 | 2 | 1 | 4 | 3.02 | 2.9 | 1015634 | 1 | 1 | 6221 | 1 | 15.4 | 149 | 0.05 | 0.0409 |  |  |  |  | Available | 40 |  |  |  |  | 6.92 | 2 | 2 |  | 0 | 0 | 50 | 49.99 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 1 | 0 | 970 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 1 | 1 | 1 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 30 | 30 | 0 | 2 | 20 | 15 | 80 | 1 | 0 | 11 | 1 | 0 | 0 | 0 | 0 | 7 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 35 | [5 empty] | 0 | 0 | 0 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 0 | 0 |  | -600 | -600 | 6 | 0 | 50 | 1500 | 5.6 | 6.7 | 6.9 | 0.1 | 3 | 0.1 | 0 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 2.5 |  | 0 | 0 | 0.2 | 4.2 |  | 10 | 0 |  |  |  | 0 |  | 5 | 5 | 5 | 5 | 5 | 60 | 28 | 40 | 30 | 50 | 180 | 28 | 40 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 2 | 10 | 2 | 1 | 1 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 2 | 10 | 2 | 1 | 1 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 4 | 0 | [479 empty] | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 12000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 10 | 1 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 32 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 | 0.95 | 0 | 60 | -33 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | 85 | 110 | 90 | 95 | 100 | 105 | 0.85 | 0.9 | 0.95 | 1 | -0.97 | -0.95 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 1 | 40 | 0 | 30 | 30 | 10 | 10 | 10 | 3 | 1 | 10000 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 4 | 4 | 0.01 | 0.01 | 0.2 | 0.2 | 1 | 1.11 | 1 | 1.11 | 1 | 30 | 1 | 2 | 1 | 100 | 100 | 10 | 50 | 50 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 5000 | -5000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 51.5 | 47.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 1 | 115 | 85 | 35 | 10 | 0 | 0 | 1 | -0.2 | 50 | 110 | 80 | 1 | 0 | 241 | 200 | 1 | 99.36 | 10 | 2 | 0.8 | 3 | 4 | 10 | 0.5 | 4 | 10000 | 20 | 40 | 5 | 10000 | 0 | 0 | 0 | 0 | 10000 | 120 | 88 | 45 | 1 | 10 | 0 | 0 | 0 | -0.2 | 50 | 110 | 60 | 1 | 0 | 241 | 200 | 1 | 100 | 100 | 10 | 2 | 0.8 | 3 | 4 | 10 | 0.5 | 4 | 10000 | 40 | 40 | 5 | 10000 | 0 | 0 | 0 | 0 | 10000 | 120 | 88 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 6 | 0 | 6000 | 0 | 100 | 50 | 75 | 500 | 100 | 460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40 | 20 | 40 | 505 | 505 | 300 | 30 | 120 | 0 |  | 0 | 0 | 0 | 1 | 1 | 0 | 0 |  | 0 |  | 0 |  |  |  | 1 | 1 |  |  |  | 1 | 1 | 0 | 1 |  | 1 | 1 | 1 |  | 1 | 1 | [8 empty] | 0 | 1 |  | 0 | 0 |  |  | 1 |  | 0 | 1 | 1 | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 12.5 |  | 620 |  |  |  |  | 11 | 0 | 300 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.2 | 0.1 | 0.01 | 3.3 | 80 | 0 | 1 | 7 | 100 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 40 | 0 | 100 | 10 | 0 | 0 | -5 | 15 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 45 | 30 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 200 | 168 | 75 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 65 | 4 | 0 | 0 | 0 | -4.5 | 10 | 1 | 20 | 15 | 0 | 2 | 1 | 1.82 | 0.6 | 0.6 | 1 | 0 | 350 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0 | 0 | 0 | 0 | 15 | 30 | 0.01 | 0.4 | 0 | 60 | 30 | 0 | 0 | 0 | 0 | 1200 | 1400 | 0 | 0.5 | 390 | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 0.2 | 0.05 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1.2 | 0.1 | 300 | 300 | 300 | 300 | 0 | 50 | 50 | 50 | 50 | 50 | 120 | 0 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.15 | 1 | 25 | 3 | 100 | 0 | 8 | 0 | 0.5 | 1 | 4 | 50 | 0 | 25 | 10 | 250 | 1 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 | 1 | 1 | 4000 | 2000 | 20000 | 10000 | 3356 | 1678 | 8 | 4 | 2 | 1 | 30 | 150 | 20 | 120 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 1 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [66 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 1200 | 1000 |  |  |  | 1000 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 50 | 1000 | 680 | 640 | 5 | 650 | 5 | 650 | 640 | 5 | 650 | 5 | 1000 | 5 | 15 | 300 | 20 | 50 | 650 | 5 | 150 | 5 | 1000 | 225 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 20 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 20 | 5 | 10 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | 0 | 20 |  | 0.98 | 1 | -0.98 | -0.95 | 0.8 | -0.92 | 1 | 7 | 0.95 | -0.95 | 20 | 80 | 4169 | 88 | 90 | 2.05 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 0 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 85 | 90 | 85 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 43.4 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 35 | 300 |  | 75 | 1.05 | 1 | 1 | 1 | 180 | 0.3 | 1.11 | 60 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 3356 | 0 | 5000 | 40 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 3356 | 1 | 2 | 0 | 1 | 1 | 2 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 4 | 20 | 0.9 | -0.95 | 1 | 0 | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 10000 | 0 | 0 | 0 | 0 | 1 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -100 | 100 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 1 | 1 | 0.8 | -0.92 | 2720 | -2720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 10 | 3.3 | 0.2 | 3.5 | 0.05 | 1.4 | 1.7 | 0.05 | 0.05 | 87 | 5 | 94 | 2 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 35 |  |  | 20 |  |  |  | 3 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.5 | 0.1 | 0.5 | 500 | 1500 | 3.5 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1.5 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 75 | 2 | 79 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 1 | 0 | 120 | 120 | 2 | 2 | 0 | 1 | 0 | 120 | 120 | 2 | 2 | 0 | 62 | 2 | 1 |  | 80 | 120 | 0.5 | 0.5 | 0 | 1 | 0 | 138 | 138 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 82 | 0 | 0 | 0 | 5 | 20 | 0 | 2 | 30 | 90 | 0 | 0 | 0 | 200 | -200 | 0 | -50 | 100 | -100 | 0 | 0 | 0 | 200 | -200 | 20 | 30 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 9.5 | 10 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 1 | 1 | 90 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 16 | 18 | 18 | 18 | [5 empty] | 15 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 462 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 1 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 0 | 0 | 20 | 4000 | 4000 |  | 700 | 30 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 5 | 5 | 5 | 5 | -5 | -5 | -5 | -5 | 12 | 12 | 12 | 12 | 4.5 |  | 45 | 270 | 70 | -144 | 0 | 80 | 350 | [24 empty] | 0 | 4 | 500 | 30 |  | 2000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 320 | 0 | -24 | -13 | 3356 | 1668 | 10 | 3335 | 1668 | 40 | 0 | 0 | [6 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 3358 | 1678 | 4222 | 2182 | 1499 | 1500 |  | 49.1 | 50.2 |  | 500 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4916 | 2159 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4916 | 2159 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4916 | 2159 | 1500 | 1500 |  | 50 | 50 |  | 660 |  | 0 | 1000 | 300 | 48 | -1.6 | -4 | 100 | 6 | 0 | 1 | 6 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6 | 0 | 0.5 | 0 | 0 | 120000 | 0 | 120000 | 0 |  | 4 | 0 | 0 | 0 |  |  |  | 75 |  | 40 | [14 empty] | 50 | 50 | 50 | 50 | [10 empty] | 0 | 0 | 1 | 3 | 55 | 57 | 2 | 2 | 58 |  | 40 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 300 | 100 | 99.36 | 100 | [8 empty] | -925 | 3700 |  | 0.2 | 80 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 300 |  | 100 | 100 | [11 empty] | 0.2 | 80 | 200 | [43 empty] | 0 | 0.1 | 0.03 | 0.02 | 100 | 50 | 0 | 1 | 2.3 | 1 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 75 | 60 | 68 | 5 | 100 | 0 | 0 | 0.1 | 0.1 | 0.01 | 100 | 40 | 0 | 1 | 6 | 1 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 60 | 71 | 0 | 100 | 5 | 0 | 0.2 | 100 | 100 | 100 | 80 | 0 | 1 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 40 | 100 | 40 | 0.15 | 0.003 | 1 | 1 | 10 | 0.4 | 0 | 1 | 3.5 | 0.01 | 0.01 | 0.1 | 0.1 | 0 | 0 | 1.1 | 0.7 | 1 | 25 | 100 | 0 | 0 | 0.1 | 0.03 | 0.02 | 100 | 50 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 130 | 100 | 110 | 60 | 100 | 35 | 0 | 0.3 | 0.01 | 0.01 | 100 | 50 | 0 | 1 | 7 | 1 | 1 | 1 | 1 | 0 | 0 | 47 | 30 | 35 | 0 | 100 | 10 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0 | 0.1 | 100 | 205 | 0 | 1 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 28 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | [42 empty] | 0 | 0.1 | 100 | 80 | 0 | 1 | 4 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 40 | 0.1 | 0.01 | 55 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 0 | 0 | 10 | 150 | 150 | 100 | 205 | 0 | 48 | 50 | 0 | 3000 | 6000 | 3000 | 6000 | 6 | 6 | 0 | 5000 | -5000 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 100 | 50 | 0 | 0.1 | 100 | 80 | 0 | 1 | 4 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 50 | 0.1 | 0.01 | 55 | 0 | 100 | 60 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 |  |  |  |  | 12 | 0 | 0 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 80 | 0 | [6 empty] | 0.01421 | 0.29619 | 0.88857 | 100 | 0 | 0 | 0.44428 | 0.23695 | 100 | 2 | 0 | 20 | 5000 | 5000 | 60 | 75 | 90 | 100 |  | 4 | 20 | 1668 | 3356 | 2 | 2 | 37 | 45 |  | -6 | -6 | -6 | -6 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -145 | 10 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 3356 | 3356 | 3356 | 3356 | 70 | 0.65 | 0.56 | 0.56 | 0.56 | 0.45 | 0.56 | 0.56 | 0.56 |  | 10 | 20 | 93 | 1 | 1 | 100.4 | 103.4 | 98 | 91 | 103.4 | 40 | 65 | 85 | 80 |  | 110 | 125 | 90 | 70 | 140 | 0 | 80 | 20 | 80 | 1 | 22.7 | 3 | 3 | 10 | 75 |  |  | 10 | 4 | 4 | 4 | 4 | 54 | 54 | 54 | 54 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 130 | 1000 | 1000 | 4000 | 3000 | 16 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 300 | 3300 | 50 | 100 | 50 | 300 | 650 | 93 | 98 | 1 | 100 | 2 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [30 empty] | 1 | 1 | 1 | 33 | 1 | 0 | 60 | 60 | 30 | 15 | 15 | 1 | 0 | 1 | 100 | 70 | 200 | 50 | 100 | 90 | 24 | 25 | 24 | 20 | 25 | 10 | 3000 | 50 | 100 | 50 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1650 | 10 | 200 | 400 | 2800 | 5 | 10000 | 0 | 3850 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 1 | 1200 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 900 |  | 0.15 | 0.7 | 4 | 95 | 2 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1500 | 6.7 | 0 | 95 | 85 | 85 | 95 | 95 | 9.54 | 9.971 | 720 |  |  | 1.35 | 1.5 | 40 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.1 |  |  | 0.74 | [13 empty] | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | [28 empty] | 1 | 1 | 0 | 2 | 0 | 2 | 1 | 1 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 3356 | 0 | 0 | 0 | 0 | 0 | 3356 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -20.11 | 4.119 | 0.1105 | 1.2056 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 76.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 384 | 367 | 364 | 365 | 364 | 358 | 370 | 373 | 369 | 360 | 371 | 359 | 0 | 0 | 0 | 0 | 369 | 368 | 371 | 366 | 372 | 366 | 370 | 523 | 522 | 519 | 519 | 520 | 520 | 518 | 522 | 520 | 520 | 523 | 520 | 518 | 0 | 0 | 0 | 0 | 520 | 520 | 520 | 518 | 519 | 516 | 518 | 4569 | Sending | 30 | 48 | 47 | 47 | 47 | 47 | 46 | 46 | 47 | 47 | 47 | 48 | 47 | 46 | 46 | 46 | 45 | 47 | 46 | 47 | 46 | 19.8149 | [23 empty] | 1592 | 3090 | 1476 | 3151 | 1782 | 1788 | 1352 | 1428 | 867 | 1718 | 1242 | 1643 | 1477 | 1406 | 3150 | 1445 | 1952 | 1518 | 1656 | 1747 | [5 empty] | 0 | 1 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 950 | 0 | 0 | 0 | 24.7 | 0 | 0 | 0 | 1.307 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2308 | 1 | 2308 | 1 | 2308 | 1 | 2308 | 1 | 2308 | 1 | 2308 | 1 | 2308 | 1 | 2308 | 1 | 2308 | 1 | 2308 | 1 | 2308 | 1 | 2308 | 1 | 2308 | 1 | 2308 | 1 | 2308 | 1 | 2308 | 1 | 2308 | 1 | 2308 | 1 | 2308 | 1 | 2308 | 1 | [8 empty] | 0 | 8.2 | 0 | 8.3 | 0 | 8.3 | 0 | 8.3 | 0 | 8.3 | 0 | 8.1 | 0 | 8.1 | 0 | 8.1 | 0 | 8.2 | 0 | 8.2 | 0 | 8.4 | 0 | 8.1 | 0 | 8.2 | 0 | 8.1 | 0 | 8.3 | 0 | 8.1 | 0 | 8.3 | 0 | 8.2 | 0 | 8 | 0 | 8 | [8 empty] | 0 | -0.1 | 0 | 0.1 | 0 | 0.2 | 0 | 0.1 | 0 | -0.1 | 0 | -0.1 | 0 | -0.1 | 0 | -0.2 | 0 | -0.1 | 0 | -0.2 | 0 | -0.1 | 0 | -0.1 | 0 | -0.1 | 0 | -0.1 | 0 | 0.1 | 0 | 0.1 | 0 | 0.1 | 0 | 0.1 | 0 | -0.1 | 0 | -0.2 | [8 empty] | 0 | 8.2 | 0 | 8.4 | 0 | 8.3 | 0 | 8.3 | 0 | 8 | 0 | 8.3 | 0 | 8.2 | 0 | 8.1 | 0 | 8.1 | 0 | 8 | 0 | 8.2 | 0 | 8.3 | 0 | 8.2 | 0 | 8.3 | 0 | 8.4 | 0 | 8.2 | 0 | 8.4 | 0 | 8.2 | 0 | 8.3 | 0 | 8 | [8 empty] | 0 | -0.1 | 0 | 0.1 | 0 | 0.1 | 0 | 0.1 | 0 | -0.1 | 0 | -0.1 | 0 | 0.1 | 0 | -0.4 | 0 | -0.1 | 0 | -0.2 | 0 | -0.1 | 0 | 0.1 | 0 | 0.1 | 0 | 0.1 | 0 | 0.1 | 0 | 0.1 | 0 | 0.1 | 0 | 0.1 | 0 | -0.1 | 0 | -0.2 | [9 empty] | 0 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1500 | 0 |  | 25.6 |  |  | 0 | 0 | BMW MÜNCHEN
12 |  |  |  |  | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","agent_conn":"Prim-SSL-NoProxy","mon_conn":"Back-SSL-NoProxy","rem_conn":"Prim-NoSSL-NoProxy"} | 0 | 0 | 0 | 0 | 0 | 0 | -0.92 | 4.23 | 0 | 740 | 0 | -343 | 0 | 3.48 | 0 | 3.15 | 4.04 | 19.3 | 0 |  |  |  | 0 | -2 | 0 | 0 | 4.99 | 0 | 5 | 0 | 0 | 0 | 4.4.0.13 | 6716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 |  | 15490 | 0 | 0 |  | 0 | -4488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 |  |  |  |  | 18103342 | 0 | 293310 | 208335 | 452 | 0 | 0 | 0 | 0 | 0 | 134 | 3991 | 1548 | 3538 | 1540 | 3538 | 508 | 1548 | 6462 | 6462 | 6462 |  | 737 |  | 44.3 | 10 | 60 | 60 | 69.3 | 71 | 60 | 5 | 20 | 19.3 | 40 | 0.999 | 0.999 | 50.1 | 120 | 120 | 59.8 | 35 | 23 | 10 | 84.5 | 84.5 | 0 | 0 | 0 | 0 | 40 | 17.2 | 10 | 40 | 30.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 39 | 60.3 | 17.8 | 23 | 17.2 | 0 | 17.5 | 30.4 | 0 | 120 | 145 | 30.6 | 0 | 2 | 7.03 | 3.5 | 145.8 | 26.73 | 26.76 | 26.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.4 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 1.1 | 36.4 | 2.2 | 3.3 | 4.4 | 5.5 | 1.7 | -2.1 | 12.8 | 27.8 | 0 | 0 | 1.1 | 36.4 | 1 | 0 | 2.2 | 0 | 3.3 | 0 | 4.4 | 0 | 5.5 | 0 | 1.7 | 1 | -2.1 | 1 | 12.8 | 1 | 27.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 41.9526 | 41.9125 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 6360 | 20 | 0 | 2478 | 0 | 0 | 2478 | -2.7 | 20.3 | 121.2 | 0 | 0 | 0 | 0 | 0 | 10.4 | 7.04 | 7.07 | 10.4 | 0 | 0 | 0 | 0 | 74 | 74 | 74.9 | 133.8 | 100 | 150 | 21.5 | -1.2 | 74 | 132.2 | 0 | 0 | 0 | 132.2 | 0 | 0 | 0 | 455 | 455 | 0 | 11.4 | 20 | 11.4 | 11.4 | 0 | 0 | 0 | 11.4 | 0 | 0 | 0 | 11.4 | 0 | 117 | 0 | 0 | 50.2 | 39.8 | 0.74 | 2.4 | 0.13 | 350 | 348 | 351 | 27.72 | 1591620533033 | 0 | 46 | 1.025 | 1 | 0 | 0 | 36 | 21.71 | 0 |  | 726 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 509 | 509 | 510 | 512 | 513 | 511 | 513 | 514 | 511 | 512 | 510 | 511 | 512 | 514 | 513 | 516 | 513 | 516 | 513 | 0 | 0 | 0 | 0 | 512 | 512 | 516 | 516 | 509 | 509 | 0 | 348 | 110 | 0 | 0 | 7 | [42 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 4287646 | 0 |  |  | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.4 | 46.2 |  |  | 50.8 | 51.1 | 45.8 | 20.6 |  |  |  |  | 3894 | 1606503803205 |  | 3355 | 0.999 | 50 | 0 | 10091 | 5832 | 10080 | 5813 | 10096 | 5829 | 10087 | 5832 | 10094 | 5810 | 10109 | 5826 | 0 | 219173 | 3320 | 66 | 0.032 | 8019 | 2.01 | -30.2 | 3.95 | 1.05 |  | 0 | 84.5 | 65.9 | 0 | 60 | 60 | 59.5 | 0 | 0 | 0 | 24.9 | 24.9 | 24.9 | 24.9 | 24.9 | 24.9 | 24.9 | 24.9 | 24.9 | 24.9 | 24.9 | 24.9 | 24.9 | 24.9 | 24.9 | 24.9 | 24.9 | 24.9 | 24.9 | 24.9 | 24.9 | 0 | 0 | 0 | 0 | 59.6 | 70.5 | 0 | 0 | 67.3 | 72.7 | 66.6 | 69.6 | 66.2 | 57.2 | 57.3 | 58.1 | 1.26 | 1.26 | 0 | 0 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 88 | 88 | 0 | 0 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 6486.8 | 6486.8 | 0 | 0 | 6486.8 | 6486.8 | 6486.8 | 6486.8 | 6486.8 | 6486.8 | 6486.8 | 6473.5 | 2018 | 2018 | 11 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 3 | 2018 | 11 | 3 | 2018 | 11 | 3 | 2018 | 11 | 3 | 2018 | 11 | 3 | 2018 | 11 | 3 | 2018 | 11 | 3 | 2018 | 9 | 3 | 2018 | 10 | 3 | 39729 | 39680 | 0 | 0 | 39678 | 39728 | 39679 | 39724 | 39692 | 39725 | 39618 | 39667 | 7.73 | 7.73 | 0 | 0 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 37 | 0 | 0 | -25 | -25 | -25 | -25 | -25 | -25 | -25 | -25 | -25 | -25 | -25 | -25 | -25 | -25 | -25 | -25 | -25 | -25 | -25 | -25 | 0 | 0 | 0 | 0 | 174 | 174 | 94 | 269 | 126 | 158 | 141 | 237 | 79 | 110 | 126 | 141 | 141 | 126 | 110 | 205 | 141 | 126 | 110 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 341 | 317 | 268 | 366 | 402 | 268 | 402 | 378 | 256 | 305 | 244 | 329 | 317 | 439 | 378 | 415 | 329 | 256 | 256 | 305 | 0 | 0 | 0 | 0 | 0.001 | 4.39 | 0 | 0 | 0 | 0 | 7.63 | 7.83 | 7.57 | 7.74 | 7.79 | 7.65 | 7.64 | 7.84 | 7.76 | 7.7 | 7.62 | 7.56 | 7.58 | 7.52 | 7.74 | 7.58 | 7.63 | 7.99 | 7.6 | 7.61 |  |  |  |  | -0.29 | -0.36 | 0.04 | -0.17 | -0.13 | -0.29 | -0.29 | -0.17 | -0.18 | -0.21 | -0.43 | -0.08 | -0.31 | -0.22 | -0.37 | -0.2 | -0.26 | -0.31 | -0.41 | -0.12 |  |  |  |  | 7.78 | 7.7 | 7.79 | 7.93 | 7.83 | 7.83 | 7.62 | 7.62 | 7.99 | 7.95 | 7.52 | 7.64 | 7.74 | 7.61 | 7.65 | 7.61 | 7.6 | 7.6 | 7.51 | 7.68 |  |  |  |  | -0.28 | -0.27 | -0.36 | -0.4 | 0.02 | -0.37 | -0.27 | -0.28 | -0.08 | -0.28 | -0.35 | -0.27 | -0.29 | -0.38 | -0.37 | -0.34 | -0.23 | -0.37 | -0.44 | -0.26 |  |  |  |  | 19205.7 | 0 | 4017.5 | 0 | 192 | 0.02 | 0.02 | 99 | 1.04 | 1.04 | 10100 | 4.4.0.0.0 | 4.4.0.4.1 | 4.4.0.0.0 | 4.4.0.2.0 | 4.4.0.1.0 | 4.4.4.23.5 | 4.7.1.2.0 | 4.4.0.4.12 | 4.4.0.0.0 | 4.4.0.5.12 | 4.4.0.0.0 | 4.4.0.0.0 | 4.4.0.7.0 | 4.4.0.1.0 | 4.4.0.0.4 | 4.4.0.6.6 | 4.4.0.6.0 | 4.4.0.0.2 | 4.4.0.0.0 | 4.4.0.0.2 | 4.4.0.1.12 | 0.0.0.0.0 | 0.0.0.0.0 | 4.4.0.4.11 | 4.4.1.1.0 | 4.4.0.2.13 | 4.4.0.3.0 | 4.3.0.0.0 | 4.4.0.3.3 | 4.9.0.0.0 | M03 | 17.3 | 15.4 | 16.5 | 16.9 | 17.4 | 17.5 | 19.1 | 17.9 | 17.4 | 17 | 18 | 20.3 | 16 | 15.7 | 17.1 | 16.4 | 16.7 | 18 | 16.2 | 16.4 | 20.5 | 0 | 0 | 0 | 0 | 20.5 | 15.4 | 903 | [30 empty] | -1 | 2 | 1 | NaN | 0.0001 | 1607427428000 | 1 | 1 | 0.1715 | 1 | NaN | 3193 | 1 | 1606867200000 | NaN | NaN | NaN | 0.03 | 5.58 | 13 |  | 2 | 0.001 | 1 | 1 | 1 | 2 |  | 0 | 1659 | 13 | 0.0335 | 1 | 1607425200000 | 2 | 1 | 1 | 2.75 | 3 | 1015632 | 1 | 1 | 6095 | 1 | 15.3 | 147 | 0.05 | 0.0413 |  |  |  |  | Running | 50 |  |  |  | 4010 | 8.57 | 2 | 2 |  | 50.01 | 50 | 50 | 50 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 1 | 0 | 970 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 1 | 1 | 1 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 30 | 30 | 0 | 2 | 20 | 15 | 80 | 1 | 0 | 11 | 1 | 0 | 0 | 0 | 0 | 7 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 35 | [5 empty] | 0 | 0 | 0 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 0 | 0 |  | -600 | -600 | 6 | 0 | 50 | 1500 | 5.6 | 6.7 | 6.9 | 0.1 | 3 | 0.1 | 0 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 2.5 |  | 0 | 0 | 0.2 | 4.2 |  | 10 | 0 |  |  |  | 0 |  | 5 | 5 | 5 | 5 | 5 | 60 | 28 | 40 | 30 | 50 | 180 | 28 | 40 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 2 | 10 | 2 | 1 | 1 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 2 | 10 | 2 | 1 | 1 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 4 | 0 | [479 empty] | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 12000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 10 | 1 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 32 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 | 0.95 | 0 | 60 | -33 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | 85 | 110 | 90 | 95 | 100 | 105 | 0.85 | 0.9 | 0.95 | 1 | -0.97 | -0.95 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 1 | 40 | 0 | 30 | 30 | 10 | 10 | 10 | 3 | 1 | 10000 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 4 | 4 | 0.01 | 0.01 | 0.2 | 0.2 | 1 | 1.11 | 1 | 1.11 | 1 | 30 | 1 | 2 | 1 | 100 | 100 | 10 | 50 | 50 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 5000 | -5000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 51.5 | 47.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 1 | 115 | 85 | 35 | 10 | 0 | 0 | 1 | -0.2 | 50 | 110 | 80 | 1 | 0 | 241 | 200 | 1 | 99.36 | 10 | 2 | 0.8 | 3 | 4 | 10 | 0.5 | 4 | 10000 | 40 | 40 | 5 | 10000 | 0 | 0 | 0 | 0 | 10000 | 120 | 88 | 45 | 1 | 10 | 0 | 0 | 0 | -0.2 | 50 | 110 | 60 | 1 | 0 | 241 | 200 | 1 | 100 | 100 | 10 | 2 | 0.8 | 3 | 4 | 10 | 0.5 | 4 | 10000 | 40 | 40 | 5 | 10000 | 0 | 0 | 0 | 0 | 10000 | 120 | 88 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 6 | 0 | 6000 | 0 | 100 | 50 | 75 | 500 | 100 | 460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40 | 20 | 40 | 505 | 505 | 300 | 30 | 120 | 0 |  | 0 | 0 | 0 | 1 | 1 | 0 | 0 |  | 0 |  | 0 |  |  |  | 1 | 1 |  |  |  | 1 | 1 | 0 | 1 |  | 1 | 1 | 1 |  | 1 | 1 | [8 empty] | 0 | 1 |  | 0 | 0 |  |  | 1 |  | 0 | 1 | 1 | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 12.5 |  | 620 |  |  |  |  | 11 | 0 | 300 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.2 | 0.1 | 0.01 | 3.3 | 80 | 0 | 1 | 7 | 100 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 40 | 0 | 100 | 10 | 0 | 0 | -5 | 15 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 45 | 30 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 200 | 168 | 75 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 65 | 4 | 0 | 0 | 0 | -4.5 | 10 | 1 | 20 | 15 | 0 | 2 | 1 | 1.82 | 0.6 | 0.6 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0 | 0 | 0 | 0 | 15 | 30 | 0.01 | 0.4 | 0 | 60 | 30 | 0 | 0 | 0 | 0 | 1200 | 1400 | 0 | 0.5 | 385 | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 0.2 | 0.05 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1.2 | 0.1 | 300 | 300 | 300 | 300 | 0 | 50 | 50 | 50 | 50 | 50 | 120 | 0 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.15 | 1 | 25 | 3 | 100 | 0 | 8 | 0 | 0.5 | 1 | 4 | 50 | 0 | 25 | 10 | 250 | 1 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 | 1 | 1 | 4000 | 2000 | 20000 | 10000 | 3356 | 1678 | 8 | 4 | 2 | 1 | 30 | 150 | 20 | 120 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 1 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [66 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 1200 | 1000 |  |  |  | 1000 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 50 | 1000 | 680 | 640 | 5 | 650 | 5 | 650 | 640 | 5 | 650 | 5 | 1000 | 5 | 15 | 300 | 20 | 50 | 650 | 5 | 200 | 5 | 1000 | 225 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 20 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 20 | 5 | 10 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | 0 | 20 |  | 0.98 | 1 | -0.98 | -0.95 | 0.8 | -0.92 | 1 | 7 | 0.95 | -0.95 | 20 | 80 | 4169 | 88 | 90 | 2.05 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 0 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 85 | 90 | 85 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 43.4 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 35 | 300 |  | 75 | 1.05 | 1 | 1 | 1 | 180 | 0.3 | 1.11 | 60 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 3356 | 0 | 5000 | 40 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 3356 | 1 | 2 | 0 | 1 | 1 | 2 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 4 | 20 | 0.9 | -0.95 | 1 | 0 | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 10000 | 0 | 0 | 0 | 0 | 1 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -100 | 100 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 1 | 1 | 0.8 | -0.92 | 2720 | -2720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 10 | 3.3 | 0.2 | 3.5 | 0.05 | 1.4 | 1.7 | 0.05 | 0.05 | 87 | 5 | 94 | 2 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 35 |  |  | 20 |  |  |  | 3 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.5 | 0.1 | 0.5 | 500 | 1500 | 3.5 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1.5 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 75 | 2 | 79 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 1 | 0 | 120 | 120 | 2 | 2 | 0 | 1 | 0 | 120 | 120 | 2 | 2 | 0 | 62 | 2 | 1 |  | 80 | 120 | 0.5 | 0.5 | 0 | 1 | 0 | 138 | 138 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 82 | 0 | 0 | 0 | 5 | 20 | 0 | 2 | 30 | 90 | 0 | 0 | 0 | 200 | -200 | 0 | -50 | 100 | -100 | 0 | 0 | 0 | 200 | -200 | 20 | 30 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 9.5 | 10 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 1 | 1 | 90 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 16 | 18 | 18 | 18 | [5 empty] | 15 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 462 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 1 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 0 | 0 | 20 | 4000 | 4000 |  | 700 | 30 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 5 | 5 | 5 | 5 | -5 | -5 | -5 | -5 | 12 | 12 | 12 | 12 | 4.5 |  | 45 | 270 | 70 | -144 | 0 | 80 | 350 | [24 empty] | 0 | 4 | 500 | 30 |  | 2000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 320 | 0 | -24 | -13 | 3335 | 1668 | 10 | 3335 | 1668 | 40 | 0 | 0 | [6 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 3347 | 1682 | 4304 | 2202 | 1499 | 1499 |  | 50.1 | 49.5 |  | 500 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4916 | 2159 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4916 | 2159 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4916 | 2159 | 1500 | 1500 |  | 50 | 50 |  | 660 |  | 0 | 1000 | 300 | 48 | -1.6 | -4 | 100 | 6 | 0 | 1 | 6 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6 | 0 | 0.5 | 0 | 0 | 120000 | 0 | 120000 | 0 |  | 4 | 0 | 0 | 0 |  |  |  | 75 |  | 40 | [14 empty] | 50 | 50 | 50 | 50 | [10 empty] | 0 | 0 | 1 | 3 | 55 | 57 | 2 | 2 | 58 |  | 40 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 300 | 100 | 99.36 | 100 | [8 empty] | -925 | 3700 |  | 0.2 | 80 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 300 |  | 100 | 100 | [11 empty] | 0.2 | 80 | 200 | [43 empty] | 0 | 0.1 | 0.03 | 0.01 | 100 | 100 | 0 | 1 | 1.5 | 1 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 60 | 60 | 5 | 100 | 0 | 0 | 0.1 | 0.1 | 0.01 | 100 | 40 | 0 | 1 | 6 | 1 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 60 | 71 | 0 | 100 | 5 | 0 | 0.2 | 100 | 100 | 100 | 80 | 0 | 1 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 35 | 40 | 100 | 40 | 0.15 | 0.003 | 1 | 1 | 10 | 0.4 | 0 | 1 | 3.5 | 0.01 | 0.01 | 0.1 | 0.1 | 0 | 0 | 1.1 | 0.7 | 1 | 25 | 100 | 0 | 0 | 0.1 | 3 | 0.02 | 100 | 50 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 130 | 100 | 110 | 60 | 100 | 30 | 0 | 0.3 | 0.01 | 0.01 | 100 | 80 | 0 | 1 | 7 | 1 | 1 | 1 | 1 | 0 | 0 | 47 | 30 | 35 | 0 | 100 | 10 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0 | 0.1 | 100 | 205 | 0 | 1 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 28 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | [42 empty] | 0 | 0.1 | 100 | 80 | 0 | 1 | 4 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 40 | 0.1 | 0.01 | 55 | 10 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 0 | 0 | 10 | 150 | 150 | 100 | 205 | 0 | 48 | 50 | 0 | 3000 | 6000 | 3000 | 6000 | 6 | 6 | 0 | 5000 | -5000 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 100 | 50 | 0 | 0.1 | 100 | 80 | 0 | 1 | 4 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 40 | 0.1 | 0.01 | 55 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 |  |  |  |  | 12 | 0 | 0 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 80 | 0 | [6 empty] | 0.01421 | 0.29619 | 0.88857 | 100 | 0 | 0 | 0.44428 | 0.23695 | 100 | 2 | 0 | 20 | 5000 | 5000 | 60 | 75 | 90 | 100 |  | 4 | 20 | 1668 | 3356 | 2 | 2 | 37 | 45 |  | -6 | -6 | -6 | -6 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -145 | 10 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 3356 | 3356 | 3356 | 3356 | 70 | 0.65 | 0.56 | 0.56 | 0.56 | 0.45 | 0.56 | 0.56 | 0.56 |  | 10 | 20 | 93 | 1 | 1 | 100.4 | 103.4 | 98 | 91 | 103.4 | 40 | 65 | 85 | 80 |  | 110 | 125 | 90 | 70 | 140 | 0 | 80 | 20 | 80 | 1 | 22.7 | 3 | 3 | 10 | 75 |  |  | 10 | 4 | 4 | 4 | 4 | 54 | 54 | 54 | 54 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 130 | 1000 | 1000 | 4000 | 3000 | 16 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 300 | 3300 | 50 | 100 | 50 | 300 | 650 | 93 | 98 | 1 | 100 | 2 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [30 empty] | 1 | 1 | 1 | 33 | 1 | 0 | 60 | 60 | 30 | 15 | 15 | 1 | 0 | 1 | 100 | 70 | 200 | 50 | 100 | 90 | 24 | 25 | 24 | 20 | 25 | 10 | 3000 | 50 | 100 | 50 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1650 | 10 | 200 | 400 | 2800 | 5 | 10000 | 0 | 3850 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 1 | 1200 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 900 |  | 0.15 | 0.7 | 4 | 95 | 2 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1500 | 6.7 | 0 | 95 | 85 | 85 | 95 | 95 | 9.54 | 9.971 | 720 |  |  | 1.35 | 1.5 | 40 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.1 |  |  | 0.74 | [13 empty] | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | [28 empty] | 1 | 1 | 0 | 2 | 0 | 2 | 1 | 1 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3354 |  |  | 3356 | 0 | 0 | 0 | 0 | 0 | 3356 | 3354 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -30.17 | 3.947 | 0.076 | 1.0385 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 368 | 375 | 368 | 365 | 367 | 367 | 369 | 365 | 374 | 370 | 369 | 367 | 0 | 0 | 0 | 0 | 368 | 367 | 364 | 367 | 365 | 366 | 362 | 514 | 515 | 515 | 516 | 518 | 516 | 516 | 517 | 517 | 518 | 515 | 517 | 518 | 0 | 0 | 0 | 0 | 515 | 517 | 514 | 516 | 514 | 515 | 512 | 5543 | Sending | 30 | 47 | 47 | 47 | 47 | 47 | 49 | 47 | 48 | 47 | 47 | 49 | 46 | 47 | 47 | 46 | 47 | 47 | 47 | 45 | 46 | 18.3859 | 20.6188 | 24.1096 | 19.3419 | 20.792 | 22.1117 | 19.4342 | 19.3787 | 21.006 | 19.4812 | 20.4262 | 19.1925 | 17.2421 | 19.4858 | 19.7662 | 21.903 | 23.9785 | 20.1564 | 20.7469 | 22.603 |  |  |  |  | 2005 | 2080 | 1865 | 1845 | 1703 | 3008 | 1716 | 1657 | 1876 | 1469 | 3150 | 1872 | 1815 | 1880 | 1923 | 2020 | 1542 | 2020 | 1841 | 1008 | [5 empty] | 0 | 1 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 0 | 0 | 199.6 | 0 | 0 | 0 | 1076 | 0 | 0 | 0 | 4.1 | 0 | 0 | 0 | 2.096 |  |  |  | 66.1 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 | [8 empty] | 0 | 7.63 | 0 | 7.83 | 0 | 7.57 | 0 | 7.74 | 0 | 7.79 | 0 | 7.65 | 0 | 7.64 | 0 | 7.84 | 0 | 7.76 | 0 | 7.7 | 0 | 7.62 | 0 | 7.56 | 0 | 7.58 | 0 | 7.52 | 0 | 7.74 | 0 | 7.58 | 0 | 7.63 | 0 | 7.99 | 0 | 7.6 | 0 | 7.61 | [8 empty] | 0 | -0.29 | 0 | -0.36 | 0 | 0.04 | 0 | -0.17 | 0 | -0.13 | 0 | -0.29 | 0 | -0.29 | 0 | -0.17 | 0 | -0.18 | 0 | -0.21 | 0 | -0.43 | 0 | -0.08 | 0 | -0.31 | 0 | -0.22 | 0 | -0.37 | 0 | -0.2 | 0 | -0.26 | 0 | -0.31 | 0 | -0.41 | 0 | -0.12 | [8 empty] | 0 | 7.78 | 0 | 7.7 | 0 | 7.79 | 0 | 7.93 | 0 | 7.83 | 0 | 7.83 | 0 | 7.62 | 0 | 7.62 | 0 | 7.99 | 0 | 7.95 | 0 | 7.52 | 0 | 7.64 | 0 | 7.74 | 0 | 7.61 | 0 | 7.65 | 0 | 7.61 | 0 | 7.6 | 0 | 7.6 | 0 | 7.51 | 0 | 7.68 | [8 empty] | 0 | -0.28 | 0 | -0.27 | 0 | -0.36 | 0 | -0.4 | 0 | 0.02 | 0 | -0.37 | 0 | -0.27 | 0 | -0.28 | 0 | -0.08 | 0 | -0.28 | 0 | -0.35 | 0 | -0.27 | 0 | -0.29 | 0 | -0.38 | 0 | -0.37 | 0 | -0.34 | 0 | -0.23 | 0 | -0.37 | 0 | -0.44 | 0 | -0.26 | [9 empty] | 0 | 0 | 1 | 1 | 17 | 0 | 100 | 0 | 0 | 0 | 0 | 24.9 | 0 | 0 | 0 | 0 | 0 | 0 | 4.39 |  | 0 | 0 | 0 | 0 |  | 100 | 100 | 100 | 100 | 24.9 | 24.9 | 24.9 | 24.9 |  | 1500 | 1500 |  | 44.3 |  |  | 0 | 0 | BMW MÜNCHEN
13 |  |  |  |  | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","rem_conn":"Back-NoSSL-NoProxy","dataItems":"0/20","agent_conn":"Prim-SSL-NoProxy","mon_conn":"Prim-NoSSL-NoProxy"} | 0 | 0 | 0 | 0 | 0 | 0 | -0.92 | 5.99 | 0 | 969 | 0 | -1464 | 0 | 6.76 | 0 | 4.57 | 4.48 | 21.7 | 0 |  |  |  | 0 | 1.3 | 0 | 0 | 5.07 | 0 | 5.08 | 0 | 0 | 0 | 4.4.0.13 | 5356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 |  | 19638 | 0 | 0 |  | 0 | -5966 | 0 | -3006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.02 |  |  |  |  | 208878 | 0 | 8175 | 329731 | 4199 | 0 | 0 | 0 | 0 | 0 | 185 | 912 | 912 | 2489 | 496989 | 596989 | 696989 | 796989 | 7511 | 7511 | 7511 |  | 1732 |  | 51.4 | 100 | 60 | 65.7 | 100 | 70 | 66.4 | 0 | 21.7 | 21.7 | 0 | 0.999 | 0.999 | 50 | 120 | 120 | 81.9 | 48 | 47.4 | 0 | 85.8 | 85.8 | 0 | 0 | 0 | 0 | 60 | 0.8 | 0 | 60 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.2 | 65.5 | 63 | 8.5 | 47.4 | 0.8 | 2 | 3.1 | 3.1 | 0 | 120 | 24.3 | 17.1 | 3935 | 0.7 | 6.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | -1.3 | 20.8 | -2.7 | -4.1 | -5.5 | -6.9 | -2.4 | 2 | 17 | 20.8 | 0 | 0 | -1.3 | 20.8 | 1 | 0 | -2.7 | 0 | -4.1 | 0 | -5.5 | 0 | -6.9 | 0 | -2.4 | 0 | 2 | 1 | 17 | 1 | 20.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 7323 | 20 | 0 | 0 | 0 | 0 | 1109 | -1.6 | 20.2 | 109.8 | 0 | 0 | 0 | 0 | 0 | 11.2 | 7.27 | 7.19 | 10.9 | 0 | 0 | 0 | 0 | 75 | 75 | 74.9 | 140.3 | 100 | 150 | 23.4 | 0 | 76 | 140.5 | 0 | 0 | 0 | 140.5 | 0 | 0 | 0 | 460 | 460 | 0 | 10.9 | 0 | 10.9 | 10.9 | 0 | 0 | 0 | 10.9 | 0 | 0 | 0 | 10.9 | 0 | 0 | 0 | 0 | 56.1 | 44.9 | 0.82 | 2.72 | 0.41 | 338 | 335 | 339 | 41.05 | 1608927073792 | 0 | 48 | 1 | 1 | 2.1 | 28.8 | 20 | 11.84 | 0 |  | 1552 |  |  |  |  | 0 | 0 | 0 | 0 | 32791 | 32974 | 31792 | 31674 | 0 | 0 | 0 | 0 | 539 | 539 | 538 | 542 | 541 | 540 | 539 | 539 | 545 | 542 | 542 | 542 | 538 | 537 | 541 | 543 | 538 | 541 | 541 | 543 | 546 | 541 | 542 | 539 | 540 | 540 | 547 | 547 | 536 | 537 | 0 | 0 | 119 | 335 | 335 | 10 | [42 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 8506497 | 0 |  |  | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.9 | 46.1 |  |  | 53.6 | 57.6 | 57.7 | 20.6 |  |  |  |  | 1 | 1606644223498 | 4490 | 4491 | 0.999 | 50 | 0 | 10257 | 5937 | 10245 | 5913 | 10293 | 5930 | 10100 | 5846 | 10081 | 5817 | 10134 | 5837 | 0 | 18926 | 4731 | 4 | 0.032 | 700 | 2.76 | -45.5 | 4.13 | 0.94 |  | 0 | 85.8 | 74 | 0 | 65.7 | 66.4 | 66.3 | 3 | 0 | 0 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 77.7 | 54.1 | 57.7 | 68 | 80 | 78 | 65 | 78.2 | 78.9 | 60.7 | 60.6 | 58.7 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 88 | 88 | 88 | 88 | 88 | 88 | 72 | 88 | 88 | 88 | 88 | 88 | 7565.7 | 7565.6 | 7565.7 | 7565.8 | 7565.7 | 7565.6 | 3001.7 | 7565.4 | 4486.2 | 7565.7 | 7565.7 | 7565.7 | 2017 | 2017 | 7 | 12 | 2017 | 12 | 12 | 2017 | 13 | 12 | 12 | 12 | 2017 | 13 | 12 | 2017 | 12 | 12 | 2019 | 13 | 11 | 2017 | 6 | 12 | 2019 | 18 | 3 | 2017 | 12 | 12 | 2017 | 7 | 12 | 2017 | 13 | 12 | 38027 | 37871 | 38032 | 38078 | 38074 | 38053 | 1132 | 37838 | 45153 | 38025 | 37872 | 38070 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | 174 | 174 | 189 | 174 | 110 | 205 | 174 | 158 | 220 | 189 | 158 | 158 | 253 | 205 | 126 | 141 | 174 | 126 | 174 | 158 | 158 | 126 | 158 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 378 | 463 | 305 | 378 | 305 | 402 | 317 | 378 | 341 | 537 | 329 | 280 | 598 | 317 | 305 | 427 | 512 | 341 | 317 | 378 | 378 | 488 | 488 | 0 | 5.95 | 0 | 0 | 0 | 0 | 7.56 | 7.53 | 7.83 | 7.76 | 7.77 | 7.84 | 7.87 | 7.78 | 7.87 | 7.75 | 7.56 | 7.64 | 7.71 | 7.74 | 7.67 | 7.62 | 7.73 | 7.67 | 7.8 | 7.89 | 7.63 | 7.56 | 7.57 | 7.51 | -0.02 | -0.04 | -0.08 | -0.08 | 0.17 | 0.14 | 0.19 | -0.03 | 0.14 | -0.13 | 0.12 | -0.05 | -0.15 | -0.26 | -0.23 | -0.12 | 0.05 | 0.06 | -0.15 | 0.18 | -0.03 | -0.21 | 0 | -0.13 | 7.52 | 7.73 | 7.77 | 7.77 | 7.87 | 7.95 | 7.72 | 8.09 | 7.91 | 7.92 | 7.83 | 7.56 | 7.74 | 7.5 | 7.8 | 7.89 | 7.74 | 7.73 | 7.95 | 7.76 | 7.66 | 7.91 | 7.74 | 7.54 | -0.04 | -0.17 | -0.08 | -0.13 | -0.02 | 0.02 | 0.11 | -0.07 | 0.08 | -0.03 | -0.2 | -0.07 | -0.03 | -0.13 | -0.17 | -0.21 | -0.06 | 0.11 | -0.02 | 0.1 | -0.03 | 0.01 | -0.14 | -0.18 | 31643.4 | 0 | 6112.9 | 0 | 256 | 0.02 | 0.02 | 129 | 1.04 | 1.04 | 10104 | 4.4.0.0.0 | 4.4.0.1.1 | 4.4.0.0.0 | 4.4.0.1.0 | 4.4.0.5.0 | 4.4.4.12.5 | 4.9.0.1.0 | 4.4.0.2.12 | 4.4.0.0.0 | 4.4.0.3.12 | 4.4.0.0.0 | 4.5.1.0.0 | 4.4.0.1.0 | 4.4.0.1.0 | 4.4.0.0.4 | 4.4.0.3.6 | 4.4.0.3.0 | 4.4.0.0.2 | 4.4.0.0.0 | 4.4.0.0.2 | 4.4.0.0.12 | 4.3.0.0.0 | 0.0.0.0.0 | 4.4.0.2.11 | 4.4.1.0.0 | 4.4.0.0.13 | 4.4.0.1.0 | 4.3.0.0.0 | 4.4.0.3.3 | 4.9.0.0.0 | M02 | 18.4 | 18.5 | 18.9 | 17.8 | 19.1 | 19.9 | 18 | 17.5 | 18.3 | 18.7 | 18.7 | 18.5 | 20.9 | 18 | 17.4 | 19 | 17.6 | 18.3 | 18.7 | 17.4 | 15.8 | 18.3 | 19.1 | 19.5 | 19.2 | 20.9 | 15.8 | 1128 | [30 empty] | -1 | 3 | 1 | NaN | 0.0001 | 1608033887000 | 1 | 1 | 0.1642 | 1 | NaN | 3623 | 1 | 1607731200000 | NaN | NaN | NaN | 0.01 | 5.11 | 12 | NaN | 4 | 0.0005 | 1 | 1 | 1 | 4 |  | 0 | 2966 | 15 | 0.0313 | 1 | 1608032820000 | 1 | 1 | 4 | 3 | 2.5 | 1015689 | 1 | 1 | 7196 | 1 | 15.2 | 146 | 0.05 | 0.0387 |  |  |  |  | Running | 50 |  |  |  |  | 4.14 | 2 | 2 |  | 50 | 50 | 50 | 50 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 1 | 0 | 970 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 1 | 1 | 1 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 30 | 30 | 0 | 2 | 12 | 15 | 80 | 2 | 0 | 11 | 1 | 0 | 0 | 0 | 0 | 7 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 35 | [5 empty] | 0 | 0 | 0 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 200 | -1000 |  | -200 | -1700 | 10 | 0 | 50 | 1500 | 5.6 | 6.7 | 6.9 | 0.1 | 3 | 0.1 | 0 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 2 |  | 0 | 0 | 0.2 | 4.2 |  | 10 | 0 |  |  |  | 0 |  | 5 | 5 | 5 | 2 | 5 | 60 | 28 | 30 | 30 | 50 | 180 | 28 | 20 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 2 | 10 | 2 | 1 | 1 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 2 | 10 | 2 | 1 | 1 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 2 | 10 | [479 empty] | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5 | 2 | 82 | 87 | 50 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 12000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 10 | 0 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 32 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 | 0.95 | 0 | 60 | -33 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | 85 | 110 | 90 | 95 | 100 | 105 | 0.85 | 0.9 | 0.95 | 1 | -0.97 | -0.95 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 1 | 40 | 0 | 30 | 30 | 10 | 10 | 10 | 3 | 1 | 10000 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 4 | 4 | 0.01 | 0.01 | 0.2 | 0.2 | 1 | 1.11 | 1 | 1.11 | 1 | 30 | 1 | 2 | 1 | 100 | 100 | 10 | 50 | 50 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 5000 | -5000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 51.5 | 47.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 1 | 115 | 85 | 35 | 10 | 0 | 0 | 1 | -0.2 | 50 | 110 | 80 | 1 | 0 | 323 | 200 | 1 | 100 | 10 | 2 | 0.8 | 3 | 4 | 10 | 0.5 | 4 | 10000 | 20 | 10 | 5 | 10000 | 0 | 0 | 0 | 0 | 10000 | 120 | 88 | 45 | 1 | 10 | 0 | 0 | 0 | -0.2 | 50 | 110 | 80 | 1 | 0 | 400 | 200 | 1 | 100 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10000 | 20 | 10 | 5 | 10000 | 0 | 0 | 0 | 0 | 10000 | 120 | 88 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 6 | 0 | 6000 | 0 | 100 | 50 | 75 | 500 | 100 | 460 | 5 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 5 | 30 | 30 | 50 | 490 | 490 | 300 | 30 | 100 | 0 |  | 1 | 0 | 0 | 1 | 1 | 0 | 0 |  | 1 |  | 0 |  |  |  | 1 | 1 |  |  |  | 1 | 1 | 0 | 1 |  | 1 | 1 | 1 |  | 1 | 1 | [8 empty] | 0 | 1 |  | 0 | 0 |  |  | 1 |  | 0 | 1 | 1 | 0 |  | 1 | 1 | 1 | 1 |  | 0 |  |  |  | 12.5 |  | 624 |  |  |  |  | 12 | 0 | 346 |  | 1 | 1 | 1 | [9 empty] | 0 | 0 | 0.1 | 0.05 | 100 | 35 | 0 | 1 | 6.5 | 100 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 60 | 30 | 0 | 100 | 0.1 | 0 | 0 | -5 | 2 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 40 | 30 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 200 | 168 | 75 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 2 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 65 | 3 | 0 | 0 | 0 | -2.5 | 10 | 1 | 20 | 15 | 0 | 2 | 1 | 1.82 | 0.6 | 0.6 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0 | 0 | 0 | 0 | 15 | 30 | 0.01 | 0.4 | 0 | 60 | 30 | 0.15 | 0 | 0 | 0 | 700 | 1400 | 0 | 0.5 | 450 | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 0.2 | 0.05 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 1 | 0 | 0.72 | 0.72 | 0.72 | 0.72 | 1.2 | 0.1 | 300 | 300 | 300 | 300 | 0 | 50 | 50 | 50 | 50 | 50 | 120 | 0 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.15 | 3.6621 | 25 | 2.9297 | 100 | 0 | 5 | 0.05 | 0.35 | 1 | 3 | 50 | 2 | 25 | 10 | 250 | 1 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 | 1 | 1 | 4000 | 2000 | 20000 | 10000 | 4500 | 2250 | 8 | 4 | 2 | 1 | 30 | 150 | 20 | 120 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 0 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 | 1.5 | 1 | 650 | 700 | 1 | 0 | 0 | 1 | [66 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 1 | 1 | 1200 | 35900 |  |  |  | 40550 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 100 | 1000 | 680 | 640 | 5 | 650 | 5 | 650 | 640 | 5 | 650 | 5 | 1000 | 5 | 15 | 300 | 20 | 50 | 650 | 2 | 120 | 5 | 1000 | 175 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | 0 | -0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 20 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 30 | 20 | 5 | 10 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | 0 | 20 |  | 0.98 | 1 | -0.98 | -0.95 | 0.8 | 0.92 | 1 | 7 | 0.9 | -0.95 | 20 | 80 | 5590 | 88 | 90 | 2.01 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 0 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 85 | 90 | 85 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 41.9 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 35 | 300 |  | 75 | 0.97 | 1 | 1 | 1 | 180 | 0.1 | 1.11 | 60 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 930 | 1 | 5000 | 40 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 4500 | 4500 | 1 | 2 | 0 | 1 | 1 | 2 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 4 | 20 | 0.8 | -0.95 | 1 | 0 | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 400 | 0 | 0 | 0 | 0 | 1 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -100 | 100 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 1 | 1 | 0.8 | -0.92 | 3600 | -3600 | 10 | 0 | 100 | 0 | 100 | 0 | 800 | -20 | 800 | -20 | 600 | 0 | 10 | 3.3 | 0.2 | 3.5 | 0.05 | 1.5 | 1.9 | 0.05 | 0.05 | 87 | 5 | 94 | 2 | 55 | 5 | 99 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 30 |  |  | 20 |  |  |  | 3 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.4 | 0.1 | 0.5 | 500 | 1500 | 3.5 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1.5 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 75 | 2 | 79 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 1 | 0 | 90 | 120 | 2 | 2 | 0 | 1 | 0 | 75 | 120 | 2 | 2 | 1 | 62 | 2 | 1 |  | 80 | 120 | 0.5 | 0.5 | 0 | 1 | 0 | 142 | 142 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 82 | 0 | 0 | 0 | 5 | 20 | 0 | 2 | 30 | 90 | 0 | 0 | 0 | 200 | -200 | 0 | -70 | 100 | -100 | 0 | 0 | 0 | 200 | -200 | 20 | 30 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 9.5 | 10 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 10 | 0 | 0 | 1 | 90 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 18 | 18 | 18 | 18 | [5 empty] | 4 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 924 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 1 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 0 | 0 | 20 | 4000 | 4000 |  | 850 | 30 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 2 | 2 | 2 | 2 | -5 | -5 | -5 | -5 | 13 | 13 | 13 | 13 | 4.5 |  | 45 | 270 | 70 | -144 | 0 | 80 | 350 | [24 empty] | 0 | 4 | 500 | 30 |  | 2000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 380 | 1 | -30 | -9 | 4500 | 2250 | 10 | 4500 | 2250 | 60 | 0 | 0 | [6 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4499 | 2249 | 5878 | 3000 | 1499 | 1498 |  | 50.9 | 49.1 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4920 | 2158 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4920 | 2158 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4920 | 2158 | 1500 | 1500 |  | 50 | 50 |  | 660 |  | 0 | 1000 | 300 | 48 | -1.6 | -4 | 100 | 10 | 0 | 1 | 10 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 |  | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 10 | 0 | 0.5 | 0 | 0 | 60000 | 0 | 60000 | 0 |  | 5 | 0 | 1 | 1 |  |  |  | 80 |  | 48 | [14 empty] | 48 | 53 | 53 | 53 | [10 empty] | 0 | 0 | 1 | 3 | 55 | 57 | 2 | 2 | 62 |  | 46 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 350 | 100.9 | 100 | 100 | [8 empty] | -1250 | 5000 |  | 0.2 | 100 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 100 |  | 100 | 100 | [11 empty] | 0.2 | 100 | 200 | [43 empty] | 0 | 0.1 | 0.3 | 0.02 | 100 | 40 | 0 | 1 | 2.5 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 60 | 69 | 5 | 100 | 0 | 0 | 0.1 | 1 | 0.01 | 100 | 40 | 0 | 1 | 4.6 | 0 | 99 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 60 | 70 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0.15 | 0.001 | 1 | 1 | 10 | 0.5 | 0 | 1 | 0.45 | 1 | 1 | 1 | 1 | 0 | 0 | 1.1 | 0.7 | 1 | 50 | 100 | 0 | 0 | 0.1 | 0.03 | 0.02 | 100 | 40 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 130 | 100 | 110 | 0 | 100 | 30 | 0 | 0.1 | 0.5 | 0.5 | 100 | 40 | 0 | 1 | 4 | 1 | 1 | 1 | 1 | 0 | 0 | 60 | 45 | 48 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0 | 0.1 | 100 | 205 | 0 | 1 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 28 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | [42 empty] | 0 | 0.1 | 100 | 50 | 0 | 1 | 2.5 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 60 | 100 | 100 | 65 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 0 | 0 | 10 | 150 | 150 | 100 | 205 | 0 | 48 | 50 | 0 | 3000 | 6000 | 3000 | 6000 | 6 | 6 | 0 | 5000 | -5000 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 100 | 50 | 0 | 0.1 | 100 | 50 | 0 | 1 | 2.5 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 60 | 100 | 100 | 60 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 |  |  |  |  | 12 | 2 | 5 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 80 | 0 | [6 empty] | 0.01421 | 0.29619 | 0.88857 | 100 | 0 | 0 | 0.44428 | 0.23695 | 100 | 2 | 0 | 20 | 5000 | 5000 | 60 | 75 | 90 | 100 |  | 4 | 20 | 2250 | 4500 | 2.5 | 2 | 37 | 45 |  | -2 | -2 | -2 | -2 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -145 | 10 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 4500 | 4500 | 4500 | 4500 | 70 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 |  | 10 | 4 | 92 | 1 | 1 | 100.4 | 103.4 | 98 | 91 | 103.4 | 40 | 65 | 85 | 80 |  | 110 | 125 | 90 | 70 | 140 | 1 | 80 | 4 | 80 | 1 | 20 | 5.55 | 1 | 4 | 90 |  |  | 10 | 4 | 4 | 4 | 4 | 56 | 56 | 56 | 56 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | -10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 130 | 400 | 400 | 5000 | 2500 | 16 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [30 empty] | 1 | 10 | 10 | 33 | 1 | 20 | 20 | 20 | 10 | 10 | 0 | 0 | 0 | 0 | 100 | 200 | 50 | 100 | 90 | 1 | 82 | 85 | 87 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.8 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1650 | 10 | 200 | 400 | 2800 | 5 | 10000 | 0 | 3850 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 1 | 1200 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 700 |  | 0.16406 | 2.1973 | 4.3945 | 95 | 2 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1500 | 6.7 | 0 | 95 | 85 | 85 | 95 | 95 | 9.54 | 9.971 | 720 |  |  | 1.45 | 1.55 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.2 |  |  | 0.59 | [13 empty] | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | [28 empty] | 1 | 1 | 0 | 2 | 0 | 2 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4489 |  |  | 4500 | 0 | 0 | 0 | 0 | 0 | 4500 | 4496 |  |  | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 366.5 | 12.7 | -45.47 | 4.13 | 0.0515 | 0.939 | 0 | 0.72 | 4496 | 0 | 0 | 2.22 | 1 | 0 | 1 | 0 | 0 | 113 | 0 | 0 | 240 | 0 | 0 | 33 | 0 | 0 | 433 | 0 | 238 | 0 | 0 | 47 | 0 | 68.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 364 | 364 | 366 | 367 | 364 | 364 | 365 | 366 | 365 | 365 | 367 | 365 | 366 | 366 | 363 | 365 | 366 | 365 | 364 | 365 | 366 | 364 | 364 | 493 | 496 | 495 | 495 | 495 | 496 | 496 | 494 | 496 | 495 | 496 | 495 | 495 | 495 | 496 | 494 | 495 | 496 | 496 | 495 | 495 | 495 | 493 | 495 | 5418 | Sending | 30 | 45 | 45 | 46 | 46 | 46 | 46 | 46 | 46 | 45 | 45 | 47 | 46 | 46 | 46 | 45 | 43 | 45 | 46 | 46 | 46 | 29.1709 | 30.0662 | 25.6747 | 26.0758 | 27.8765 | 29.6787 | 24.7782 | 25.4708 | 27.5717 | 28.7744 | 29.8708 | 31.475 | 23.3717 | 24.2767 | 30.9749 | 26.9799 | 29.7696 | 30.476 | 29.7709 | 23.0775 | 29.6712 | 29.6731 | 25.5245 | 30.1666 | 1091 | 1170 | 1127 | 1013 | 1013 | 1269 | 1706 | 1264 | 1092 | 1173 | 1391 | 3008 | 1656 | 1442 | 1089 | 1305 | 1387 | 1180 | 2017 | 1878 | 1298 | 1123 | 1207 | 1125 |  | 0 | 1 | [11 empty] | 67.6 | 67.7 | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 263.5 | 0 | 0 | 0 | 1059 | 0 | 0 | 0 | 5.9 | 0 | 0 | 0 | 2.05 |  |  |  | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  |  | 454 | 5204 | 1 | 5204 | 1 | 5204 | 1 | 5204 | 1 | 5204 | 1 | 5204 | 1 | 5204 | 1 | 5204 | 1 | 5204 | 1 | 5204 | 1 | 5204 | 1 | 5204 | 1 | 5204 | 1 | 5204 | 1 | 5204 | 1 | 5204 | 1 | 5204 | 1 | 5204 | 1 | 5204 | 1 | 5204 | 1 | 5204 | 1 | 5204 | 1 | 5204 | 1 | 5204 | 1 | 0.01 | 7.56 | 0.27 | 7.53 | 0.01 | 7.83 | -0.16 | 7.76 | 0.03 | 7.77 | -0.24 | 7.84 | -0.17 | 7.87 | 0.02 | 7.78 | -0.07 | 7.87 | 0.15 | 7.75 | 0.14 | 7.56 | -0.14 | 7.64 | -0.01 | 7.71 | 0.16 | 7.74 | 0.03 | 7.67 | 0.28 | 7.62 | -0.13 | 7.73 | 0.23 | 7.67 | 0.3 | 7.8 | 0.01 | 7.89 | 0.47 | 7.63 | 0.34 | 7.56 | 0.33 | 7.57 | 0.39 | 7.51 | 0.03 | -0.02 | 0.07 | -0.04 | 0.11 | -0.08 | 0.1 | -0.08 | 0.003 | 0.017 | -0.13 | 0.14 | -0.19 | 0.19 | 0.05 | -0.03 | -0.13 | 0.14 | 0.15 | -0.13 | -0.11 | 0.12 | 0.08 | -0.05 | 0.15 | -0.15 | 0.29 | -0.26 | 0.24 | -0.23 | 0.14 | -0.12 | -0.03 | 0.05 | -0.05 | 0.06 | 0.16 | -0.15 | -0.17 | 0.18 | 0.06 | -0.03 | 0.23 | -0.21 | 0.03 | 0 | 0.15 | -0.13 | 0.08 | 7.52 | 0.02 | 7.73 | 0.03 | 7.77 | -0.17 | 7.77 | -0.07 | 7.87 | -0.45 | 7.95 | -0.02 | 7.72 | -0.29 | 8.09 | -0.11 | 7.91 | -0.02 | 7.92 | -0.13 | 7.83 | 0.04 | 7.56 | -0.14 | 7.74 | 0.4 | 7.5 | 0 | 7.8 | 0.11 | 7.89 | -0.04 | 7.74 | -0.13 | 7.73 | 0.05 | 7.95 | 0.04 | 7.76 | 0.14 | 7.66 | -0.11 | 7.91 | 0.16 | 7.74 | 0.36 | 7.54 | 0.06 | -0.04 | 0.18 | -0.17 | 0.09 | -0.08 | 0.15 | -0.13 | 0.04 | -0.02 | 0.01 | 0.02 | -0.09 | 0.11 | 0.09 | -0.07 | -0.06 | 0.08 | 0.05 | -0.03 | 0.21 | -0.2 | 0.09 | -0.07 | 0.03 | -0.03 | 0.16 | -0.13 | 0.18 | -0.17 | 0.22 | -0.21 | 0.09 | -0.06 | -0.08 | 0.11 | 0.04 | -0.02 | -0.09 | 0.1 | 0.05 | -0.03 | 0.01 | 0.01 | 0.17 | -0.14 | 0.2 | -0.18 |  | 0 | 1 | 1 | 1 | 17 | 0 | 99.9 | 99.9 | 99.5 | 0 | 0 | 8.2 | 8.6 | 0 | 8.6 | 0 | 0 | 0 | 5.95 |  | 0 | 0 | 0 | 0 |  | 99.9 | 99.9 | 99.9 | 99.9 | 8.2 | 8.2 | 8.2 | 8.2 |  | 1500 | 1498 |  | 51.4 |  |  | 0 | 0 | BMW MÜNCHEN
14 |  |  |  |  | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","rem_conn":"Back-NoSSL-NoProxy","dataItems":"0/20","agent_conn":"Back-SSL-NoProxy","mon_conn":"Prim-NoSSL-NoProxy"} | 0 | 0 | 0 | 0 | 0 | 0 | -0.92 | 6.01 | 0 | 962 | 0 | -1573 | 0 | 6.99 | 0 | 4.59 | 4.4 | 18.5 | 0 |  |  |  | 0 | -1.3 | 0 | 0 | 4.81 | 0 | 4.82 | 0 | 0 | 0 | 4.4.0.13 | 5588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 |  | 19704 | 0 | 0 |  | 0 | -5986 | 0 | -2998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 |  |  |  |  | 8286 | 0 | 179258 | 333944 | 1054 | 0 | 0 | 0 | 0 | 0 | 233 | 990 | 479 | 2479 | -271 | 2479 | 66 | 479 | 7521 | 7521 | 7521 |  | 1700 |  | 51.4 | 100 | 60 | 66.6 | 100 | 70 | 66.6 | 0 | 20 | 18.5 | 0 | 0.999 | 0.999 | 50 | 120 | 120 | 81.3 | 48 | 47.9 | 23.1 | 85.9 | 85.9 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.7 | 66.6 | 63.2 | 9.5 | 47.9 | 0 | 0 | 1.6 | 3.7 | 0 | 120 | 34.6 | 13.8 | 3911 | 2.4 | 6.34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 10.2 | 84.9 | 20.4 | 30.6 | 40.8 | 51 | 55.5 | 60.3 | 75.3 | 84.9 | 0 | 0 | 10.2 | 84.9 | 1 | 0 | 20.4 | 0 | 30.6 | 0 | 40.8 | 0 | 51 | 0 | 55.5 | 1 | 60.3 | 1 | 75.3 | 1 | 84.9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 7289 | 15 | 0 | 1181 | 0 | 0 | 1181 | 9.4 | 20 | 99.6 | 0 | 0 | 0 | 0 | 0 | 11 | 6.69 | 6.78 | 10.8 | 0 | 0 | 0 | 0 | 74 | 74 | 74.9 | 139.6 | 100 | 150 | 22.7 | -2.7 | 74 | 140.1 | 0 | 0 | 0 | 140.1 | 0 | 0 | 0 | 462 | 462 | 20.3 | 10.9 | 20.2 | 10.9 | 11 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 11 | 0 | 107 | 0 | 0 | 62.7 | 51.7 | 0.77 | 2.06 | 0.94 | 337 | 335 | 339 | 35.85 | 1604884407845 | 0 | 47 | 1 | 1 | 2.1 | 27.6 | 84 | 10.24 | 0 |  | 1611 |  |  |  |  | 0 | 0 | 0 | 0 | 33008 | 33072 | 31698 | 31577 | 0 | 0 | 0 | 0 | 538 | 538 | 540 | 540 | 539 | 539 | 542 | 543 | 542 | 539 | 542 | 541 | 541 | 538 | 541 | 539 | 540 | 541 | 541 | 542 | 544 | 538 | 543 | 541 | 540 | 540 | 544 | 544 | 538 | 537 | 0 | 0 | 121 | 337 | 334 | 7 | [42 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2887957 | 0 |  |  | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53.2 | 46.7 |  |  | 56.7 | 55.7 | 53.8 | 20.7 |  |  |  |  | 6489 | 1605105735482 |  | 4503 | 0.999 | 50 | 0 | 10259 | 5937 | 10249 | 5913 | 10295 | 5933 | 10187 | 5907 | 10195 | 5873 | 10217 | 5890 | 0 | 50715 | 4610 | 11 | 0.015 | 875 | 2.05 | -43.2 | 4.05 | 0.76 |  | 0 | 85.9 | 73.8 | 0 | 66.6 | 66.6 | 66.3 | 9 | 0 | 0 | 22 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 69.8 | 55.1 | 55.3 | 68.3 | 71.7 | 78.9 | 67.2 | 68.6 | 73.8 | 60.8 | 60.7 | 54.7 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 7603.3 | 7589.4 | 7589.4 | 7589.4 | 7589.4 | 7589.1 | 7589.4 | 7589.4 | 7589.4 | 7589.4 | 7589.3 | 7589.4 | 2017 | 2017 | 7 | 12 | 2017 | 7 | 12 | 2017 | 10 | 12 | 30 | 10 | 2017 | 8 | 12 | 2014 | 12 | 9 | 2017 | 8 | 12 | 2017 | 7 | 12 | 2017 | 7 | 12 | 2017 | 9 | 12 | 2017 | 10 | 12 | 2017 | 10 | 12 | 37106 | 37882 | 37875 | 37933 | 37910 | 18127 | 37909 | 37879 | 37878 | 37930 | 37950 | 37932 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 39 | 0 | 0 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | -10 | 141 | 205 | 284 | 269 | 189 | 126 | 158 | 220 | 110 | 126 | 332 | 220 | 189 | 189 | 158 | 205 | 158 | 158 | 141 | 141 | 189 | 158 | 237 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 366 | 561 | 439 | 378 | 390 | 488 | 500 | 451 | 390 | 378 | 366 | 329 | 525 | 463 | 402 | 390 | 439 | 329 | 439 | 415 | 354 | 390 | 366 | 0 | 5.97 | 0 | 0 | 0 | 0 | 7.64 | 7.68 | 7.55 | 7.58 | 7.58 | 7.57 | 7.71 | 7.69 | 7.87 | 7.95 | 7.73 | 7.59 | 7.76 | 7.82 | 7.7 | 8.11 | 7.62 | 7.58 | 7.86 | 7.87 | 7.94 | 7.82 | 7.75 | 7.68 | 0.08 | -0.04 | 0 | 0.09 | -0.26 | 0 | 0.06 | -0.03 | 0.05 | -0.05 | -0.01 | -0.11 | -0.43 | 0.03 | -0.42 | 0.05 | -0.18 | -0.09 | -0.07 | -0.18 | -0.34 | -0.2 | -0.15 | -0.34 | 7.64 | 7.72 | 7.65 | 7.87 | 7.93 | 7.69 | 7.54 | 7.97 | 7.88 | 7.99 | 7.96 | 7.68 | 7.83 | 7.77 | 7.82 | 7.9 | 7.7 | 7.74 | 7.56 | 7.88 | 7.69 | 7.67 | 7.81 | 7.68 | 0.03 | -0.02 | 0.11 | -0.01 | -0.11 | -0.13 | -0.13 | -0.37 | -0.27 | -0.01 | -0.06 | -0.07 | -0.25 | -0.26 | -0.21 | -0.11 | 0.05 | -0.17 | 0.11 | -0.31 | -0.21 | -0.18 | 0 | -0.43 | 31936.5 | 0 | 5847.9 | 0.1 | 252 | 0.02 | 0.02 | 109 | 1.04 | 1.04 | 10203 | 4.4.0.0.0 | 4.4.0.1.1 | 4.4.0.0.0 | 4.4.0.1.0 | 4.4.0.5.0 | 4.4.4.12.5 | 4.9.0.1.0 | 4.4.0.2.12 | 4.4.0.0.0 | 4.4.0.3.12 | 4.4.0.0.0 | 4.5.1.0.0 | 4.4.0.1.0 | 4.4.0.1.0 | 4.4.0.0.4 | 4.4.0.3.6 | 4.4.0.3.0 | 4.4.0.0.2 | 4.4.0.0.0 | 4.4.0.0.2 | 4.4.0.0.12 | 4.3.0.0.0 | 0.0.0.0.0 | 4.4.0.2.11 | 4.4.1.0.0 | 4.4.0.0.13 | 4.4.0.1.0 | 4.3.0.0.0 | 4.4.0.3.3 | 4.9.0.0.0 | M01 | 25.8 | 27.1 | 23.3 | 26.4 | 23.9 | 30.7 | 28.8 | 26.9 | 26 | 26.2 | 28 | 25.1 | 26 | 22.5 | 22.3 | 23.8 | 28.6 | 25.3 | 26.6 | 24.8 | 25.6 | 26.9 | 26.5 | 21.5 | 27.6 | 30.7 | 21.5 | 1545 | [30 empty] | -1 | 2 | 1 | NaN | 0.0001 | 1608554175000 | 1 | 1 | 0.1518 | 1 | NaN | 3057 | 1 | 1608076800000 | NaN | NaN | NaN | 0.01 | 5.64 | 5 | NaN | 2 | 0.0005 | 1 | 1 | 1 | 4 |  | 0 | 934 | 11 | 0.0302 | 1 | 1608550320000 | 2 | 1 | 5 | 2.39 | 2.9 | 1014360 | 1 | 1 | 7254 | 1 | 15 | 143 | 0.05 | 0.038 |  |  |  |  | Running | 50 |  |  |  | 5325 | 4.18 | 2 | 2 |  | 50 | 50 | 50 | 50 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 1 | 0 | 970 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 1 | 1 | 1 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 30 | 30 | 0 | 2 | 12 | 15 | 80 | 2 | 0 | 11 | 1 | 0 | 0 | 0 | 0 | 7 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 35 | [5 empty] | 0 | 0 | 0 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 200 | -1000 |  | -200 | -1700 | 10 | 0 | 50 | 1500 | 5.6 | 6.7 | 6.9 | 0.1 | 3 | 0.1 | 0 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 2 |  | 0 | 0 | 0.2 | 4.2 |  | 10 | 0 |  |  |  | 0 |  | 5 | 5 | 5 | 2 | 5 | 60 | 28 | 35 | 30 | 50 | 180 | 28 | 25 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 2 | 10 | 2 | 1 | 1 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 2 | 10 | 2 | 1 | 1 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 4 | 0 | [479 empty] | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.5 | 70 | 80 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5 | 2 | 80 | 85 | 50 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 12000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 10 | 0 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 32 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 | 0.95 | 0 | 60 | -33 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | 85 | 110 | 90 | 95 | 100 | 105 | 0.85 | 0.9 | 0.95 | 1 | -0.97 | -0.95 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 1 | 40 | 0 | 30 | 30 | 10 | 10 | 10 | 3 | 1 | 10000 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 4 | 4 | 0.01 | 0.01 | 0.2 | 0.2 | 1 | 1.11 | 1 | 1.11 | 1 | 30 | 1 | 2 | 1 | 100 | 100 | 10 | 50 | 50 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 5000 | -5000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 51.5 | 47.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 1 | 115 | 85 | 35 | 10 | 0 | 0 | 1 | -0.2 | 50 | 110 | 80 | 1 | 0 | 323 | 200 | 1 | 100 | 10 | 2 | 0.8 | 3 | 4 | 10 | 0.5 | 4 | 10000 | 20 | 10 | 5 | 10000 | 0 | 0 | 0 | 0 | 10000 | 120 | 88 | 45 | 1 | 10 | 0 | 0 | 0 | -0.2 | 50 | 110 | 80 | 1 | 0 | 400 | 200 | 1 | 100 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10000 | 20 | 10 | 5 | 10000 | 0 | 0 | 0 | 0 | 10000 | 120 | 88 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 6 | 0 | 6000 | 250 | 100 | 50 | 75 | 500 | 100 | 460 | 5 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 5 | 35 | 30 | 60 | 490 | 490 | 300 | 30 | 120 | 0 |  | 1 | 0 | 0 | 1 | 1 | 0 | 0 |  | 1 |  | 0 |  |  |  | 1 | 1 |  |  |  | 1 | 1 | 0 | 1 |  | 1 | 1 | 1 |  | 1 | 1 | [8 empty] | 0 | 1 |  | 0 | 0 |  |  | 1 |  | 0 | 1 | 1 | 0 |  | 1 | 1 | 1 | 1 |  | 0 |  |  |  | 12.5 |  | 624 |  |  |  |  | 11 | 0 | 346 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.5 | 0.1 | 0.1 | 100 | 35 | 0 | 1 | 6.5 | 100 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 60 | 30 | 0 | 100 | 5 | 0 | 0 | -5 | 2 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 40 | 30 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 200 | 168 | 75 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 2 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 65 | 3 | 0 | 0 | 0 | -2.5 | 10 | 1 | 20 | 15 | 0 | 2 | 1 | 1.82 | 0.6 | 0.6 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0.1 | 0 | 0 | 0 | 15 | 30 | 0.01 | 0.4 | 0 | 60 | 30 | 0.15 | 0 | 0 | 0 | 800 | 1200 | 0 | 0.5 | 450 | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 0.02 | 0.1 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 1 | 0 | 0.72 | 0.72 | 0.72 | 0.72 | 1.2 | 0.1 | 300 | 300 | 300 | 300 | 0 | 50 | 50 | 50 | 50 | 50 | 120 | 0 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.15 | 3.6621 | 25 | 2.9297 | 100 | 0 | 5 | 0.09997 | 0.25 | 1 | 3.5 | 50 | 2 | 25 | 10 | 250 | 1 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 | 1 | 1 | 4001 | 2001 | 20000 | 10000 | 4500 | 2250 | 8 | 4 | 2 | 1 | 30 | 150 | 20 | 120 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 0 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 | 1.5 | 1 | 650 | 700 | 1 | 0 | 0 | 1 | [66 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 1 | 1 | 1200 | 35900 |  |  |  | 40550 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 100 | 1000 | 680 | 640 | 5 | 650 | 5 | 650 | 640 | 5 | 650 | 5 | 1000 | 5 | 15 | 300 | 20 | 50 | 650 | 5 | 120 | 5 | 1000 | 175 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | 0.1 | -0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 20 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 10 | 20 | 5 | 10 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | 0 | 20 |  | 0.98 | 1 | -0.98 | -0.95 | 0.8 | 0.92 | 1 | 7 | 0.95 | -0.95 | 20 | 80 | 5590 | 88 | 90 | 2.01 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 0 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 85 | 90 | 85 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 43.1 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 35 | 300 |  | 75 | 0.97 | 1 | 1 | 1 | 180 | 0.1 | 1.11 | 60 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 930 | 1 | 5000 | 40 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 4500 | 4500 | 1 | 2 | 0 | 1 | 1 | 2 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 4 | 20 | 0.8 | -0.95 | 1 | 0 | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 400 | 0 | 0 | 0 | 0 | 1 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -100 | 100 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 1 | 1 | 0.8 | -0.92 | 3600 | -3600 | 10 | 0 | 100 | 0 | 100 | 0 | 800 | -20 | 800 | -20 | 600 | 0 | 10 | 3.3 | 0.2 | 3.5 | 0.05 | 1 | 1.8 | 0.05 | 0.05 | 87 | 5 | 94 | 2 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 30 |  |  | 20 |  |  |  | 3 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.4 | 0.1 | 0.5 | 500 | 1500 | 3.5 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1.5 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 75 | 2 | 79 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 1 | 0 | 90 | 120 | 2 | 2 | 0 | 1 | 0 | 85 | 120 | 2 | 1 | 1 | 62 | 2 | 1 |  | 85 | 120 | 0.5 | 0.5 | 0 | 1 | 0 | 142 | 142 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 82 | 0 | 0 | 0 | 5 | 20 | 0 | 2 | 30 | 90 | 0 | 0 | 0 | 200 | -200 | 0 | -70 | 100 | -100 | 0 | 0 | 0 | 200 | -200 | 20 | 30 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 9.5 | 10 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 10 | 0 | 0 | 1 | 90 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 18 | 18 | 18 | 18 | [5 empty] | 4 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 924 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 1 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 0 | 0 | 20 | 4000 | 4000 |  | 850 | 30 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 2 | 2 | 2 | 2 | -5 | -5 | -5 | -5 | 13 | 13 | 13 | 13 | 4.5 |  | 45 | 270 | 70 | -144 | 0 | 80 | 350 | [24 empty] | 0 | 4 | 500 | 30 |  | 2000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 380 | 1 | -30 | -9 | 4500 | 2250 | 10 | 4500 | 2250 | 60 | 0 | 0 | [6 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4517 | 2274 | 5840 | 3018 | 1499 | 1499 |  | 49.9 | 50.1 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4919 | 2157 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4919 | 2157 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4919 | 2157 | 1500 | 1500 |  | 50 | 50 |  | 660 |  | 0 | 1000 | 300 | 48 | -1.6 | -4 | 100 | 10 | 0 | 1 | 10 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 |  | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 10 | 0 | 0.5 | 0 | 0 | 60000 | 0 | 60000 | 0 |  | 5 | 0 | 1 | 1 |  |  |  | 80 |  | 48 | [14 empty] | 50 | 53 | 53 | 53 | [10 empty] | 0 | 0 | 1 | 3 | 55 | 57 | 2 | 2 | 62 |  | 46 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 350 | 100 | 100 | 100 | [8 empty] | -1250 | 5000 |  | 0.2 | 100 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 350 |  | 100 | 100 | [11 empty] | 0.2 | 100 | 200 | [43 empty] | 0 | 0.1 | 100 | 100 | 100 | 40 | 0 | 1 | 2.5 | 1 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 60 | 69 | 0 | 100 | 0 | 0 | 0.1 | 1 | 0.01 | 100 | 40 | 0 | 1 | 4.6 | 0 | 99 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 60 | 70 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 20 | 0 | 100 | 0 | 0.15 | 0.003 | 1 | 1 | 10 | 0.5 | 0 | 1 | 0.45 | 1 | 1 | 1 | 1 | 0 | 0 | 1.1 | 0.7 | 1 | 0 | 100 | 0 | 0 | 0.1 | 100 | 0.01 | 100 | 40 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 130 | 120 | 120 | 0 | 100 | 30 | 0 | 0.1 | 0.5 | 0.5 | 100 | 40 | 0 | 1 | 4 | 1 | 1 | 1 | 1 | 0 | 0 | 60 | 45 | 48 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0 | 0.1 | 100 | 205 | 0 | 1 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 28 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | [42 empty] | 0 | 0.1 | 100 | 50 | 0 | 1 | 2.5 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 60 | 100 | 100 | 60 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 0 | 0 | 10 | 150 | 150 | 100 | 205 | 0 | 48 | 50 | 0 | 3000 | 6000 | 3000 | 6000 | 6 | 6 | 0 | 5000 | -5000 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 100 | 50 | 0 | 0.1 | 100 | 50 | 0 | 1 | 2.5 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 60 | 60 | 100 | 100 | 60 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 |  |  |  |  | 12 | 2 | 5 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 80 | 0 | [6 empty] | 0.01421 | 0.29619 | 0.88857 | 100 | 0 | 0 | 0.44428 | 0.23695 | 100 | 2 | 0 | 20 | 5000 | 5000 | 60 | 75 | 90 | 100 |  | 4 | 20 | 2250 | 4500 | 2.5 | 2 | 37 | 45 |  | -2 | -2 | -2 | -2 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -145 | 10 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 4500 | 4500 | 4500 | 4500 | 70 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 |  | 10 | 4 | 92 | 1 | 1 | 100.4 | 103.4 | 98 | 91 | 103.4 | 40 | 65 | 85 | 80 |  | 110 | 125 | 90 | 70 | 140 | 1 | 80 | 4 | 80 | 1 | 20 | 5.55 | 1 | 4 | 90 |  |  | 10 | 4 | 4 | 4 | 4 | 56 | 56 | 56 | 56 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 130 | 400 | 400 | 5000 | 2500 | 16 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [30 empty] | 1 | 10 | 10 | 33 | 1 | 20 | 20 | 20 | 10 | 10 | 0 | 0 | 0 | 0 | 100 | 200 | 50 | 100 | 90 | 0 | 80 | 90 | 91 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1650 | 10 | 200 | 400 | 2800 | 5 | 10000 | 0 | 3850 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 1 | 1200 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 800 |  | 0.16406 | 2.1973 | 4.3945 | 95 | 2 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1500 | 6.7 | 0 | 95 | 85 | 85 | 95 | 95 | 9.54 | 9.971 | 720 |  |  | 1.4 | 1.45 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.2 |  |  | 0.59 | [13 empty] | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | [28 empty] | 1 | 1 | 0 | 2 | 0 | 2 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4501 |  |  | 4500 | 0 | 0 | 0 | 0 | 0 | 4500 | 4496 |  |  | 2.99 | 2.99 | 0 | 0 | 0 | 0 | 0 | 0 | 1036.3 | 18.1 | -43.41 | 4.054 | 0.04 | 0.75164 | 0 | 0.72 | 4495 | 0 | 0 | 2.17 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 65.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 366 | 365 | 366 | 366 | 366 | 364 | 365 | 366 | 366 | 367 | 367 | 366 | 365 | 366 | 365 | 365 | 366 | 367 | 369 | 367 | 367 | 366 | 366 | 495 | 496 | 494 | 496 | 493 | 494 | 492 | 495 | 494 | 494 | 494 | 493 | 496 | 494 | 494 | 496 | 495 | 495 | 493 | 494 | 494 | 493 | 495 | 494 | 2951 | Sending | 30 | 47 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 44 | 45 | 42 | 44 | 45 | 46 | 46 | 45 | 45 | 44 | 45 | 45 | 28.6459 | 27.3329 | 29.6313 | 28.3352 | 26.5565 | 30.3673 | 29.8498 | 28.4603 | 28.8483 | 25.4401 | 25.4441 | 28.1464 | 26.7354 | 27.639 | 30.2376 | 25.656 | 25.0299 | 29.253 | 27.6338 | 28.2438 | 27.4486 | 28.9602 | 30.3629 | 24.7539 | 634 | 1098 | 756 | 1049 | 359 | 469 | 719 | 798 | 797 | 1098 | 887 | 846 | 1226 | 1045 | 1052 | 469 | 863 | 761 | 928 | 848 | 756 | 723 | 2793 | 668 |  | 0 | 1 | [11 empty] | 68 | 67.8 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 277.2 | 0 | 0 | 0 | 1004 | 0 | 0 | 0 | 4.9 | 0 | 0 | 0 | 2.046 |  |  |  | 36.7 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  |  | 394 |  | 1 |  | 1 | 5129 | 1 | 5129 | 1 | 5129 | 1 | 5129 | 1 | 5129 | 1 | 5129 | 1 | 5129 | 1 | 5129 | 1 | 5129 | 1 | 5129 | 1 | 5129 | 1 | 5129 | 1 | 5129 | 1 | 5129 | 1 | 5129 | 1 | 5129 | 1 | 5129 | 1 | 5129 | 1 | 5129 | 1 | 5129 | 1 | 5129 | 1 | 5129 | 1 | 0 | 7.64 | 0 | 7.68 | 0.25 | 7.55 | -0.25 | 7.85 | 0.22 | 7.58 | 0.03 | 7.57 | -0.01 | 7.71 | 0.11 | 7.69 | -0.07 | 7.87 | -0.05 | 7.95 | -0.03 | 7.73 | -0.09 | 7.59 | -0.06 | 7.76 | 0.08 | 7.82 | 0 | 7.7 | -0.21 | 8.11 | -0.02 | 7.62 | 0.32 | 7.58 | 0.24 | 7.86 | 0.03 | 7.87 | 0.16 | 7.94 | 0.08 | 7.82 | 0.15 | 7.75 | 0.22 | 7.68 | 0 | 0.08 | 0 | -0.04 | 0.03 | 0 | -0.07 | 0.09 | 0.28 | -0.26 | 0.01 | 0 | -0.06 | 0.06 | 0.05 | -0.03 | -0.04 | 0.05 | 0.07 | -0.05 | 0.02 | -0.01 | 0.14 | -0.11 | 0.43 | -0.43 | 0 | 0.03 | 0.43 | -0.42 | -0.03 | 0.05 | 0.2 | -0.18 | 0.1 | -0.09 | 0.08 | -0.07 | 0.19 | -0.18 | 0.37 | -0.34 | 0.22 | -0.2 | 0.18 | -0.15 | 0.36 | -0.34 | 0 | 7.64 | 0 | 7.72 | 0.15 | 7.65 | -0.27 | 7.87 | -0.13 | 7.93 | -0.19 | 7.69 | 0.16 | 7.54 | -0.17 | 7.97 | -0.08 | 7.88 | -0.09 | 7.99 | -0.26 | 7.96 | -0.08 | 7.68 | -0.23 | 7.83 | 0.13 | 7.77 | -0.02 | 7.82 | 0.1 | 7.9 | 0 | 7.7 | -0.14 | 7.74 | 0.44 | 7.56 | -0.08 | 7.88 | 0.11 | 7.69 | 0.13 | 7.67 | 0.09 | 7.81 | 0.22 | 7.68 | 0 | 0.03 | 0 | -0.02 | -0.1 | 0.11 | 0.03 | -0.01 | 0.13 | -0.11 | 0.16 | -0.13 | 0.15 | -0.13 | 0.39 | -0.37 | 0.29 | -0.27 | 0.03 | -0.01 | 0.07 | -0.06 | 0.09 | -0.07 | 0.25 | -0.25 | 0.29 | -0.26 | 0.22 | -0.21 | 0.12 | -0.11 | -0.04 | 0.05 | 0.2 | -0.17 | -0.09 | 0.11 | 0.32 | -0.31 | 0.23 | -0.21 | 0.2 | -0.18 | 0.03 | 0 | 0.45 | -0.43 |  | 0 | 1 | 1 | 1 | 17 | 0 | 100 | 100 | 99.4 | 0 | 0 | 9 | 8 | 0 | 8.3 | 0 | 0 | 0 | 5.97 |  | 0 | 0 | 0 | 0 |  | 100 | 100 | 100 | 100 | 9 | 9 | 9 | 9 |  | 1500 | 1499 |  | 51.4 |  |  | 0 | 0 | BMW MÜNCHEN
15 |  |  |  |  | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","agent_conn":"Prim-SSL-NoProxy","mon_conn":"Prim-NoSSL-NoProxy","rem_conn":"Prim-NoSSL-NoProxy"} | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 5.29 | 0 | 0 | 0.96 | 19.3 | 0 |  |  |  | 0 | 1.1 | 0 | 0 | 0.07 | 0 | 0.07 | 0 | 0 | 0 | 4.4.0.13 | 5076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 |  | 0 | 0 | 0 |  | 0 | -962 | 0 | -956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 |  |  |  |  | 8348 | 0 | 291871 | 335284 | 1040 | 0 | 0 | 0 | 0 | 0 | 358 | 1744 | 360 | 2359 | 360 | 360 | 437 | 360 | 7641 | 7642 | 7642 |  | 1415 |  | 42.7 | 0 | 60 | 15.6 | 0 | 60 | 23.1 | 0 | 20 | 19.3 | 0 | 1 | 1 | 50.4 | 100 | 33.8 | 0 | 40 | 0 | 0 | 75 | 47.5 | 0 | 0 | 0 | 0 | 55 | 0.1 | 0 | 55 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 27.2 | 15.4 | 8 | 0 | 0.1 | 0.2 | 2.3 | 3 | 0 | 118 | 1.9 | 1.5 | 4.5 | 1.5 | 5.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | -0.7 | -9.7 | -1.4 | -2.2 | -2.9 | -3.7 | 0 | 11.5 | 3.1 | -9.7 | 0 | 0 | -0.7 | -9.7 | 1 | 0 | -1.4 | 0 | -2.2 | 0 | -2.9 | 0 | -3.7 | 1 | 0 | 1 | 11.5 | 1 | 3.1 | 1 | -9.7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 7605 | 15 | 0 | 1617 | 0 | 0 | 1618 | 1.3 | 20.3 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224 | 100 | 150 | 0 | -2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 0 | 0 | 0.1 | 0.1 | 0 | 2.52 | 1.03 | 32 | 33 | 31 | 37.27 | 1608672445784 | 0 | 47 | 1 | 0 | 2.1 | 18.5 | 0 | 21.25 | 0 |  | 1132 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 45 | 44 | 45 | 45 | 45 | 44 | 45 | 45 | 44 | 45 | 45 | 45 | 45 | 44 | 43 | 45 | 44 | 45 | 45 | 45 | 44 | 45 | 45 | 44 | 544 | 46 | 548 | 43 | 541 | 0 | 0 | 24 | 25 | 24 | 7 | [42 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6898667 | 0 |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6 | 15.6 |  |  | 15.3 | 15.7 | 16.2 | 0 |  |  |  |  | 7 | 1606645062549 |  | 0 | 0 | 0 | 0 | 10266 | 5942 | 10260 | 5918 | 10298 | 5937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118289 | 4549 | 26 | 0.094 | 12565 | 2.22 | 0.6 | 0 | 0.07 |  | 0 | 47.5 | 16.5 | 0 | 15.6 | 23.1 | 20.8 | 0 | 0 | 0 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 59 | 54.5 | 56.3 | 54.2 | 55.3 | 52.8 | 57.2 | 59 | 56.7 | 56.8 | 45.3 | 55.3 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 7694.9 | 7694.9 | 7694.9 | 7694.8 | 7694.9 | 7695 | 7695 | 7695 | 7694.9 | 7694.9 | 7695 | 7695 | 2017 | 2017 | 12 | 12 | 2017 | 10 | 12 | 2017 | 8 | 12 | 11 | 12 | 2017 | 11 | 12 | 2017 | 11 | 12 | 2017 | 11 | 12 | 2017 | 11 | 12 | 2017 | 11 | 12 | 2017 | 11 | 12 | 2017 | 11 | 12 | 2017 | 7 | 12 | 37994 | 38039 | 37947 | 37894 | 38008 | 37992 | 37962 | 37979 | 37964 | 37980 | 37993 | 37883 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.561 | 0.39 | 0 | 0 | 0 | 0 | 7.73 | 7.58 | 7.72 | 7.57 | 7.63 | 7.54 | 7.59 | 7.63 | 7.86 | 7.77 | 7.77 | 7.74 | 7.64 | 7.75 | 7.83 | 7.61 | 7.87 | 7.71 | 7.73 | 7.86 | 7.78 | 7.84 | 7.77 | 7.61 | 0.2 | 0.11 | 0 | 0.1 | 0 | -0.07 | 0.26 | 0.11 | 0.14 | 0.14 | 0 | 0.12 | -0.04 | -0.14 | -0.1 | -0.08 | -0.16 | -0.12 | -0.28 | -0.25 | -0.2 | -0.01 | -0.09 | -0.32 | 7.73 | 7.95 | 7.81 | 7.81 | 7.95 | 7.76 | 7.82 | 7.66 | 7.79 | 7.88 | 7.95 | 7.55 | 7.7 | 7.92 | 7.76 | 7.71 | 7.92 | 7.95 | 7.63 | 7.92 | 7.89 | 8.01 | 7.86 | 7.82 | -0.4 | 0 | -0.47 | -0.15 | -0.21 | -0.08 | -0.16 | 0.07 | -0.09 | 0.11 | -0.48 | 0.04 | -0.15 | -0.07 | -0.09 | -0.17 | 0.02 | -0.19 | -0.05 | 0.04 | -0.31 | 0.06 | 0.11 | -0.33 | 31968.5 | 0 | 3186.2 | 0 | 0 | 0.02 | 0.02 | 0 | 1.04 | 1.04 | 0 | ....0 | ....1 | ....0 | ....0 | ....0 | ....5 | ....0 | ....12 | ....0 | ....12 | ....0 | ....0 | ....0 | ....0 | ....4 | ....6 | ....0 | ....2 | ....0 | ....2 | ....12 | ....0 | ....0 | ....11 | ....0 | ....13 | ....0 | ....0 | ....3 | ....0 | M03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1465 | [30 empty] | -1 | 2 | 1 | NaN | 0.0001 | 1608293160000 | 1 | 1 | 0.1562 | 1 | NaN | 3649 | 1 | 1607990400000 | NaN | NaN | NaN | 0.01 | 4.99 | 14 | NaN | 3 | 0.0006 | 1 | 1 | 1 | 7 |  | 1 | 4599 | 13 | 0.0309 | 1 | 1608292800000 | 2 | 1 | 4 | 3.2 | 2.4 | 1015690 | 1 | 1 | 7499 | 1 | 15.1 | 145 | 0.05 | 0.0372 |  |  |  |  | Not Available | 60 |  |  |  |  | 5.3 | 2 | 2 |  | 0 | 0 | 50 | 50.01 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 1 | 0 | 970 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 1 | 1 | 1 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 30 | 30 | 0 | 2 | 12 | 15 | 80 | 2 | 0 | 11 | 1 | 0 | 0 | 0 | 0 | 7 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 35 | 25 | 35 | [5 empty] | 0 | 0 | 0 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 200 | -1000 |  | -200 | -1700 | 10 | 0 | 50 | 1500 | 5.6 | 6.7 | 6.9 | 0.1 | 3 | 0.1 | 0 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 2 |  | 0 | 0 | 0.2 | 4.2 |  | 10 | 0 |  |  |  | 0 |  | 5 | 5 | 5 | 2 | 5 | 60 | 28 | 20 | 30 | 50 | 180 | 28 | 20 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 2 | 10 | 2 | 1 | 1 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 2 | 10 | 2 | 1 | 1 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 4 | 0 | [479 empty] | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5 | 2 | 82 | 87 | 50 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 12000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 10 | 0 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 32 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 | 0.95 | 0 | 60 | -33 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | 85 | 110 | 90 | 95 | 100 | 105 | 0.85 | 0.9 | 0.95 | 1 | -0.97 | -0.95 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 1 | 40 | 0 | 30 | 30 | 10 | 10 | 10 | 3 | 1 | 10000 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 4 | 4 | 0.01 | 0.01 | 0.2 | 0.2 | 1 | 1.11 | 1 | 1.11 | 1 | 30 | 1 | 2 | 1 | 100 | 100 | 10 | 50 | 50 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 5000 | -5000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 51.5 | 47.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 1 | 115 | 85 | 35 | 10 | 0 | 0 | 1 | -0.2 | 50 | 110 | 80 | 1 | 0 | 323 | 200 | 1 | 100 | 10 | 2 | 0.8 | 3 | 4 | 10 | 0.5 | 4 | 10000 | 20 | 10 | 5 | 10000 | 0 | 0 | 0 | 0 | 10000 | 120 | 88 | 45 | 1 | 10 | 0 | 0 | 0 | -0.2 | 50 | 110 | 80 | 1 | 0 | 400 | 200 | 1 | 100 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10000 | 20 | 10 | 5 | 10000 | 0 | 0 | 0 | 0 | 10000 | 120 | 88 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 6 | 0 | 6000 | 250 | 100 | 50 | 75 | 500 | 100 | 460 | 5 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 5 | 35 | 30 | 60 | 490 | 490 | 300 | 30 | 180 | 0 |  | 1 | 0 | 0 | 1 | 1 | 0 | 0 |  | 1 |  | 0 |  |  |  | 1 | 1 |  |  |  | 1 | 1 | 0 | 1 |  | 1 | 1 | 1 |  | 1 | 1 | [8 empty] | 0 | 1 |  | 0 | 0 |  |  | 1 |  | 0 | 1 | 1 | 0 |  | 1 | 1 | 1 | 1 |  | 0 |  |  |  | 12.5 |  | 624 |  |  |  |  | 13 | 0 | 346 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.5 | 0.1 | 0.1 | 100 | 35 | 0 | 1 | 6.5 | 100 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 55 | 30 | 0 | 100 | 5 | 0 | 0 | -5 | 2 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 35 | 30 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 200 | 168 | 75 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 2 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 65 | 3 | 0 | 0 | 0 | -2.5 | 10 | 1 | 20 | 15 | 0 | 2 | 1 | 1.82 | 0.6 | 0.6 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0 | 0 | 0 | 0 | 15 | 30 | 0.01 | 0.4 | 0 | 60 | 30 | 0.15 | 0 | 0 | 0 | 800 | 1200 | 0 | 0.5 | 450 | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 0.2 | 0.05 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 1 | 0 | 0.72 | 0.72 | 0.72 | 0.72 | 1.2 | 0.1 | 300 | 300 | 300 | 300 | 0 | 50 | 50 | 50 | 50 | 50 | 120 | 0 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.15 | 3.6621 | 25 | 2.9297 | 100 | 0 | 6 | 0.1 | 0.5 | 1 | 7 | 50 | 2 | 25 | 10 | 250 | 1 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 | 1 | 1 | 4000 | 2000 | 20000 | 10000 | 4500 | 2250 | 8 | 4 | 2 | 1 | 30 | 150 | 20 | 120 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 0 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 | 1.5 | 1 | 650 | 700 | 1 | 0 | 0 | 1 | [66 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 1 | 1 | 1200 | 35900 |  |  |  | 40550 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 100 | 1000 | 680 | 640 | 5 | 650 | 5 | 650 | 640 | 5 | 650 | 5 | 1000 | 5 | 15 | 300 | 20 | 50 | 650 | 5 | 120 | 5 | 1000 | 100 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | 0.1 | -0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 20 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 10 | 20 | 5 | 10 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | 0 | 20 |  | 0.98 | 1 | -0.98 | -0.95 | 0.8 | 0.92 | 1 | 7 | 0.95 | -0.95 | 20 | 80 | 5590 | 88 | 90 | 2.01 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 0 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 85 | 90 | 85 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 42.2 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 35 | 300 |  | 75 | 0.97 | 1 | 1 | 1 | 180 | 0.1 | 1.11 | 60 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 930 | 1 | 5000 | 40 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 0 | 20 | 4500 | 4500 | 1 | 2 | 0 | 1 | 1 | 2 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 4 | 20 | 0.8 | -0.95 | 1 | 0 | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 400 | 0 | 0 | 0 | 0 | 1 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -100 | 100 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 1 | 1 | 0.8 | -0.92 | 3600 | -3600 | 10 | 0 | 100 | 0 | 100 | 0 | 800 | -20 | 800 | -20 | 600 | 0 | 10 | 3.3 | 0.2 | 3.5 | 0.05 | 1.5 | 1.9 | 0.05 | 0.05 | 87 | 5 | 94 | 2 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 30 |  |  | 20 |  |  |  | 3 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.4 | 0.1 | 0.5 | 500 | 1500 | 3.5 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1.5 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 75 | 2 | 79 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 1 | 0 | 90 | 120 | 2 | 2 | 0 | 1 | 0 | 75 | 120 | 2 | 2 | 1 | 62 | 2 | 1 |  | 72 | 120 | 0.5 | 0.5 | 0 | 1 | 0 | 142 | 142 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 82 | 0 | 0 | 0 | 5 | 20 | 0 | 2 | 30 | 90 | 0 | 0 | 0 | 200 | -200 | 0 | -70 | 100 | -100 | 0 | 0 | 0 | 200 | -200 | 20 | 30 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 9.5 | 10 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 10 | 0 | 0 | 1 | 90 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 18 | 18 | 18 | 18 | [5 empty] | 4 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 924 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 1 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 0 | 0 | 20 | 4000 | 4000 |  | 850 | 30 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 2 | 2 | 2 | 2 | -5 | -5 | -5 | -5 | 13 | 13 | 13 | 13 | 4.5 |  | 45 | 270 | 70 | -144 | 0 | 80 | 350 | [24 empty] | 0 | 4 | 500 | 30 |  | 2000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 380 | 1 | -30 | -9 | 4500 | 2250 | 10 | 4500 | 2250 | 60 | 0 | 0 | [6 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4501 | 2251 | 5825 | 2990 | 1499 | 1499 |  | 47.7 | 48.4 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4915 | 2155 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4915 | 2155 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4915 | 2155 | 1500 | 1500 |  | 50 | 50 |  | 660 |  | 0 | 1000 | 300 | 48 | -1.6 | -4 | 100 | 10 | 0 | 1 | 10 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 |  | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 10 | 0 | 0.5 | 0 | 0 | 60000 | 0 | 60000 | 0 |  | 5 | 0 | 1 | 1 |  |  |  | 80 |  | 48 | [14 empty] | 48 | 53 | 53 | 53 | [10 empty] | 0 | 0 | 1 | 3 | 55 | 57 | 2 | 2 | 62 |  | 46 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 350 | 100 | 100 | 100 | [8 empty] | -1250 | 5000 |  | 0.2 | 100 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 100 |  | 100 | 100 | [11 empty] | 0.2 | 100 | 200 | [43 empty] | 0 | 0.1 | 100 | 0.02 | 100 | 40 | 0 | 1 | 2.5 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 60 | 69 | 0 | 100 | 0 | 0 | 0.1 | 1 | 0.01 | 100 | 40 | 0 | 1 | 4.6 | 0 | 99 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 73 | 60 | 70 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0.15 | 0.001 | 1 | 1 | 10 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1.1 | 0.8 | 1 | 0 | 100 | 0 | 0 | 0.1 | 0.03 | 0.02 | 100 | 40 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 130 | 100 | 120 | 0 | 100 | 30 | 0 | 0.1 | 0.5 | 0.5 | 100 | 35 | 0 | 1 | 4 | 1 | 1 | 1 | 1 | 0 | 0 | 60 | 40 | 40 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0 | 0.1 | 100 | 205 | 0 | 1 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 28 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | [42 empty] | 0 | 0.1 | 100 | 50 | 0 | 1 | 2.5 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 55 | 100 | 0.02 | 65 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 0 | 0 | 10 | 150 | 150 | 100 | 205 | 0 | 48 | 50 | 0 | 3000 | 6000 | 3000 | 6000 | 6 | 6 | 0 | 5000 | -5000 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 100 | 50 | 0 | 0.1 | 100 | 50 | 0 | 1 | 2.5 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 55 | 100 | 0.02 | 65 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 |  |  |  |  | 12 | 2 | 5 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 80 | 0 | [6 empty] | 0.01421 | 0.29619 | 0.88857 | 100 | 0 | 0 | 0.44428 | 0.23695 | 100 | 2 | 0 | 20 | 5000 | 5000 | 60 | 75 | 90 | 100 |  | 4 | 20 | 2250 | 4500 | 2.5 | 2 | 35 | 45 |  | -2 | -2 | -2 | -2 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -145 | 10 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 4500 | 4500 | 4500 | 4500 | 50 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 |  | 10 | 4 | 92 | 1 | 1 | 100.4 | 103.4 | 98 | 91 | 103.4 | 40 | 65 | 85 | 80 |  | 110 | 125 | 90 | 70 | 140 | 1 | 80 | 4 | 80 | 1 | 20 | 5.55 | 1 | 4 | 90 |  |  | 10 | 4 | 4 | 4 | 4 | 56 | 56 | 56 | 56 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 130 | 400 | 400 | 5000 | 2500 | 16 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [30 empty] | 1 | 10 | 10 | 33 | 1 | 20 | 20 | 20 | 10 | 10 | 0 | 0 | 0 | 0 | 100 | 200 | 50 | 100 | 90 | 1 | 82 | 85 | 87 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1650 | 10 | 200 | 400 | 2800 | 5 | 10000 | 0 | 3850 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 1 | 1200 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 800 |  | 0.16406 | 2.1973 | 4.3945 | 95 | 2 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1500 | 6.7 | 0 | 95 | 85 | 85 | 95 | 95 | 9.54 | 9.971 | 720 |  |  | 1.3 | 1.35 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.2 |  |  | 0.59 | [13 empty] | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | [28 empty] | 1 | 1 | 0 | 2 | 0 | 2 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 4500 | 0 | 0 | 0 | 0 | 0 | 4274 | 0 |  |  | 0.95 | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -39.15 | 3.996 | 0.0805 | 0.80082 | 0 | 0.72 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 73.93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 360 | 364 | 365 | 368 | 367 | 366 | 367 | 362 | 365 | 367 | 367 | 359 | 367 | 365 | 363 | 362 | 363 | 363 | 366 | 366 | 365 | 363 | 364 | 494 | 495 | 495 | 496 | 494 | 496 | 496 | 496 | 495 | 497 | 494 | 494 | 495 | 496 | 496 | 493 | 495 | 495 | 494 | 495 | 495 | 497 | 493 | 495 | 3332 | Sending | 30 | 45 | 45 | 46 | 45 | 46 | 46 | 47 | 47 | 45 | 46 | 46 | 46 | 45 | 45 | 45 | 44 | 45 | 46 | 44 | 46 | 24.145 | 26.3447 | 28.7933 | 25.2472 | 23.9364 | 24.4532 | 24.4438 | 21.8537 | 24.6468 | 24.1443 | 26.1436 | 24.2429 | 23.2363 | 21.9818 | 24.8413 | 24.5289 | 23.7283 | 22.9621 | 22.902 | 22.9428 | 25.2531 | 25.9696 | 25.6664 | 23.7475 | 593 | 973 | 1896 | 761 | 382 | 886 | 884 | 1104 | 720 | 599 | 578 | 31 | 919 | 1138 | 667 | 973 | 799 | 2147 | 1055 | 802 | 508 | 343 | 382 | 1047 |  | 0 | 1 | [11 empty] | 21.5 | 21.4 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 948 | 0 | 0 | 0 | 19.8 | 0 | 0 | 0 | 1.2 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  |  | 371 | 4650 | 1 | 4650 | 1 | 4650 | 1 | 4650 | 1 | 4650 | 1 | 4650 | 1 | 4650 | 1 | 4650 | 1 | 4650 | 1 | 4650 | 1 | 4650 | 1 | 4650 | 1 | 4650 | 1 | 4650 | 1 | 4650 | 1 | 4650 | 1 | 4650 | 1 | 4650 | 1 | 4650 | 1 | 4650 | 1 | 4650 | 1 | 4650 | 1 | 4650 | 1 | 4650 | 1 | -0.03 | 7.73 | 0.22 | 7.58 | 0.08 | 7.72 | 0.23 | 7.57 | 0.17 | 7.63 | 0.16 | 7.54 | 0.21 | 7.59 | -0.03 | 7.63 | -0.06 | 7.86 | -0.07 | 7.77 | -0.07 | 7.77 | 0.06 | 7.74 | 0.06 | 7.64 | 0.05 | 7.75 | -0.23 | 7.83 | 0.09 | 7.61 | -0.07 | 7.87 | -0.01 | 7.71 | -0.13 | 7.73 | 0.24 | 7.86 | -0.13 | 7.78 | 0.06 | 7.84 | -0.07 | 7.77 | 0.09 | 7.61 | -0.2 | 0.2 | -0.11 | 0.11 | 0 | 0 | -0.1 | 0.1 | 0 | 0 | 0.07 | -0.07 | -0.26 | 0.26 | -0.11 | 0.11 | -0.14 | 0.14 | -0.14 | 0.14 | 0 | 0 | -0.02 | 0.12 | 0.04 | -0.04 | 0.14 | -0.14 | 0.1 | -0.1 | 0.08 | -0.08 | 0.16 | -0.16 | 0.12 | -0.12 | 0.28 | -0.28 | 0.25 | -0.25 | 0.2 | -0.2 | 0.01 | -0.01 | 0.09 | -0.09 | 0.32 | -0.32 | -0.13 | 7.73 | -0.15 | 7.95 | -0.11 | 7.81 | 0.09 | 7.81 | -0.05 | 7.95 | 0.14 | 7.76 | -0.12 | 7.82 | 0.04 | 7.66 | 0.11 | 7.79 | -0.08 | 7.88 | -0.05 | 7.95 | 0.35 | 7.55 | 0.1 | 7.7 | -0.02 | 7.92 | 0.04 | 7.76 | 0.09 | 7.71 | -0.02 | 7.92 | -0.15 | 7.95 | 0.27 | 7.63 | 0.28 | 7.92 | 0.06 | 7.89 | -0.21 | 8.01 | -0.06 | 7.86 | -0.02 | 7.82 | 0.4 | -0.4 | 0 | 0 | 0.47 | -0.47 | 0.15 | -0.15 | 0.21 | -0.21 | 0.08 | -0.08 | 0.16 | -0.16 | -0.07 | 0.07 | 0.09 | -0.09 | -0.11 | 0.11 | 0.48 | -0.48 | -0.04 | 0.04 | 0.15 | -0.15 | 0.07 | -0.07 | 0.09 | -0.09 | 0.17 | -0.17 | -0.02 | 0.02 | 0.19 | -0.19 | 0.05 | -0.05 | -0.04 | 0.04 | 0.31 | -0.31 | -0.06 | 0.06 | -0.11 | 0.11 | 0.33 | -0.33 |  | 0 | 1 | 0 | 0 | 19 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0.8 | 0 | 0 | 0 | 0.96 |  | 0 | 0 | 0 | 0 |  | 1.9 | 1.9 | 1.9 | 1.9 | 0 | 0 | 0 | 0 |  | 1500 | 0 |  | 42.7 |  |  | 0 | 0 | BMW MÜNCHEN
16 |  | 40 | 1 | 0 | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","agent_conn":"Back-SSL-NoProxy","mon_conn":"Prim-SSL-NoProxy","rem_conn":"Prim-NoSSL-NoProxy"} | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.97 | 0 | 0 | 0.98 | 26.5 | 0 |  |  |  | 0 | 6.6 | 0 | 0 | 0.22 | 0.14 | 0.22 | 0 | 0 | 0 | 4.4.0.5 | 6652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 |  | 0 | 0 | 0 |  | 0 | -973 | 0 | -974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.02 |  |  |  |  | 43800784 | 0 | 13056871 | 587074 | 2270 | 0 | 0 | 0 | 0 | 0 | 19 | 592 | 592 | 8592 | 487 | 8594 | 1326 | 2594 | 11542 | 11542 | 11542 |  | 1130 |  | 54.8 | 0 | 55 | 17.2 | 8 | 60 | 18.9 | 0 | 26.5 | 26.5 | 0 | 1 | 1 | 50 | 95 | 36.1 | 0 | 30 | 1.8 | 0 | 75 | 59.7 | 0 | 80 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.8 | 26.6 | 15.4 | 7.4 | 1.8 | 0 | 0 | 2.3 | 2.2 | 9.8 | 0 | 0.5 | 0.4 | 0 | 2 | 8.7 | 7.8 | 8 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 8.4 | 41.4 | 16.8 | 25.3 | 33.7 | 42.2 | 48.7 | 49.8 | 50.7 | 41.4 | 0 | 0 | 8.4 | 41.4 | 1 | 0 | 16.8 | 0 | 25.3 | 0 | 33.7 | 0 | 42.2 | 1 | 48.7 | 1 | 49.8 | 1 | 50.7 | 1 | 41.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 11482 | 20 | 0 | 5209 | 0 | 0 | 5208 | -2.9 | 20.2 | 129.8 | 0 | 0 | 0 | 0 | 0 | 4.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.8 | 100 | 150 | 0 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133.8 | 0 | 0 | 4.5 | 0.4 | 0.01 | 2.7 | 0.86 | 20 | 22 | 19 | 33.56 | 1600820314907 | 0 | 46 | 1 | 0 | 3.4 | 15.2 | 0 | 18.15 | 0 |  | 1097 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 56 | 54 | 55 | 55 | 56 | 56 | 57 | 54 | 56 | 57 | 57 | 55 | 56 | 56 | 55 | 55 | 55 | 56 | 55 | 57 | 55 | 57 | 55 | 55 | 550 | 57 | 555 | 54 | 547 | 0 | 0 | 31 | 33 | 32 | 8 | [42 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 9409836 | 0 |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.3 | 30.3 |  |  | 28.7 | 28.9 | 29.7 | 0 |  |  |  |  | 10154 |  |  | 0 | 0.999 | 0 | 0 | 20926 | 12121 | 20969 | 12040 | 20942 | 12118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31385 | 3923 | 8 | 0.129 | 4550 | 2.27 | 0.4 | 0.01 | 0.2 |  | 0 | 59.7 | 27.8 | 0 | 17.2 | 18.9 | 29.9 | 0 | 0 | 0 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 68.1 | 63.6 | 67.3 | 66.7 | 68.6 | 68.2 | 68 | 68.6 | 55.8 | 67 | 66.7 | 65.8 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 11586.1 | 11586 | 11586 | 10235.4 | 11586.1 | 11586 | 11585.9 | 11586.1 | 11586 | 11585.9 | 11586.1 | 11586 | 2017 | 2017 | 25 | 10 | 2017 | 28 | 10 | 2017 | 11 | 9 | 25 | 10 | 2017 | 25 | 10 | 2017 | 28 | 10 | 2017 | 26 | 10 | 2017 | 25 | 10 | 2017 | 25 | 10 | 2017 | 26 | 10 | 2017 | 25 | 10 | 2017 | 28 | 10 | 36975 | 36957 | 37007 | 36271 | 36942 | 36999 | 36995 | 36988 | 36979 | 36992 | 36983 | 37008 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.558 | 0.42 | 0 | 1 | 0 | 0 | 7.79 | 7.56 | 7.65 | 7.59 | 7.71 | 7.7 | 7.83 | 7.8 | 7.62 | 7.61 | 7.64 | 7.72 | 7.63 | 7.63 | 7.62 | 7.72 | 7.57 | 7.92 | 7.66 | 7.52 | 7.5 | 7.67 | 7.65 | 7.54 | 0.2 | -0.23 | -0.3 | -0.16 | -0.26 | -0.31 | -0.11 | 0.12 | -0.02 | -0.14 | -0.09 | -0.4 | -0.19 | -0.1 | -0.28 | -0.24 | -0.07 | -0.25 | -0.26 | 0.01 | -0.36 | -0.37 | -0.21 | -0.45 | 7.73 | 7.59 | 7.8 | 7.89 | 7.63 | 7.87 | 8.04 | 7.82 | 7.94 | 7.87 | 7.58 | 7.75 | 7.68 | 7.83 | 7.62 | 7.75 | 7.61 | 7.93 | 7.69 | 7.63 | 7.59 | 7.73 | 7.76 | 7.68 | -0.41 | -0.3 | -0.15 | -0.15 | -0.21 | -0.08 | -0.14 | 0.12 | -0.23 | -0.11 | -0.12 | 0.01 | -0.15 | -0.01 | -0.2 | -0.29 | -0.13 | -0.16 | -0.13 | -0.33 | -0.26 | -0.16 | 0 | -0.38 | 47130.6 | 0 | 13936.3 | 0 | 0 | 0.02 | 0 | 0 | 1.04 | 0 | 0 | 4.4.0.0.0 | 4.4.0.1.1 | 4.4.0.0.0 | 4.5.3.0.0 | 4.4.0.1.6 | 4.4.4.16.6 | 4.7.1.0.0 | 4.4.0.3.12 | 4.5.2.0.0 | 4.4.0.4.12 | 4.4.0.1.0 | 4.5.1.0.0 | 4.4.0.2.0 | 4.4.0.0.0 | 4.4.0.0.4 | 4.4.0.5.6 | 4.4.0.5.0 | 4.4.0.0.2 | 4.4.0.0.0 | 4.4.0.0.2 | 4.4.0.2.12 | 4.3.0.0.0 | 0.0.0.0.0 | 4.4.0.5.11 | 4.4.1.0.0 | 4.4.0.0.12 | 4.4.0.1.0 | 4.3.0.0.0 | 4.4.0.3.3 | 4.9.0.0.0 | M04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1242 | 30.72 | 105 | 4.21 | 1527 | 1509 | 470 | 89 | 6 | 0 | 0 | 40 | 70 | 100 | 150 | 250 | 0 | 0 | 9008 | 0 | 12 | 133.02 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 29.15 | -1 | 2 | 1 | NaN | 0.0001 | 1607530194000 | 1 | 1 | 0.2681 | 1 | NaN | 4110 | 1 | 1606780800000 | NaN | NaN | NaN | 0.05 | 6.48 | 4 | NaN | 1 | 0.0008 | 1 | 1 | 1 | 1 | 0 | 0 | 927 | 9 | 0.0294 | 1 | 1607502600000 | 3 | 1 | 1 | 1.62 | 5.7 | 89454 | 1 | 1 | 11062 | 1 | 13.3 | 119 | 0.05 | 0.0369 | 6739 | 100 | 3 | 305 | Not Available | 60 |  | 0 | 0 | 8283 | 10.17 | 2 | 2 |  | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 1 | 0 | 970 | 40 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 0 | 0 | 1 | 1 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 30 | 30 | 0 | 1.4 | 20 | 10 | 50 | 2 | 0 | 11 | 1 | 0 | 0 | 0 | 0 | 7 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 35 | [5 empty] | 0 | 0 | 1 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 200 | -1000 |  | -200 | -1700 | 10 | 0 | 50 | 1500 | 5.6 | 6.7 | 6.9 | 0.1 | 3 | 0.1 | 0 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 3.5 |  | 0 | 0 | 0.2 | 4.2 |  | 10 | 0 |  |  |  | 1 |  | 5 | 5 | 5 | 5 | 5 | 60 | 28 | 35 | 30 | 50 | 180 | 28 | 35 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 2 | 10 | 2 | 1 | 1 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 2 | 10 | 2 | 1 | 1 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 2 | 10 | [479 empty] | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 12000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 2 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 10 | 0 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 32 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 | 0.95 | 0 | 60 | -33 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | 85 | 110 | 90 | 95 | 100 | 105 | 0.85 | 0.9 | 0.95 | 1 | -0.97 | -0.95 | 0 | 0 | 1 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 1 | 40 | 0 | 30 | 30 | 10 | 10 | 10 | 3 | 1 | 10000 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 4 | 4 | 0.01 | 0.01 | 0.2 | 0.2 | 1 | 1.11 | 1 | 1.11 | 1 | 30 | 0 | 2 | 1 | 100 | 100 | 10 | 50 | 50 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 5000 | -5000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 51.5 | 47.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 1 | 115 | 85 | 35 | 10 | 0 | 0 | 1 | -0.2 | 50 | 110 | 80 | 1 | 0 | 323 | 200 | 1 | 200 | 10 | 10 | 0.8 | 3 | 4 | 10 | 0.5 | 4 | 20000 | 20 | 10 | 5 | 10000 | 0 | 0 | 0 | 0 | 20000 | 120 | 80 | 45 | 0 | 10 | 0 | 0 | 0 | -0.4 | 50 | 110 | 80 | 0 | 1 | 400 | 200 | 0 | 100 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 90 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 6 | 0 | 6000 | 0 | 100 | 50 | 65 | 500 | 100 | 460 | 0 | 0 | 0 | 50 | -10 | 0 | 0 | 0 | 1 | 0 | 5 | 30 | 30 | 50 | 490 | 490 | 300 | 30 | 100 | 0 |  | 1 | 0 | 0 | 1 | 1 | 0 | 0 |  | 1 |  | 0 |  |  |  | 1 | 1 |  |  |  | 1 | 1 | 0 | 1 |  | 1 | 1 | 1 |  | 1 | 1 | [8 empty] | 0 | 1 |  | 0 | 0 |  |  | 1 |  | 0 | 1 | 1 | 0 |  | 1 | 1 | 1 | 1 |  | 0 |  |  |  | 12.5 |  | 624 |  |  |  |  | 14 | 0 | 346 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.2 | 1 | 0.01 | 100 | 30 | 0 | 1 | 5.2 | 100 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 40 | 0 | 100 | 10 | 0 | 0 | -5 | 2 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 40 | 30 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 200 | 168 | 75 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 3 | 1 | 2 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 65 | 4 | 0 | 0 | 0 | -2.5 | 10 | 1 | 20 | 15 | 1 | 2 | 1 | 1.82 | 0.6 | 0.6 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0.1 | 0 | 0 | 0 | 15 | 30 | 0.01 | 0.4 | 0 | 60 | 30 | 0 | 0 | 0 | 0 | 1200 | 1400 | 0 | 0.5 | 450 | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 0.2 | 0.04 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 1 | 0 | 0.72 | 0.72 | 0.72 | 0.72 | 1.2 | 0.1 | 300 | 300 | 300 | 300 | 0 | 50 | 50 | 50 | 50 | 50 | 120 | 0 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.15 | 3.6621 | 25 | 2.9297 | 100 | 0 | 8 | 0.1 | 0.5 | 1 | 7 | 100 | 2 | 25 | 10 | 250 | 4 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 | 1 | 1 | 4000 | 2000 | 20000 | 10000 | 4500 | 2250 | 8 | 4 | 2 | 1 | 30 | 150 | 20 | 120 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 1 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 | 1.5 | 1 | 650 | 700 | 1 | 0 | 0 | 1 | [66 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 1 | 1 | 1200 | 38000 |  |  |  | 44800 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 100 | 1000 | 680 | 640 | 5 | 650 | 5 | 650 | 640 | 5 | 650 | 5 | 1000 | 5 | 15 | 300 | 20 | 50 | 650 | 3 | 125 | 5 | 1000 | 200 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | 0 | -0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 20 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 10 | 20 | 5 | 10 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | 0 | 20 |  | 0.98 | 1 | -0.98 | -0.95 | 0.8 | -0.95 | 1 | 7 | 0.95 | -0.95 | 20 | 80 | 5590 | 88 | 90 | 2.01 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 0 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 85 | 90 | 85 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 42.8 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 35 | 300 |  | 75 | 0.97 | 1 | 1 | 1 | 180 | 0.1 | 1.11 | 60 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 930 | 0 | 5000 | 40 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 2250 | 4500 | 1 | 2 | 0 | 1 | 1 | 2 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 4 | 20 | 0.8 | -0.925 | 1 | 0 | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 400 | 0 | 0 | 0 | 0 | 1 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -100 | 100 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 1 | 1 | 0.8 | -0.92 | -3600 | 3600 | 10 | 0 | 100 | 0 | 100 | 0 | 800 | -20 | 800 | -20 | 600 | 0 | 10 | 3.3 | 0.2 | 3 | 0.05 | 1.5 | 1.9 | 0.05 | 0.05 | 87 | 5 | 94 | 2 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 30 |  |  | 20 |  |  |  | 3 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.4 | 0.1 | 0.5 | 500 | 1500 | 3.5 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1.5 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 75 | 2 | 79 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 1 | 0 | 95 | 120 | 2 | 2 | 0 | 1 | 0 | 74 | 120 | 2 | 2 | 1 | 62 | 2 | 1 |  | 74 | 120 | 0.5 | 0.5 | 0 | 1 | 0 | 140 | 140 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 82 | 0 | 0 | 0 | 5 | 20 | 0 | 2 | 30 | 90 | 0 | 0 | 0 | 200 | -200 | 0 | -70 | 100 | -100 | 0 | 0 | 0 | 200 | -200 | 20 | 30 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 50 | 100 | 1 | 8.5 | 9 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 10 | 0 | 0 | 1 | 90 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 18 | 18 | 18 | 18 | [5 empty] | 4 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 924 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 1 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 0 | 0 | 20 | 4000 | 4000 |  | 850 | 30 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 2 | 2 | 2 | 2 | -5 | -5 | -5 | -5 | 13 | 13 | 13 | 13 | 4.5 |  | 45 | 270 | 70 | -144 | 0 | 80 | 350 | [24 empty] | 0 | 4 | 500 | 30 |  | 2000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 380 | 1 | -30 | -9 | 4500 | 2250 | 10 | 4500 | 2250 | 60 | 0 | 0 | [6 empty] | 0.0007 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4500 | 2250 | 5959 | 3073 | 1498 | 1499 |  | 49.9 | 50.1 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4934 | 2163 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4934 | 2163 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4934 | 2163 | 1500 | 1500 |  | 50 | 50 |  | 660 |  | 0 | 1000 | 300 | 48 | -1.6 | -4 | 100 | 10 | 0 | 1 | 10 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 |  | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 10 | 0 | 0.5 | 0 | 0 | 60000 | 0 | 60000 | 0 |  | 5 | 0 | 1 | 1 |  |  |  | 80 |  | 45 | [14 empty] | 50 | 53 | 53 | 53 | [10 empty] | 0 | 0 | 1 | 3 | 55 | 57 | 2 | 2 | 60 |  | 45 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 350 | 200 | 200 | 100 | [8 empty] | -1250 | 5000 |  | 0.2 | 100 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.4 |  |  | 100 | 0.2 |  | 100 |  | 100 | 100 | [11 empty] | 0.2 | 100 | 200 | [43 empty] | 0 | 0.2 | 100 | 0.01 | 5 | 45 | 0 | 1 | 3.4 | 1 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 55 | 67 | 8 | 100 | 0 | 9 | 0.1 | 100 | 0.01 | 5 | 80 | 0 | 1 | 6 | 1 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 60 | 70 | 0 | 100 | 5 | 0 | 0.2 | 100 | 100 | 100 | 120 | 0 | 1 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 100 | 0.15 | 0.003 | 1 | 1 | 10 | 0.08 | 0 | 1 | 1.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1.1 | 0.7 | 1 | 0 | 100 | 0 | 0 | 0.1 | 100 | 0.02 | 5 | 60 | 0 | 1 | 7.2 | 1 | 1 | 1 | 1 | 0 | 0 | 140 | 95 | 127 | 0 | 100 | 10 | 0 | 0.1 | 0.5 | 0.01 | 5 | 100 | 0 | 1 | 6.5 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 45 | 0 | 100 | 15 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0.05 | 0.1 | 100 | 90 | 0 | 1 | 3 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 110 | 80 | 100 | 100 | 80 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | [42 empty] | 6 | 0.1 | 5 | 30 | 0 | 1 | 3.5 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 0 | 100 | 100 | 55 | 0 | 100 | 15 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 0 | 0 | 10 | 150 | 150 | 100 | 205 | 0 | 48 | 50 | 0 | 3000 | 6000 | 3000 | 6000 | 6 | 6 | 0 | 5000 | -5000 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 100 | 50 | 6 | 0.1 | 5 | 30 | 0 | 1 | 3.5 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 0 | 100 | 100 | 55 | 0 | 100 | 15 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 |  |  |  |  | 12 | 2 | 5 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 80 | 0 | [6 empty] | 0.01421 | 0.29619 | 0.88857 | 100 | 0 | 0 | 0.44428 | 0.23695 | 100 | 2 | 0 | 20 | 5000 | 5000 | 60 | 75 | 90 | 100 |  | 4 | 20 | 2250 | 4500 | 2.5 | 2 | 38 | 45 |  | -2 | -2 | -2 | -2 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -145 | 10 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 4500 | 4500 | 4500 | 4500 | 50 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 |  | 10 | 10 | 93 | 1 | 1 | 100.4 | 103.4 | 98 | 91 | 103.4 | 40 | 65 | 85 | 80 |  | 110 | 125 | 90 | 70 | 140 | 1 | 80 | 10 | 80 | 1 | 20 | 5.55 | 1 | 1 | 100 |  |  | 5 | 4 | 4 | 4 | 4 | 56 | 56 | 56 | 56 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 130 | 400 | 400 | 5005 | 2500 | 16 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 0.72 | 1200 | 150 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | [30 empty] | 1 | 1 | 1 | 35 | 10 | 0 | 0 | 5 | 20 | 20 | 5 | 0 | 0 | 1 | 115 | 80 | 0 | 89 | 110 | 0 | 1800 | 75 | 5 | 80 | 5 | 1 | 3150 | 180 | 280 | 110 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1650 | 10 | 200 | 400 | 2800 | 5 | 10000 | 0 | 3850 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 1 | 1200 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 800 |  | 0.16406 | 2.1973 | 4.3945 | 95 | 2 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1500 | 6.7 | 0 | 95 | 85 | 85 | 95 | 95 | 9.54 | 9.971 | 720 |  |  | 1.45 | 1.65 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.1 |  |  | 0.59 | [13 empty] | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | [28 empty] | 1 | 1 | 1 | 2 | 0 | 2 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  |  | 4500 | 0 | 0 | 0 | 0 | 0 | 4500 | 0 |  |  | 0.97 | 0.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -46.17 | 3.993 | 0.074 | 0.91291 | 0 | 0.72 | 0 | 0 | 0 | 0.02 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 67.31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361 | 361 | 361 | 360 | 362 | 362 | 362 | 363 | 363 | 362 | 362 | 364 | 362 | 360 | 362 | 356 | 360 | 362 | 361 | 364 | 360 | 363 | 356 | 358 | 492 | 492 | 490 | 494 | 494 | 494 | 492 | 495 | 495 | 497 | 494 | 494 | 493 | 493 | 495 | 491 | 492 | 495 | 495 | 495 | 494 | 494 | 491 | 493 | 5269 | Sending | 30 | 45 | 45 | 44 | 45 | 44 | 44 | 45 | 43 | 44 | 45 | 45 | 45 | 46 | 46 | 45 | 45 | 45 | 45 | 46 | 45 | 27.1574 | 29.3787 | 30.4243 | 28.6696 | 29.7829 | 30.4735 | 29.9739 | 27.8837 | 27.9694 | 29.6723 | 26.4602 | 29.8682 | 27.5682 | 25.6863 | 26.6641 | 28.8767 | 28.4618 | 28.6745 | 29.0711 | 27.8633 | 30.7787 | 26.3708 | 30.2753 | 24.677 | 1356 | 1551 | 1138 | 1391 | 3151 | 1350 | 1431 | 3080 | 3008 | 3007 | 1265 | 1514 | 1355 | 1116 | 1556 | 1432 | 1299 | 1434 | 1515 | 1351 | 1356 | 1517 | 1478 | 1176 |  | 0 | 1 | [11 empty] | 30.4 | 30.5 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 963 | 0 | 0 | 0 | 27.9 | 0 | 0 | 0 | 1.45 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 | 6686 | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 | 6686 | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 | 0 | 7.79 | 0 | 7.56 | 0 | 7.65 | 0 | 7.59 | 0 | 7.71 | 0 | 7.68 | 0 | 7.83 | 0 | 7.8 | 0 | 7.62 | 0 | 7.61 | 0 | 7.64 | 0 | 7.72 | 0 | 7.63 | 0 | 7.69 | 0 | 7.62 | 0 | 7.72 | 0 | 7.57 | 0 | 7.92 | 0 | 7.66 | 0 | 7.52 | 0 | 7.5 | 0 | 7.67 | 0 | 7.65 | 0 | 7.54 | 0 | 0.2 | 0 | -0.23 | 0 | -0.3 | 0 | -0.16 | 0 | -0.26 | 0 | 0 | 0 | -0.11 | 0 | 0.12 | 0 | -0.02 | 0 | -0.14 | 0 | -0.09 | 0 | -0.4 | 0 | -0.19 | 0 | 0 | 0 | -0.28 | 0 | -0.24 | 0 | -0.07 | 0 | -0.25 | 0 | -0.26 | 0 | 0.01 | 0 | -0.36 | 0 | -0.37 | 0 | -0.21 | 0 | -0.45 | 0 | 7.73 | 0 | 7.59 | 0 | 7.8 | 0 | 7.89 | 0 | 7.63 | 0 | 7.4 | 0 | 8.04 | 0 | 7.82 | 0 | 7.94 | 0 | 7.87 | 0 | 7.58 | 0 | 7.75 | 0 | 7.68 | 0 | 7.63 | 0 | 7.62 | 0 | 7.75 | 0 | 7.61 | 0 | 7.93 | 0 | 7.69 | 0 | 7.63 | 0 | 7.59 | 0 | 7.73 | 0 | 7.76 | 0 | 7.68 | 0 | -0.41 | 0 | -0.3 | 0 | -0.15 | 0 | -0.15 | 0 | -0.21 | 0 | 0 | 0 | -0.14 | 0 | 0.12 | 0 | -0.23 | 0 | -0.11 | 0 | -0.12 | 0 | 0.01 | 0 | -0.15 | 0 | 0 | 0 | -0.2 | 0 | -0.29 | 0 | -0.13 | 0 | -0.16 | 0 | -0.13 | 0 | -0.33 | 0 | -0.26 | 0 | -0.16 | 0 | 0 | 0 | -0.38 |  | 0 | 1 | 0 | 0 | 19 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0.98 |  | 0 | 0 | 0 | 0 |  | 1.9 | 1.9 | 1.9 | 1.9 | 0 | 0 | 0 | 0 |  | 1500 | 0 |  | 54.8 |  |  | 0 | 0 | BMW LANDSHUT 4.10
17 |  | 37 | 1 | 0 | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","agent_conn":"Back-SSL-NoProxy","mon_conn":"Back-NoSSL-NoProxy","rem_conn":"Prim-NoSSL-NoProxy"} | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 3.88 | 0 | 0 | 0.98 | 26.7 | 0 |  |  |  | 0 | 13.8 | 0 | 0 | 0.05 | -4 | 0.04 | 0 | 0 | 0 | 4.4.0.5 | 5555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 |  | 0 | 0 | 0 |  | 0 | -972 | 0 | -975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 |  |  |  |  | 35961079 | 0 | 8872987 | 420282 | 785 | 0 | 0 | 0 | 0 | 0 | -29 | 1073 | 811 | 776 | 776 | 776 | 1902 | 776 | 9224 | 9224 | 9224 | 0 | 1331 |  | 52.3 | 0 | 55 | 17 | 8 | 65 | 19.1 | 0 | 26.7 | 26.7 | 0 | 1 | 1 | 50 | 100 | 29 | 0 | 30 | 0 | 0 | 75 | 55.6 | 0 | 80 | 3.8 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.4 | 26.9 | 14.8 | 7.4 | 0 | 0 | 0 | 2.8 | 2.3 | 7.5 | 0 | 0.2 | 0.2 | 0 | 2 | 8.5 | 4.4 | 3.8 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0.4 | -28.3 | 0.8 | 1.2 | 1.6 | 2 | -0.4 | -3.7 | -14.2 | -28.8 | 0 | 0 | 0.4 | -28.3 | 1 | 0 | 0.8 | 0 | 1.2 | 0 | 1.6 | 0 | 2 | 1 | -0.4 | 1 | -3.7 | 1 | -14.2 | 1 | -28.8 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 9220 | 20 | 0 | 2928 | 0 | 0 | 2930 | -2.5 | 20.2 | 117.6 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189.7 | 100 | 150 | 0 | -0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.4 | 0 | 0 | 0.9 | 0.4 | 0 | 2.68 | 1.53 | 19 | 19 | 18 | 8.42 | 1608540250453 | 0 | 46 | 1 | 0 | 2.7 | 11.8 | 0 | 23 | 0 |  | 1181 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 51 | 51 | 52 | 53 | 54 | 50 | 52 | 52 | 52 | 52 | 53 | 52 | 51 | 52 | 51 | 52 | 51 | 52 | 52 | 52 | 51 | 53 | 52 | 51 | 554 | 54 | 556 | 50 | 549 | 0 | 0 | 19 | 33 | 31 | 7 | [42 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6547217 | 0 |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.4 | 30.3 |  |  | 28.9 | 29.1 | 30 | 0 |  |  |  |  | 1 | 1606566361694 |  | 0 | 0.999 | 0 | 0 | 20901 | 12107 | 20945 | 12023 | 20919 | 12107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31868 | 4552 | 7 | 0.031 | 1120 | 2.3 | 0.5 | 0.01 | 0.03 |  | 0 | 55.6 | 28.8 | 0 | 17 | 19.1 | 29.9 | 0 | 0 | 0 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 67.5 | 67.5 | 65.5 | 63.1 | 68.3 | 66.1 | 62.8 | 64.2 | 65.8 | 67.3 | 68.3 | 63.8 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 9275.3 | 8764.6 | 9275.1 | 9190.4 | 9275.2 | 9275.3 | 9275.1 | 9275.2 | 9275.1 | 9275.2 | 9275.2 | 9275.2 | 2017 | 2017 | 28 | 10 | 2017 | 5 | 10 | 2018 | 23 | 4 | 6 | 10 | 2017 | 5 | 10 | 2017 | 5 | 10 | 2017 | 5 | 10 | 2017 | 5 | 10 | 2017 | 6 | 10 | 2017 | 8 | 10 | 2017 | 8 | 10 | 2017 | 5 | 10 | 36499 | 37005 | 36442 | 40766 | 36431 | 36454 | 36430 | 36444 | 36484 | 36505 | 36504 | 36443 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.574 | 0.4 | 0 | 0 | 0 | 0 | 7.61 | 7.69 | 7.93 | 7.71 | 7.71 | 7.58 | 7.82 | 7.73 | 7.57 | 7.82 | 7.61 | 7.57 | 7.8 | 7.84 | 7.7 | 7.86 | 8.07 | 7.76 | 7.86 | 8.1 | 7.79 | 7.52 | 7.95 | 7.97 | -0.09 | -0.21 | -0.32 | 0 | 0 | -0.12 | -0.25 | -0.2 | 0.06 | 0.12 | -0.26 | 0 | -0.07 | 0.28 | -0.32 | -0.05 | -0.28 | -0.07 | 0.33 | -0.31 | -0.32 | -0.18 | -0.03 | 0.15 | 7.74 | 7.75 | 7.83 | 7.78 | 7.73 | 7.63 | 7.8 | 7.97 | 8.07 | 7.71 | 7.86 | 7.76 | 7.83 | 7.9 | 7.88 | 7.82 | 7.77 | 7.76 | 7.77 | 7.86 | 7.71 | 7.63 | 7.81 | 7.68 | -0.27 | -0.32 | -0.04 | -0.12 | 0.03 | -0.16 | -0.32 | -0.07 | -0.06 | -0.24 | 0.08 | -0.2 | -0.33 | 0.27 | -0.08 | -0.25 | -0.33 | -0.26 | -0.21 | 0.17 | -0.24 | -0.49 | 0 | -0.19 | 38588.1 | 0 | 11490.9 | 0 | 0 | 0.02 | 0 | 0 | 1.04 | 0 | 0 | 4.4.0.0.0 | ....1 | ....0 | ....0 | ....6 | ....6 | ....0 | ....12 | ....0 | ....12 | ....0 | ....0 | ....0 | ....0 | ....4 | ....6 | ....0 | ....2 | ....0 | ....2 | ....12 | ....0 | ....0 | ....11 | ....0 | ....12 | ....0 | ....0 | ....3 | ....0 | M01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1716 | [30 empty] | -1 | 2 | 1 | NaN | 0.0001 | 1607519055000 | 1 | 1 | 0.2606 | 1 | NaN | 3796 | 1 | 1607040000000 | NaN | NaN | NaN | 0.01 | 6.73 | 4 | NaN | 1 | 0.0008 | 1 | 1 | 1 | 1 | 0 | 0 | 871 | 10 | 0.0303 | 1 | 1607511600000 | 4 | 1 | 1 | 2.31 | 5.9 | 89456 | 1 | 1 | 8945 | 1 | 13.2 | 120 | 0.05 | 0.0355 |  |  |  |  | Not Available | 60 |  | 0 | 0 | 7632 | 6.96 | 2 | 2 |  | 0 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 33.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 1 | 0 | 970 | 40 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 0 | 0 | 1 | 1 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 30 | 30 | 0 | 1.4 | 20 | 5 | 50 | 2 | 0 | 11 | 1 | 0 | 0 | 0 | 0 | 7 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 35 | [5 empty] | 0 | 0 | 1 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 200 | -1000 |  | -200 | -1700 | 10 | 0 | 50 | 1500 | 5.6 | 6.7 | 6.9 | 0.1 | 3 | 0.1 | 0 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 3.5 |  | 0 | 0 | 0.2 | 4.2 |  | 10 | 0 |  |  |  | 1 |  | 5 | 5 | 5 | 5 | 5 | 60 | 28 | 35 | 30 | 50 | 180 | 28 | 35 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 2 | 10 | 2 | 1 | 1 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 2 | 10 | 2 | 1 | 1 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 4 | 0 | [479 empty] | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 12000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 2 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 10 | 0 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 32 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 | 0.95 | 0 | 60 | -33 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | 85 | 110 | 90 | 95 | 100 | 105 | 0.85 | 0.9 | 0.95 | 1 | -0.97 | -0.95 | 0 | 0 | 1 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 1 | 40 | 0 | 30 | 30 | 10 | 10 | 10 | 3 | 1 | 10000 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 4 | 4 | 0.01 | 0.01 | 0.2 | 0.2 | 1 | 1.11 | 1 | 1.11 | 1 | 30 | 0 | 2 | 1 | 100 | 100 | 10 | 50 | 50 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 5000 | -5000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 51.5 | 47.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 1 | 115 | 85 | 35 | 10 | 0 | 0 | 1 | -0.2 | 50 | 110 | 80 | 1 | 0 | 323 | 200 | 1 | 200 | 10 | 10 | 0.8 | 3 | 4 | 10 | 0.5 | 4 | 20000 | 20 | 10 | 5 | 10000 | 0 | 0 | 0 | 0 | 20000 | 120 | 80 | 45 | 0 | 10 | 0 | 0 | 0 | -0.4 | 50 | 110 | 80 | 0 | 1 | 400 | 200 | 0 | 100 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 90 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 6 | 0 | 6000 | 0 | 100 | 50 | 60 | 500 | 100 | 460 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 5 | 30 | 30 | 60 | 490 | 490 | 300 | 30 | 120 | 0 |  | 1 | 0 | 0 | 1 | 1 | 0 | 0 |  | 1 |  | 0 |  |  |  | 1 | 1 |  |  |  | 1 | 1 | 0 | 1 |  | 1 | 1 | 1 |  | 1 | 1 | [8 empty] | 0 | 1 |  | 0 | 0 |  |  | 1 |  | 0 | 1 | 1 | 0 |  | 1 | 1 | 1 | 1 |  | 0 |  |  |  | 12.5 |  | 624 |  |  |  |  | 11 | 0 | 346 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.2 | 1 | 0.01 | 100 | 30 | 0 | 1 | 5.2 | 100 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 40 | 0 | 100 | 10 | 0 | 0 | -5 | 2 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 45 | 30 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 200 | 168 | 75 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 3 | 1 | 2 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 65 | 4 | 0 | 0 | 0 | -2.5 | 10 | 1 | 20 | 15 | 1 | 2 | 1 | 1.82 | 0.6 | 0.6 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0.2 | 0 | 0 | 0 | 15 | 30 | 0.01 | 0.4 | 0 | 60 | 30 | 0 | 0 | 0 | 0 | 1200 | 1400 | 0 | 0.5 | 450 | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 0.2 | 0.05 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 1 | 0 | 0.72 | 0.72 | 0.72 | 0.72 | 1.2 | 0.1 | 300 | 300 | 300 | 300 | 0 | 50 | 50 | 50 | 50 | 50 | 120 | 0 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.15 | 3.6621 | 25 | 2.9297 | 100 | 0 | 8 | 0.1 | 0.5 | 1 | 7 | 100 | 2 | 25 | 10 | 250 | 4 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 | 1 | 1 | 4000 | 2000 | 20000 | 10000 | 4500 | 2250 | 8 | 4 | 2 | 1 | 30 | 150 | 20 | 120 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 1 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 | 1.5 | 1 | 650 | 700 | 1 | 0 | 0 | 1 | [66 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 1 | 1 | 1200 | 38000 |  |  |  | 44800 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 100 | 1000 | 680 | 640 | 5 | 650 | 5 | 650 | 640 | 5 | 650 | 5 | 1000 | 5 | 15 | 300 | 20 | 50 | 650 | 3 | 125 | 5 | 1000 | 200 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | 0 | -0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 20 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 10 | 20 | 5 | 10 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | 0 | 20 |  | 0.98 | 1 | -0.98 | -0.95 | 0.8 | -0.95 | 1 | 7 | 0.95 | -0.95 | 20 | 80 | 5590 | 88 | 90 | 2.01 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 0 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 85 | 90 | 85 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 42.7 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 35 | 300 |  | 75 | 0.97 | 1 | 1 | 1 | 180 | 0.1 | 1.11 | 60 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 930 | 0 | 5000 | 40 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 2250 | 4500 | 1 | 2 | 0 | 1 | 1 | 2 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 4 | 20 | 0.8 | -0.925 | 1 | 0 | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 400 | 0 | 0 | 0 | 0 | 1 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -100 | 100 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 1 | 1 | 0.8 | -0.92 | -3600 | 3600 | 10 | 0 | 100 | 0 | 100 | 0 | 800 | -20 | 800 | -20 | 600 | 0 | 10 | 3.3 | 0.2 | 3 | 0.05 | 1.5 | 1.9 | 0.05 | 0.05 | 87 | 5 | 94 | 2 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 30 |  |  | 20 |  |  |  | 3 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.4 | 0.1 | 0.5 | 500 | 1500 | 3.5 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1.5 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 75 | 2 | 79 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 1 | 0 | 95 | 120 | 2 | 2 | 0 | 1 | 0 | 74 | 120 | 2 | 2 | 1 | 62 | 2 | 1 |  | 74 | 120 | 0.5 | 0.5 | 0 | 1 | 0 | 140 | 140 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 82 | 0 | 0 | 0 | 5 | 20 | 0 | 2 | 30 | 90 | 0 | 0 | 0 | 200 | -200 | 0 | -70 | 100 | -100 | 0 | 0 | 0 | 200 | -200 | 20 | 30 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 9.5 | 10 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 10 | 0 | 0 | 1 | 90 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 18 | 18 | 18 | 18 | [5 empty] | 4 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 924 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 1 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 0 | 0 | 20 | 4000 | 4000 |  | 850 | 30 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 3 | 3 | 3 | 3 | -5 | -5 | -5 | -5 | 13 | 13 | 13 | 13 | 4.5 |  | 45 | 270 | 70 | -144 | 0 | 80 | 350 | [24 empty] | 0 | 4 | 500 | 30 |  | 2000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 380 | 1 | -30 | -9 | 4500 | 2250 | 10 | 4500 | 2250 | 60 | 0 | 0 | [6 empty] | 0.0007 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4498 | 2248 | 5927 | 2997 | 1498 | 1499 |  | 49.9 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4912 | 2154 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4912 | 2154 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4912 | 2154 | 1500 | 1500 |  | 50 | 50 |  | 660 |  | 0 | 1000 | 300 | 48 | -1.6 | -4 | 100 | 10 | 0 | 1 | 10 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 |  | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 10 | 0 | 0.5 | 0 | 0 | 60000 | 0 | 60000 | 0 |  | 5 | 0 | 1 | 1 |  |  |  | 80 |  | 45 | [14 empty] | 50 | 53 | 53 | 53 | [10 empty] | 0 | 0 | 1 | 3 | 55 | 57 | 2 | 2 | 60 |  | 45 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 350 | 200 | 200 | 100 | [8 empty] | -1250 | 5000 |  | 0.2 | 100 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.4 |  |  | 100 | 0.2 |  | 100 |  | 100 | 100 | [11 empty] | 0.2 | 100 | 200 | [43 empty] | 0 | 0.2 | 100 | 0.01 | 100 | 45 | 0 | 1 | 3.4 | 1 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 55 | 67 | 8 | 100 | 0 | 0 | 0.2 | 100 | 0.01 | 100 | 40 | 0 | 1 | 2 | 1 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 65 | 70 | 0 | 100 | 5 | 0 | 0.2 | 100 | 100 | 100 | 120 | 0 | 1 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 25 | 0 | 100 | 0 | 0.15 | 0.003 | 1 | 1 | 10 | 0.08 | 0 | 1 | 1.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1.1 | 0.7 | 1 | 0 | 100 | 0 | 0 | 0.1 | 100 | 0.02 | 100 | 60 | 0 | 1 | 7.2 | 1 | 1 | 1 | 1 | 0 | 0 | 140 | 100 | 127 | 0 | 100 | 0 | 0 | 0.3 | 0.5 | 0.01 | 100 | 100 | 0 | 1 | 6.5 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 45 | 0 | 100 | 15 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0.05 | 0.1 | 100 | 50 | 0 | 1 | 5.5 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 110 | 80 | 100 | 100 | 80 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | [42 empty] | 0 | 0.3 | 100 | 100 | 0 | 1 | 6.5 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 15 | 100 | 100 | 55 | 0 | 100 | 15 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 0 | 0 | 10 | 150 | 150 | 100 | 205 | 0 | 48 | 50 | 0 | 3000 | 6000 | 3000 | 6000 | 6 | 6 | 0 | 5000 | -5000 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 100 | 50 | 0 | 0.3 | 100 | 100 | 0 | 1 | 6.5 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 0 | 100 | 100 | 55 | 0 | 100 | 15 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 |  |  |  |  | 12 | 2 | 5 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 80 | 0 | [6 empty] | 0.01421 | 0.29619 | 0.88857 | 100 | 0 | 0 | 0.44428 | 0.23695 | 100 | 2 | 0 | 20 | 5000 | 5000 | 60 | 75 | 90 | 100 |  | 4 | 20 | 2250 | 4500 | 2.5 | 2 | 42 | 45 |  | -2 | -2 | -2 | -2 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -145 | 10 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 4500 | 4500 | 4500 | 4500 | 50 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 |  | 10 | 10 | 93 | 1 | 1 | 100.4 | 103.4 | 98 | 91 | 103.4 | 40 | 65 | 85 | 80 |  | 110 | 125 | 90 | 70 | 140 | 1 | 80 | 10 | 80 | 1 | 20 | 5.55 | 1 | 1 | 100 |  |  | 5 | 4 | 4 | 4 | 4 | 56 | 56 | 56 | 56 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 130 | 400 | 400 | 5000 | 2510 | 16 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 0.72 | 1200 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | [30 empty] | 1 | 1 | 1 | 35 | 10 | 0 | 0 | 5 | 20 | 20 | 5 | 0 | 0 | 1 | 100 | 80 | 0 | 89 | 110 | 0 | 1800 | 75 | 5 | 80 | 5 | 1 | 3150 | 180 | 280 | 110 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1650 | 10 | 200 | 400 | 2800 | 5 | 10000 | 0 | 3850 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 1 | 1200 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 800 |  | 0.16406 | 2.1973 | 4.3945 | 95 | 2 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1500 | 6.7 | 0 | 95 | 85 | 85 | 95 | 95 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.1 |  |  | 0.59 | [13 empty] | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | [28 empty] | 1 | 1 | 1 | 2 | 0 | 2 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 4500 | 0 | 0 | 0 | 0 | 0 | 3004 | 0 |  |  | 0.97 | 0.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0.3 | -38.01 | 4 | 0.0495 | 0.673 | 0 | 0.72 | 3187 | 0 | 0 | 0.03 | 1 | 0 | 1 | 0 | 0 | 215 | 0 | 0 | 237 | 0 | 0 | 27 | 0 | 0 | 490 | 0 | 320 | 0 | 0 | 10 | 300 | 64.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 361 | 363 | 366 | 367 | 364 | 362 | 363 | 362 | 366 | 362 | 366 | 360 | 364 | 363 | 360 | 361 | 364 | 363 | 368 | 365 | 368 | 361 | 361 | 492 | 494 | 493 | 496 | 496 | 497 | 495 | 497 | 495 | 495 | 494 | 496 | 492 | 493 | 494 | 492 | 492 | 495 | 495 | 497 | 493 | 496 | 493 | 493 | 6034 | Sending | 30 | 45 | 45 | 46 | 46 | 46 | 45 | 45 | 45 | 45 | 46 | 46 | 46 | 46 | 45 | 44 | 43 | 43 | 46 | 46 | 46 | 26.1798 | 30.1748 | 25.4766 | 27.0775 | 26.7813 | 28.0288 | 26.381 | 27.4841 | 25.4831 | 20.9828 | 25.7833 | 27.8826 | 27.0786 | 24.5826 | 21.9791 | 28.1266 | 26.6789 | 26.2203 | 29.279 | 24.4859 | 25.8793 | 27.3808 | 29.0789 | 27.8793 | 1049 | 2294 | 3079 | 3151 | 3080 | 3008 | 1453 | 1085 | 3054 | 3007 | 1717 | 1112 | 1322 | 1362 | 1146 | 1182 | 1023 | 1446 | 1131 | 1516 | 1013 | 1110 | 3226 | 1115 |  | 0 | 1 | [11 empty] | 30.7 | 30.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 963 | 0 | 0 | 0 | 28.5 | 0 | 0 | 0 | 1.55 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 | 2902 | 1 |  | 1 | 2902 | 1 |  | 1 | 0 | 7.61 | 0 | 7.69 | 0 | 7.93 | 0 | 7.71 | 0 | 7.71 | 0 | 7.58 | 0 | 7.82 | 0 | 7.73 | 0 | 7.57 | 0 | 7.82 | 0 | 7.61 | 0 | 7.57 | 0 | 7.8 | 0 | 7.84 | 0 | 7.7 | 0 | 7.86 | 0 | 8.07 | 0 | 7.76 | 0 | 7.86 | 0 | 8.1 | 0 | 7.35 | 0 | 7.52 | 0 | 7.4 | 0 | 7.97 | 0 | -0.09 | 0 | -0.21 | 0 | -0.32 | 0 | 0 | 0 | 0 | 0 | -0.12 | 0 | -0.25 | 0 | -0.2 | 0 | 0.06 | 0 | 0.12 | 0 | -0.26 | 0 | 0 | 0 | -0.07 | 0 | 0.28 | 0 | -0.32 | 0 | -0.05 | 0 | -0.28 | 0 | -0.07 | 0 | 0.33 | 0 | -0.31 | 0 | -0.45 | 0 | -0.18 | 0 | -0.5 | 0 | 0.15 | 0 | 7.74 | 0 | 7.75 | 0 | 7.83 | 0 | 7.78 | 0 | 7.73 | 0 | 7.63 | 0 | 7.8 | 0 | 7.97 | 0 | 8.07 | 0 | 7.71 | 0 | 7.86 | 0 | 7.76 | 0 | 7.83 | 0 | 7.9 | 0 | 7.88 | 0 | 7.82 | 0 | 7.77 | 0 | 7.76 | 0 | 7.77 | 0 | 7.86 | 0 | 7.4 | 0 | 7.63 | 0 | 7.4 | 0 | 7.68 | 0 | -0.27 | 0 | -0.32 | 0 | -0.04 | 0 | -0.12 | 0 | 0.03 | 0 | -0.16 | 0 | -0.32 | 0 | -0.07 | 0 | -0.06 | 0 | -0.24 | 0 | 0.08 | 0 | -0.2 | 0 | -0.33 | 0 | 0.27 | 0 | -0.08 | 0 | -0.25 | 0 | -0.33 | 0 | -0.26 | 0 | -0.21 | 0 | 0.17 | 0 | -0.5 | 0 | -0.49 | 0 | -0.4 | 0 | -0.19 |  | 0 | 1 | 0 | 0 | 19 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0.97 |  | 0 | 0 | 0 | 0 |  | 1.9 | 1.9 | 1.9 | 1.9 | 0 | 0 | 0 | 0 |  | 1500 | 0 |  | 52.3 |  |  | 0 | 0 | BMW LANDSHUT M1
18 |  | 40 | 1 | 0 | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","agent_conn":"Prim-SSL-NoProxy","mon_conn":"Prim-NoSSL-NoProxy","rem_conn":"Back-NoSSL-NoProxy"} | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2 | 0 | 6.09 | 0 | 0 | 0.97 | 27.8 | 0 |  |  |  | 0 | 8.2 | 0 | 0 | 0.04 | 0.19 | 0.05 | 0 | 0 | 0 | 4.4.0.5 | 2043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 |  | 0 | 0 | 0 |  | 0 | -976 | 0 | -974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.03 |  |  |  |  | 35885378 | 0 | 9972143 | 473876 | 781 | 0 | 0 | 0 | 0 | 0 | 50 | 756 | 519 | 519 | 519 | 519 | 46 | 519 | 9481 | 9481 | 9481 |  | 1147 |  | 52.7 | 0 | 55 | 18 | 8 | 65 | 20.1 | 0 | 27.8 | 27.8 | 0 | 1 | 1 | 50 | 100 | 37.1 | 0 | 30 | 0 | 0 | 75 | 56.6 | 0 | 80 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.2 | 27.7 | 15.8 | 7.4 | 0 | 0 | 0 | 2.9 | 2.3 | 9.2 | 0 | 0 | 0 | 2.2 | 1.3 | 8.5 | 7.8 | 7.7 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 4.3 | 0.8 | 8.7 | 13.1 | 17.4 | 21.8 | 20.3 | 20.1 | 19.8 | 6.4 | 0 | 0 | 4.3 | 0.8 | 1 | 0 | 8.7 | 0 | 13.1 | 0 | 17.4 | 0 | 21.8 | 1 | 20.3 | 1 | 20.1 | 1 | 19.8 | 1 | 6.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 9457 | 20 | 1 | 4925 | 0 | 0 | 3332 | -2.3 | 20.2 | 134.4 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.8 | 100 | 150 | 0 | 14.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141.4 | 0 | 0 | 1.3 | 0.4 | 0 | 2.7 | 1.21 | 27 | 28 | 26 | 22.1 | 1608749665369 | 0 | 48 | 1 | 0 | 3.3 | 13.4 | 0 | 29.19 | 0 |  | 2954 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 53 | 52 | 52 | 53 | 53 | 53 | 55 | 51 | 52 | 52 | 54 | 52 | 52 | 51 | 50 | 53 | 52 | 53 | 51 | 52 | 52 | 55 | 53 | 52 | 556 | 55 | 561 | 51 | 552 | 0 | 0 | 32 | 34 | 33 | 9 | [42 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5817918 | 0 |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.9 | 31.5 |  |  | 30.3 | 30.7 | 31.3 | 0 |  |  |  |  | 2 |  |  | 0 | 0 | 0 | 0 | 20896 | 12099 | 20926 | 12023 | 20913 | 12098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53313 | 4101 | 13 | 0.054 | 3255 | 1.99 | 0.6 | 0.01 | 0.04 |  | 0 | 56.6 | 29.9 | 0 | 18 | 20.1 | 31.5 | 0 | 0 | 0 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 68 | 63.5 | 57.8 | 64.7 | 65 | 68 | 57.3 | 65.6 | 68.7 | 66.7 | 66.8 | 68.1 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 9523.8 | 9523.7 | 9523.6 | 3992.2 | 9523.7 | 9523.7 | 9523.7 | 9523.8 | 9523.8 | 9523.7 | 9523.7 | 9523.8 | 2017 | 2017 | 28 | 10 | 2017 | 25 | 10 | 2019 | 14 | 3 | 5 | 10 | 2017 | 28 | 10 | 2017 | 28 | 10 | 2017 | 25 | 10 | 2017 | 6 | 10 | 2017 | 11 | 9 | 2017 | 25 | 10 | 2017 | 28 | 10 | 2017 | 25 | 10 | 36452 | 37022 | 36939 | 45107 | 37029 | 37028 | 36949 | 36489 | 36274 | 36977 | 37002 | 36989 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.572 | 0.4 | 0 | 1 | 0 | 0 | 7.66 | 7.74 | 7.77 | 7.63 | 7.54 | 7.67 | 7.72 | 7.8 | 7.73 | 7.81 | 7.63 | 7.87 | 7.68 | 7.71 | 7.93 | 7.6 | 7.64 | 7.64 | 7.55 | 7.69 | 7.74 | 7.8 | 7.69 | 7.82 | -0.07 | -0.02 | -0.31 | -0.46 | -0.18 | -0.26 | -0.16 | -0.03 | -0.2 | -0.39 | -0.28 | -0.13 | 0 | 0.07 | -0.23 | -0.07 | -0.21 | -0.32 | -0.32 | -0.19 | -0.12 | -0.06 | -0.21 | -0.08 | 7.8 | 7.73 | 7.64 | 7.99 | 7.54 | 7.61 | 7.96 | 7.85 | 7.81 | 7.83 | 7.75 | 8.07 | 7.76 | 7.68 | 7.76 | 7.61 | 7.64 | 7.5 | 7.59 | 7.84 | 7.83 | 7.89 | 7.59 | 7.81 | -0.07 | -0.1 | -0.28 | -0.27 | -0.31 | -0.06 | -0.26 | -0.07 | -0.15 | -0.13 | -0.26 | -0.08 | -0.22 | 0.13 | -0.14 | -0.2 | -0.28 | -0.28 | -0.41 | -0.14 | -0.2 | -0.02 | -0.32 | -0.4 | 38424.5 | 0 | 10916.4 | 0 | 0 | 0.02 | 0 | 0 | 1.04 | 0 | 0 | 4.4.0.0.0 | 4.4.0.1.1 | 4.4.0.0.0 | 4.5.3.0.0 | 4.4.0.1.6 | 4.4.4.15.6 | 4.7.1.0.0 | 4.4.0.3.12 | 4.5.2.0.0 | 4.4.0.4.12 | 4.4.0.1.0 | 4.5.1.0.0 | 4.4.0.1.0 | 4.4.0.0.0 | 4.4.0.0.4 | 4.4.0.5.6 | 4.4.0.5.0 | 4.4.0.0.2 | 4.4.0.0.0 | 4.4.0.0.2 | 4.4.0.2.12 | 4.3.0.0.0 | 0.0.0.0.0 | 4.4.0.4.11 | 4.4.1.0.0 | 4.4.0.0.12 | 4.4.0.1.0 | 4.3.0.0.0 | 4.4.0.3.3 | 4.9.0.0.0 | M03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1701 | 32.87 | 92 | 653.8 | 742 | 780 | 199 | 46 | 1 | 0 | 0 | 40 | 70 | 100 | 150 | 250 | 0 | 0 | 4179 | 0 | 12 | 80.39 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 31.66 | -1 | 2 | 1 | NaN | 0.0001 | 1607931998000 | 1 | 1 | 0.2893 | 1 | NaN | 3848 | 1 | 1607385600000 | NaN | NaN | NaN | 0.04 | 5.56 | 14 | NaN | 3 | 0.0009 | 1 | 1 | 1 | 3 | 0 | 0 | 2781 | 16 | 0.0311 | 1 | 1607761800000 | 4 | 1 | 3 | 2.1 | 4.5 | 1028109 | 1 | 1 | 9281 | 1 | 14.6 | 137 | 0.05 | 0.0401 | 5380 | 100 | 3 | 305 | Not Available | 60 |  |  |  |  | 8.58 | 2 | 2 |  | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 1 | 0 | 970 | 40 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 0 | 0 | 1 | 1 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 30 | 30 | 0 | 1.4 | 20 | 10 | 50 | 2 | 0 | 11 | 1 | 0 | 0 | 0 | 0 | 7 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 35 | [5 empty] | 0 | 0 | 1 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 200 | -1000 |  | -200 | -1700 | 10 | 0 | 50 | 1500 | 5.6 | 6.7 | 6.9 | 0.1 | 3 | 0.1 | 0 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 3.5 |  | 0 | 0 | 0.2 | 4.2 |  | 10 | 0 |  |  |  | 1 |  | 5 | 5 | 2.5 | 5 | 2.5 | 35 | 28 | 30 | 32 | 50 | 180 | 35 | 40 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 2 | 10 | 2 | 1 | 1 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 2 | 10 | 2 | 1 | 1 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 2 | 10 | [479 empty] | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 12000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 2 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 10 | 0 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 32 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 | 0.95 | 0 | 60 | -33 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | 85 | 110 | 90 | 95 | 100 | 105 | 0.85 | 0.9 | 0.95 | 1 | -0.97 | -0.95 | 0 | 0 | 1 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 1 | 40 | 0 | 30 | 30 | 10 | 10 | 10 | 3 | 1 | 10000 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 4 | 4 | 0.01 | 0.01 | 0.2 | 0.2 | 1 | 1.11 | 1 | 1.11 | 1 | 30 | 0 | 2 | 1 | 100 | 100 | 10 | 50 | 50 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 5000 | -5000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 51.5 | 47.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 1 | 115 | 85 | 35 | 10 | 0 | 0 | 1 | -0.2 | 50 | 110 | 80 | 1 | 0 | 323 | 200 | 1 | 200 | 10 | 10 | 0.8 | 3 | 4 | 10 | 0.5 | 4 | 20000 | 20 | 10 | 5 | 10000 | 0 | 0 | 0 | 0 | 20000 | 120 | 80 | 45 | 0 | 10 | 0 | 0 | 0 | -0.4 | 50 | 110 | 80 | 0 | 1 | 400 | 200 | 0 | 100 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 90 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 6 | 0 | 6000 | 0 | 100 | 50 | 60 | 500 | 100 | 460 | 0 | 0 | 0 | 50 | -40 | 0 | 0 | 0 | 1 | 0 | 5 | 30 | 30 | 50 | 490 | 490 | 300 | 30 | 100 | 0 |  | 1 | 0 | 0 | 1 | 1 | 0 | 0 |  | 1 |  | 0 |  |  |  | 1 | 1 |  |  |  | 1 | 1 | 0 | 1 |  | 1 | 1 | 1 |  | 1 | 1 | [8 empty] | 0 | 1 |  | 0 | 0 |  |  | 1 |  | 0 | 1 | 1 | 0 |  | 1 | 1 | 1 | 1 |  | 0 |  |  |  | 12.5 |  | 624 |  |  |  |  | 13 | 0 | 346 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.2 | 1 | 0.01 | 100 | 30 | 0 | 1 | 5.2 | 100 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 40 | 0 | 100 | 10 | 0 | 0 | -5 | 2 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 45 | 30 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 200 | 168 | 75 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 3 | 1 | 2 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 1 | 65 | 4 | 0 | 0 | 0 | -2.5 | 10 | 1 | 20 | 15 | 1 | 2 | 1 | 1.82 | 0.6 | 0.6 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0.1 | 0 | 0 | 0 | 15 | 30 | 0.01 | 0.4 | 0 | 60 | 30 | 0 | 0 | 0 | 0 | 1200 | 1400 | 0 | 0.5 | 450 | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 0.125 | 0.05 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 1 | 0 | 0.72 | 0.72 | 0.72 | 0.72 | 1.2 | 0.1 | 300 | 300 | 300 | 300 | 0 | 50 | 50 | 50 | 50 | 50 | 120 | 0 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.15 | 3.6621 | 25 | 2.9297 | 100 | 0 | 8 | 0.1 | 0.5 | 1 | 4 | 100 | 2 | 25 | 10 | 250 | 4 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 | 1 | 1 | 4000 | 2000 | 20000 | 10000 | 4500 | 2250 | 8 | 4 | 2 | 1 | 30 | 150 | 20 | 120 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 1 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 | 1.5 | 1 | 650 | 700 | 1 | 0 | 0 | 1 | [66 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 1 | 1 | 1200 | 38000 |  |  |  | 44800 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 100 | 1000 | 680 | 640 | 5 | 650 | 5 | 650 | 640 | 5 | 650 | 5 | 1000 | 5 | 15 | 300 | 20 | 50 | 650 | 3 | 125 | 5 | 1000 | 200 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | 0 | -0.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 20 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 10 | 20 | 5 | 10 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | 0 | 20 |  | 0.98 | 1 | -0.98 | -0.95 | 0.8 | -0.95 | 1 | 7 | 0.95 | -0.95 | 20 | 80 | 5590 | 88 | 90 | 2.01 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 0 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 85 | 90 | 85 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 43.9 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 35 | 300 |  | 75 | 0.97 | 1 | 1 | 1 | 180 | 0.1 | 1.11 | 60 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 930 | 0 | 5000 | 40 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 2250 | 4500 | 1 | 2 | 0 | 1 | 1 | 2 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 4 | 20 | 0.8 | -0.925 | 1 | 0 | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 400 | 0 | 0 | 0 | 0 | 1 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -100 | 100 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 1 | 1 | 0.8 | -0.92 | -3600 | 3600 | 10 | 0 | 100 | 0 | 100 | 0 | 800 | -20 | 800 | -20 | 600 | 0 | 10 | 3.3 | 0.2 | 3 | 0.05 | 1.5 | 1.9 | 0.05 | 0.05 | 87 | 5 | 94 | 2 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 30 |  |  | 20 |  |  |  | 3 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.4 | 0.1 | 0.5 | 500 | 1500 | 3.5 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1.5 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 75 | 2 | 79 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 1 | 0 | 95 | 120 | 2 | 2 | 0 | 1 | 0 | 74 | 120 | 2 | 2 | 1 | 62 | 2 | 1 |  | 74 | 120 | 0.5 | 0.5 | 0 | 1 | 0 | 140 | 140 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 82 | 0 | 0 | 0 | 5 | 20 | 0 | 2 | 30 | 90 | 0 | 0 | 0 | 200 | -200 | 0 | -70 | 100 | -100 | 0 | 0 | 0 | 200 | -200 | 20 | 30 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 9.5 | 10 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 10 | 0 | 0 | 1 | 90 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 18 | 18 | 18 | 18 | [5 empty] | 4 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 924 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 1 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 0 | 0 | 20 | 4000 | 4000 |  | 850 | 30 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 2 | 2 | 2 | 2 | -5 | -5 | -5 | -5 | 13 | 13 | 13 | 13 | 4.5 |  | 45 | 270 | 70 | -144 | 0 | 80 | 350 | [24 empty] | 0 | 4 | 500 | 30 |  | 2000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 380 | 1 | -30 | -9 | 4500 | 2250 | 10 | 4500 | 2250 | 60 | 0 | 0 | [6 empty] | 0.0007 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4523 | 2250 | 5920 | 2996 | 1499 | 1499 |  | 50.1 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4922 | 2159 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4922 | 2159 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4922 | 2159 | 1500 | 1500 |  | 50 | 50 |  | 660 |  | 0 | 1000 | 300 | 48 | -1.6 | -4 | 100 | 10 | 0 | 1 | 10 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 |  | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 10 | 0 | 0.5 | 0 | 0 | 60000 | 0 | 60000 | 0 |  | 5 | 0 | 1 | 1 |  |  |  | 80 |  | 45 | [14 empty] | 50 | 53 | 53 | 53 | [10 empty] | 0 | 0 | 1 | 3 | 55 | 57 | 2 | 2 | 60 |  | 45 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 350 | 200 | 200 | 100 | [8 empty] | -1250 | 5000 |  | 0.2 | 100 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.4 |  |  | 100 | 0.2 |  | 100 |  | 100 | 100 | [11 empty] | 0.2 | 100 | 200 | [43 empty] | 0 | 0.2 | 100 | 0.01 | 100 | 45 | 0 | 1 | 3.4 | 1 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 55 | 67 | 8 | 100 | 0 | 0 | 0.2 | 100 | 0.01 | 100 | 40 | 0 | 1 | 2 | 1 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 65 | 71 | 0 | 100 | 5 | 0 | 0.2 | 100 | 100 | 100 | 120 | 0 | 1 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 20 | 0.15 | 0.003 | 1 | 1 | 10 | 0.08 | 0 | 1 | 1.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1.1 | 0.7 | 1 | 0 | 100 | 0 | 0 | 0.1 | 100 | 0.02 | 100 | 60 | 0 | 1 | 7.2 | 1 | 1 | 1 | 1 | 0 | 0 | 140 | 100 | 127 | 0 | 100 | 0 | 0 | 0.3 | 0.5 | 0.01 | 100 | 100 | 0 | 1 | 6.5 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 45 | 0 | 100 | 15 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0.05 | 0.1 | 100 | 50 | 0 | 1 | 5.5 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 110 | 80 | 100 | 100 | 80 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | [42 empty] | 0 | 0.3 | 100 | 100 | 0 | 1 | 6.5 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 0 | 100 | 100 | 55 | 0 | 100 | 15 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 0 | 0 | 10 | 150 | 150 | 100 | 205 | 0 | 48 | 50 | 0 | 3000 | 6000 | 3000 | 6000 | 6 | 6 | 0 | 5000 | -5000 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 100 | 50 | 0 | 0.3 | 100 | 100 | 0 | 1 | 6.5 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 0 | 100 | 100 | 55 | 0 | 100 | 15 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 |  |  |  |  | 12 | 2 | 5 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 80 | 0 | [6 empty] | 0.01421 | 0.29619 | 0.88857 | 100 | 0 | 0 | 0.44428 | 0.23695 | 100 | 2 | 0 | 20 | 5000 | 5000 | 60 | 75 | 90 | 100 |  | 4 | 20 | 2250 | 4500 | 2.5 | 2 | 42 | 45 |  | -2 | -2 | -2 | -2 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -145 | 10 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 4500 | 4500 | 4500 | 4500 | 50 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 |  | 10 | 12 | 93 | 1 | 1 | 100.4 | 103.4 | 98 | 91 | 103.4 | 40 | 65 | 85 | 80 |  | 110 | 125 | 90 | 70 | 140 | 1 | 80 | 10 | 80 | 1 | 20 | 5.55 | 1 | 1 | 100 |  |  | 5 | 4 | 4 | 4 | 4 | 56 | 56 | 56 | 56 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 130 | 400 | 400 | 5000 | 2500 | 16 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 0.72 | 1200 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | [30 empty] | 1 | 1 | 1 | 35 | 10 | 0 | 0 | 5 | 20 | 20 | 5 | 0 | 0 | 1 | 110 | 80 | 0 | 89 | 110 | 0 | 1800 | 75 | 5 | 80 | 5 | 1 | 3150 | 180 | 280 | 110 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1650 | 10 | 200 | 400 | 2800 | 5 | 10000 | 0 | 3850 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 1 | 1200 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 800 |  | 0.16406 | 2.1973 | 4.3945 | 95 | 2 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1500 | 6.7 | 0 | 95 | 85 | 85 | 95 | 95 | 9.54 | 9.971 | 720 |  |  | 1.45 | 1.65 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.1 |  |  | 0.59 | [13 empty] | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | [28 empty] | 1 | 1 | 1 | 2 | 0 | 2 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  |  | 4500 | 0 | 0 | 0 | 0 | 0 | 4500 | 0 |  |  | 0.97 | 0.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | -43.24 | 4.003 | 0.052 | 0.68345 | 0 | 0.72 | 2250 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 596 | 0 | 0 | 264 | 0 | 0 | 27 | 0 | 0 | 903 | 0 | 303 | 0 | 0 | 14 | 300 | 68.57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 362 | 362 | 361 | 365 | 363 | 364 | 366 | 366 | 365 | 365 | 364 | 363 | 363 | 363 | 359 | 359 | 363 | 363 | 366 | 365 | 366 | 360 | 363 | 495 | 495 | 492 | 494 | 494 | 493 | 495 | 494 | 495 | 499 | 496 | 493 | 495 | 494 | 494 | 491 | 492 | 494 | 494 | 497 | 492 | 501 | 493 | 494 | 6150 | Sending | 30 | 46 | 46 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 46 | 47 | 46 | 46 | 46 | 46 | 47 | 47 | 46 | 47 | 46 | 25.9952 | 24.1118 | 25.0747 | 27.5682 | 29.6146 | 26.1951 | 26.8765 | 26.7862 | 27.8311 | 26.7619 | 23.8533 | 29.8577 | 23.0946 | 25.0063 | 23.9143 | 26.6963 | 23.8123 | 27.0905 | 27.2761 | 26.1871 | 27.2813 | 25.1076 | 28.3702 | 24.2135 | 2123 | 1594 | 761 | 1677 | 3722 | 2017 | 1559 | 1746 | 1772 | 2232 | 2019 | 1349 | 1592 | 1265 | 1803 | 1656 | 1623 | 1550 | 1861 | 2361 | 1045 | 2359 | 1788 | 2247 |  | 0 | 1 | [11 empty] | 32.1 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 958 | 0 | 0 | 0 | 29.4 | 0 | 0 | 0 | 1.45 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 | 0 | 7.66 | 0 | 7.74 | 0 | 7.77 | 0 | 7.63 | 0 | 7.54 | 0 | 7.67 | 0 | 7.72 | 0 | 7.8 | 0 | 7.73 | 0 | 7.81 | 0 | 7.63 | 0 | 7.87 | 0 | 7.68 | 0 | 7.71 | 0 | 7.93 | 0 | 7.6 | 0 | 7.64 | 0 | 7.64 | 0 | 7.55 | 0 | 7.69 | 0 | 7.74 | 0 | 7.8 | 0 | 7.69 | 0 | 7.82 | 0 | -0.07 | 0 | -0.02 | 0 | -0.31 | 0 | -0.46 | 0 | -0.18 | 0 | -0.26 | 0 | -0.16 | 0 | -0.03 | 0 | -0.2 | 0 | -0.39 | 0 | -0.28 | 0 | -0.13 | 0 | 0 | 0 | 0.07 | 0 | -0.23 | 0 | -0.07 | 0 | -0.21 | 0 | -0.32 | 0 | -0.32 | 0 | -0.19 | 0 | -0.12 | 0 | -0.06 | 0 | -0.21 | 0 | -0.08 | 0 | 7.8 | 0 | 7.73 | 0 | 7.64 | 0 | 7.99 | 0 | 7.54 | 0 | 7.61 | 0 | 7.96 | 0 | 7.85 | 0 | 7.81 | 0 | 7.83 | 0 | 7.75 | 0 | 8.07 | 0 | 7.76 | 0 | 7.68 | 0 | 7.76 | 0 | 7.61 | 0 | 7.64 | 0 | 7.5 | 0 | 7.59 | 0 | 7.84 | 0 | 7.83 | 0 | 7.89 | 0 | 7.59 | 0 | 7.81 | 0 | -0.07 | 0 | -0.1 | 0 | -0.28 | 0 | -0.27 | 0 | -0.31 | 0 | -0.06 | 0 | -0.26 | 0 | -0.07 | 0 | -0.15 | 0 | -0.13 | 0 | -0.26 | 0 | -0.08 | 0 | -0.22 | 0 | 0.13 | 0 | -0.14 | 0 | -0.2 | 0 | -0.28 | 0 | -0.28 | 0 | -0.41 | 0 | -0.14 | 0 | -0.2 | 0 | -0.02 | 0 | -0.32 | 0 | -0.4 |  | 0 | 1 | 0 | 0 | 19 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0.97 |  | 0 | 0 | 0 | 0 |  | 1.9 | 1.9 | 1.9 | 1.9 | 0 | 0 | 0 | 0 |  | 1500 | 0 |  | 52.7 |  |  | 0 | 0 | BMW LANDSHUT 4.10
19 |  | 46 | 1.007 | 0 | {"pendingUploads":"21/0","dataItemsValid":"true","edge":"true","rem_conn":"Prim-SSL-NoProxy","dataItems":"0/20","agent_conn":"Prim-SSL-NoProxy","mon_conn":"Back-NoSSL-NoProxy"} | 0 | 0 | 0 | 0 | 0 | 0 | -0.92 | 6.1 | 0 | 0 | 0 | -1432 | 0 | 6.69 | 0 | 4.66 | 4.6 | 21 | 0 |  |  |  | 0 | 0 | 0 | 0 | 4.94 | 0 | 4.94 | 0 | 0 | 0 | 4.4.0.13 | 3299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 |  | 19728 | 0 | 0 |  | 0 | -6072 | 0 | -2917 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 737 | 1737 | 2737 | 498639 | 598639 | 698639 | 798639 | 11165 | 11164 | 11164 |  | 267 |  | 55.2 | 65.3 | 60 | 70.5 | 84.2 | 71 | 70.7 | 0 | 21 | 21 | 20 | 0.819 | 0.989 | 50.4 | 97.8 | 97.8 | 0 | 55.2 | 55.2 | 0 | 90 | 90 | 0 | 100 | 97.8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [53 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 48 | 1 | 0 | 5.1 | 45.7 | 0 | 15.99 | 0 |  | 1361 |  |  |  |  | 0 | 0 | 0 | 0 | 41237 | 41355 | 34024 | 34106 | 0 | 0 | 0 | 0 | 566 | 567 | 566 | 569 | 568 | 569 | 569 | 571 | 570 | 567 | 568 | 569 | 575 | 574 | 576 | 575 | 580 | 573 | 574 | 576 | 580 | 575 | 578 | 574 | 572 | 572 | 580 | 580 | 566 | 566 | 0 | 0 | 138 | 357 | 358 | 14 | [42 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.5 | 49.6 |  |  | 70.7 | 68.8 | 70.1 | 24.1 |  |  |  |  | 37 | 1606634243136 |  | 4551 | 0.989 | 50 | 0 | 20558 | 11870 | 20544 | 11863 | 20550 | 11863 | 10448 | 6024 | 10447 | 6047 | 10446 | 6020 | 0 | 13508 | 4502 | 3 | 0.125 | 1900 | 2.31 | -50.6 | 3.97 | 0.97 |  | 0 | 90 | 76 | 0 | 70.5 | 70.7 | 70.7 | 11 | 0 | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 61.2 | 76.7 | 70.2 | 72.2 | 59 | 70.7 | 76.2 | 83.9 | 74.1 | 71 | 64.1 | 70.1 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 88 | 88 | 88 | 88 | 72 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 11214.4 | 11214.4 | 11214.5 | 11214.5 | 1361.1 | 9949.1 | 7285.3 | 11214.5 | 11214.3 | 11214.5 | 11214.5 | 11214.4 | 2017 | 2017 | 27 | 4 | 2017 | 27 | 4 | 2017 | 27 | 4 | 28 | 4 | 2019 | 15 | 11 | 2014 | 19 | 11 | 2016 | 25 | 10 | 2017 | 27 | 4 | 2017 | 27 | 4 | 2017 | 28 | 4 | 2017 | 28 | 4 | 2017 | 27 | 4 | 34184 | 34121 | 34128 | 34161 | 1276 | 19621 | 32097 | 34157 | 34160 | 34169 | 34172 | 34162 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0 | 0 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | 220 | 237 | 174 | 126 | 141 | 79 | 220 | 300 | 94 | 141 | 141 | 205 | 126 | 220 | 110 | 189 | 253 | 158 | 110 | 284 | 205 | 141 | 110 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 476 | 390 | 378 | 549 | 317 | 305 | 451 | 463 | 366 | 415 | 488 | 451 | 366 | 378 | 512 | 415 | 354 | 378 | 476 | 683 | 366 | 463 | 512 | -0.009 | 6.05 | 0 | 0 | 0 | 0 | 7.7 | 7.57 | 7.61 | 7.6 | 7.63 | 7.41 | 7.43 | 7.5 | 7.49 | 7.74 | 7.51 | 7.51 | 7.6 | 7.4 | 7.6 | 7.4 | 7.4 | 7.49 | 7.38 | 7.69 | 7.51 | 7.61 | 7.52 | 7.63 | -0.06 | -0.12 | -0.22 | -0.28 | -0.09 | -0.28 | -0.15 | -0.13 | 0.04 | -0.09 | -0.06 | 0.07 | -0.26 | -0.26 | -0.16 | -0.34 | -0.16 | -0.14 | -0.3 | -0.29 | -0.15 | -0.4 | -0.12 | -0.28 | 7.57 | 7.5 | 7.63 | 7.87 | 7.57 | 7.59 | 7.64 | 7.72 | 7.69 | 7.71 | 7.45 | 7.68 | 7.61 | 7.52 | 7.41 | 7.54 | 7.49 | 7.46 | 7.48 | 7.59 | 7.4 | 7.4 | 7.58 | 7.74 | -0.11 | -0.28 | -0.15 | -0.08 | -0.26 | -0.23 | -0.36 | -0.1 | -0.37 | -0.08 | -0.13 | -0.28 | -0.43 | -0.1 | -0.22 | -0.27 | -0.28 | -0.14 | -0.23 | -0.12 | -0.09 | -0.02 | -0.24 | -0.08 | 50188.8 | 0 | 6089.9 | 0 | 252 | 0.02 | 0 | 638 | 1.04 | 0 | 10452 | 4.4.0.0.0 | 4.4.0.0.1 | 4.4.0.0.0 | 4.4.1.0.10 | 4.4.0.0.10 | 4.4.4.3.8 | 4.7.1.0.0 | 4.4.0.0.12 | 4.4.2.0.8 | 4.4.0.0.12 | 4.4.0.0.0 | 4.4.0.0.8 | 4.4.0.0.0 | 4.4.0.0.0 | 4.4.0.0.9 | 4.4.0.2.10 | 4.4.0.0.0 | 4.4.0.0.2 | 4.4.0.0.0 | 4.4.0.0.2 | 4.4.0.0.12 | 4.3.0.0.0 | 0.0.0.0.0 | 4.4.0.0.11 | 4.4.1.0.0 | 4.4.0.0.13 | 4.4.0.0.9 | 4.3.0.0.0 | 4.4.0.0.6 | 4.4.0.0.0 | M01 | 20.6 | 21 | 19.2 | 22 | 19.3 | 23.3 | 20.1 | 21.3 | 21.5 | 20.9 | 22.7 | 24.3 | 21.7 | 18.7 | 17.9 | 18.3 | 19.8 | 20 | 21.1 | 20.8 | 19.7 | 20.2 | 19.5 | 23.2 | 18.5 | 24.3 | 17.9 | 1066 | [82 empty] | Running | 50 |  | 0 | 0 |  | 40.38 | 2 | 1 |  | 50 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 |  | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 100 | 0 | 1 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 1 | 0 | 970 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 2 | 2 | 1 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 30 | 30 | 0 | 1.4 | 20 | 1.5 | 80 | 4 | 4 | 11 | 3 | 0 | 0 | 0 | 0 | 7 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 30 | [5 empty] | 0 | 0 | 1 | 120 | 1 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 300 | -1200 |  | -200 | -1900 | 10 | 0 | 50 | 1500 | 5.6 | 6.7 | 6.9 | 0.1 | 2.7 | 0.1 | 1 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 3.6 |  | 0 | 0 | 0.2 | 0 |  | 10 | 0 |  |  |  | 0 |  | 5 | 5 | 5 | 5 | 5 | 60 | 28 | 40 | 30 | 50 | 180 | 28 | 40 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 1 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 1 | 1 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 100 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 4 | 0 | [479 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 17 | 17 | 17 | 17 | 18 | 18 | 18 | 18 | 10 | 0 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 32 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 | 0.95 | 0 | 60 | -27 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | 85 | 110 | 90 | 95 | 100 | 105 | 0.85 | 0.9 | 0.95 | 1 | -0.97 | -0.95 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 1 | 40 | 0 | 30 | 30 | 10 | 10 | 10 | 3 | 1 | 10500 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 1 | 2 | 4 | 0 | 0 | 0.2 | 0.2 | 1 | 0.56 | 0 | 0.56 | 0 | 30 | 0 | 0 | 0 | 100 | 100 | 0 | 50 | 50 | 1 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 15000 | -15000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 51.5 | 47.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 1 | 115 | 85 | 35 | 8 | 330 | 0 | 1 | -0.4 | 50 | 110 | 80 | 1 | 0 | 307 | 200 | 1 | 200 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 20000 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 20000 | 120 | 88 | 45 | 0 | 10 | 0 | 0 | 0 | -0.4 | 50 | 110 | 80 | 0 | 1 | 400 | 200 | 0 | 100 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 90 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 250 | 100 | 50 | 80 | 500 | 100 | 460 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 5 | 0 | 30 | 50 | 0 | 0 | 0 | 30 | 0 | 0 |  | 1 | 0 | 0 | 1 | 1 | 0 | 0 |  | 1 |  | 0 |  |  |  | 1 | 1 |  |  | 0 | 1 | 0 | 1 | 1 |  | 1 | 1 | 1 |  | 0 | 0 | [8 empty] | 0 | 1 |  | 0 | 0 |  |  | 1 |  | 0 | 0 | 1 | 1 |  | 1 | 1 | 1 | 1 |  | 0 |  |  |  | 11.5 |  | 624 |  |  |  |  | 11 | 0 | 365 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.5 | 0.1 | 0.1 | 100 | 75 | 0 | 0 | 5 | 100 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 30 | 50 | 90 | 0 | 0 | 0 | -5 | 15 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 35 | 30 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 191 | 146 | 33 | 50 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 65 | 1 | 0 | 0 | 0 | -2.5 | 10 | 0 | 20 | 15 | 0 | 2 | 1 | 1.82 | 0.6 | 0.6 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0 | 0 | 0 | 0 | 15 | 30 | 0.01 | 0.4 | 0 | 60 | 30 | 0 | 0 | 0 | 0 | 1200 | 1400 | 0 | 0.5 | 450 | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 0.2 | 0.05 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1.2 | 0.1 | 300 | 300 | 300 | 300 | 0 | 50 | 50 | 50 | 50 | 50 | 120 | 1 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 1 | 1 | 3 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.09375 | 3.6621 | 25 | 2.9297 | 100 | 0 | 10 | 0.1 | 0.5 | 1 | 7 | 100 | 0 | 25 | 10 | 250 | 4 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 | 0 | 0 | 4000 | 2000 | 20000 | 10000 | 0 | 0 | 0 | 0 | 2 | 1 | 30 | 150 | 20 | 120 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 0 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | 0 | 100 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 | 1.5 | 1 | 650 | 700 | 0 | 0 | 0 | 0 | [66 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 1 | 1 | 1200 | 38000 |  |  |  | 44800 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 100 | 1000 | 680 | 640 | 5 | 650 | 5 | 650 | 640 | 5 | 650 | 5 | 1000 | 5 | 15 | 300 | 20 | 50 | 650 | 5 | 200 | 5 | 1000 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 20 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 10 | 20 | 5 | 0 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | 0 | 20 |  | 0.98 | 1 | -0.98 | -0.95 | 0.8 | -0.95 | 0.99 | 5 | 0.95 | -0.95 | 20 | 80 | 5592 | 88 | 90 | 1.84 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 0 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 85 | 90 | 85 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 45 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 45 | 300 |  | 75 | 0.94 | 0 | 0 | 0 | 60 | 0.1 | 1.11 | 60 | 1 | 90 | 80 | 70 | 60 | 55 | 0 | 20 | 0 | 5000 | 0 | 5000 | 50 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 2250 | 4499 | 1 | 0 | 0 | 0 | 1 | 1 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 0 | 20 | 0.8 | -0.95 | 1 | 0 | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 10500 | 0 | 0 | 0 | 0 | 2 | 1000 | 500 | 250 | -250 | -500 | 4 | 20 | -4000 | 4000 | 0 | 1 | 4 | 20 | -9999 | 9999 | 0 | 0 | 0 | 1 | -0.9 | -100 | 100 | 10 | 0 | 100 | 0 | 100 | 0 | 800 | -20 | 800 | -20 | 0 | 0 | 10 | 3.3 | 0.2 | 3.1 | 0.05 | 1.5 | 1.7 | 0.05 | 0.05 | 120 | 5 | 120 | 5 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 30 |  |  | 20 |  |  |  | 3 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.6 | 0.2 | 0.5 | 500 | 1500 | 3.5 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1.5 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 120 | 2 | 120 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 1 | 0 | 76 | 120 | 2 | 2 | 0 | 1 | 0 | 76 | 120 | 2 | 2 | 1 | 58 | 2 | 1 |  | 75 | 120 | 0.5 | 0.5 | 0 | 1 | 0 | 99 | 200 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 82 | 0 | 0 | 0 | 5 | 20 | 0 | 2 | 30 | 90 | 0 | 0 | 0 | 200 | -200 | 0 | -60 | 100 | -100 | 0 | 0 | 0 | 200 | -200 | 20 | 30 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 9.5 | 10 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 10 | 0 | 0 | 1 | 90 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 18 | 18 | 18 | 18 | [5 empty] | 4 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 924 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 1 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 0 | 0 | 20 | 4000 | 4000 |  | 850 | 30 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 5 | 5 | 5 | 5 | -5 | -5 | -5 | -5 | 13 | 13 | 13 | 13 | 4.5 |  | 45 | 270 | 70 | -144 | 0 | 80 | 350 | [24 empty] | 0 | 4 | 500 | 30 |  | 2000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 380 | 1 | -30 | -9 | 4300 | 1300 | 10 | 4300 | 2600 | 60 | 0 | 0 | [6 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4499 | 2249 | 6080 | 3100 | 1498 | 1499 |  | 55.5 | 54.5 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4900 | 2150 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4900 | 2150 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4900 | 2150 | 1500 | 1500 |  | 50 | 50 |  | 660 |  | 0 | 1000 | 300 | 48 | -1.6 | -4 | 100 | 10 | 0 | 1 | 10 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 |  | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 10 | 0 | 0.5 | 0 | 0 | 60000 | 0 | 60000 | 0 |  | 4 | 0 | 1 | 1 |  |  |  | 80 |  | 40 | [14 empty] | 55 | 55 | 55 | 55 | [10 empty] | 0 | 0 | 1 | 3 | 57 | 59 | 2 | 2 | 62 |  | 50 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.4 |  |  | 100 | 0.2 |  | 394 | 200 | 193 | 105 | [8 empty] | -1250 | 5000 |  | 0.2 | 100 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.4 |  |  | 100 | 0.2 |  | 100 |  | 100 | 100 | [11 empty] | 0.2 | 100 | 200 | [43 empty] | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 75 | 60 | 70 | 50 | 100 | 0 | 0.1 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 2.5 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 65 | 71 | 50 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 27 | 20 | 100 | 20 | 1.5 | 0.003 | 1 | 1 | 10 | 0.35 | 0 | 1 | 4 | 1 | 1 | 1 | 1 | 0 | 0 | 1.1 | 0.7 | 1 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | 0 | 0.1 | 0.5 | 0.5 | 100 | 40 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 50 | 0 | 100 | 10 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0 | 0.1 | 100 | 205 | 0 | 1 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 102 | 0 | 100 | 100 | 100 | 0 | 100 | 5 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | [42 empty] | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 20 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 0 | 0 | 10 | 150 | 150 | 100 | 205 | 0 | 48 | 50 | 0 | 3000 | 6000 | 3000 | 6000 | 6 | 6 | 0 | 5000 | -5000 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 100 | 50 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  |  | 1 | 0 |  |  |  |  | 12 | 2 | 5 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 80 | 0 | [6 empty] | 0.01421 | 0.29619 | 0.88857 | 100 | 0 | 0 | 0.44428 | 0.23695 | 100 | 0 | 0 | 20 | 5000 | 5000 | 60 | 75 | 90 | 100 |  | 0 | 20 | 2250 | 4499 | 2.5 | 2 | 35 | 45 |  | -2 | -2 | -2 | -2 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -145 | 10 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 4499 | 4499 | 4499 | 4499 | 50 | 0.58 | 0.58 | 0.58 | 0.58 | 0.2 | 0.58 | 0.58 | 0.58 |  | 10 | 6 | 95 | 1 | 1 | 101 | 105.8 | 98 | 91 | 105.8 | 50 | 65 | 85 | 75 |  | 110 | 120 | 95 | 70 | 140 | 0 | 80 | 6 | 81.5 | 1 | 19 | 5.75 | 3 | 6 | 78 |  |  | 10 | 4 | 4 | 4 | 4 | 58 | 58 | 58 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [30 empty] | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1650 | 10 | 200 | 400 | 2800 | 5 | 10000 | 0 | 3850 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 0 | 1500 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 800 |  | 0.16406 | 2.1973 | 4.3945 | 100 | 0 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1500 | 6.7 | 0 | 95 | 85 | 85 | 95 | 95 | 9.54 | 9.971 | 720 |  |  | 1.35 | 1.55 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.1 |  |  | 0.59 | [13 empty] | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | [28 empty] | 1 | 1 | 1 | 2 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4504 |  |  | 4499 | 0 | 0 | 0 | 0 | 0 | 4499 | 4257 |  |  | 2.92 | 2.91 | 0 | 0 | 0 | 0 | 0 | 0 | 1273.7 | 21.3 | -50.32 | 3.975 | 0.079 | 0.96555 | 0 | 0.2 | 4499 | 0 | 0 | 2.18 | 1 | 0 | 1 | 0 | 0 | 470 | 0 | 0 | 262 | 0 | 0 | 32 | 0 | 0 | 769 | 769 | 298 | 0 | 0 | 3 | 0 | 69.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 366 | 366 | 367 | 373 | 367 | 366 | 369 | 367 | 368 | 370 | 367 | 366 | 368 | 368 | 364 | 367 | 366 | 367 | 367 | 369 | 368 | 366 | 368 | 495 | 493 | 498 | 495 | 494 | 495 | 496 | 495 | 496 | 495 | 495 | 495 | 495 | 496 | 495 | 494 | 491 | 495 | 493 | 495 | 495 | 496 | 495 | 497 |  | Sending | 30 | 46 | 47 | 44 | 45 | 47 | 46 | 46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [24 empty] | 1426 | 994 | 2722 | 992 | 1051 | 3008 | 1424 | 2864 | 2865 | 1305 | 1136 | 1427 | 1172 | 1217 | 1171 | 964 | 3008 | 1431 | 2911 | 3150 | 3055 | 1058 | 1224 | 1181 |  | 0 | 1 | [11 empty] | 72.4 | 72.4 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 273.2 | 0 | 0 | 0 | 1134 | 0 | 0 | 0 | 23.4 | 0 | 0 | 0 | 1.954 |  |  |  | 23.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 | 11027 | 1 | 11027 | 1 | 11027 | 1 | 11027 | 1 | 11027 | 1 | 11027 | 1 | 11027 | 1 | 11027 | 1 | 11027 | 1 | 11027 | 1 | 11027 | 1 | 11027 | 1 | 11027 | 1 | 11027 | 1 | 11027 | 1 | 11027 | 1 | 11027 | 1 | 11027 | 1 | 11027 | 1 | 11027 | 1 | 11027 | 1 | 11027 | 1 | 11027 | 1 | 11027 | 1 | 0 | 7.7 | 0 | 7.57 | 0 | 7.61 | 0 | 7.6 | 0 | 7.63 | 0 | 7.41 | 0 | 7.43 | 0 | 7.5 | 0 | 7.49 | 0 | 7.74 | 0 | 7.51 | 0 | 7.51 | 0 | 7.6 | 0 | 7.4 | 0 | 7.6 | 0 | 7.4 | 0 | 7.4 | 0 | 7.49 | 0 | 7.38 | 0 | 7.69 | 0 | 7.51 | 0 | 7.61 | 0 | 7.52 | 0 | 7.63 | 0 | -0.06 | 0 | -0.12 | 0 | -0.22 | 0 | -0.28 | 0 | -0.09 | 0 | -0.28 | 0 | -0.15 | 0 | -0.13 | 0 | 0.04 | 0 | -0.09 | 0 | -0.06 | 0 | 0.07 | 0 | -0.26 | 0 | -0.26 | 0 | -0.16 | 0 | -0.34 | 0 | -0.16 | 0 | -0.14 | 0 | -0.3 | 0 | -0.29 | 0 | -0.15 | 0 | -0.4 | 0 | -0.12 | 0 | -0.28 | 0 | 7.57 | 0 | 7.5 | 0 | 7.63 | 0 | 7.87 | 0 | 7.57 | 0 | 7.59 | 0 | 7.64 | 0 | 7.72 | 0 | 7.69 | 0 | 7.71 | 0 | 7.45 | 0 | 7.68 | 0 | 7.61 | 0 | 7.52 | 0 | 7.41 | 0 | 7.54 | 0 | 7.49 | 0 | 7.46 | 0 | 7.48 | 0 | 7.59 | 0 | 7.4 | 0 | 7.4 | 0 | 7.58 | 0 | 7.74 | 0 | -0.11 | 0 | -0.28 | 0 | -0.15 | 0 | -0.08 | 0 | -0.26 | 0 | -0.23 | 0 | -0.36 | 0 | -0.1 | 0 | -0.37 | 0 | -0.08 | 0 | -0.13 | 0 | -0.28 | 0 | -0.43 | 0 | -0.1 | 0 | -0.22 | 0 | -0.27 | 0 | -0.28 | 0 | -0.14 | 0 | -0.23 | 0 | -0.12 | 0 | -0.09 | 0 | -0.02 | 0 | -0.24 | 0 | -0.08 |  | 0 | 1 | 1 | 1 | 12 | 0 | 100 | 99 | 100 | 0 | 0 | 16.6 | 16.2 | 0 | 16.1 | 0 | 0 | 0 | 6.04 |  | 0 | 0 | 0 | 0 |  | 100 | 86.8 | 25.3 | 86.8 | 16.6 | 16.6 | 16.6 | 16.6 |  | 1500 | 1499 |  | 55.2 |  |  | 0 | 0 | LES COURONNERIES
20 |  | 44 | 1 | 0 | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","rem_conn":"Back-NoSSL-NoProxy","dataItems":"4802/9426","agent_conn":"Prim-NoSSL-NoProxy","mon_conn":"Back-NoSSL-NoProxy"} | 0 | 0 | 0 | 0 | 0 | 0 | -0.92 | 4.59 | 0 | 0 | 0 | -495 | 0 | 6.78 | 0 | 3.44 | 4.2 | 18.1 | 0 |  |  |  | 0 | 0 | 0 | 0 | 4.48 | 0 | 4.47 | 0 | 0 | 0 | 4.4.0.7 | 6561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | -4754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.02 |  |  |  |  | 0 | 0 | 0 | 25732 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 178 | 1370 | 2460 | 494122 | 594122 | 694122 | 794122 | 5878 | 5885 | 5885 |  | 119 |  | 49.3 | 0 | 70 | 68.9 | 100 | 70 | 0 | 0 | 20 | 18.1 | 0 | 0.957 | 0.962 | 51.8 | 85 | 0 | 100 | 49.3 | 49.3 | 0 | 86.3 | 86.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [53 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [99 empty] | 39.9917 | 40.0067 | [27 empty] | 0 | 0 | 0 | 0 |  | 0 | [10 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 |  |  |  | 0 |  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1608925274661 | 0 | 48 | 1 |  | 0 | 0 |  | 37.41 | 0 |  | 5878 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3276 | 560 | 559 | 555 | 558 | 560 | 561 | 563 | 560 | 565 | 561 | 562 | 560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 561 | 565 | 566 | 555 | 556 | 0 | 373 | 3276 | 0 | 0 | 10 | [42 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.3 | 37.9 |  |  | 84 | 83.2 | 82.5 | 38.2 |  |  |  |  | 3 | 1606308361547 |  | 2115 | 0.962 | 50.01 | 0 | 20310 | 11682 | 20378 | 11808 | 20289 | 11713 | 408 | 235 | 407 | 236 | 407 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 2.22 | -22.5 | 4.07 | 0.4 |  | 0 | 86.3 | 74.6 | 0 | 68.9 | 0 | 68.9 | 5 | 0 | 0 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 57.6 | 65.2 | 61.7 | 66.3 | 74.2 | 0 | 0 | 0 | 1.26 | 0 | 0 | 0 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 88 | 88 | 88 | 88 | 88 | 0 | 0 | 0 | 5888.2 | 0 | 0 | 0 | 5888.2 | 5888.2 | 5888.2 | 5888.2 | 5888.2 | 0 | 0 | 0 | 2017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 9 | 2017 | 7 | 9 | 2017 | 5 | 9 | 2017 | 29 | 8 | 2017 | 29 | 8 | 2017 | 5 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36046 | 0 | 0 | 0 | 36194 | 36110 | 35987 | 36022 | 36108 | 0 | 0 | 0 | 7.73 | 0 | 0 | 0 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 0 | 0 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | -10.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 158 | 141 | 220 | 141 | 110 | 79 | 110 | 237 | 126 | 79 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1196 | 622 | 671 | 2002 | 1355 | 2759 | 610 | 659 | 671 | 415 | 647 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.017 | 4.73 | 0 | 5 | 0 | 0 | 8.1 | 7.77 | 7.88 | 7.8 | 7.79 | 7.79 | 7.96 | 7.9 | 8.08 | 7.79 | 7.79 | 7.77 | [12 empty] | 0.27 | -0.24 | 0.11 | -0.45 | 0.1 | -0.48 | -0.01 | -0.26 | -0.29 | -0.32 | -0.3 | -0.19 | [12 empty] | 8.09 | 8.09 | 8.09 | 7.96 | 7.79 | 8.04 | 8.01 | 7.77 | 7.95 | 7.79 | 7.79 | 7.79 | [12 empty] | -0.09 | -0.15 | -0.42 | -0.35 | -0.32 | -0.16 | -0.09 | -0.23 | -0.23 | -0.21 | -0.35 | -0.1 | [12 empty] | 11922.3 | 0 | 3731 | 0 | 2967 | 0.02 | 0 | 570 | 1.04 | 0 | 407 | 4.4.0.0.0 | 4.4.0.0.1 | 4.4.0.0.0 | 4.4.0.0.0 | 4.4.0.0.0 | 4.4.4.1.4 | 4.4.0.0.0 | 4.4.0.0.7 | 4.4.0.0.0 | 4.4.0.0.7 | 4.4.0.0.0 | 4.4.0.0.0 | 4.4.0.0.0 | 4.4.0.0.0 | 4.4.0.0.4 | 4.4.0.1.0 | 4.4.0.0.0 | 4.4.0.0.2 | 4.4.0.0.0 | 4.4.0.0.2 | 4.4.0.0.2 | 4.3.0.0.0 | 0.0.0.0.0 | 4.4.0.0.0 | 4.4.1.0.0 | 4.4.0.0.0 | 4.4.0.0.7 | 4.3.0.0.0 | 4.4.0.0.3 | 4.4.0.0.0 | M01 | 18.5 | 18.8 | 18.6 | 18.4 | 19.3 | 17.8 | 17.9 | 18 | 17.3 | 18.6 | 19.6 | 18.9 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6 | 17.3 | 2000 | [82 empty] | Running | 50 |  |  |  |  | 46.6 | 2 | 2 | 0 | 50.01 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 0 | 0 | 970 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 2 | 1 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 30 | 30 | 0 | 1.4 | 20 | 1.5 | 80 | 2 | 0 | 10 | 3 | 0 | 0 | 0 | 0 | 7 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 25 | [5 empty] | 0 | 0 | 0 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 200 | -300 |  | -100 | -700 | 6 | 0 | 50 | 1500 | 3 | 3.7 | 3.9 | 0.1 | 2.7 | 0.1 | 0 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 4.2 |  | 0 | 0 | 0 | 0 |  | 10 | 0 |  |  |  | 0 |  | 5 | 5 | 5 | 5 | 5 | 60 | 28 | 40 | 30 | 50 | 180 | 28 | 40 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 10 | 10 | 2 | 0 | 0 | 1 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 10 | 10 | 2 | 0 | 0 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 4 | 0 | [479 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 10 | 0 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 35 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 | 0.95 | 0 | 60 | -27 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | 85 | 110 | 90 | 95 | 100 | 105 | 0.85 | 0.9 | 0.95 | 1 | -0.97 | -0.95 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 1 | 40 | 0 | 30 | 30 | 10 | 10 | 10 | 3 | 1 | 415 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 4 | 4 | 0.01 | 0.01 | 0.2 | 0.2 | 1 | 0 | 1 | 0 | 1 | 30 | 0 | 0 | 0 | 100 | 100 | 10 | 50 | 50 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 5000 | -5000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 51.5 | 47.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 1 | 115 | 85 | 35 | 8 | 330 | 0 | 1 | -0.35 | 50 | 110 | 80 | 1 | 0 | 3622 | 200 | 1 | 200 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 20000 | 20 | 10 | 3 | 400 | 1 | 0 | 1 | 1 | 20000 | 120 | 88 | 45 | 0 | 10 | 0 | 0 | 0 | -0.4 | 50 | 110 | 80 | 0 | 0 | 400 | 200 | 0 | 100 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 90 | 45 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [8 empty] | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  |  |  | 1 | 0 |  |  | 0 | 0 | 0 | 1 | 1 |  | 0 | 0 | 0 |  | 0 | 0 | [8 empty] | 0 | 1 |  | 0 | 0 |  |  | 1 |  | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 1 |  | 612 |  |  |  |  | 1 | 0 | 177 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.5 | 0.1 | 0.1 | 100 | 41 | 0 | 0 | 1 | 100 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 30 | 0 | 100 | 0 | 0 | 0 | -5 | 15 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 33 | 30 | 0 | 0 | 9600 | 2 | 1 | 111 | 1 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 31 | 168 | 2 | 502 | 11 | 255 | 0 | 255 | 0 | 1 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 65 | 1 | 0 | 0 | 0 | -4.5 | 10 | 0 | 60 | 55 | 0 | 2 | 1.65 | 1.82 | 0.6 | 0.6 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 0.39062 | 0.07812 | 100 | 0 | 0 | 0.39062 | 0.07812 | 100 | 0 | 0 | 0.39062 | 0.07812 | 100 | 0 | 0 | 0.39062 | 0.07812 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0 | 0 | 0 | 0 | 15 | 30 | 0.01 | 0.4 | 0 | 60 | 30 | 0.3 | 0 | 0 | 0 | 1200 | 1400 | 1 | 0.5 | 360 | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 0.3 | 0.1 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 0.2 | 300 | 300 | 300 | 300 | 0 | 50 | 50 | 50 | 50 | 50 | 120 | 1 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 0 | 1 | 3 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.3 | 1 | 25 | 6.5 | 100 | 0 | 20 | 0 | 0.5 | 0 | 4 | 50 | 0 | 25 | 10 | 250 | 3 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 0 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | 0 | 100 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 5 | 7 | 8.5 | 10 | 12 | 13.5 | 15.3 | 25 | 25 | 60 | 0 | 30 | 0 | 1 | 6 | 0.8 | 6 | 0 | 3.5 | 1 | 6 | 0 | 10 | 92 | 0 | 8000 | 0 | 0 | 540 | 27 | 1000 | 0 | 0 | 1 | 300 | 0 | 300 | 0 | 3 | 300 | 0 | 150 | 8.2 | 7.5 | 180 | 90 | 900 | 30 | 200 | 300 | 40 | 20 | 100 | 0 | 100 | 0 | 0 | 300 | 500 | 600 | 0 | 500 | 600 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 1200 | 1000 |  |  |  | 1000 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 50 | 1000 | 680 | 640 | 5 | 650 | 5 | 1000 | 640 | 5 | 680 | 5 | 1000 | 5 | 15 | 300 | 20 | 50 | 650 | 5 | 120 | 5 | 450 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | -0.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 20 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 20 | 5 | 10 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | 4 | 20 |  | 0.98 | 1 | -0.98 | -0.95 | 0.8 | -0.95 | 1 | 4 | 0.95 | -0.95 | 20 | 80 | 2509 | 88 | 90 | 2.43 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 0 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 85 | 90 | 85 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 59.9 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 45 | 300 |  | 75 | 1.3 | 0 | 0 | 0 | 180 | 0.1 | 0 | 60 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 930 | 0 | 5000 | 50 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 500 | 1000 | 1 | 0 | 0 | 0 | 1 | 1 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 0 | 20 | 0.8 | -0.95 | 1 | 0 | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 400 | 0 | 0 | 0 | 0 | 1 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -100 | 100 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 0 | 0 | 1 | -0.9 | -100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 2.5 | 0.2 | 3.1 | 0.05 | 1.5 | 1.8 | 0.05 | 0.05 | 120 | 5 | 120 | 5 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 30 |  |  | 20 |  |  |  | 3 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.5 | 0.1 | 0.5 | 500 | 1500 | 4.6 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1.5 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 120 | 2 | 120 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 1 | 0 | 74 | 75 | 2 | 0.5 | 0 | 0 | 0 | 120 | 120 | 2 | 2 | 0 | 62 | 2 | 1 |  | 75 | 120 | 2 | 0.5 | 0 | 0 | 0 | 200 | 200 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 82 | 0 | 0 | 0 | 5 | 20 | 0 | 2 | 30 | 90 | 0 | 0 | 0 | 200 | -200 | -1 | -50 | 100 | -100 | 0 | 0 | 0 | 200 | -200 | 20 | 30 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 9.5 | 10 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 1 | 1 | 90 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 18 | 18 | 18 | 18 | [5 empty] | 15 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 462 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 1 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 4 | 0 | 20 | 4000 | 4000 |  | 400 | 20 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 2 | 2 | 2 | 2 | -5 | -5 | -5 | -5 | 14 | 14 | 14 | 14 | 4.5 |  | 45 | 660 | 660 | -144 | 0 | 60 | 50 | [24 empty] | 0 | 4 | 500 | 30 |  | 8000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 190 | 0 | -24 | -13 | 1630 | 960 | 10 | 1630 | 960 | 60 | 0 | 0 | [6 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2029 | 1017 | 4715 | 2302 | 1499 | 1499 |  | 49.3 | 42.9 |  | 300 | [7 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 1640 | 820 | 2850 | 1500 | 1500 | 1500 |  | 45 | 43 |  | 300 | [7 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 1640 | 820 | 2850 | 1500 | 1500 | 1500 |  | 45 | 43 |  | 300 | [7 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 1640 | 820 | 2850 | 1500 | 1500 | 1500 |  | 45 | 43 |  | 300 |  | 0 | 1000 | 300 | 48 | -1.6 | -4 | 100 | 6 | 0 | 1 | 6 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6 | 0 | 0.5 | 0 | 0 | 120000 | 0 | 120000 | 0 |  | 4 | 0 | 0 | 0 |  |  |  | 75 |  | 40 | [14 empty] | 55 | 55 | 55 | 55 | [10 empty] | 0 | 0 | 1 | 3 | 47 | 49 | 2 | 2 | 62 |  | 45 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.35 |  |  | 100 | 0.2 |  | 4000 | 51.19 | 200 | 1 | [8 empty] | -575 | 2300 |  | 0.2 | 73 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.4 |  |  | 100 | 0.2 |  | 100 |  | 100 | 100 | [11 empty] | 0.2 | 100 | 200 | [43 empty] | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 75 | 70 | 73 | 100 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 75 | 70 | 73 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 1.5 | 0.001 | 1 | 1 | 10 | 0.6 | 0 | 1 | 12 | 1 | 1 | 1 | 1 | 0 | 0 | 1.1 | 0.7 | 1 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | 0 | 0.1 | 0.5 | 0.5 | 100 | 40 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 50 | 0 | 100 | 10 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | 0 | 0.2 | 1 | 1 | 5 | 50 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 7 | 0 | 100 | -100 | 0 | 0.1 | 5 | 5 | 10 | 10 | 0 | 0 | 2 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 0 | 15 | 0 | 100 | -100 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 0 | 0 | 10 | 150 | 150 | 100 | 205 | 0 | 48 | 50 | 0 | 3000 | 6000 | 3000 | 6000 | 6 | 6 | 0 | 5000 | -5000 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 100 | 50 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  |  |  |  | 12 | 2 | 5 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 80 | 0 | [6 empty] | 0.09478 | 0.44429 | 1.1848 | 100 | 0 | 0.02843 | 0.74047 | 0.4739 | 100 | 0 | 4 | 20 | 1013 | 2025 | 60 | 75 | 90 | 100 |  | 4 | 20 | 1014 | 2029 | 2 | 2 | 35 | 45 |  | -6 | -6 | -6 | -6 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -90 | 6 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 2029 | 2026 | 2026 | 2026 | 50 | 0.53 | 0.53 | 0.53 | 0.53 | 0.48 | 0.53 | 0.53 | 0.53 |  | 10 | 5 | 95 | 1 | 1 | 101 | 105.8 | 98 | 91 | 105.8 | 50 | 65 | 85 | 75 |  | 105 | 120 | 95 | 70 | 140 | 0 | 80 | 5 | 82 | 1 | 25 | 3.55 | 3 | 5 | 74 |  |  | 10 | 4 | 4 | 4 | 4 | 58 | 58 | 58 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [30 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1450 | 10 | 200 | 400 | 2800 | 5 | 400 | 0 | 3450 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 0 | 1500 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 900 |  | 0.15 | 0.64 | 7.7 | 80 | 0 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1500 | 6.7 | 0 | 95 | 85 | 85 | 95 | 95 | 9.54 | 9.971 | 720 |  |  | 1.57 | 1.87 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.1 |  |  | 0.74 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [28 empty] | 1 | 1 | 1 | 2 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2034 |  |  | 2029 | 0 | 0 | 0 | 0 | 0 | 2029 | 2027 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 301.8 | 23 | -22.84 | 4.058 |  | 0.39827 | 0 | 0.48 | 2027 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 163 | 197 | 142 | 125 | 73 | 27 | 27 | 27 | 397 | 393 | 325 | 0 | 124 | 73 | 75 | 25 | 0 | 65.21 | [73 empty] | Sending | 30 | 44 | 44 | 45 | 46 | 42 | 44 | 43 | 45 | 41 | 44 | 45 | 48 | 48 | 43 | 42 | 43 | 42 | 43 | 47 | 44 | 21 | 23.2 | 24.8 | 24.4 | 26.5 | 23.1 | 21.9 | 23.35 | 22.8 | 28 | 25.8 | 22.6 | [12 empty] | 1092 | 1264 | 1230 | 1143 | 1266 | 1238 | 1442 | 1659 | 1108 | 3151 | 1141 | 1081 | [13 empty] | 52 | 1 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 117.7 | 0 | 0 | 0 | 1161 | 0 | 0 | 0 | 17.4 | 0 | 0 | 0 | 2.018 |  |  |  | 38.7 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 | [24 empty] | 0 | 8.1 | 0 | 7.77 | 0 | 7.88 | 0 | 7.8 | 0 | 7.79 | 0 | 7.79 | 0 | 7.96 | 0 | 7.9 | 0 | 8.08 | 0 | 7.79 | 0 | 7.79 | 0 | 7.77 | [24 empty] | 0 | 0.27 | 0 | -0.24 | 0 | 0.11 | 0 | -0.45 | 0 | 0.1 | 0 | -0.48 | 0 | -0.01 | 0 | -0.26 | 0 | -0.29 | 0 | -0.32 | 0 | -0.3 | 0 | -0.19 | [24 empty] | 0 | 8.09 | 0 | 8.09 | 0 | 8.09 | 0 | 7.96 | 0 | 7.79 | 0 | 8.04 | 0 | 8.01 | 0 | 7.77 | 0 | 7.95 | 0 | 7.79 | 0 | 7.79 | 0 | 7.79 | [24 empty] | 0 | -0.09 | 0 | -0.15 | 0 | -0.42 | 0 | -0.35 | 0 | -0.32 | 0 | -0.16 | 0 | -0.09 | 0 | -0.23 | 0 | -0.23 | 0 | -0.21 | 0 | -0.35 | 0 | -0.1 | [25 empty] | 0 | 0 | 1 | 1 | 17 | 0 | 100 | 0 | 0 | 0 | 0 | 36.5 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7 |  | 0 | 0 | 0 | 0 |  | 100 | 100 | 100 | 100 | 36.5 | 36.5 | 36.5 | 36.5 |  | 1500 | 1499 |  | 49.3 |  |  | 0 | 0 | DALOMA
21 |  |  |  |  | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","rem_conn":"Prim-NoSSL-NoProxy","dataItems":"4802/12594","agent_conn":"Back-SSL-NoProxy","mon_conn":"Prim-NoSSL-NoProxy"} | 0 | 0 | 0 | 0 | 0 | 0 | -0.95 | 4.65 | 0 | 0 | 0 | -500 | 0 | 5.73 | 0 | 3.48 | 4.29 | 8 | 1001 |  |  |  | 0 | 0 | 0 | 0 | 4.69 | 0 | 4.7 | 0 | 0 | 0 | 4.4.0.8 | 3621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 |  |  | 0 | 0 |  | -10 | 14 | 45 | 0 | -70.6 | 0 | 0 | 4.83 | 4.88 | 0 | -65.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0.04 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 438 | 99187 | 456 | 417 | 591300 | 691300 | 791300 | 8792 | 8787 | 8787 |  | 126 |  | 55.5 | 79.9 | 66 | 84 | 100 | 71.5 | 72.2 | 44 | 20 | 8 | 0 | 1 | 1 | 49.9 | 93.2 | 93.2 | 0 | 55.5 | 55.5 | 0 | 88.3 | 88.3 | 0 | 95 | 93.2 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [53 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [131 empty] | 0 | [12 empty] | 0 | 0 |  |  | 0 | 0 |  | 0 |  | 0 | [20 empty] | 0 | [16 empty] | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 1608926541599 | 0 | 40 | 1 |  | 0 | 0 |  | 28.37 | 0 |  | 8700 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3276 | 526 | 520 | 525 | 530 | 531 | 525 | 530 | 527 | 531 | 522 | 530 | 527 | 529 | 529 | 529 | 528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 527 | 527 | 531 | 531 | 520 | 520 | 0 | 346 | 3276 | 0 | 0 | 11 | [42 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.3 | 19.6 |  |  | 70.7 | 70.4 | 67.6 | 27 |  |  |  |  | 5 | 1606645134461 |  | 2680 | -0.999 | 49.99 | 0 | 5618 | 3243 | 5600 | 3240 | 5602 | 3228 | 5620 | 3244 | 5602 | 3241 | 5599 | 3229 | 0 | 0 | 0 | 0 | 0 | 0 | 2.08 | -26.8 | 3.98 | 0.71 |  | 0 | 88.3 | 78.5 | 0 | 84 | 72.2 | 72.1 | 11 | 0 | 0 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.2 | 0 | 0 | 0 | 58.7 | 58.2 | 66.2 | 55.7 | 61.5 | 67 | 72.2 | 0 | 1.24 | 0 | 0 | 0 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 88 | 0 | 0 | 0 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 0 | 8798.9 | 0 | 0 | 0 | 8798.9 | 8798.9 | 8798.9 | 8799 | 8798.9 | 8799 | 8799 | 0 | 1905-07-09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 10 | 1905-07-09 | 1900-01-27 | 1900-01-09 | 1905-07-09 | 1900-01-27 | 1900-01-09 | 1905-07-09 | 1900-01-27 | 1900-01-09 | 1905-07-09 | 1900-01-27 | 1900-01-09 | 1905-07-09 | 1900-01-24 | 1900-01-09 | 1905-07-09 | 1900-01-27 | 1900-01-09 | 1905-07-09 | 1900-01-24 | 1900-01-09 | 0 | 0 | 0 | 2001-04-15 | 0 | 0 | 0 | 37016 | 37027 | 2001-05-04 | 37021 | 36982 | 2001-05-15 | 36986 | 0 | 1900-01-06 16:48 | 0 | 0 | 0 | 7.7 | 7.7 | 1900-01-06 16:48 | 7.7 | 7.7 | 1900-01-06 16:48 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | -20.2 | -20.2 | -20.2 | -20.2 | -20.2 | -20.2 | -20.2 | -20.2 | -20.2 | -20.2 | -20.2 | -20.2 | -20.2 | -20.2 | -20.2 | -20.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 127 | 111 | 207 | 176 | 111 | 191 | 95 | 78 | 176 | 111 | 159 | 176 | 191 | 127 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 386 | 399 | 612 | 732 | 519 | 615 | 596 | 453 | 315 | 418 | 433 | 444 | 414 | 371 | 394 | 483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.79 | 0 | 0 | 0 | 0 | 7.8 | 7.77 | 7.57 | 7.82 | 7.9 | 7.98 | 8 | 7.77 | 7.67 | 8.06 | 7.73 | 7.7 | 7.95 | 7.95 | 8.05 | 7.63 | [8 empty] | 0 | 0.49 | 0.32 | 0.41 | -0.28 | 0.38 | 0.27 | -0.23 | -0.12 | -0.27 | -0.24 | -0.14 | -0.01 | -0.28 | -0.43 | -0.28 | [8 empty] | 7.99 | 7.86 | 7.77 | 8.08 | 7.86 | 7.86 | 8.16 | 8.15 | 7.93 | 7.95 | 7.7 | 7.75 | 7.6 | 8.08 | 7.92 | 7.71 | [8 empty] | 0.01 | -0.28 | -0.24 | 0.14 | -0.11 | -0.09 | -0.01 | 0.28 | -0.11 | -0.2 | -0.23 | -0.05 | -0.11 | -0.46 | -0.26 | -0.11 | [8 empty] | 22930.3 | 0 | 979.8 | 0 | 276 | 0.02 | 0 | -67 | 1.04 | 0 | 5604 | 4.4.0.0.0 | 4.4.0.0.1 | 4.4.0.0.0 | 4.4.1.0.8 | 4.4.0.0.6 | 4.4.4.3.8 | 4.4.0.0.0 | 4.4.0.0.8 | 4.4.2.0.8 | 4.4.0.0.7 | 4.4.0.0.0 | 4.4.0.0.8 | 4.4.0.0.0 | 4.4.0.0.0 | 4.4.0.0.8 | 4.4.0.1.5 | 4.4.0.0.0 | 4.4.0.0.2 | 4.4.0.0.0 | 4.4.0.0.2 | 4.4.0.0.8 | 4.3.0.0.0 | 0.0.0.0.0 | 4.4.0.0.6 | 4.4.1.0.0 | 4.4.0.0.8 | 4.4.0.0.7 | 4.3.0.0.0 | 4.4.0.0.6 | 4.4.0.0.0 | M03 | 13.8 | 15.4 | 13 | 13.7 | 13.5 | 13.8 | 14.7 | 13.6 | 14.8 | 13.7 | 13.2 | 13.9 | 13.5 | 14.1 | 12.9 | 13.1 | 14.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.4 | 12.9 | 1644 | [82 empty] | Running | 50 |  |  |  |  | 67.46 | 2 | 2 |  | 50 | 0 | 49.99 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 1 | 1 | 1010 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 1 | 0 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 30 | 30 | 0 | 1.4 | 20 | 1.5 | 80 | 2 | 0 | 11 | 3 | 0 | 0 | 0 | 0 | 7 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 34 | [5 empty] | 1700 | 800 | 1 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 200 | -300 |  | -100 | -700 | 6 | 0 | 50 | 1500 | 3 | 3.7 | 3.9 | 0.1 | 2.7 | 0.1 | 0 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 3.9 |  | 0 | 0 | 0 | 0 |  | 10 | 0 |  |  |  | 0 |  | 5 | 5 | 5 | 5 | 5 | 60 | 28 | 40 | 30 | 50 | 180 | 28 | 40 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 0 | 0 | 1 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 0 | 0 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 8 | [479 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 10 | 0 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 32 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 | 0.95 | 0 | 60 | -27 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | 85 | 110 | 90 | 95 | 100 | 105 | 0.85 | 0.9 | 0.95 | 1 | -0.97 | -0.95 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 1 | 40 | 0 | 30 | 30 | 10 | 10 | 10 | 3 | 1 | 5500 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 4 | 4 | 0.01 | 0.01 | 0.2 | 0.2 | 1 | 1.11 | 1 | 1.11 | 1 | 30 | 0 | 0 | 0 | 100 | 100 | 10 | 50 | 50 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 5000 | -5000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 51.5 | 47.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 1 | 115 | 85 | 35 | 7 | 0 | 0 | 1 | -0.2 | 50 | 110 | 80 | 1 | 0 | 349 | 200 | 1 | 55 | 10 | 2 | 0.8 | 3 | 4 | 10 | 0.5 | 4 | 5500 | 20 | 10 | 3 | 5500 | 0 | 0 | 0 | 0 | 5500 | 120 | 88 | 45 | 0 | 10 | 0 | 0 | 0 | -0.4 | 50 | 110 | 80 | 0 | 0 | 400 | 200 | 0 | 100 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 90 | 45 | [6 empty] | 0 | [34 empty] | 0 | 0 | 0 | 1 | 1 | 0 | 0 |  | 0 |  | 0 |  |  |  | 1 | 1 |  |  |  | 0 | 0 | 1 | 1 |  | 1 | 1 | 1 |  | 0 | 0 | [8 empty] | 0 | 1 |  | 0 | 0 |  |  | 1 |  | 0 | 0 | 1 | 1 |  | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 1 |  | 616 |  |  |  |  | 11 | 0 | 233 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.2 | 100 | 0.02 | 100 | 50 | 0 | 0 | 4.5 | 100 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 30 | 100 | 90 | 0 | 1 | 0 | -5 | 15 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 1 | 6 | 0 | 0 | 0 | 1 | 6 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 33 | 30 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 7 | 24 | 7 | 12 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 65 | 1 | 0 | 0 | 0 | -4.5 | 10 | 1 | 60 | 55 | 0 | 2 | 1.65 | 1.82 | 0.6 | 0.6 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0 | 0 | 0 | 0 | 15 | 30 | 0.01 | 0.4 | 0 | 60 | 30 | 0.3 | 0 | 0 | 0 | 1200 | 1400 | 0 | 0.5 | 360 | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 0.3 | 0.1 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 0.2 | 300 | 300 | 300 | 300 | 0 | 50 | 50 | 50 | 50 | 50 | 120 | 1 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 0 | 1 | 3 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.3 | 1 | 25 | 6.5 | 100 | 0 | 7 | 0 | 0.5 | 0 | 4 | 50 | 0 | 25 | 10 | 250 | 2 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 | [16 empty] | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 0 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 |  |  |  |  | 0 | 0 | 0 | 0 | [66 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 1200 | 1000 |  |  |  | 1000 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 50 | 1000 | 680 | 640 | 5 | 650 | 5 | 1000 | 640 | 5 | 680 | 5 | 1000 | 5 | 15 | 300 | 20 | 50 | 650 | 5 | 160 | 5 | 460 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 20 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 20 | 5 | 10 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | 4 | 20 |  | 0.98 | 1 | -0.98 | -0.95 | 0.8 | -0.93 | 1 | 4 | 0.95 | -0.9 | 20 | 80 | 3321 | 88 | 90 | 1.88 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 0 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 75 | 90 | 75 | 80 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 50 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 45 | 300 |  | 75 | 1.5 | 0 | 0 | 0 | 180 | 0.1 | 1.11 | 60 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 930 | 0 | 5000 | 50 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 500 | 1000 | 1 | 0 | 0 | 0 | 1 | 1 | 0.95 | 0.98 | 1 | -0.98 | -0.9 | 0 | 20 | 0.8 | -0.9 | 1 | 0 | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 400 | 0 | 0 | 0 | 0 | 1 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -100 | 100 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 0 | 1 | 1 | -0.9 | -100 | 100 | [12 empty] | 10 | 2.5 | 0.2 | 3.1 | 0.05 | 1.5 | 1.7 | 0.05 | 0.05 | 120 | 5 | 120 | 5 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 30 |  |  | 20 |  |  |  | 3 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.5 | 0.1 | 0.5 | 500 | 1500 | 4.6 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1.5 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 120 | 2 | 120 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 1 | 0 | 100 | 120 | 2 | 0.5 | 0 | 1 | 0 | 78 | 120 | 2 | 0.5 | 0 | 62 | 2 | 1 |  | 77 | 120 | 2 | 0.5 | 0 | 1 | 0 | 200 | 200 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 82 | 0 | 0 | 0 | 5 | 20 | 0 | 2 | 30 | 90 | 0 | 0 | 1 | 200 | -200 | -1 | -50 | 100 | -100 | 0 | 0 | 1 | 200 | -200 | 20 | 30 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 9.5 | 10 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 1 | 1 | 90 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 18 | 18 | 18 | 18 | [5 empty] | 15 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 462 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 1 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 4 | 0 | 20 | 4000 | 4000 |  | 550 | 25 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 4 | 4 | 4 | 4 | -5 | -5 | -5 | -5 | 14 | 14 | 14 | 14 | 4.5 |  | 45 | 660 | 660 | -144 | 0 | 60 | 50 | [24 empty] | 0 | 4 | 500 | 30 |  | 8000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 250 | 0 | -24 | -13 | 2175 | 1280 | 10 | 2175 | 1280 | 60 | 0 | 0 | [6 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2679 | 1324 | 4795 | 2310 | 1499 | 1500 |  | 55.1 | 48.1 |  | 400 | [7 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2190 | 1100 | 2950 | 1550 | 1500 | 1500 |  | 47 | 44 |  | 400 | [7 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2190 | 1100 | 2950 | 1550 | 1500 | 1500 |  | 47 | 44 |  | 400 | [7 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2190 | 1100 | 2950 | 1550 | 1500 | 1500 |  | 47 | 44 |  | 400 |  | 0 | 1000 | 300 | 48 | -1.6 | -4 | 100 | 6 | 0 | 1 | 6 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6 | 0 | 0.5 | 0 | 0 | 120000 | 0 | 120000 | 0 |  | 4 | 0 | 0 | 0 |  |  |  | 75 |  | 40 | [14 empty] | 55 | 55 | 50 | 50 | [10 empty] | 0 | 0 | 1 | 3 | 47 | 49 | 2 | 2 | 62 |  | 45 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 400 | 55 | 55 | 55 | [8 empty] | -750 | 3000 |  | 0.2 | 100 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.4 |  |  | 100 | 0.2 |  | 100 |  | 100 | 100 | [11 empty] | 0.2 | 100 | 200 | [43 empty] | 0 | 0.1 | 100 | 100 | 100 | 45 | 0 | 1 | 4 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 102 | 60 | 66 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 50 | 0 | 1 | 4 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 60 | 71.5 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 150 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 1.5 | 0.002 | 1 | 1 | 10 | 0.6 | 0 | 1 | 12 | 1 | 1 | 1 | 1 | 0 | 0 | 1.1 | 0.7 | 1 | 50 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | 0 | 0.1 | 0.5 | 0.5 | 100 | 40 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 50 | 0 | 100 | 10 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 75 | 100 | 100 | 95 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | [42 empty] | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 0 | 0 | 10 | 150 | 150 | 100 | 205 | 0 | 48 | 50 | 0 | 3000 | 6000 | 3000 | 6000 | 6 | 6 | 0 | 5000 | -5000 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 100 | 50 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 |  |  |  |  | 12 | 2 | 5 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 80 | 0 | [6 empty] | 0.09478 | 0.4 | 0.7 | 100 | 0 | 0.02843 | 0.74047 | 0.4739 | 100 | 0 | 4 | 20 | 1338 | 2678 | 60 | 75 | 90 | 100 |  | 4 | 20 | 1338 | 2679 | 2 | 2 | 35 | 45 |  | -6 | -6 | -6 | -6 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -130 | 8 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 2679 | 2679 | 2679 | 2679 | 50 | 0.2 | 0.63 | 0.63 | 0.63 | 0.2 | 0.63 | 0.63 | 0.63 |  | 10 | 0 | 150 | 1 | 1 | 101 | 105.8 | 98 | 91 | 105.8 | 50 | 65 | 85 | 75 |  | 105 | 120 | 95 | 70 | 140 | 0 | 80 | 15 | 82 | 1 | 22.7 | 3.85 | 0 | 0 | 120 |  |  | 10 | 4 | 4 | 4 | 4 | 58 | 58 | 58 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [30 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.4 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1450 | 10 | 200 | 400 | 2800 | 5 | 400 | 0 | 3450 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 0 | 1500 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 900 |  | 0.15 | 0.64 | 7.7 | 80 | 0 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1500 | 6.7 | 0 | 95 | 85 | 85 | 95 | 95 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.1 |  |  | 0.74 | [13 empty] | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | [28 empty] | 1 | 1 | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2679 |  |  | 2679 | 0 | 0 | 0 | 0 | 0 | 2679 | 2679 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 684.2 | 20.2 | -26.79 | 3.995 |  | 0.71 | 0 | 0.2 | 2679 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 414 | 471 | 86 | 74 | 63 | 25 | 25 | 25 | 529 | 555 | 569 | 569 | 97 | 24 | 40 | 8 | 0 | 62.67 | [73 empty] | Sending | 30 | 38 | 37 | 38 | 37 | 39 | 38 | 37 | 37 | 37 | 38 | 37 | 38 | 38 | 39 | 39 | 40 | 40 | 38 | 38 | 40 | 25.5 | 26.5 | 27.4986 | 24.1 | 32.1 | 27.65 | 22.7 | 25.9 | 27.4995 | 28.1 | 31.3 | 26.5 | 32.1 | 25.75 | 23.6 | 29.9 | [8 empty] | 2094 | 1919 | 2093 | 1894 | 2257 | 2245 | 1812 | 2168 | 1897 | 2022 | 2129 | 2381 | 2173 | 1896 | 2023 | 2004 | [9 empty] | 47 | 1 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 167.4 | 0 | 0 | 0 | 1153 | 0 | 0 | 0 | 38.6 | 0 | 0 | 0 | 2.044 |  |  |  | 53.7 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 | [16 empty] | 0 | 7.8 | 0 | 7.77 | 0 | 7.57 | 0 | 7.82 | 0 | 7.9 | 0 | 7.98 | 0 | 8 | 0 | 7.77 | 0 | 7.67 | 0 | 8.06 | 0 | 7.73 | 0 | 7.7 | 0 | 7.95 | 0 | 7.95 | 0 | 8.05 | 0 | 7.63 | [16 empty] | 0 | 0 | 0 | 0.49 | 0 | 0.32 | 0 | 0.41 | 0 | -0.28 | 0 | 0.38 | 0 | 0.27 | 0 | -0.23 | 0 | -0.12 | 0 | -0.27 | 0 | -0.24 | 0 | -0.14 | 0 | -0.01 | 0 | -0.28 | 0 | -0.43 | 0 | -0.28 | [16 empty] | 0 | 7.99 | 0 | 7.86 | 0 | 7.77 | 0 | 8.08 | 0 | 7.86 | 0 | 7.86 | 0 | 8.16 | 0 | 8.15 | 0 | 7.93 | 0 | 7.95 | 0 | 7.7 | 0 | 7.75 | 0 | 7.6 | 0 | 8.08 | 0 | 7.92 | 0 | 7.71 | [16 empty] | 0 | 0.01 | 0 | -0.28 | 0 | -0.24 | 0 | 0.14 | 0 | -0.11 | 0 | -0.09 | 0 | -0.01 | 0 | 0.28 | 0 | -0.11 | 0 | -0.2 | 0 | -0.23 | 0 | -0.05 | 0 | -0.11 | 0 | -0.46 | 0 | -0.26 | 0 | -0.11 | [17 empty] | 0 | 0 | 1 | 1 | 17 | 0 | 100 | 0 | 0 | 0 | 0 | 30.2 | 0 | 0 | 0 | 0 | 0 | 0 | 4.79 |  | 0 | 0 | 0 | 0 |  | 100 | 100 | 100 | 100 | 30.2 | 30.2 | 30.2 | 30.2 |  | 1500 | 1499 |  | 55.5 |  |  | 0 | 0 | GAZ DE LACQ
22 |  |  |  |  | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","rem_conn":"Prim-NoSSL-Proxy","dataItems":"0/20","agent_conn":"Prim-SSL-Proxy","mon_conn":"Prim-NoSSL-Proxy"} | 0 | 0 | 0 | 0 | 0 | 0 | -0.92 | 5.98 | 0 | 928 | 0 | -1564 | 0 | 6.01 | 0 | 4.56 | 4.37 | 26.1 | 0 |  |  |  | 0 | -0.5 | 0 | 0 | 4.65 | 0 | 4.65 | 0 | 0 | 0 | 4.4.0.7 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 |  | 19200 | 0 | 0 |  | 0 | -5971 | 0 | -2757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 |  |  |  |  | 30805700 | 0 | 7168700 | 482948 | 85 | 0 | 0 | 0 | 0 | 0 | 193 | 1332 | 504 | 504 | 504 | 503 | 340 | 504 | 9496 | 9496 | 9496 |  | 643 |  | 52.7 | 59.2 | 68 | 81.8 | 100 | 70 | 70.1 | 66.6 | 30 | 26.1 | 5 | 1.074 | 1.075 | 46 | 134.6 | 134.5 | 65.1 | 45 | 45 | 27.9 | 93.9 | 93.9 | 0 | 0 | 0 | 0 | 50 | 30.9 | 10 | 128 | 127.9 | 50.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9 | 6.8 | 5.5 | 81.8 | 30.9 | 134.5 | 79.8 | 45 | 0 | 81.5 | 70.1 | 31.3 | 52.8 | 135.1 | 127.9 | 81.5 | 31.9 | 22.9 | 11.5 | 3537.6 | 644.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 491.2357 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0.2 | 28.4 | 0.5 | 0.8 | 1.1 | 1.4 | 1.4 | 1.4 | 16.4 | 28.4 | 0 | 0 | 0.2 | 28.4 | 1 | 0 | 0.5 | 0 | 0.8 | 0 | 1.1 | 0 | 1.4 | 0 | 1.4 | 1 | 1.4 | 1 | 16.4 | 1 | 28.4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 9393 | 17 | 0 | 3158 | 0 | 0 | 3158 | -0.7 | 20.2 | 114 | 0 | 0 | 0 | 0 | 0 | 10 | 6.06 | 6.72 | 10.8 | 0 | 0 | 0 | 0 | 74 | 74 | 74.9 | 138.8 | 100 | 150 | 20.2 | 0.4 | 66 | 149.6 | 0 | 0 | 0 | 149.6 | 0 | 0 | 0 | 493 | 493 | 0 | 10.9 | 19.4 | 10.9 | 11 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 11 | 0 | 122.8 | 0 | 0 | 59.2 | 49.2 | 0.71 | 2.72 | 0.01 | 345 | 343 | 345 | 41.92 | 1608943323274 | 0 | 45 | 1 | 1 | 2.3 | 43.3 | 28 | -6.65 | 0 |  | 3144 |  |  |  |  | 0 | 0 | 0 | 0 | 42056 | 42034 | 33017 | 32977 | 0 | 0 | 0 | 0 | 539 | 546 | 543 | 546 | 544 | 547 | 549 | 551 | 547 | 546 | 545 | 542 | 545 | 542 | 544 | 545 | 539 | 540 | 544 | 544 | 544 | 545 | 548 | 545 | 544 | 544 | 551 | 550 | 539 | 539 | 0 | 0 | 134 | 342 | 339 | 11 | [42 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3373442 | 0 |  |  | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 45.4 |  |  | 64 | 66.7 | 65.5 | 16 |  |  |  |  | 1 | 1606657426313 |  | 4749 | -0.924 | 50.01 | 0 | 20984 | 12128 | 21008 | 12115 | 21022 | 12137 | 10239 | 5924 | 10251 | 5908 | 10239 | 5913 | 0 | 12282 | 4094 | 3 | 0.129 | 1785 | 2.25 | -44.9 | 3.91 | 0.73 |  | 0 | 93.9 | 79.7 | 0 | 0 | 0 | 70.1 | 3 | 0 | 0 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 62.2 | 84.7 | 86.1 | 82.7 | 62 | 66.1 | 76.2 | 81.5 | 85.5 | 69 | 72.2 | 81.2 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 9533.5 | 9533.5 | 9518.7 | 9533.5 | 9533.5 | 9533.6 | 9533.5 | 9533.4 | 9533.5 | 9533.4 | 9533.4 | 9533.4 | 2018 | 2018 | 23 | 4 | 2017 | 18 | 10 | 2018 | 17 | 4 | 17 | 4 | 2018 | 23 | 4 | 2018 | 17 | 4 | 2018 | 23 | 4 | 2018 | 18 | 4 | 2018 | 17 | 4 | 2018 | 17 | 4 | 2018 | 18 | 4 | 2018 | 17 | 4 | 40710 | 40752 | 36616 | 40684 | 40767 | 40694 | 40751 | 40732 | 40711 | 40697 | 40731 | 40706 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 0 | -9.8 | -9.8 | -9.8 | -9.8 | -9.8 | -9.8 | -9.8 | -9.8 | -9.8 | -9.8 | -9.8 | -9.8 | -9.8 | -9.8 | -9.8 | -9.8 | -9.8 | -9.8 | -9.8 | -9.8 | -9.8 | -9.8 | -9.8 | -9.8 | 284 | 269 | 126 | 141 | 220 | 79 | 126 | 158 | 220 | 141 | 317 | 110 | 141 | 189 | 189 | 237 | 126 | 110 | 141 | 237 | 364 | 205 | 189 | 189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 329 | 341 | 439 | 366 | 341 | 634 | 354 | 402 | 341 | 390 | 427 | 341 | 476 | 427 | 549 | 561 | 390 | 341 | 427 | 427 | 525 | 341 | 305 | -0.001 | 5.94 | 0 | 0 | 0 | 0 | 7.65 | 7.61 | 7.7 | 7.83 | 7.69 | 7.64 | 7.76 | 7.61 | 7.59 | 7.74 | 7.82 | 7.64 | 7.65 | 7.7 | 7.62 | 7.65 | 7.69 | 7.68 | 7.75 | 7.86 | 7.71 | 7.64 | 7.93 | 7.84 | -0.17 | -0.04 | -0.13 | -0.29 | 0.24 | -0.25 | 0.06 | 0.36 | -0.03 | -0.06 | -0.27 | 0.12 | -0.05 | -0.15 | 0 | -0.09 | -0.22 | -0.21 | -0.18 | -0.09 | -0.49 | -0.26 | 0 | -0.01 | 7.6 | 7.73 | 7.75 | 7.73 | 7.73 | 7.93 | 7.75 | 7.75 | 7.7 | 7.86 | 7.88 | 7.77 | 7.57 | 7.55 | 7.85 | 7.68 | 7.73 | 7.51 | 7.65 | 7.51 | 7.56 | 7.61 | 7.53 | 7.77 | -0.06 | -0.32 | -0.21 | -0.28 | -0.27 | -0.23 | -0.45 | -0.25 | -0.21 | -0.05 | -0.37 | -0.14 | -0.16 | -0.46 | -0.29 | -0.19 | -0.13 | -0.09 | -0.47 | -0.1 | -0.07 | -0.04 | -0.09 | 0.18 | 40714.6 | 0 | 10029.2 | 0 | 266 | 0.02 | 0 | -1807 | 1.04 | 0 | 10244 | 4.4.0.0.0 | 4.4.0.1.1 | 4.7.1.1.0 | 4.5.3.1.0 | 4.4.0.1.6 | 4.4.4.17.6 | 4.7.1.0.0 | 4.4.0.6.12 | 4.5.2.0.0 | 4.4.0.4.12 | 4.4.0.1.0 | 4.5.1.0.0 | 4.4.0.2.0 | 4.4.0.1.0 | 4.4.0.0.4 | 4.4.0.5.6 | 4.4.0.4.0 | 4.4.0.0.2 | 4.4.0.0.0 | 4.4.0.0.2 | 4.4.0.2.12 | 4.3.0.0.0 | 0.0.0.0.0 | 4.4.0.3.11 | 4.4.1.0.0 | 4.4.0.2.12 | 4.4.0.0.0 | 4.3.0.0.0 | 4.4.0.3.3 | 4.9.0.0.0 | M06 | 26.4 | 29.6 | 23.9 | 27.8 | 24 | 27.2 | 21.5 | 25.2 | 27.5 | 28.9 | 28.8 | 28.2 | 29.2 | 23.4 | 23.8 | 25.6 | 29.2 | 25.7 | 26.4 | 27.7 | 24.7 | 29 | 25.1 | 27.4 | 26.5 | 29.7 | 21.4 | 1594 | [30 empty] | -1 | 2 | 1 | NaN | 0.0001 | 1608120516000 | 1 | 1 | 0.1441 | 1 | NaN | 3670 | 1 | 1607904000000 | NaN | NaN | NaN | 0.01 | 6.07 | 6 | NaN | 1 | 0.0006 | 1 | 1 | 1 | 1 | 52 | 0 | 2707 | 9 | 0.0281 | 1 | 1608119280000 | 2 | 1 | 2 | 2.16 | 3.1 | 1025657 | 1 | 1 | 9189 | 1 | 14.4 | 133 | 0.05 | 0.0344 |  |  |  |  | Running | 50 |  | 0 | 0 | 6186 | 14.2 | 2 | 2 |  | 50 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 1 | 0 | 970 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 1 | 1 | 1 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 30 | 30 | 0 | 1.4 | 20 | 1.5 | 80 | 1 | 0 | 11 | 1 | 0 | 0 | 0 | 0 | 7 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 35 | [5 empty] | 0 | 0 | 0 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 200 | -1000 |  | -200 | -1700 | 10 | 0 | 50 | 1500 | 5.6 | 6.7 | 6.9 | 0.1 | 3 | 0.1 | 0 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 3.5 |  | 0 | 0 | 0.2 | 4.2 |  | 10 | 0 |  |  |  | 0 |  | 5 | 5 | 5 | 2.5 | 5 | 60 | 28 | 40 | 30 | 50 | 180 | 35 | 40 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 2 | 10 | 2 | 1 | 1 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 2 | 10 | 2 | 1 | 1 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 2 | 10 | [479 empty] | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 2 | 2 | 0 | 8.5 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 5000 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2500 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 12000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 10 | 0 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 32 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 | 0.95 | 0 | 60 | -33 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | 85 | 110 | 90 | 95 | 100 | 105 | 0.85 | 0.9 | 0.95 | 1 | -0.97 | -0.95 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 1 | 40 | 0 | 30 | 30 | 10 | 10 | 10 | 3 | 1 | 10000 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 4 | 4 | 0.01 | 0.01 | 0.2 | 0.2 | 0 | 1.11 | 0 | 1.11 | 0 | 30 | 0 | 2 | 0 | 100 | 100 | 10 | 50 | 50 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 5000 | -5000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 51.5 | 47.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 1 | 115 | 85 | 35 | 10 | 0 | 0 | 1 | -0.2 | 50 | 110 | 80 | 1 | 0 | 323 | 200 | 1 | 200 | 10 | 2 | 0.8 | 3 | 4 | 10 | 0.5 | 4 | 20000 | 20 | 10 | 5 | 10000 | 0 | 0 | 0 | 0 | 20000 | 120 | 88 | 45 | 0 | 10 | 0 | 0 | 0 | -0.4 | 50 | 110 | 80 | 0 | 1 | 400 | 200 | 0 | 100 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 90 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 6 | 0 | 6000 | 250 | 100 | 50 | 75 | 500 | 100 | 460 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 5 | 35 | 30 | 60 | 490 | 490 | 300 | 30 | 120 | 0 |  | 1 | 0 | 0 | 1 | 1 | 0 | 0 |  | 1 |  | 0 |  |  |  | 1 | 1 |  |  |  | 1 | 1 | 0 | 1 |  | 1 | 1 | 1 |  | 1 | 1 | [8 empty] | 0 | 1 |  | 1 | 0 |  |  | 1 |  | 0 | 1 | 1 | 0 |  | 1 | 1 | 1 | 1 |  | 0 |  |  |  | 12.5 |  | 624 |  |  |  |  | 15 | 0 | 360 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.2 | 100 | 0.01 | 100 | 41 | 0 | 1 | 3.5 | 100 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 60 | 30 | 0 | 100 | 0 | 0 | 0 | -5 | 2 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 35 | 30 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 200 | 168 | 75 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 65 | 4 | 0 | 0 | 0 | -2.5 | 10 | 1 | 20 | 15 | 1 | 2 | 1 | 1.82 | 0.6 | 0.6 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0.2 | 0 | 0 | 0 | 7 | 15 | 0.01 | 0.4 | 0 | 60 | 30 | 0 | 0 | 0 | 0 | 1200 | 1400 | 0 | 0.5 | 450 | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 0.1 | 0.05 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 1 | 0 | 0.72 | 0.72 | 0.72 | 0.72 | 1.2 | 0.1 | 300 | 300 | 300 | 300 | 0 | 50 | 50 | 50 | 50 | 50 | 120 | 0 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.15 | 3.6621 | 25 | 2.9297 | 100 | 0 | 6 | 0.1 | 0.5 | 1 | 7 | 100 | 2 | 25 | 10 | 250 | 2 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 | 1 | 1 | 4000 | 2000 | 20000 | 10000 | 4500 | 2250 | 8 | 4 | 2 | 1 | 30 | 150 | 20 | 120 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 0 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | [66 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 1 | 1 | 1200 | 38000 |  |  |  | 44800 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 100 | 1000 | 680 | 640 | 0 | 650 | 5 | 650 | 640 | 5 | 650 | 5 | 1000 | 5 | 15 | 300 | 20 | 50 | 650 | 5 | 200 | 5 | 1000 | 175 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 20 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 30 | 20 | 5 | 10 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | 0 | 20 |  | 0.98 | 1 | -0.98 | -0.95 | 0.8 | -0.93 | 1 | 7 | 0.95 | -0.95 | 20 | 80 | 5590 | 88 | 90 | 2.01 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 0 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 85 | 90 | 85 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 44.4 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 35 | 300 |  | 75 | 1.03 | 1 | 0 | 1 | 180 | 0.1 | 1.11 | 60 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 4500 | 0 | 5000 | 40 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 2250 | 4500 | 1 | 2 | 0 | 1 | 1 | 2 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 4 | 20 | 0.8 | -0.925 | 1 | 0 | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 10000 | 0 | 0 | 0 | 0 | 1 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -4000 | 4000 | 0 | 0 | 4 | 20 | -4000 | 4000 | 5000 | 1 | 0 | 0.8 | -0.92 | -3600 | 3600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 10 | 3.3 | 0.2 | 3.2 | 0.05 | 1.5 | 1.7 | 0.05 | 0.05 | 87 | 5 | 94 | 2 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 30 |  |  | 20 |  |  |  | 3 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.4 | 0.1 | 0.5 | 500 | 1500 | 3.5 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1.5 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 75 | 2 | 79 | 2 | 38 | 3 | 0 | 0 | 85 | 0.1 | 0 | 0 | 1 | 0 | 0 | 0 | 70 | 120 | 2 | 2 | 0 | 0 | 0 | 70 | 120 | 2 | 2 | 1 | 62 | 2 | 1 |  | 76 | 120 | 0.5 | 0.5 | 0 | 0 | 0 | 133 | 133 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 82 | 0 | 0 | 0 | 5 | 20 | 0 | 2 | 30 | 90 | 0 | 0 | 0 | 200 | -200 | 0 | -70 | 100 | -100 | 0 | 0 | 0 | 200 | -200 | 20 | 30 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 9.5 | 10 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 10 | 0 | 0 | 1 | 90 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 18 | 18 | 18 | 18 | [5 empty] | 4 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 924 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 1 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 0 | 0 | 20 | 4000 | 4000 |  | 850 | 30 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 2 | 2 | 2 | 2 | -5 | -5 | -5 | -5 | 13 | 13 | 13 | 13 | 4.5 |  | 45 | 270 | 70 | -144 | 0 | 80 | 350 | [24 empty] | 0 | 4 | 500 | 30 |  | 4000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 380 | 1 | -30 | -9 | 4500 | 2250 | 10 | 4500 | 2250 | 60 | 0 | 0 | [6 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4492 | 2249 | 6035 | 3130 | 1499 | 1499 |  | 52.8 | 53.4 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4924 | 2161 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4924 | 2161 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4924 | 2161 | 1500 | 1500 |  | 50 | 50 |  | 660 |  | 0 | 1000 | 300 | 48 | -1.6 | -4 | 100 | 10 | 0 | 1 | 10 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 |  | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 10 | 0 | 0.5 | 0 | 0 | 60000 | 0 | 60000 | 0 |  | 5 | 0 | 1 | 1 |  |  |  | 85 |  | 48 | [14 empty] | 53 | 53 | 53 | 53 | [10 empty] | 0 | 0 | 1 | 3 | 57 | 59 | 2 | 2 | 60 |  | 48 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 350 | 200 | 200 | 100 | [8 empty] | -1250 | 5000 |  | 0.2 | 100 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.4 |  |  | 100 | 0.2 |  | 100 |  | 100 | 100 | [11 empty] | 0.2 | 100 | 200 | [43 empty] | 0 | 0.1 | 100 | 0.01 | 100 | 80 | 0 | 1 | 4.5 | 1 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 60 | 68 | 0 | 100 | 0 | 0 | 0.1 | 100 | 0.01 | 100 | 40 | 0 | 0 | 4.6 | 1 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 58 | 70 | 100 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 80 | 0 | 1 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 30 | 35 | 5 | 100 | 35 | 0 | 0.001 | 1 | 1 | 10 | 0.4 | 0 | 1 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1.1 | 0.7 | 1 | 0 | 100 | 0 | 0 | 0.1 | 0.05 | 0.01 | 100 | 35 | 0 | 1 | 15 | 1 | 1 | 1 | 1 | 0 | 0 | 135 | 130 | 132 | 0 | 100 | 50 | 0 | 0.3 | 100 | 0.01 | 100 | 80 | 0 | 1 | 2.6 | 1 | 1 | 1 | 1 | 0 | 0 | 47 | 30 | 45 | 0 | 100 | 10 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0 | 0.1 | 100 | 205 | 0 | 1 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 28 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | [42 empty] | 0 | 0.3 | 100 | 50 | 0 | 1 | 4 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 40 | 100 | 0.01 | 50 | 0 | 100 | 10 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 0 | 0 | 10 | 150 | 150 | 100 | 205 | 0 | 48 | 50 | 0 | 3000 | 6000 | 3000 | 6000 | 6 | 6 | 0 | 5000 | -5000 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 100 | 50 | 0 | 0.2 | 100 | 80 | 0 | 1 | 2.5 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 140 | 120 | 100 | 0.05 | 128 | 0 | 100 | 40 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 |  |  |  |  | 12 | 2 | 5 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 80 | 0 | [6 empty] | 0.01421 | 0.29619 | 0.88857 | 100 | 0 | 0 | 0.44428 | 0.23695 | 100 | 2 | 0 | 20 | 5000 | 5000 | 60 | 75 | 90 | 100 |  | 4 | 20 | 2250 | 4500 | 2.5 | 2 | 40 | 45 |  | -2 | -2 | -2 | -2 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -145 | 10 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 4500 | 4500 | 4500 | 4500 | 64 | 0.72 | 0.72 | 0.72 | 0.72 | 0.5 | 0.72 | 0.72 | 0.72 |  | 10 | 12 | 95 | 1 | 1 | 100.4 | 103.4 | 98 | 91 | 103.4 | 40 | 65 | 85 | 80 |  | 110 | 125 | 90 | 70 | 140 | 1 | 80 | 5 | 83 | 1 | 20 | 5.55 | 3 | 5 | 85 |  |  | 10 | 4 | 4 | 4 | 4 | 56 | 56 | 56 | 56 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 16 | 16 | 200 | 200 | 200 | 200 | 200 | 200 | 1 | 1200 | 150 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | [30 empty] | 1 | 100 | 100 | 33 | 1 | 60 | 60 | 60 | 30 | 0 | 5 | 0 | 0 | 0 | 100 | 125 | 135 | 95 | 60 | 110 | 0 | 1800 | 0 | 0 | 0 | 1 | 3150 | 180 | 330 | 110 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1650 | 10 | 200 | 400 | 2800 | 5 | 10000 | 0 | 3850 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 1 | 1200 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 800 |  | 0.16406 | 2.1973 | 4.3945 | 95 | 2 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1501 | 6.7 | 0 | 95 | 85 | 85 | 95 | 95 | 9.54 | 9.971 | 720 |  |  | 1.6 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.1 |  |  | 0.58 | [13 empty] | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | [28 empty] | 1 | 1 | 1 | 2 | 0 | 2 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4391 |  |  | 4500 | 0 | 0 | 0 | 0 | 0 | 4500 | 4375 |  |  | 2.75 | 2.76 | 0 | 0 | 0 | 0 | 0 | 0 | 405.9 | 21.6 | -43.86 | 3.911 | 0.056 | 0.733 | 0 | 1 | 4498 | 0 | 0 | 2.24 | 1 | 0 | 1 | 0 | 850 | 602 | 236 | 230 | 208 | 34 | 30 | 29 | 1160 | 1041 | 877 | 0 | 315 | 40 | 52 | 37 | 0 | 76.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 365 | 366 | 365 | 367 | 367 | 365 | 363 | 367 | 362 | 368 | 367 | 367 | 365 | 365 | 365 | 364 | 366 | 368 | 368 | 369 | 368 | 369 | 365 | 365 | 494 | 496 | 494 | 496 | 495 | 495 | 497 | 496 | 496 | 497 | 495 | 495 | 495 | 495 | 496 | 494 | 494 | 496 | 497 | 496 | 495 | 497 | 492 | 495 | 5628 | Sending | 30 | 45 | 47 | 47 | 46 | 45 | 45 | 47 | 47 | 47 | 47 | 47 | 46 | 44 | 45 | 46 | 45 | 45 | 46 | 46 | 45 | 24.8413 | 20.8343 | 22.7434 | 21.5029 | 24.3036 | 24.9033 | 23.1033 | 22.6038 | 24.6037 | 25.0037 | 24.0037 | 26.0037 | 20.0033 | 20.5848 | 23.7034 | 22.1425 | 24.1032 | 26.0033 | 23.3441 | 22.2031 | 23.5038 | 21.3871 | 25.1035 | 21.0393 | 380 | 1099 | 541 | 1011 | 634 | 722 | 924 | 542 | 594 | 549 | 542 | 470 | 1010 | 1050 | 919 | 505 | 926 | 801 | 667 | 988 | 423 | 973 | 549 | 673 |  | 48 | 1 | [11 empty] | 72 | 72 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 261.4 | 0 | 0 | 0 | 1025 | 0 | 0 | 0 | -1.2 | 0 | 0 | 0 | 2.058 |  |  |  | 31.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 | 0 | 7.65 | 0 | 7.61 | 0 | 7.7 | 0 | 7.83 | 0 | 7.69 | 0 | 7.64 | 0 | 7.76 | 0 | 7.61 | 0 | 7.59 | 0 | 7.74 | 0 | 7.82 | 0 | 7.64 | 0 | 7.65 | 0 | 7.7 | 0 | 7.62 | 0 | 7.65 | 0 | 7.69 | 0 | 7.68 | 0 | 7.75 | 0 | 7.86 | 0 | 7.71 | 0 | 7.64 | 0 | 7.93 | 0 | 7.84 | 0 | -0.17 | 0 | -0.04 | 0 | -0.13 | 0 | -0.29 | 0 | 0.24 | 0 | -0.25 | 0 | 0.06 | 0 | 0.36 | 0 | -0.03 | 0 | -0.06 | 0 | -0.27 | 0 | 0.12 | 0 | -0.05 | 0 | -0.15 | 0 | 0 | 0 | -0.09 | 0 | -0.22 | 0 | -0.21 | 0 | -0.18 | 0 | -0.09 | 0 | -0.49 | 0 | -0.26 | 0 | 0 | 0 | -0.01 | 0 | 7.6 | 0 | 7.73 | 0 | 7.75 | 0 | 7.73 | 0 | 7.73 | 0 | 7.93 | 0 | 7.75 | 0 | 7.75 | 0 | 7.7 | 0 | 7.86 | 0 | 7.88 | 0 | 7.77 | 0 | 7.57 | 0 | 7.55 | 0 | 7.85 | 0 | 7.68 | 0 | 7.73 | 0 | 7.51 | 0 | 7.65 | 0 | 7.51 | 0 | 7.56 | 0 | 7.61 | 0 | 7.53 | 0 | 7.77 | 0 | -0.06 | 0 | -0.32 | 0 | -0.21 | 0 | -0.28 | 0 | -0.27 | 0 | -0.23 | 0 | -0.45 | 0 | -0.25 | 0 | -0.21 | 0 | -0.05 | 0 | -0.37 | 0 | -0.14 | 0 | -0.16 | 0 | -0.46 | 0 | -0.29 | 0 | -0.19 | 0 | -0.13 | 0 | -0.09 | 0 | -0.47 | 0 | -0.1 | 0 | -0.07 | 0 | -0.04 | 0 | -0.09 | 0 | 0.18 |  | 0 | 0 | 1 | 1 | 17 | 0 | 100 | 99.8 | 99.5 | 0 | 0 | 9.7 | 8.8 | 0 | 9 | 0 | 0 | 0 | 5.94 |  | 0 | 0 | 0 | 0 |  | 100 | 100 | 100 | 100 | 9.7 | 9.7 | 9.7 | 9.7 |  | 1501 | 1498 |  | 52.7 |  |  | 0 | 0 | BMW DINGOLFING 2.4
23 |  |  |  |  | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","agent_conn":"Prim-SSL-Proxy","mon_conn":"Prim-NoSSL-Proxy","rem_conn":"Prim-SSL-Proxy"} | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 6.05 | 0 | 0 | 0.97 | 5.1 | 0 |  |  |  | 0 | 23.3 | 0 | 0 | 0.06 | 0 | 0.07 | 0 | 0 | 0 | 4.4.0.7 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 |  | 0 | 0 | 0 |  | 0 | -978 | 0 | -974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 |  |  |  |  | 33159800 | 0 | 7348200 | 483434 | 600 | 0 | 0 | 0 | 0 | 0 | 158 | 4658 | 692 | 692 | 692 | 702 | 158 | 692 | 9308 | 9308 | 9308 |  | 634 |  | 52.8 | 0 | 60 | 50.2 | 0 | 58 | 25.5 | 100 | 30 | 5.1 | 40 | 1 | 1 | 50.5 | 130 | 46 | 0 | 30 | 0.2 | 0 | 75 | 58.3 | 0 | 0 | 0 | 0 | 40 | 1.9 | 0 | 120 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 4.7 | 50.2 | 1.9 | 46 | 79.6 | 0.2 | 0 | 18.4 | 25.5 | 6.8 | 6.8 | 71.7 | 79 | 9.2 | 8.3 | 0 | 1.5 | 0 | 2.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 13.7 | 101.2 | 27.5 | 41.3 | 55.1 | 68.9 | 68.9 | 68.9 | 73.6 | 86.2 | 0 | 0 | 13.7 | 101.2 | 1 | 0 | 27.5 | 0 | 41.3 | 0 | 55.1 | 0 | 68.9 | 0 | 68.9 | 1 | 68.9 | 1 | 73.6 | 1 | 86.2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 9303 | 17 | 0 | 3046 | 0 | 0 | 3046 | -2.5 | 20.2 | 113.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 202.8 | 100 | 150 | 0 | -0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0 | 0.1 | 0 | 0.08 | 2.5 | 0.66 | 41 | 39 | 42 | 42.25 | 1608765016163 | 0 | 47 | 1 | 0 | 2.4 | 11.4 | 0 | 14.01 | 0 |  | 3037 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 54 | 54 | 54 | 54 | 54 | 55 | 54 | 55 | 55 | 54 | 53 | 54 | 53 | 53 | 55 | 55 | 55 | 54 | 55 | 54 | 53 | 53 | 54 | 553 | 55 | 559 | 53 | 548 | 0 | 0 | 74 | 34 | 32 | 11 | [42 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3459387 | 0 |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29.5 | 30.8 |  |  | 30.3 | 31 | 31.2 | 0 |  |  |  |  | 1 | 1606552842359 | 6275 | 0 | 0 | 0 | 0 | 20975 | 12118 | 20996 | 12105 | 21002 | 12132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13672 | 3418 | 4 | 0.189 | 2905 | 1.82 | 0.4 | -0.01 | 0.08 |  | 0 | 58.3 | 28 | 0 | 0 | 0 | 29.6 | 0 | 0 | 0 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 66.6 | 68.5 | 57 | 56.7 | 65.2 | 60.7 | 65.1 | 56.2 | 62.2 | 67.5 | 57.8 | 57.3 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 9351.1 | 9351.1 | 9351.1 | 9351.1 | 9351.1 | 9351.1 | 9351 | 9351 | 9351 | 9351.1 | 9351.1 | 9351.1 | 2018 | 2018 | 9 | 5 | 2018 | 8 | 5 | 2018 | 11 | 5 | 9 | 5 | 2018 | 10 | 5 | 2018 | 10 | 5 | 2018 | 9 | 5 | 2018 | 10 | 5 | 2018 | 10 | 5 | 2018 | 12 | 5 | 2018 | 9 | 5 | 2018 | 9 | 5 | 41047 | 41112 | 41046 | 41177 | 41128 | 41131 | 41075 | 41143 | 41129 | 41189 | 41049 | 41086 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.562 | 0.41 | 0 | 0 | 0 | 0 | 7.77 | 7.54 | 7.63 | 7.61 | 7.78 | 7.59 | 7.75 | 7.65 | 7.79 | 7.82 | 7.93 | 7.6 | 7.74 | 7.73 | 7.56 | 7.82 | 7.73 | 8.01 | 7.66 | 8.03 | 7.65 | 7.76 | 7.58 | 7.79 | -0.19 | -0.25 | 0.08 | -0.37 | 0.06 | -0.34 | -0.12 | 0.09 | -0.31 | -0.18 | -0.17 | -0.21 | 0.21 | -0.09 | -0.45 | 0.2 | -0.17 | -0.23 | -0.18 | -0.1 | -0.36 | -0.02 | -0.42 | 0.1 | 7.57 | 7.59 | 7.73 | 7.51 | 7.61 | 7.5 | 7.68 | 7.53 | 7.51 | 7.78 | 7.81 | 7.59 | 7.79 | 7.6 | 7.52 | 7.78 | 7.58 | 7.58 | 7.85 | 7.85 | 7.76 | 7.74 | 7.51 | 7.86 | -0.06 | -0.35 | -0.27 | -0.15 | -0.27 | -0.39 | -0.13 | -0.35 | -0.29 | -0.01 | -0.12 | -0.28 | 0.01 | -0.09 | -0.37 | -0.13 | -0.08 | 0.04 | -0.11 | 0.01 | -0.28 | -0.36 | -0.33 | -0.35 | 39858.4 | 0 | 10231.4 | 0 | 0 | 0.02 | 0 | 0 | 1.04 | 0 | 0 | 4.4.0.0.0 | 4.4.0.1.1 | 4.7.1.1.0 | 4.5.3.1.0 | 4.4.0.1.6 | 4.4.4.17.6 | 4.7.1.0.0 | 4.4.0.6.12 | 4.5.2.0.0 | 4.4.0.4.12 | 4.4.0.1.0 | 4.5.1.0.0 | 4.4.0.2.0 | 4.4.0.1.0 | 4.4.0.0.4 | 4.4.0.5.6 | 4.4.0.4.0 | 4.4.0.0.2 | 4.4.0.0.0 | 4.4.0.0.2 | 4.4.0.2.12 | 4.3.0.0.0 | 0.0.0.0.0 | 4.4.0.3.11 | 4.4.1.0.0 | 4.4.0.2.12 | 4.4.0.0.0 | 4.3.0.0.0 | 4.4.0.3.3 | 4.9.0.0.0 | M07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1555 | [30 empty] | -1 | 2 | 1 | NaN | 0.0001 | 1607949900000 | 3 | 1 | 0.1433 | 1 | NaN | 3701 | 1 | 1607472000000 | NaN | NaN | NaN | 0.01 | 7.89 | 2 | NaN | 1 | 0.0006 | 1 | 1 | 1 | 1 | 439 | 0 | 2246 | 2 | 0.0295 | 1 | 1607943600000 | 5 | 1 | 2 | 1.11 | 4.8 | 1025656 | 1 | 1 | 8966 | 1 | 13.9 | 127 | 0.05 | 0.0338 |  |  |  |  | Available | 40 |  | 0 | 0 | 6271 | 14.19 | 2 | 2 |  | 0 | 0 | 49.99 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 1 | 0 | 970 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 1 | 1 | 1 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 30 | 30 | 0 | 1.4 | 20 | 1.5 | 80 | 1 | 0 | 11 | 1 | 0 | 0 | 0 | 0 | 7 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 35 | [5 empty] | 0 | 0 | 0 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 200 | -1000 |  | -200 | -1700 | 10 | 0 | 50 | 1500 | 5.6 | 6.7 | 6.9 | 0.1 | 3 | 0.1 | 0 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 3.5 |  | 0 | 0 | 0.2 | 4.2 |  | 10 | 0 |  |  |  | 0 |  | 5 | 5 | 5 | 5 | 5 | 60 | 20 | 40 | 30 | 50 | 180 | 35 | 40 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 2 | 10 | 2 | 1 | 1 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 2 | 10 | 2 | 1 | 1 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 2 | 10 | [479 empty] | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 2 | 2 | 0 | 8.5 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 5000 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 2500 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 135 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 4 | 12000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 10 | 0 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 32 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 | 0.95 | 0 | 60 | -33 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | 85 | 110 | 90 | 95 | 100 | 105 | 0.85 | 0.9 | 0.95 | 1 | -0.97 | -0.95 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 1 | 40 | 0 | 30 | 30 | 10 | 10 | 10 | 3 | 1 | 10000 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 4 | 4 | 0.01 | 0.01 | 0.2 | 0.2 | 0 | 1.11 | 0 | 1.11 | 0 | 30 | 0 | 2 | 0 | 100 | 100 | 10 | 50 | 50 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 5000 | -5000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 51.5 | 47.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 1 | 115 | 85 | 35 | 10 | 0 | 0 | 1 | -0.2 | 50 | 110 | 80 | 1 | 0 | 323 | 200 | 1 | 200 | 10 | 2 | 0.8 | 3 | 4 | 10 | 0.5 | 4 | 20000 | 20 | 10 | 5 | 10000 | 0 | 0 | 0 | 0 | 20000 | 120 | 88 | 45 | 0 | 10 | 0 | 0 | 0 | -0.4 | 50 | 110 | 80 | 0 | 1 | 400 | 200 | 0 | 100 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 90 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 6 | 0 | 6000 | 250 | 100 | 50 | 75 | 500 | 100 | 460 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 5 | 35 | 30 | 60 | 490 | 490 | 300 | 30 | 120 | 0 |  | 1 | 0 | 0 | 1 | 1 | 0 | 0 |  | 1 |  | 0 |  |  |  | 1 | 1 |  |  |  | 1 | 1 | 0 | 1 |  | 1 | 1 | 1 |  | 1 | 1 | [8 empty] | 0 | 1 |  | 0 | 0 |  |  | 1 |  | 0 | 1 | 1 | 0 |  | 1 | 1 | 1 | 1 |  | 0 |  |  |  | 12.5 |  | 624 |  |  |  |  | 15 | 0 | 360 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.2 | 100 | 0.01 | 100 | 41 | 0 | 1 | 3.5 | 100 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 60 | 30 | 0 | 100 | 0 | 0 | 0 | -5 | 2 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 35 | 30 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 200 | 168 | 75 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 65 | 4 | 0 | 0 | 0 | -2.5 | 10 | 1 | 20 | 15 | 1 | 2 | 1 | 1.82 | 0.6 | 0.6 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0.2 | 0 | 0 | 0 | 7 | 15 | 0.01 | 0.4 | 0 | 60 | 30 | 0.1 | 0 | 0 | 0 | 1200 | 1400 | 0 | 0.5 | 450 | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 0.125 | 0.06 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 1 | 0 | 0.72 | 0.72 | 0.72 | 0.72 | 1.2 | 0.1 | 300 | 300 | 300 | 300 | 0 | 50 | 50 | 50 | 50 | 50 | 120 | 0 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.15 | 3.6621 | 25 | 2.9297 | 100 | 0 | 6 | 0.1 | 0.5 | 1 | 3.5 | 100 | 2 | 25 | 10 | 250 | 3 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 | 1 | 1 | 4000 | 2000 | 20000 | 10000 | 4500 | 2250 | 8 | 4 | 2 | 1 | 30 | 150 | 20 | 120 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 0 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | [66 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 1 | 1 | 1200 | 38000 |  |  |  | 44800 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 100 | 1000 | 680 | 640 | 0 | 650 | 5 | 650 | 640 | 5 | 650 | 5 | 1000 | 5 | 15 | 300 | 20 | 50 | 650 | 5 | 200 | 5 | 1000 | 175 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 20 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 30 | 20 | 5 | 10 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | 0 | 20 |  | 0.98 | 1 | -0.98 | -0.95 | 0.8 | -0.93 | 1 | 7 | 0.95 | -0.95 | 20 | 80 | 5590 | 88 | 90 | 2.01 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 0 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 85 | 90 | 85 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 48.5 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 35 | 300 |  | 75 | 1.03 | 1 | 0 | 1 | 180 | 0.1 | 1.11 | 60 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 4500 | 0 | 5000 | 40 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 2250 | 4500 | 1 | 2 | 0 | 1 | 1 | 2 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 4 | 20 | 0.8 | -0.925 | 1 | 0 | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 10000 | 0 | 0 | 0 | 0 | 1 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -4000 | 4000 | 0 | 0 | 4 | 20 | -4000 | 4000 | 5000 | 1 | 0 | 0.8 | -0.92 | -3600 | 3600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 10 | 3.3 | 0.2 | 3.2 | 0.05 | 1.5 | 1.7 | 0.05 | 0.05 | 87 | 5 | 94 | 2 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 30 |  |  | 20 |  |  |  | 3 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.4 | 0.1 | 0.5 | 500 | 1500 | 3.5 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1.5 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 75 | 2 | 79 | 2 | 38 | 3 | 0 | 0 | 85 | 0.1 | 0 | 0 | 1 | 0 | 0 | 0 | 70 | 120 | 2 | 2 | 0 | 0 | 0 | 70 | 120 | 2 | 2 | 1 | 62 | 2 | 1 |  | 76 | 120 | 0.5 | 0.5 | 0 | 0 | 0 | 133 | 133 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 82 | 0 | 0 | 0 | 5 | 20 | 0 | 2 | 30 | 90 | 0 | 0 | 0 | 200 | -200 | 0 | -70 | 100 | -100 | 0 | 0 | 0 | 200 | -200 | 20 | 30 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 9.5 | 10 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 10 | 0 | 0 | 1 | 90 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 18 | 18 | 18 | 18 | [5 empty] | 4 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 924 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 1 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 0 | 0 | 20 | 4000 | 4000 |  | 850 | 30 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 3 | 3 | 3 | 3 | -5 | -5 | -5 | -5 | 13 | 13 | 13 | 13 | 4.5 |  | 45 | 270 | 70 | -144 | 0 | 80 | 350 | [24 empty] | 0 | 4 | 500 | 30 |  | 4000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 380 | 1 | -30 | -9 | 4500 | 2250 | 10 | 4500 | 2250 | 60 | 0 | 0 | [6 empty] | 0 | 0.39054 |  | 0.0583 | 2.5 | 1.1 | [5 empty] | 4501 | 2247 | 5931 | 3044 | 1500 | 1499 |  | 53 | 53 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4922 | 2159 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4922 | 2159 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4922 | 2159 | 1500 | 1500 |  | 50 | 50 |  | 660 |  | 0 | 1000 | 300 | 48 | -1.6 | -4 | 100 | 10 | 0 | 1 | 10 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 |  | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 10 | 0 | 0.5 | 0 | 0 | 60000 | 0 | 60000 | 0 |  | 5 | 0 | 1 | 1 |  |  |  | 85 |  | 48 | [14 empty] | 53 | 53 | 53 | 53 | [10 empty] | 0 | 0 | 1 | 3 | 57 | 59 | 2 | 2 | 60 |  | 48 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 350 | 200 | 200 | 100 | [8 empty] | -1250 | 5000 |  | 0.2 | 100 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.4 |  |  | 100 | 0.2 |  | 100 |  | 100 | 100 | [11 empty] | 0.2 | 100 | 200 | [43 empty] | 0 | 0.1 | 100 | 0.01 | 100 | 80 | 0 | 1 | 4.5 | 1 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 60 | 68 | 0 | 100 | 0 | 0 | 0.1 | 100 | 0.01 | 100 | 40 | 0 | 0 | 4.6 | 1 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 58 | 70 | 100 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 80 | 0 | 1 | 4.2 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 30 | 35 | 40 | 100 | 40 | 0 | 0.001 | 1 | 1 | 10 | 0.4 | 0 | 1 | 3.5 | 1 | 1 | 1 | 1 | 0 | 0 | 1.1 | 0.7 | 1 | 0 | 100 | 0 | 0 | 0.1 | 0.05 | 0.01 | 100 | 35 | 0 | 1 | 15 | 1 | 1 | 1 | 1 | 0 | 0 | 140 | 130 | 135 | 0 | 100 | 50 | 0 | 0.3 | 100 | 0.01 | 100 | 80 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 47 | 30 | 45 | 0 | 100 | 10 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0 | 0.1 | 100 | 205 | 0 | 1 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 28 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | [42 empty] | 0 | 0.3 | 100 | 80 | 0 | 1 | 6 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 40 | 100 | 0.01 | 50 | 0 | 100 | 10 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 0 | 0 | 10 | 150 | 150 | 100 | 205 | 0 | 48 | 50 | 0 | 3000 | 6000 | 3000 | 6000 | 6 | 6 | 0 | 5000 | -5000 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 100 | 50 | 0 | 0.1 | 100 | 40 | 0 | 1 | 0.5 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 140 | 120 | 100 | 0.05 | 128 | 0 | 100 | 40 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 |  |  |  |  | 12 | 2 | 5 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 80 | 0 | [6 empty] | 0.01421 | 0.29619 | 0.88857 | 100 | 0 | 0 | 0.44428 | 0.23695 | 100 | 2 | 0 | 20 | 5000 | 5000 | 60 | 75 | 90 | 100 |  | 4 | 20 | 2250 | 4500 | 2.5 | 2 | 40 | 45 |  | -2 | -2 | -2 | -2 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -145 | 10 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 4500 | 4500 | 4500 | 4500 | 64 | 0.72 | 0.72 | 0.72 | 0.72 | 0.5 | 0.72 | 0.72 | 0.72 |  | 10 | 5 | 95 | 1 | 1 | 100.4 | 103.4 | 98 | 91 | 103.4 | 40 | 65 | 85 | 80 |  | 110 | 125 | 90 | 70 | 140 | 1 | 80 | 8 | 83 | 1 | 20 | 5.55 | 3 | 5 | 85 |  |  | 10 | 4 | 4 | 4 | 4 | 56 | 56 | 56 | 56 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 16 | 16 | 200 | 200 | 200 | 200 | 200 | 200 | 1 | 1200 | 150 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4 | [30 empty] | 1 | 100 | 100 | 33 | 1 | 60 | 60 | 60 | 30 | 0 | 5 | 0 | 0 | 0 | 100 | 125 | 135 | 95 | 60 | 110 | 0 | 1800 | 0 | 0 | 0 | 1 | 3150 | 180 | 330 | 110 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1650 | 10 | 200 | 400 | 2800 | 5 | 10000 | 0 | 3850 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 1 | 1200 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 800 |  | 0.16406 | 2.1973 | 4.3945 | 95 | 2 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1501 | 6.7 | 0 | 95 | 85 | 85 | 95 | 95 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.65 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.1 |  |  | 0.58 | [13 empty] | 1 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 1 | [28 empty] | 1 | 1 | 1 | 2 | 0 | 2 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  |  | 4500 | 0 | 0 | 0 | 0 | 0 | 4500 | 0 |  |  | 0.97 | 0.97 | 0 | 0 | 0 | 0 | 0 | 0 | 15.8 | 4.9 | -49.97 | 3.927 | 0.0445 | 0.74909 | 0 | 0.5 | 4494 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 935 | 926 | 236 | 240 | 313 | 32 | 33 | 32 | 1155 | 1238 | 1305 | 0 | 376 | 44 | 31 | 35 | 300 | 81.37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 361 | 362 | 362 | 363 | 362 | 362 | 363 | 362 | 364 | 363 | 364 | 361 | 362 | 362 | 361 | 361 | 363 | 366 | 365 | 365 | 363 | 360 | 361 | 490 | 496 | 494 | 490 | 495 | 492 | 494 | 494 | 493 | 493 | 491 | 496 | 493 | 494 | 491 | 491 | 493 | 493 | 493 | 496 | 495 | 496 | 493 | 493 | 5077 | Sending | 30 | 45 | 45 | 46 | 46 | 46 | 45 | 45 | 45 | 45 | 45 | 44 | 44 | 46 | 44 | 44 | 45 | 46 | 44 | 45 | 46 | 23.6379 | 24.5327 | 24.6886 | 22.5357 | 26.8347 | 25.4358 | 26.6363 | 21.832 | 25.9369 | 24.3389 | 19.8496 | 26.8222 | 21.7304 | 23.0366 | 25.435 | 25.7801 | 24.8664 | 26.9089 | 27.2397 | 23.2351 | 26.6006 | 25.149 | 25.9392 | 22.0148 | 1012 | 885 | 611 | 1136 | 924 | 721 | 929 | 1013 | 847 | 761 | 719 | 635 | 1261 | 926 | 1013 | 594 | 595 | 672 | 793 | 1304 | 882 | 1171 | 793 | 921 |  | 51 | 1 | [11 empty] | 30.4 | 30.3 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 969 | 0 | 0 | 0 | 29.9 | 0 | 0 | 0 | 1.45 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 | 0 | 7.77 | 0 | 7.54 | 0 | 7.63 | 0 | 7.61 | 0 | 7.78 | 0 | 7.59 | 0 | 7.75 | 0 | 7.65 | 0 | 7.79 | 0 | 7.82 | 0 | 7.93 | 0 | 7.6 | 0 | 7.74 | 0 | 7.73 | 0 | 7.56 | 0 | 7.82 | 0 | 7.73 | 0 | 8.01 | 0 | 7.66 | 0 | 8.03 | 0 | 7.65 | 0 | 7.76 | 0 | 7.58 | 0 | 7.79 | 0 | -0.19 | 0 | -0.25 | 0 | 0.08 | 0 | -0.37 | 0 | 0.06 | 0 | -0.34 | 0 | -0.12 | 0 | 0.09 | 0 | -0.31 | 0 | -0.18 | 0 | -0.17 | 0 | -0.21 | 0 | 0.21 | 0 | -0.09 | 0 | -0.45 | 0 | 0.2 | 0 | -0.17 | 0 | -0.23 | 0 | -0.18 | 0 | -0.1 | 0 | -0.36 | 0 | -0.02 | 0 | -0.42 | 0 | 0.1 | 0 | 7.57 | 0 | 7.59 | 0 | 7.73 | 0 | 7.51 | 0 | 7.61 | 0 | 7.5 | 0 | 7.68 | 0 | 7.53 | 0 | 7.51 | 0 | 7.78 | 0 | 7.81 | 0 | 7.59 | 0 | 7.79 | 0 | 7.6 | 0 | 7.52 | 0 | 7.78 | 0 | 7.58 | 0 | 7.58 | 0 | 7.85 | 0 | 7.85 | 0 | 7.76 | 0 | 7.74 | 0 | 7.51 | 0 | 7.86 | 0 | -0.06 | 0 | -0.35 | 0 | -0.27 | 0 | -0.15 | 0 | -0.27 | 0 | -0.39 | 0 | -0.13 | 0 | -0.35 | 0 | -0.29 | 0 | -0.01 | 0 | -0.12 | 0 | -0.28 | 0 | 0.01 | 0 | -0.09 | 0 | -0.37 | 0 | -0.13 | 0 | -0.08 | 0 | 0.04 | 0 | -0.11 | 0 | 0.01 | 0 | -0.28 | 0 | -0.36 | 0 | -0.33 | 0 | -0.35 |  | 0 | 0 | 0 | 0 | 5 | 0 | 1.9 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 1.3 | 0 | 0 | 0 | 0.97 |  | 0 | 0 | 0 | 0 |  | 1.9 | 1.9 | 1.9 | 1.9 | 0 | 0 | 0 | 0 |  | 1501 | 0 |  | 52.8 |  |  | 0 | 0 | BMW DINGOLFING 2.4
24 |  |  |  |  | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","rem_conn":"Back-NoSSL-NoProxy","dataItems":"4802/9421","agent_conn":"Back-SSL-NoProxy","mon_conn":"Prim-SSL-NoProxy"} | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11 | 0 | 4.72 | 0 | 0 | 0.98 | 19.5 | 989 |  |  |  | 0 | 0 | 0 | 0 | 0.05 | 0 | 0.06 | 0 | 0 | 0 | 4.4.0.9 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0 |  |  | 0 | 0 |  | 0 | -4 | 3 | 0 | 0.1 | 0 | 0 | 0.98 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 |  |  |  |  | 2000 | 0 | 2000 | 500 | 250 | 0 | 0 | 0 | 0 | 0 | 581 | 1227 | 3222 | 195 | 492356 | 592356 | 692356 | 792356 | 8003 | 8003 | 8003 |  | 316 |  | 32 | 0 | 74 | 48.2 | 0 | 75 | 7.4 | 0 | 20 | 19.5 | 20 | 1 | 1 | 50 | 99 | 3276.6 | 100 | 50 | 32 | 0 | 75 | 58.4 | 0 | 80 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [53 empty] | 2 | 51 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 51 | 2 | 2 | 51 | 2 | 2 | 51 | [99 empty] | 40.8251 | 40.8564 | [30 empty] | 0 | [12 empty] | 0 | 0 |  |  | 0 | 0 |  | 0 |  | 0 | [20 empty] | 0 | [16 empty] | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 1608825981992 | 0 | 49 | 1 |  | 0 | 0 |  | 39.96 | 0 |  | 7644 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 51 | 50 | 51 | 49 | 50 | 50 | 50 | 50 | 49 | 52 | 51 | 52 | 50 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 553 | 52 | 560 | 48 | 547 | 0 | 18 | 0 | 0 | 0 | 13 | [42 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 13.3 |  |  | 17.3 | 17.1 | 17.6 | 0 |  |  |  |  | 14 | 1606649632360 |  | 0 | 0 | 0 | 0 | 10723 | 6341 | 10707 | 6148 | 10669 | 6046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24320 | 2026 | 12 | 0.073 | 2000 | 2.14 | 0.7 | 0.08 | -0.01 |  | 0 | 58.4 | 14.3 | 0 | 0 | 7.4 | 48.2 | 3 | 0 | 0 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.2 | 0 | 0 | 0 | 54.6 | 52.5 | 54.2 | 54.1 | 58.5 | 58 | 59.1 | 0 | 1.24 | 0 | 0 | 0 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 88 | 0 | 0 | 0 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 0 | 8019.1 | 0 | 0 | 0 | 8019.1 | 8018.9 | 8019 | 8018.9 | 8018.9 | 8019 | 8018.9 | 0 | 2018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 3 | 2018 | 17 | 3 | 2018 | 15 | 3 | 2018 | 15 | 3 | 2018 | 15 | 3 | 2018 | 15 | 3 | 2018 | 15 | 3 | 2018 | 15 | 3 | 0 | 0 | 0 | 40005 | 0 | 0 | 0 | 40004 | 39877 | 39852 | 39875 | 39891 | 39836 | 39853 | 0 | 7.7 | 0 | 0 | 0 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.683 | 0.3 | 0 | 18 | 0 | 0 | 7.84 | 7.68 | 7.67 | 7.71 | 7.82 | 7.82 | 7.69 | 7.77 | 7.62 | 7.65 | 7.51 | 7.57 | 7.59 | 7.76 | 7.54 | 7.67 | [8 empty] | -0.45 | -0.24 | -0.26 | -0.24 | -0.16 | -0.24 | -0.27 | -0.1 | -0.28 | -0.21 | -0.36 | -0.23 | -0.36 | -0.32 | -0.28 | -0.29 | [8 empty] | 7.66 | 7.66 | 7.59 | 7.75 | 7.76 | 7.66 | 7.77 | 7.71 | 7.71 | 7.64 | 7.65 | 7.55 | 7.65 | 7.59 | 7.52 | 7.79 | [8 empty] | -0.47 | -0.29 | -0.22 | -0.14 | -0.23 | -0.24 | -0.26 | -0.34 | -0.33 | -0.16 | -0.22 | -0.15 | -0.32 | -0.27 | -0.36 | -0.13 | [8 empty] | 17777.1 | 0 | 2715.1 | 0 | 0 | 0.02 | 0 | 0 | 1.04 | 0 | 0 | 4.4.0.0.0 | 4.4.0.0.1 | 4.4.0.0.0 | 4.4.1.0.8 | 4.4.0.0.6 | 4.4.4.5.8 | 4.4.0.0.0 | 4.4.0.0.8 | 4.4.2.0.8 | 4.4.0.0.7 | 4.4.0.0.0 | 4.4.0.0.8 | 4.4.0.0.0 | 4.4.0.0.0 | 4.4.0.0.9 | 4.4.0.3.9 | 4.4.0.0.0 | 4.4.0.0.2 | 4.4.0.0.0 | 4.4.0.0.2 | 4.4.0.0.8 | 4.3.0.0.0 | 0.0.0.0.0 | 4.4.0.0.6 | 4.4.1.0.0 | 4.4.0.0.8 | 4.4.0.0.9 | 4.3.0.0.0 | 4.4.0.0.6 | 4.4.0.0.0 | M01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | [82 empty] | Available | 40 |  |  |  |  | 24.98 | 2 | 2 |  | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 0 | 1 | 1000 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 1 | 1 | 1 | 1.4 | 1.5 | 20 | 60 | 60 | 30 | 30 | 60 | 30 | 30 | 0 | 1.4 | 20 | 1.5 | 70 | 1 | 0 | 11 | 1 | 0 | 0 | 0 | 0 | 7 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 40 | [5 empty] | 1700 | 800 | 1 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 200 | -300 |  | -100 | -700 | 6 | 0 | 50 | 1500 | 3 | 3.7 | 3.9 | 0.1 | 2.7 | 0.1 | 0 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 3.7 |  | 0 | 0 | 0 | 0 |  | 10 | 0 |  |  |  | 0 |  | 5 | 5 | 5 | 5 | 5 | 60 | 28 | 30 | 30 | 50 | 180 | 28 | 20 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 0 | 0 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | [479 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 10 | 0 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 32 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 | 0.95 | 0 | 60 | -27 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | 85 | 110 | 90 | 95 | 100 | 105 | 0.85 | 0.9 | 0.95 | 1 | -0.97 | -0.95 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 1 | 1 | 40 | 0 | 30 | 30 | 10 | 10 | 10 | 3 | 1 | 10500 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 4 | 4 | 0.01 | 0.01 | 0.2 | 0.2 | 1 | 1.11 | 1 | 1.11 | 1 | 30 | 0 | 0 | 0 | 100 | 100 | 10 | 50 | 50 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 5000 | -5000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 51.5 | 47.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 1 | 115 | 85 | 35 | 10 | 0 | 0 | 1 | -0.25 | 50 | 110 | 80 | 1 | 0 | 183 | 200 | 1 | 110 | 10 | 2 | 0.8 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 85 | 45 | 0 | 10 | 0 | 0 | 0 | -0.4 | 50 | 110 | 80 | 0 | 0 | 400 | 200 | 0 | 100 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 90 | 45 | [6 empty] | 0 | [34 empty] | 0 | 0 | 0 | 1 | 1 | 0 | 0 |  | 0 |  | 0 |  |  |  | 1 | 1 |  |  |  | 1 | 0 | 1 | 1 |  | 1 | 1 | 1 |  | 0 | 1 | [8 empty] | 0 | 1 |  | 0 | 0 |  |  | 1 |  | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 11.5 |  | 616 |  |  |  |  | 11 | 0 | 233 |  | 1 | 1 | 1 | [9 empty] | 3 | 0.3 | 0.1 | 0.1 | 100 | 45 | 0 | 1 | 6 | 100 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 54 | 50 | 0 | 100 | 0 | 1 | 0 | -5 | 15 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 1 | 6 | 0 | 0 | 0 | 1 | 6 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 41 | 30 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 200 | 168 | 75 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 65 | 1 | 0 | 0 | 0 | -4.5 | 10 | 0 | 60 | 55 | 0 | 2 | 1.65 | 1.82 | 0.6 | 0.6 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0 | 0 | 0 | 0 | 15 | 30 | 0.01 | 0.4 | 0 | 60 | 30 | 0.3 | 0 | 0 | 0 | 1200 | 1400 | 0 | 0.5 | 360 | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 0.3 | 0.1 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 0.2 | 300 | 300 | 300 | 300 | 0 | 50 | 50 | 50 | 50 | 50 | 120 | 1 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.3 | 1 | 25 | 6.5 | 100 | 0 | 8 | 0 | 0.5 | 0 | 4 | 50 | 0 | 25 | 10 | 250 | 6 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 | [16 empty] | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 0 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 |  |  |  |  | 0 | 0 | 0 | 0 | [66 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 1200 | 1000 |  |  |  | 1000 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 50 | 1000 | 680 | 640 | 5 | 650 | 5 | 1000 | 640 | 5 | 680 | 5 | 1000 | 5 | 15 | 300 | 20 | 50 | 650 | 5 | 1000 | 5 | 1000 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | -0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 20 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 20 | 5 | 0 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | 4 | 20 |  | 0.98 | 1 | -0.98 | -0.95 | 0.8 | -0.95 | 1 | 4 | 0.95 | -0.95 | 20 | 80 | 3325 | 88 | 90 | 2.41 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 1 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 75 | 90 | 75 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 44 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 45 | 300 |  | 75 | 1.21 | 0 | 0 | 0 | 180 | 0.1 | 1.11 | 60 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 930 | 0 | 5000 | 50 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 500 | 1000 | 1 | 4 | 0 | 0 | 1 | 2 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 4 | 20 | 0.8 | -0.95 | 0.99 | 0 | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 400 | 0 | 0 | 0 | 0 | 1 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -100 | 100 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 0 | 0 | 1 | -0.9 | -100 | 100 | [12 empty] | 10 | 2.5 | 0.2 | 3.1 | 0.05 | 1.5 | 1.7 | 0.05 | 0.05 | 92 | 5 | 94 | 5 | 55 | 5 | 97 | 0.1 | 40 | 3 | 60 | 4 |  |  | 1 | 30 |  |  | 20 |  |  |  | 12 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.5 | 0.1 | 0.5 | 500 | 1500 | 4.6 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 120 | 2 | 120 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 0 | 0 | 75 | 120 | 2 | 2 | 0 | 1 | 0 | 85 | 120 | 2 | 2 | 0 | 62 | 2 | 1 |  | 88 | 120 | 2 | 0.1 | 0 | 0 | 0 | 200 | 200 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 82 | 0 | 0 | 0 | 5 | 20 | 0 | 2 | 30 | 90 | 0 | 0 | 1 | 100 | -100 | 3 | -50 | 100 | -100 | 0 | 0 | 1 | 100 | -100 | 20 | 30 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 9.5 | 10 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 1 | 1 | 90 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 18 | 18 | 18 | 18 | [5 empty] | 15 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 462 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 1 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 4 | 0 | 20 | 4000 | 4000 |  | 550 | 25 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 3 | 3 | 3 | 3 | -5 | -5 | -5 | -5 | 14 | 14 | 14 | 14 | 4.5 |  | 45 | 660 | 660 | -144 | 0 | 60 | 50 | [24 empty] | 0 | 4 | 500 | 30 |  | 8000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 250 | 0 | -20 | -20 | 2678 | 1339 | 10 | 2175 | 1280 | 60 | 0 | 0 | [6 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2674 | 1338 | 4405 | 2252 | 1499 | 1500 |  | 54.2 | 54.2 |  | 400 | [7 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2190 | 1100 | 2950 | 1550 | 1500 | 1500 |  | 47 | 44 |  | 400 | [7 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2190 | 1100 | 2950 | 1550 | 1500 | 1500 |  | 47 | 44 |  | 400 | [7 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2190 | 1100 | 2950 | 1550 | 1500 | 1500 |  | 47 | 44 |  | 400 |  | 0 | 1000 | 300 | 48 | -1.6 | -4 | 100 | 6 | 0 | 1 | 6 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6 | 0 | 0.5 | 0 | 0 | 120000 | 0 | 120000 | 0 |  | 4 | 0 | 0 | 0 |  |  |  | 75 |  | 40 | [14 empty] | 54 | 55 | 55 | 50 | [10 empty] | 0 | 0 | 1 | 3 | 51 | 53 | 2 | 2 | 62 |  | 45 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.25 |  |  | 100 | 0.2 |  | 298 | 105 | 110 | 105 | [8 empty] | -750 | 3000 |  | 0.2 | 100 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.4 |  |  | 100 | 0.2 |  | 100 |  | 100 | 100 | [11 empty] | 0.2 | 100 | 200 | [43 empty] | 4 | 0.1 | 100 | 100 | 100 | 50 | 0 | 1 | 2 | 1 | 99 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 84 | 74 | 76 | 0 | 100 | 0 | 1 | 0.2 | 100 | 100 | 100 | 60 | 0 | 1 | 2 | 1 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 84 | 75 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 20 | 100 | 0 | 0.5 | 0.003 | 1 | 1 | 10 | 0.6 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1.05 | 0.8 | 1 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | 0 | 0.1 | 0.5 | 0.5 | 100 | 40 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 55 | 50 | 55 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 40 | 0 | 0 | 10 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 78 | 10 | 100 | 10 | 3 | 0.3 | 100 | 60 | 0 | 1 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 83 | 80 | 100 | 100 | 81 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | [42 empty] | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 0 | 0 | 10 | 150 | 150 | 100 | 205 | 0 | 48 | 50 | 0 | 3000 | 6000 | 3000 | 6000 | 6 | 6 | 0 | 5000 | -5000 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 100 | 50 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 |  |  |  |  | 12 | 2 | 5 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 80 | 0 | [6 empty] | 0.09478 | 0.4474 | 0.7987 | 100 | 0 | 0.02843 | 0.74047 | 0.4739 | 85 | 0 | 0 | 20 | 1340 | 2678 | 60 | 75 | 90 | 100 |  | 4 | 20 | 1339 | 2678 | 2 | 2 | 40 | 45 |  | -3 | -6 | -6 | -6 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -130 | 8 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 2678 | 2678 | 2678 | 2678 | 50 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 |  | 10 | 2 | 96 | 1 | 1 | 100.6 | 103.1 | 98 | 91 | 103.1 | 50 | 65 | 85 | 75 |  | 105 | 120 | 95 | 70 | 140 | 0 | 80 | 2 | 81 | 1 | 22.7 | 3.85 | 2 | 2 | 84 |  |  | 10 | 4 | 4 | 4 | 4 | 58 | 58 | 58 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [30 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.8 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1450 | 10 | 200 | 400 | 2800 | 5 | 400 | 0 | 3450 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 0 | 1500 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 900 |  | 0.15 | 0.64 | 7.7 | 80 | 0 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1500 | 6.7 | 0 | 95 | 85 | 85 | 95 | 95 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.7 | 30 | 70 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.1 |  |  | 0.74 | [13 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | [28 empty] | 1 | 1 | 0 | 2 | 0 | 2 | 1 | 1 | 0 | 2 | 1 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2678 | 0 | 0 | 0 | 0 | 0 | 2678 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 5.8 | -7.93 | 4.238 | 0.1355 | 0.52455 | 0 | 0.63 | 1339 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 65 | 0 | 0 | 68 | 0 | 0 | 23 | 0 | 0 | 240 | 0 | 140 | 0 | 0 | 83 | 300 | 61.1 | [73 empty] | Sending | 30 | 47 | 48 | 46 | 46 | 47 | 48 | 47 | 49 | 53 | 52 | 50 | 49 | 47 | 48 | 49 | 49 | 48 | 53 | 49 | 49 | [24 empty] | 1865 | 2257 | 1409 | 2126 | 2170 | 2219 | 2193 | 1840 | 1674 | 2193 | 2300 | 2319 | 2004 | 1923 | 1841 | 2132 | [9 empty] | 0 | 1 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 982 | 0 | 0 | 0 | 23.8 | 0 | 0 | 0 | 1.25 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 | [16 empty] | 0 | 7.84 | 0 | 7.68 | 0 | 7.67 | 0 | 7.71 | 0 | 7.82 | 0 | 7.82 | 0 | 7.69 | 0 | 7.77 | 0 | 7.62 | 0 | 7.65 | 0 | 7.51 | 0 | 7.57 | 0 | 7.59 | 0 | 7.76 | 0 | 7.54 | 0 | 7.67 | [16 empty] | 0 | -0.45 | 0 | -0.24 | 0 | -0.26 | 0 | -0.24 | 0 | -0.16 | 0 | -0.24 | 0 | -0.27 | 0 | -0.1 | 0 | -0.28 | 0 | -0.21 | 0 | -0.36 | 0 | -0.23 | 0 | -0.36 | 0 | -0.32 | 0 | -0.28 | 0 | -0.29 | [16 empty] | 0 | 7.66 | 0 | 7.66 | 0 | 7.59 | 0 | 7.75 | 0 | 7.76 | 0 | 7.66 | 0 | 7.77 | 0 | 7.71 | 0 | 7.71 | 0 | 7.64 | 0 | 7.65 | 0 | 7.55 | 0 | 7.65 | 0 | 7.59 | 0 | 7.52 | 0 | 7.79 | [16 empty] | 0 | -0.47 | 0 | -0.29 | 0 | -0.22 | 0 | -0.14 | 0 | -0.23 | 0 | -0.24 | 0 | -0.26 | 0 | -0.34 | 0 | -0.33 | 0 | -0.16 | 0 | -0.22 | 0 | -0.15 | 0 | -0.32 | 0 | -0.27 | 0 | -0.36 | 0 | -0.13 | [17 empty] | 0 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1500 | 0 |  | 32 |  |  | 0 | 0 | FRONERI - FERENTINO
25 |  |  |  |  | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","rem_conn":"Back-NoSSL-NoProxy","dataItems":"4664/9424","agent_conn":"Prim-NoSSL-NoProxy","mon_conn":"Back-SSL-NoProxy"} | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.01 | 0 | 0 | 1 | 19.3 | 0 |  |  |  | 0 | 0 | [8 empty] | 4.4.0.8 | 8410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 1 | 0 | 1 | 0 |  |  | 0 | 0 |  | 0 | -1013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 |  |  |  |  | 0 | 0 | 0 | 4661 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 1220 | 3220 | 9220 | 499220 | 599220 | 699220 | 799220 | 780 | 780 | 780 |  | 40 |  | 26.6 | 0 | 0 | 14.7 | 100 | 0 | 14.9 | 0 | 20 | 19.3 | 0 | 1 | 1 | 50 | 99 | 3276.6 | 100 | 30 | 26.6 | 0 | 75 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [53 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | [99 empty] | 40.0671 | 39.9665 | [99 empty] | 1606784138142 | 0 | 49 | 1 |  | 0 | 0 |  | 32.39 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 3276 | 3276 | 48 | 50 | 50 | 51 | 51 | 53 | 52 | 53 | 52 | 52 | 50 | 51 | 52 | 52 | 53 | 52 | 52 | 52 | 52 | 49 | 0 | 0 | 0 | 0 | 51 | 557 | 53 | 560 | 48 | 554 | 0 | 18 | 0 | 0 | 0 | 6 | [44 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 1 | [7 empty] | 14 | 14.8 |  |  | 14.9 | 15.9 | 16.8 | 0 |  |  |  |  | 1 | 1606650938553 | [18 empty] | 10027 | 3342 | 3 | 0 | 0 | 1.94 | 0.5 | 0.1 | -0.08 |  | 0 | 59 | 12.5 | 0 | 3276.6 | 14.9 | 14.7 | 30 | 0 | 0 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 0 | 0 | 0 | 56.2 | 55.3 | 0 | 0 | 54.5 | 54.5 | 55.8 | 55.8 | 54.5 | 59.2 | 52.1 | 56.1 | 1.24 | 1.24 | 0 | 0 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1.24 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 88 | 88 | 0 | 0 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 789.7 | 789.7 | 0 | 0 | 789.7 | 789.7 | 789.7 | 789.7 | 789.7 | 789.7 | 789.7 | 789.7 | 2018 | 2018 |  |  | 0 |  |  | 0 |  |  |  |  | 2018 |  |  | 2018 |  |  | 2018 |  |  | 2018 |  |  | 2018 |  |  | 2018 |  |  | 2018 |  |  | 2018 |  |  | 40156 | 40157 | 0 | 0 | 40161 | 40158 | 40155 | 40154 | 40160 | 40041 | 40045 | 40166 | 7.7 | 7.7 | 0 | 0 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.745 | 0.25 | 0 |  | 0 | 0 | 7.37 | 7.59 | 7.39 | 7.51 | 7.7 | 7.62 | 7.51 | 7.68 | 7.51 | 7.63 | 7.44 | 7.62 | 7.57 | 7.54 | 7.47 | 7.59 | 7.56 | 7.49 | 7.63 | 7.58 |  |  |  |  | -0.35 | -0.14 | -0.38 | -0.44 | -0.49 | -0.32 | -0.49 | -0.14 | -0.47 | -0.41 | -0.62 | -0.33 | 0.04 | -0.37 | -0.18 | -0.33 | -0.2 | -0.3 | -0.28 | -0.16 |  |  |  |  | 7.52 | 7.58 | 7.54 | 7.56 | 7.63 | 7.61 | 7.58 | 7.55 | 7.56 | 7.52 | 7.57 | 7.63 | 7.55 | 7.61 | 7.55 | 7.59 | 7.52 | 7.65 | 7.51 | 7.7 |  |  |  |  | -0.23 | -0.29 | -0.3 | -0.22 | -0.14 | -0.37 | -0.44 | -0.36 | -0.03 | -0.25 | -0.48 | -0.32 | -0.28 | -0.26 | -0.3 | -0.3 | -0.48 | -0.3 | -0.34 | -0.4 |  |  |  |  | 2623.1 |  | 316.9 |  | 0 | 0.02 | 0 | 0 | 1.04 | 0 | 0 | 4.4.0.0.0 | 4.4.0.0.1 | 4.4.0.0.0 | 4.4.1.0.8 | 4.4.0.0.6 | 4.4.4.0.8 | 4.4.0.0.0 | 4.4.0.0.8 | 4.4.2.0.8 | 4.4.0.0.7 | 4.4.0.0.0 | 4.4.0.0.8 | 4.4.0.0.0 | 4.4.0.0.0 | 4.4.0.0.8 | 4.4.0.1.5 | 4.4.0.0.0 | 4.4.0.0.2 | 4.4.0.0.0 | 4.4.0.0.2 | 4.4.0.0.8 | 4.3.0.0.0 | 0.0.0.0.0 | 4.4.0.0.6 | 4.4.1.0.0 | 4.4.0.0.8 | 4.4.0.0.7 | 4.3.0.0.0 | 4.4.0.0.6 | 4.4.0.0.0 | TOMVILLE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 960 | [82 empty] | Available | 40 |  |  |  |  | 19.5 | [41 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 1 | 0 | 970 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 1 | 1 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 30 | 30 | 0 | 1.4 | 20 | 1.5 | 80 | 1 | 0 | 11 | 3 | 0 | 0 | 0 | 0 | 7 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 30 | [5 empty] | 0 | 0 | 1 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 200 | -300 |  | -100 | -700 | 6 | 0 | 50 | 1500 | 3 | 3.7 | 3.9 | 0.1 | 2.7 | 0.1 | 0 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 2.8 |  | 0 | 0 | 0.2 | 0 |  | 10 | 0 |  |  |  | 0 |  | 5 | 5 | 5 | 5 | 5 | 60 | 28 | 40 | 30 | 50 | 180 | 28 | 40 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 0 | 0 | 1 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 0 | 0 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [481 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 18 | 18 | 19 | 19 | 18 | 18 | 18 | 18 | 10 | 0 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 32 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 | 0.95 | 0 | 60 | -27 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | 85 | 110 | 90 | 95 | 100 | 105 | 0.85 | 0.9 | 0.95 | 1 | -0.97 | -0.95 | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 1 | 40 | 0 | 30 | 30 | 10 | 10 | 10 | 3 | 1 | 10500 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 4 | 4 | 0.01 | 0.01 | 0.2 | 0.2 | 1 | 1.11 | 1 | 1.11 | 1 | 30 | 0 | 0 | 0 | 100 | 100 | 10 | 50 | 50 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 5000 | -5000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 51.5 | 47.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 1 | 115 | 85 | 35 | 8 | 330 | 0 | 1 | -0.2 | 50 | 110 | 80 | 1 | 0 | 229 | 200 | 1 | 200 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 20000 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 20000 | 120 | 88 | 45 | 0 | 10 | 0 | 0 | 0 | -0.4 | 50 | 110 | 80 | 0 | 0 | 400 | 200 | 0 | 100 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 90 | 45 | [41 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0 |  | 0 |  |  |  | 1 | 1 |  |  |  | 1 | 0 | 1 | 1 |  | 1 | 1 | 0 |  | 0 | 0 | [8 empty] | 0 | 1 |  | 0 | 0 |  |  | 1 |  | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 1 |  | 620 |  |  |  |  | 11 | 0 | 300 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.5 | 0.1 | 0.1 | 100 | 41 | 0 | 0 | 1 | 100 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 30 | 0 | 100 | 0 | 0 | 0 | -5 | 15 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 33 | 30 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 231 | 168 | 2 | 502 | 11 | 255 | 0 | 255 | 0 | 1 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 65 | 1 | 0 | 0 | 0 | -4.5 | 10 | 0 | 60 | 55 | 0 | 2 | 1.65 | 1.82 | 0.6 | 0.6 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0 | 0 | 0 | 0 | 15 | 30 | 0.01 | 0.4 | 0 | 60 | 30 | 0.1 | 0 | 0 | 0 | 1200 | 1400 | 0 | 0.5 | 360 | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 0.3 | 0.1 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 0.2 | 300 | 300 | 300 | 300 | 0 | 50 | 50 | 50 | 50 | 50 | 120 | 1 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 0 | 1 | 3 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.3 | 1 | 25 | 6.5 | 100 | 0 | 20 | 0 | 0.5 | 0 | 4 | 50 | 0 | 25 | 10 | 250 | 6 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 | [16 empty] | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 0 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 |  |  |  |  | 0 | 0 | 0 | 0 | [66 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 1200 | 1000 |  |  |  | 1000 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 50 | 1000 | 680 | 640 | 5 | 650 | 5 | 1000 | 640 | 5 | 680 | 5 | 1000 | 5 | 15 | 300 | 20 | 50 | 650 | 5 | 1000 | 5 | 1000 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 20 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 20 | 5 | 10 | 5 | 10 | 5 | 10 | 5 | 10 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | 4 | 20 |  | 0.98 | 1 | -0.98 | -0.95 | 0.8 | -0.95 | 1 | 4 | 0.95 | -0.95 | 20 | 80 | 4078 | 88 | 90 | 1.85 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 0 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 85 | 90 | 85 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 45 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 45 | 300 |  | 75 | 0.952 | 0 | 0 | 0 | 180 | 0.1 | 1.11 | 60 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 930 | 0 | 5000 | 50 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 500 | 1000 | 1 | 0 | 0 | 0 | 1 | 2 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 0 | 20 | 0.8 | -0.95 | 1 | 0 | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 400 | 0 | 0 | 0 | 0 | 1 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -100 | 100 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 0 | 0 | 1 | -0.9 | -100 | 100 | [12 empty] | 10 | 2.5 | 0.2 | 3.1 | 0.05 | 1.5 | 1.7 | 0.05 | 0.05 | 120 | 5 | 120 | 5 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 30 |  |  | 20 |  |  |  | 3 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.5 | 0.1 | 0.5 | 500 | 1500 | 4.6 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 120 | 2 | 120 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 0 | 0 | 75 | 120 | 2 | 2 | 0 | 1 | 0 | 120 | 120 | 2 | 2 | 0 | 62 | 2 | 1 |  | 74 | 120 | 2 | 0.5 | 0 | 0 | 0 | 200 | 200 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 82 | 0 | 0 | 0 | 5 | 20 | 0 | 2 | 30 | 90 | 0 | 0 | 0 | 200 | -200 | 0 | -50 | 100 | -100 | 0 | 0 | 0 | 200 | -200 | 20 | 30 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 9.5 | 10 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 1 | 90 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 18 | 18 | 18 | 18 | [5 empty] | 15 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 462 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 1 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 4 | 0 | 20 | 4000 | 4000 |  | 700 | 30 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 5 | 5 | 2 | 2 | -5 | -5 | -5 | -5 | 14 | 14 | 14 | 14 | 4.5 |  | 45 | 660 | 660 | -144 | 0 | 60 | 50 | [24 empty] | 0 | 4 | 500 | 30 |  | 8000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 320 | 0 | -24 | -13 | 2717 | 1600 | 10 | 2717 | 1600 | 40 | 0 | 0 | [6 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 3353 | 1658 | 4674 | 2100 | 1500 | 1499 |  | 50.9 | 48.1 |  | 500 | [7 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2733 | 1362 | 3050 | 1650 | 1500 | 1500 |  | 50 | 45 |  | 500 | [7 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2733 | 1362 | 3050 | 1650 | 1500 | 1500 |  | 50 | 45 |  | 500 | [7 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2733 | 1362 | 3050 | 1650 | 1500 | 1500 |  | 50 | 45 |  | 500 |  | 0 | 1000 | 300 | 48 | -1.6 | -4 | 100 | 6 | 0 | 1 | 6 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6 | 0 | 0.5 | 0 | 0 | 120000 | 0 | 120000 | 0 |  | 4 | 0 | 0 | 0 |  |  |  | 75 |  | 40 | [14 empty] | 55 | 50 | 50 | 50 | [10 empty] | 0 | 0 | 1 | 3 | 47 | 49 | 2 | 2 | 62 |  | 40 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 300 | 195 | 200 | 100 | [8 empty] | -925 | 3700 |  | 0.2 | 80 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.4 |  |  | 100 | 0.2 |  | 100 |  | 100 | 100 | [11 empty] | 0.2 | 100 | 200 | [43 empty] | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 70 | 70 | 100 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 70 | 70 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 1.5 | 0.003 | 1 | 1 | 10 | 0.6 | 0 | 1 | 4 | 1 | 1 | 1 | 1 | 0 | 0 | 1.1 | 0.7 | 1 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | 0 | 0.1 | 0.5 | 0.5 | 100 | 40 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 50 | 0 | 100 | 10 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | [42 empty] | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 0 | 0 | 10 | 150 | 150 | 100 | 205 | 0 | 48 | 50 | 0 | 3000 | 6000 | 3000 | 6000 | 6 | 6 | 0 | 5000 | -5000 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 100 | 50 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 |  |  |  |  | 12 | 2 | 5 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 80 | 0 | [6 empty] | 0.09478 | 0.15 | 0.4 | 100 | 0 | 0.02843 | 0.74047 | 0.4739 | 100 | 0 | 4 | 20 | 1678 | 3356 | 60 | 75 | 90 | 100 |  | 4 | 20 | 1678 | 3356 | 2 | 2 | 35 | 45 |  | -6 | -6 | -6 | -6 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -145 | 10 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 3356 | 3356 | 3356 | 3356 | 50 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 |  | 10 | 0 | 150 | 1 | 1 | 101 | 105.8 | 98 | 91 | 105.8 | 50 | 65 | 85 | 75 |  | 105 | 120 | 95 | 70 | 140 | 0 | 80 | 0 | 120 | 1 | 22.7 | 3.85 | 0 | 0 | 120 |  |  | 10 | 4 | 4 | 4 | 4 | 58 | 58 | 58 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [30 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1450 | 10 | 200 | 400 | 2800 | 5 | 400 | 0 | 3450 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 0 | 1500 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 900 |  | 0.15 | 0.64 | 7.7 | 80 | 0 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1500 | 6.7 | 0 | 95 | 85 | 85 | 95 | 95 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.1 |  |  | 0.74 | [13 empty] | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | [28 empty] | 1 | 1 | 1 | 2 | 0 | 0 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 3356 | 0 | 0 | 0 | 0 | 0 | 1678 | 0 | [10 empty] | 2097.1 | 6.7 | -29.83 | 4.248 |  | 1.0102 | 0 | 0.56 | 3356 |  |  |  | 1 | 0 | 1 |  | 0 | 171 | 0 | 0 | 237 | 0 | 0 | 25 | 0 | 0 | 500 | 0 | 244 | 0 | 0 | 66 | 300 | 66.96 | [73 empty] | Sending | 30 | 47 | 47 | 47 | 46 | 46 | 47 | 47 | 46 | 46 | 47 | 46 | 48 | 51 | 49 | 50 | 47 | 47 | 48 | 47 | 47 | [24 empty] | 932 | 1138 | 2579 | 1363 | 1304 | 2722 | 974 | 1177 | 2721 | 1178 | 976 | 2578 | 1207 | 1202 | 2864 | 1012 | 1225 | 1769 | 1261 | 852 | [5 empty] | 0 | [19 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1006 | 0 | 0 | 0 | 24.1 | 0 | 0 | 0 | 1.45 |  |  |  | 0 | 0 | 0 | 0 | [8 empty] | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 | [8 empty] | 0 | 7.37 | 0 | 7.59 | 0 | 7.39 | 0 | 7.51 | 0 | 7.7 | 0 | 7.62 | 0 | 7.51 | 0 | 7.68 | 0 | 7.51 | 0 | 7.63 | 0 | 7.44 | 0 | 7.62 | 0 | 7.57 | 0 | 7.54 | 0 | 7.47 | 0 | 7.59 | 0 | 7.56 | 0 | 7.49 | 0 | 7.63 | 0 | 7.58 | [8 empty] | 0 | -0.35 | 0 | -0.14 | 0 | -0.38 | 0 | -0.44 | 0 | -0.49 | 0 | -0.32 | 0 | -0.49 | 0 | -0.14 | 0 | -0.47 | 0 | -0.41 | 0 | -0.62 | 0 | -0.33 | 0 | 0.04 | 0 | -0.37 | 0 | -0.18 | 0 | -0.33 | 0 | -0.2 | 0 | -0.3 | 0 | -0.28 | 0 | -0.16 | [8 empty] | 0 | 7.52 | 0 | 7.58 | 0 | 7.54 | 0 | 7.56 | 0 | 7.63 | 0 | 7.61 | 0 | 7.58 | 0 | 7.55 | 0 | 7.56 | 0 | 7.52 | 0 | 7.57 | 0 | 7.63 | 0 | 7.55 | 0 | 7.61 | 0 | 7.55 | 0 | 7.59 | 0 | 7.52 | 0 | 7.65 | 0 | 7.51 | 0 | 7.7 | [8 empty] | 0 | -0.23 | 0 | -0.29 | 0 | -0.3 | 0 | -0.22 | 0 | -0.14 | 0 | -0.37 | 0 | -0.44 | 0 | -0.36 | 0 | -0.03 | 0 | -0.25 | 0 | -0.48 | 0 | -0.32 | 0 | -0.28 | 0 | -0.26 | 0 | -0.3 | 0 | -0.3 | 0 | -0.48 | 0 | -0.3 | 0 | -0.34 | 0 | -0.4 | [9 empty] | 0 | 1 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1500 | 0 |  | 26.6 |  |  | 0 | 0 | TOM VILLE
26 |  |  |  |  | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","agent_conn":"Prim-SSL-NoProxy","mon_conn":"Prim-NoSSL-NoProxy","rem_conn":"Back-SSL-NoProxy"} | 0 | 0 | 0 | 0 | 0 | 0 | -0.92 | 5.2 | 0 | 0 | 0 | -1001 | 0 | 6.46 | 0 | 3.93 | 4.24 | -3270 | 0 |  |  |  | 0 | 0 | 0 | 0 | 4.78 | 6.04 | 4.79 | 0 | 0 | 0 | 4.5.1.9 | 5419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 |  | 16983 | 0 | 0 | 0 | 0 | -5271 | 0 | -1380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18 | 0.01 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 747 | 2727 | 6927 | 98770 | 490727 | 590727 | 690727 | 790727 | 9273 | 9273 | 9273 |  | 165 |  | 52.3 | 28.3 | 70 | 67.5 | 100 | 68 | 67.2 | 66.6 | 20 | -3270 | 0 | 0 | 0 | 0 | 85 | 0 | 100 | 50 | 52.3 | 100 | 83.3 | 83.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [53 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.62 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1608950342332 | 0 | 44 | 1 | 0 | 0 | 0 | 0 | -1.01 | 0 |  | 9109 |  |  |  |  | 0 | 0 | 0 | 0 | 39642 | 39578 | 0 | 0 | 0 |  | 0 | 0 | 554 | 561 | 555 | 554 | 554 | 558 | 560 | 559 | 559 | 556 | 555 | 555 | 554 | 556 | 552 | 556 | 556 | 556 | 558 | 559 | 555 | 557 | 556 | 554 | 556 | 555 | 561 | 561 | 552 | 552 | 0 | 0 | 360 | 362 | 361 | 9 | [42 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 40.6 |  |  | 91.8 | 91.6 | 92.1 | 29.4 |  |  |  |  | 1 | 1604965750368 |  | 4424 | 0.948 | 50.02 | 0 | 10300 | 5951 | 10285 | 5943 | 10309 | 5943 | 10308 | 5943 | 10293 | 5955 | 10306 | 5937 | 0 | 0 | 0 | 0 | 0 | 0 | 2.26 | -38.5 | 4.05 | 0.73 |  | 0 | 83.3 | 71.7 | 0 | 67.5 | 67.2 | 67.9 | 1 | 0 | 0 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 67.2 | 71.3 | 70.2 | 81 | 67.2 | 65 | 73 | 74.8 | 68.3 | 66.1 | 64.6 | 72.5 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 9297.1 | 9297.1 | 9297.1 | 9297.1 | 9297.1 | 9297.1 | 9297 | 9518.8 | 9136 | 9297.1 | 9297.1 | 9297.1 | 2018 | 2018 | 10 | 8 | 2018 | 10 | 8 | 2018 | 10 | 8 | 10 | 8 | 2018 | 10 | 8 | 2018 | 9 | 8 | 2018 | 10 | 8 | 2018 | 8 | 10 | 2018 | 7 | 9 | 2018 | 7 | 9 | 2018 | 10 | 8 | 2018 | 10 | 8 | 42597 | 42580 | 42555 | 42593 | 42543 | 42539 | 42544 | 43201 | 42839 | 42845 | 42554 | 42594 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | -14.3 | -14.3 | -14.3 | -14.3 | -14.3 | -14.3 | -14.3 | -14.3 | -14.3 | -14.3 | -14.3 | -14.3 | -14.3 | -14.3 | -14.3 | -14.3 | -14.3 | -14.3 | -14.3 | -14.3 | -14.3 | -14.3 | -14.3 | -14.3 | 348 | 284 | 269 | 141 | 189 | 189 | 141 | 174 | 237 | 174 | 126 | 205 | 269 | 174 | 110 | 126 | 174 | 158 | 110 | 110 | 189 | 189 | 174 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 427 | 402 | 329 | 341 | 256 | 378 | 317 | 329 | 427 | 280 | 586 | 293 | 293 | 317 | 427 | 402 | 280 | 244 | 341 | 268 | 390 | 329 | 390 | -0.009 | 5.26 | 0 | 0 | 0 | 0 | 7.28 | 7.39 | 7.44 | 7.42 | 7.5 | 7.39 | 7.19 | 7.16 | 7.39 | 7.43 | 7.6 | 7.19 | 7.13 | 7.32 | 7.5 | 7.49 | 7.48 | 7.55 | 7.37 | 7.52 | 7.38 | 7.27 | 7.17 | 7.33 | -0.7 | -0.54 | -1.05 | -0.5 | -0.49 | -0.38 | -0.61 | -0.48 | -0.72 | -0.48 | -0.69 | -0.57 | -0.45 | -0.67 | -0.63 | -0.23 | -0.48 | -0.8 | -0.57 | -0.53 | -0.3 | -0.64 | -0.33 | -0.65 | 7.49 | 7.51 | 7.19 | 7.46 | 7.29 | 7.42 | 7.36 | 7.37 | 7.41 | 7.57 | 7.45 | 7.42 | 7.37 | 7.31 | 7.39 | 7.51 | 7.59 | 7.17 | 7.47 | 7.48 | 7.49 | 7.33 | 7.44 | 7.3 | -0.71 | -0.59 | -0.47 | -0.63 | -0.63 | -0.39 | -0.87 | -0.53 | -0.58 | -0.59 | -0.38 | -0.92 | -0.5 | -0.69 | -0.54 | -0.54 | -0.54 | -0.63 | -0.8 | -0.36 | -0.39 | -0.36 | -0.52 | -0.72 | 36840.6 | 0 | 11983.9 | 0 | 246 | 0.02 | 0 | 1383 | 1.1 | 0 | 10308 | 4.5.1.0.1 | 4.5.2.0.3 | 4.5.1.0.6 | 4.5.4.0.2 | 4.5.0.0.0 | 4.5.6.7.3 | 4.9.0.0.9 | 4.5.2.0.9 | 4.5.3.0.2 | 4.5.1.0.8 | 4.5.1.0.0 | 4.5.1.0.0 | 4.5.4.0.3 | 4.5.4.0.0 | 4.5.0.2.4 | 4.5.3.2.0 | 4.5.0.0.3 | 4.5.0.0.0 | 4.5.0.0.0 | 4.5.1.0.0 | 4.5.1.0.6 | 4.5.0.0.0 | 0.0.0.0.0 | 4.5.2.2.5 | 4.5.0.0.0 | 4.5.2.0.9 | 4.5.1.0.2 | 4.5.0.0.0 | 4.5.1.0.0 | 4.4.0.0.0 | M06 | 15.5 | 17.8 | 14.8 | 15.8 | 14.7 | 14.5 | 15.1 | 16.5 | 15.8 | 15.9 | 16 | 15.5 | 15.3 | 15.6 | 15.6 | 14.8 | 15.5 | 16.3 | 14.7 | 15.6 | 15.8 | 17.6 | 14.6 | 15.3 | 15.2 | 18 | 14.3 | 1603 | [31 empty] | 0 |  |  | 0 |  | 0 |  | 1691 | 0 |  |  | 0 | 1607644800000 |  | 0 | 399659 |  | 8.3 | 1 |  | 0 | 10 |  | 1 | 0 | 4 |  | 0 | 0 | 10 | 279 | 0 |  | 5 |  | 1 | 1.38 | 4.48 |  | 0 |  | 8920 |  | 13.39 | 118.9 | 0 | 340 |  |  |  |  | Running | 50 |  |  |  |  | 61.48 | 2 | 2 | 50.02 | 50.02 | 0 | 50.02 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 1 | 0 | 970 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 1 | 0 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 300 | 30 | 1 | 1.4 | 60 | 1.5 | 80 | 14 | 6 | 11 | 1 | 0 | 0 | 0 | 0 | 7 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 30 | [5 empty] | 0 | 0 | 1 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 200 | -800 |  | -200 | -1500 | 10 | 0 | 50 | 1500 | 5.6 | 6.7 | 6.9 | 0.1 | 2.7 | 0.1 | 0 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 5.4 |  | 0 | 0 | 0.2 | 0 |  | 10 | 0 |  |  |  | 0 |  | 5 | 5 | 5 | 5 | 5 | 60 | 28 | 40 | 30 | 50 | 180 | 28 | 40 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 0 | 0 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | [479 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 5 | 0 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 32 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 |  |  | 60 | -27 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | [12 empty] | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 1 | 1 | 40 | 0 | 30 | 30 | 10 | 10 | 10 | 3 | 1 | 10500 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 5 | 5 | 0.05 | 0.05 | 0.2 | 0.2 | 1 | 0.56 | 0 | 0.56 | 1 | 30 | 1 | 0 | 0 | 439.7 | 439.7 | 4.4 | 50 | 50 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 5000 | -5000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 47.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 0 | 110 | 90 | 35 | 10 | 0 | 0 | 1 | -0.2 | 50 | 110 | 80 | 0 | 0 | 301 | 200 | 1 | 105 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10000 | 0 | 0 | 0 | 0 | 10500 | 120 | 95 | 45 | 0 | 10 | 0 | 0 | 0 | -0.4 | 50 | 110 | 80 | 0 | 1 | 400 | 200 | 0 | 100 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 90 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 6000 | 250 | 100 | 50 | 80 | 500 | 100 | 460 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 5 | 30 | 30 | 70 | 490 | 490 | 300 | 30 | 120 | 30 |  | 1 |  | 0 | 1 | 0 | 0 | 0 |  | 0 |  | 0 |  |  |  | 1 | 1 |  |  |  | 0 | 0 |  | 1 |  | 1 | 1 | 0 |  | 0 | 1 | [8 empty] | 0 | 1 |  | 0 | 0 |  |  | 0 |  | 0 | 0 | 1 | 0 |  | 1 | 1 | 0 | 0 |  | 0 |  |  |  | 12.5 |  | 624 |  |  |  |  | 11 | 0 | 336 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.8 | 100 | 0.02 | 100 | 41 | 0 | 1 | 7 | 100 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 30 | 0 | 100 | 0 | 0 | 0 | -5 | 15 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 35 | 30 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 206 | 168 | 75 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 65 | 3 | 0 | 0 | 0 | -2.5 | 10 | 1 | 20 | 15 | 1 | 2 | 1 | 1.82 | 0.6 | 0.6 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0.05 | 0 | 0 | 0 | 15 | 30 | 0.01 | 0.4 | 0 | 60 | 30 | 0 | 0 | 0 | 0 | 1200 | 1400 | 0 | 0.5 | 450 | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 0.2 | 0.05 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1.2 | 0.1 | 280 | 280 | 280 | 280 | 0 | 50 | 50 | 50 | 50 | 50 | 120 | 1 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.3 | 1 | 25 | 5 | 100 | 0 | 10 | 0.01 | 0.5 | 1 | 3 | 60 | 2 | 25 | 10 | 250 | 3 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 | 0 | 1 | 4000 | 2000 | 20000 | 10000 | 4397 | 2198 | 8 | 4 | 2 | 1 | 30 | 150 | 20 | 120 | 0 | 1 | 1 | 1 | 1 | 0 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 0 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 |  | 1 | 650 | 700 | 1 | 0 | 0 | 0 | [66 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 1 | 1 | 1200 | 38000 |  |  |  | 44800 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 100 | 1000 | 680 | 640 |  | 650 |  |  | 640 | 5 | 650 | 5 | [7 empty] | 5 | 500 |  |  | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | -0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 20 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 10 | 20 | 5 | 0 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | [15 empty] | 5468 | 88 | 90 | 2.16 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 1 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 75 | 90 | 75 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 43.9 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 45 | 300 |  | 75 | 1.2 | 0 | 0 | 0 |  | 0.1 | 0.84 | 60 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 930 | 0 | 5000 | 50 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 500 | 1000 |  |  |  | 0 | 1 | 1 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 0 | 20 | 0.9 | -0.95 | 0.95 |  | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 10500 |  |  | 1 | 0 | 2 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -1476 | 3280 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 0 | 1 | 1 | -0.9 | -3400 | 3400 | 10 | 0 | 100 | 0 | 100 | 0 | 800 | -20 | 800 | -20 | 600 | 0 | 10 | 3.3 | 0.2 | 3.1 | 0.05 | 1.5 | 1.7 | 0.05 | 0.05 | 120 | 5 | 120 | 5 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 30 |  |  | 20 |  |  |  | 3 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.4 | 0.1 | 0.5 | 500 | 1500 | 3.5 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1.5 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 120 | 2 | 120 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 1 | 0 | 75 | 120 | 2 | 2 | 0 | 1 | 0 | 75 | 120 | 2 | 2 | 1 | 62 | 2 | 1 |  | 75 | 120 | 0.5 | 0.5 | 0 | 0 | 0 | 99 | 200 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 84 | 0 | 0 | 0 | 5 | 20 | 0 | 2 | 30 | 90 | 0 | 0 | 0 | 200 | -200 | 0 | -70 | 100 | -100 | 0 | 0 | 0 | 200 | -200 | 20 | 30 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 50 | 100 | 1 | 9.5 | 10 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 10 | 0 | 0 | 1 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 18 | 18 | 18 | 18 | [5 empty] | 4 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 924 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 1 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 0 | 0 | 20 | 4000 | 4000 |  | 850 | 30 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 3 | 3 | 3 | 3 | -5 | -5 | -5 | -5 | 13 | 13 | 13 | 13 | 4.5 |  | 45 | 270 | 70 | -144 | 0 | 80 | 350 | [24 empty] | 0 | 4 | 500 | 30 |  | 4000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 380 | 1 | -30 | -9 | 4300 | 1300 | 10 | 4300 | 2600 | 60 | 0 | 0 | [6 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4393 | 2198 | 5400 | 2777 | 1499 | 1499 |  | 51.8 | 51.8 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4901 | 2150 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4901 | 2150 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4901 | 2150 | 1500 | 1500 |  | 50 | 50 |  | 660 |  | 0 | 1000 | 300 | 48 | -1.6 | -4 | 100 | 10 | 0 | 1 | 10 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 |  | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 10 | 0 | 0.5 | 0 | 0 | 60000 | 0 | 60000 | 0 |  | 4 | 0 | 1 | 0 |  |  |  | 80 |  | 48 | [14 empty] | 52 | 53 | 53 | 53 | [10 empty] | 0 | 0 | 1 | 3 | 57 | 59 | 2 | 2 | 60 |  | 48 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 350 | 105 | 105 | 105 | [8 empty] | -1225 | 4900 |  | 0.2 | 100 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.4 |  |  | 100 | 0.2 |  | 100 |  | 100 | 100 | [11 empty] | 0.2 | 100 | 200 | [43 empty] | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 65 | 70 | 100 | 100 | 0 | 0 | 1 | 1 | 0.02 | 100 | 49 | 0 | 1 | 7 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 45 | 68 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 1.5 | 0.003 | 1 | 1 | 10 | 0.6 | 0 | 1 | 12 | 1 | 1 | 1 | 1 | 0 | 0 | 1.1 | 0.7 | 1 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | 0 | 0.1 | 0.5 | 0.5 | 100 | 40 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 50 | 0 | 100 | 10 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | [42 empty] | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 1 | 0 | 10 | 10 | 10 | 2 | 5 | 0 | 48 | 50 | 1 | 5000 | 8000 | 5000 | 8000 | 6 | 6 | 0 | 5000 | -5000 | 0 | 0 | 0.02 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 98.7 | 92.7 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 12 | 2 | 5 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 80 | 0 | [6 empty] | 0.01789 | 0.03456 | 0.60321 | 100 | 0 | 0 | 0.44428 | 0.23695 | 98 | 2 | 0 | 20 | 5000 | 5000 | 60 | 75 | 90 | 100 |  | 0 | 20 | 2198 | 4397 | 2.5 | 1.25 | 35 | 45 |  | -2 | -2 | -2 | -2 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -145 | 10 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 4397 | 4397 | 4397 | 4397 | 50 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 |  | 10 | 0 | 150 | 1 | 1 | 102 | 112 | 98 | 91 | 112 | 50 | 65 | 85 | 75 |  | 105 | 120 | 95 | 70 | 140 | 0 | 80 | 0 | 120 | 1 | 20 | 5.55 | 0 | 0 | 120 |  |  | 5 | 4 | 4 | 4 | 4 | 56 | 56 | 56 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [30 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.5 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1650 | 10 | 200 | 400 | 2800 | 5 | 10000 | 0 | 3850 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 0 | 1500 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 800 |  | 0.2 | 0.7 | 4 | 98 | 2 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1500 | 6.7 | 0 | 95 | 85 | 85 | 95 | 95 | 9.54 | 9.971 | 720 |  |  | 1.28 | 1.55 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.1 |  |  | 0.58 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | [28 empty] | 1 | 1 | 0 | 2 | 0 | 2 | 1 | 1 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4207 |  |  | 4397 | 0 | 0 | 0 | 0 | 0 | 4397 | 4203 |  |  | 2.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185.1 | 21.1 | -38.75 | 4.052 |  | 0.725 | 0 | 0.56 | 4203 | 0 | 0 | 2.21 | 1 | 0 | 1 | 0 | 0 | 186 | 0 | 0 | 264 | 0 | 0 | 28 | 0 | 0 | 507 | 506 | 320 | 0 | 0 | 29 | 0 | 72.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 367 | 368 | 375 | 382 | 371 | 370 | 371 | 371 | 372 | 369 | 374 | 371 | 370 | 371 | 367 | 371 | 371 | 369 | 375 | 370 | 373 | 368 | 363 | 0 | 504 | 496 | 489 | 493 | 495 | 496 | 505 | 494 | 491 | 500 | 0 | 495 | 506 | 500 | 494 | 493 | 498 | 499 | 0 | 503 | 496 | 0 | 497 |  | Sending | 30 | 40 | 40 | 40 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 42 | 43 | 42 | 41 | 41 | 42 | 42 | 45 | 42 | 43 | 25 | 24.9 | 21.7004 | 22.3001 | 20.7004 | 24.8 | 19.9505 | 18.3037 | 25.9 | 21.8001 | 25.4003 | 25.5 | 27.9997 | 25.1 | 27.8016 | 19.7004 | 25.3004 | 26.8022 | 24.0022 | 17.5001 | 23.1005 | 25.2999 | 22.3005 | 31.0003 | 1517 | 2003 | 1880 | 2066 | 2003 | 1968 | 1783 | 1842 | 2016 | 1839 | 1843 | 1968 | 1967 | 1867 | 2131 | 1869 | 1950 | 2068 | 2120 | 1925 | 1578 | 2130 | 1880 | 2005 |  | 0 | 1 | [11 empty] | 68.1 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 251.6 | 0 | 0 | 0 | 1080 | 0 | 0 | 0 | 12.5 | 0 | 0 | 0 | 1.891 |  |  |  | 32.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 7 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 | 0 | 7.28 | 0 | 7.39 | 0 | 7.44 | 0 | 7.42 | 0 | 7.5 | 0 | 7.39 | 0 | 7.19 | 0 | 7.16 | 0 | 7.39 | 0 | 7.43 | 0 | 7.6 | 0 | 7.19 | 0 | 7.13 | 0 | 7.32 | 0 | 7.5 | 0 | 7.49 | 0 | 7.48 | 0 | 7.55 | 0 | 7.37 | 0 | 7.52 | 0 | 7.38 | 0 | 7.27 | 0 | 7.17 | 0 | 7.33 | 0 | -0.7 | 0 | -0.54 | 0 | -1.05 | 0 | -0.5 | 0 | -0.49 | 0 | -0.38 | 0 | -0.61 | 0 | -0.48 | 0 | -0.72 | 0 | -0.48 | 0 | -0.69 | 0 | -0.57 | 0 | -0.45 | 0 | -0.67 | 0 | -0.63 | 0 | -0.23 | 0 | -0.48 | 0 | -0.8 | 0 | -0.57 | 0 | -0.53 | 0 | -0.3 | 0 | -0.64 | 0 | -0.33 | 0 | -0.65 | 0 | 7.49 | 0 | 7.51 | 0 | 7.19 | 0 | 7.46 | 0 | 7.29 | 0 | 7.42 | 0 | 7.36 | 0 | 7.37 | 0 | 7.41 | 0 | 7.57 | 0 | 7.45 | 0 | 7.42 | 0 | 7.37 | 0 | 7.31 | 0 | 7.39 | 0 | 7.51 | 0 | 7.59 | 0 | 7.17 | 0 | 7.47 | 0 | 7.48 | 0 | 7.49 | 0 | 7.33 | 0 | 7.44 | 0 | 7.3 | 0 | -0.71 | 0 | -0.59 | 0 | -0.47 | 0 | -0.63 | 0 | -0.63 | 0 | -0.39 | 0 | -0.87 | 0 | -0.53 | 0 | -0.58 | 0 | -0.59 | 0 | -0.38 | 0 | -0.92 | 0 | -0.5 | 0 | -0.69 | 0 | -0.54 | 0 | -0.54 | 0 | -0.54 | 0 | -0.63 | 0 | -0.8 | 0 | -0.36 | 0 | -0.39 | 0 | -0.36 | 0 | -0.52 | 0 | -0.72 |  | 0 | 0 | 1 | 1 | 17 | 0 | 98 | 97.2 | 96.9 | 0 | 0 | 14.1 | 14.5 | 0 | 14.3 | 0 | 0 | 0 | 5.25 |  | 0 | 0 | 0 | 0 |  | 98 | 98 | 98 | 98 | 14.1 | 14.1 | 14.1 | 14.1 |  | 1500 | 1499 |  | 52.3 |  |  | 0 | 0 | ABINSK
27 |  |  |  |  | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","rem_conn":"Back-NoSSL-NoProxy","dataItems":"0/20","agent_conn":"Prim-SSL-NoProxy","mon_conn":"Prim-NoSSL-NoProxy"} | 0 | 0 | 0 | 0 | 0 | 0 | -0.92 | 5.56 | 0 | 0 | 0 | -1398 | 0 | 6.46 | 0 | 4.22 | 4.17 | -3270 | 0 |  |  |  | 0 | 0 | 0 | 0 | 4.71 | 6.1 | 4.72 | 0 | 0 | 0 | 4.5.1.9 | 6050 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 |  | 18053 | 0 | 0 | 0 | 0 | -5594 | 0 | -1354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0.04 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | 8 | 8 | 499008 | 599008 | 699008 | 799008 | 8221 | 24650 | 24650 |  | 224 |  | 51.6 | 29.9 | 70 | 67.4 | 100 | 68 | 67.1 | 72.5 | 20 | -3270 | 0 | 0 | 0 | 0 | 85 | 0 | 100 | 50 | 51.6 | 100 | 83.1 | 83.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [53 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1583308008807 | 0 | 40 | 1 | 0 | 0 | 0 | 0 | 9.7 | 0 |  | 992 |  |  |  |  | 0 | 0 | 0 | 0 | 40818 | 41343 | 0 | 0 | 0 |  | 0 | 0 | 538 | 540 | 538 | 543 | 541 | 540 | 545 | 543 | 545 | 547 | 541 | 539 | 538 | 540 | 542 | 543 | 542 | 540 | 541 | 542 | 541 | 543 | 543 | 543 | 541 | 541 | 547 | 546 | 538 | 537 | 0 | 0 | 346 | 349 | 345 | 9 | [42 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.9 | 38.4 |  |  | 85.2 | 86.1 | 85.9 | 29.2 |  |  |  |  | 7257 |  |  | 4419 | 0.949 | 50 | 0 | 10302 | 5949 | 10279 | 5943 | 10294 | 5934 | 10287 | 5955 | 10287 | 5943 | 10306 | 5942 | 0 | 0 | 0 | 0 | 0 | 0 | 2.25 | -40.1 | 4 | 0.71 |  | 0 | 83.1 | 71.9 | 0 | 67.4 | 67.1 | 67.3 | 1 | 0 | 0 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 62.3 | 65.8 | 68.6 | 66.2 | 65.8 | 72.2 | 74.1 | 79.1 | 75.7 | 60.7 | 65.6 | 67.2 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 8252.5 | 8252.6 | 8252.6 | 8252.6 | 8252.5 | 8252.5 | 8252.2 | 8413.1 | 3928.3 | 8248.5 | 8252.4 | 8252.4 | 2018 | 2018 | 14 | 9 | 2018 | 7 | 9 | 2018 | 10 | 9 | 10 | 9 | 2018 | 7 | 9 | 2018 | 7 | 9 | 2018 | 6 | 9 | 2018 | 10 | 8 | 2015 | 26 | 5 | 2018 | 24 | 5 | 2018 | 10 | 9 | 2018 | 6 | 9 | 42904 | 42947 | 42871 | 42891 | 42873 | 42854 | 42825 | 42598 | 22498 | 41568 | 42889 | 42829 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 36 | 0 | 0 | -9.5 | -9.5 | -9.5 | -9.5 | -9.5 | -9.5 | -9.5 | -9.5 | -9.5 | -9.5 | -9.5 | -9.5 | -9.5 | -9.5 | -9.5 | -9.5 | -9 | -9.5 | -9.5 | -9.5 | -9.5 | -9.5 | -9.5 | -9.5 | 300 | 174 | 126 | 189 | 141 | 253 | 126 | 174 | 141 | 79 | 141 | 158 | 174 | 110 | 141 | 300 | 174 | 126 | 205 | 189 | 332 | 110 | 126 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 268 | 317 | 268 | 268 | 402 | 329 | 341 | 354 | 610 | 244 | 427 | 488 | 207 | 329 | 329 | 402 | 427 | 317 | 317 | 366 | 244 | 378 | 305 | 341 | 0.01 | 5.55 | 0 | 0 | 0 | 0 | 7.64 | 7.43 | 7.62 | 7.61 | 7.35 | 7.51 | 7.59 | -0.32 | 7.48 | 7.48 | 7.57 | 7.55 | 7.49 | 7.37 | 7.98 | 7.51 | 7.48 | 7.4 | 7.61 | 7.64 | 7.61 | 7.84 | 7.35 | 7.56 | -0.11 | -0.07 | -0.15 | -0.43 | -0.41 | 0.01 | -0.09 | -0.03 | -0.51 | -0.65 | -0.38 | -0.25 | 0.33 | -0.47 | 8.14 | -0.55 | -0.32 | -0.19 | -0.12 | 0.08 | -0.35 | -0.1 | 7.78 | 0.01 | 7.63 | 7.59 | 7.52 | 7.46 | 7.42 | 7.33 | 7.39 | 7.68 | 7.35 | 7.48 | 7.6 | 7.46 | 7.67 | 5.36 | 7.98 | 7.53 | 7.43 | 7.48 | 7.54 | 7.99 | 7.82 | 7.37 | 7.57 | 7.79 | -0.13 | -0.24 | -0.16 | -0.27 | -0.45 | -0.04 | -0.16 | -0.33 | -0.52 | -0.47 | -0.51 | -0.15 | 0.36 | -0.29 | -0.17 | -0.56 | -0.05 | -0.23 | -0.35 | 0.01 | -0.2 | -0.23 | -0.39 | -0.17 | 33704.1 | 0 | 10716.8 | 0 | 247 | 0.02 | 0 | 1379 | 1.1 | 0 | 10286 | 4.5.1.0.1 | 4.5.2.0.3 | 4.5.1.0.6 | 4.5.4.0.2 | 4.5.0.0.0 | 4.5.6.7.3 | 4.9.0.0.9 | 4.5.2.0.9 | 4.5.3.0.2 | 4.5.1.0.8 | 4.5.1.0.0 | 4.5.1.0.0 | 4.5.4.0.3 | 4.5.4.0.0 | 4.5.0.2.4 | 4.5.3.2.0 | 4.5.0.0.3 | 4.5.0.0.0 | 4.5.0.0.0 | 4.5.1.0.0 | 4.5.1.0.6 | 4.5.0.0.0 | 0.0.0.0.0 | 4.5.2.2.5 | 4.5.0.0.0 | 4.5.2.0.9 | 4.5.1.0.2 | 4.5.0.0.0 | 4.5.1.0.0 | 4.4.0.0.0 | M09 | 19.3 | 19.4 | 18.5 | 20.6 | 18.5 | 18.9 | 18.6 | 18.9 | 19.3 | 22 | 18.2 | 20.1 | 20.8 | 20.2 | 19.2 | 18.8 | 19 | 19 | 20.2 | 18.9 | 19.5 | 18.3 | 19.2 | 19.5 | 19.6 | 22 | 18.2 | 1648 | [31 empty] | 0 |  |  | 0 |  | 0 |  | 1795 | 0 |  |  | 17 | 1607299200000 |  | 0 | 385954 |  | 4.7 | 8 |  | 2 | 12 |  | 1 | 0 | 6 |  | 2 | 1620 | 15 | 294 | 0 |  | 1 |  | 4 | 3.58 | 2.63 |  | 1 |  | 7850 |  | 14.02 | 75.05 | 0 | 382 |  |  |  |  | Running | 50 |  | 0 | 0 |  | 36.76 | 2 | 2 | 50 | 50.02 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 1 | 0 | 970 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 1 | 0 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 300 | 30 | 1 | 1.4 | 60 | 1.5 | 80 | 14 | 6 | 11 | 1 | 0 | 0 | 0 | 0 | 7 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 30 | [5 empty] | 0 | 0 | 1 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 200 | -1000 |  | -200 | -1700 | 10 | 0 | 50 | 1500 | 5.6 | 6.7 | 6.9 | 0.1 | 2.7 | 0.1 | 0 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 5.4 |  | 0 | 0 | 0.2 | 0 |  | 10 | 0 |  |  |  | 0 |  | 5 | 5 | 5 | 5 | 5 | 60 | 28 | 40 | 30 | 50 | 180 | 28 | 40 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 0 | 0 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | [479 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 5 | 0 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 35 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 |  |  | 60 | -27 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | [12 empty] | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 1 | 1 | 40 | 0 | 30 | 30 | 10 | 10 | 10 | 3 | 1 | 10500 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 5 | 5 | 0.05 | 0.05 | 0.2 | 0.2 | 1 | 0.56 | 0 | 0.56 | 1 | 30 | 1 | 0 | 0 | 439.7 | 439.7 | 4.5 | 50 | 50 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 5000 | -5000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 47.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 0 | 110 | 90 | 35 | 10 | 0 | 0 | 1 | -0.2 | 50 | 110 | 80 | 0 | 0 | 301 | 200 | 1 | 105 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10000 | 0 | 0 | 0 | 0 | 10500 | 120 | 95 | 45 | 0 | 10 | 0 | 0 | 0 | -0.4 | 50 | 110 | 80 | 0 | 1 | 400 | 200 | 0 | 100 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 90 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30 | 30 | 70 | 490 | 490 | 300 | 0 | 120 | 30 |  | 1 |  | 0 | 1 | 0 | 0 | 0 |  | 0 |  | 0 |  |  |  | 1 | 1 |  |  |  | 0 | 0 |  | 1 |  | 1 | 1 | 0 |  | 0 | 1 | [8 empty] | 0 | 1 |  | 0 | 0 |  |  | 0 |  | 0 | 0 | 1 | 0 |  | 1 | 1 | 0 | 0 |  | 0 |  |  |  | 12.5 |  | 624 |  |  |  |  | 11 | 0 | 336 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.8 | 0.1 | 0.03 | 100 | 41 | 0 | 1 | 8 | 100 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 30 | 0 | 100 | 0 | 0 | 0 | -5 | 15 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 35 | 30 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 209 | 168 | 75 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 65 | 3 | 0 | 0 | 0 | -2.5 | 10 | 1 | 20 | 15 | 1 | 2 | 1 | 1.82 | 0.6 | 0.6 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0.05 | 0 | 0 | 0 | 15 | 40 | 0.01 | 0.4 | 0 | 60 | 30 | 0 | 0 | 0 | 0 | 1200 | 1400 | 0 | 0.5 | 450 | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 0.2 | 0.05 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1.2 | 0.1 | 280 | 280 | 280 | 280 | 0 | 50 | 50 | 50 | 50 | 50 | 120 | 1 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.3 | 1 | 25 | 5 | 100 | 0 | 10 | 0.01 | 0.5 | 1 | 3 | 60 | 2 | 25 | 10 | 250 | 3 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 | 0 | 1 | 4000 | 2000 | 20000 | 10000 | 4397 | 2198 | 0 | 0 | 2 | 0 | 30 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 0 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 |  | 1 | 650 | 700 | 1 | 0 | 0 | 0 | [66 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 1 | 1 | 1200 | 38000 |  |  |  | 44800 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 100 | 1000 | 680 | 640 |  | 650 |  |  | 640 | 5 | 650 | 5 | [7 empty] | 5 | 450 |  |  | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 20 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 10 | 20 | 5 | 0 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | [15 empty] | 5468 | 88 | 90 | 2.16 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 1 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 75 | 90 | 75 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 45 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 45 | 300 |  | 75 | 1.2 | 0 | 0 | 0 |  | 0.1 | 0.84 | 60 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 930 | 0 | 5000 | 50 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 500 | 1000 |  |  |  | 0 | 1 | 1 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 0 | 20 | 0.9 | -0.95 | 0.95 |  | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 10500 |  |  | 1 | 0 | 2 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -1476 | 3280 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 0 | 1 | 1 | -0.9 | -3400 | 3400 | 10 | 0 | 100 | 0 | 100 | 0 | 800 | -20 | 800 | -20 | 600 | 0 | 10 | 3.3 | 0.2 | 3.1 | 0.05 | 1.5 | 1.7 | 0.05 | 0.05 | 120 | 5 | 120 | 5 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 30 |  |  | 20 |  |  |  | 3 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.6 | 0.2 | 0.5 | 500 | 1500 | 3.5 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1.5 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 120 | 2 | 120 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 1 | 0 | 75 | 120 | 2 | 2 | 0 | 1 | 0 | 75 | 120 | 2 | 2 | 1 | 62 | 2 | 1 |  | 75 | 120 | 0.5 | 0.5 | 0 | 0 | 0 | 99 | 200 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 84 | 0 | 0 | 0 | 5 | 20 | 0 | 2 | 30 | 90 | 0 | 0 | 0 | 200 | -200 | 0 | -70 | 100 | -100 | 0 | 0 | 0 | 200 | -200 | 20 | 30 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 50 | 100 | 1 | 9.5 | 10 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 10 | 0 | 0 | 1 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 18 | 18 | 18 | 18 | [5 empty] | 4 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 924 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 1 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 0 | 0 | 20 | 4000 | 4000 |  | 850 | 30 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 2 | 3 | 3 | 3 | -5 | -5 | -5 | -5 | 13 | 13 | 13 | 13 | 4.5 |  | 45 | 270 | 70 | -144 | 0 | 80 | 350 | [24 empty] | 0 | 4 | 500 | 30 |  | 4000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 380 | 1 | -30 | -9 | 4300 | 1300 | 10 | 4300 | 2600 | 60 | 0 | 0 | [6 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4397 | 2190 | 5777 | 2939 | 1497 | 1499 |  | 51.2 | 51.9 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4900 | 2150 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4900 | 2150 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4900 | 2150 | 1500 | 1500 |  | 50 | 50 |  | 660 |  | 0 | 1000 | 300 | 48 | -1.6 | -4 | 100 | 10 | 0 | 1 | 10 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 |  | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 10 | 0 | 0.5 | 0 | 0 | 60000 | 0 | 60000 | 0 |  | 4 | 0 | 1 | 0 |  |  |  | 80 |  | 48 | [14 empty] | 52 | 53 | 53 | 53 | [10 empty] | 0 | 0 | 1 | 3 | 57 | 59 | 2 | 2 | 60 |  | 48 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 350 | 105 | 105 | 105 | [8 empty] | -1225 | 4900 |  | 0.2 | 100 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.4 |  |  | 100 | 0.2 |  | 100 |  | 100 | 100 | [11 empty] | 0.2 | 100 | 200 | [43 empty] | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 65 | 70 | 100 | 100 | 0 | 0 | 1 | 1 | 0.02 | 100 | 49 | 0 | 1 | 7 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 45 | 67 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 1.5 | 0.003 | 1 | 1 | 10 | 0.6 | 0 | 1 | 12 | 1 | 1 | 1 | 1 | 0 | 0 | 1.1 | 0.7 | 1 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | 0 | 0.1 | 0.5 | 0.5 | 100 | 40 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 50 | 0 | 100 | 10 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | [42 empty] | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 1 | 0 | 10 | 10 | 10 | 2 | 5 | 0 | 48 | 50 | 1 | 5000 | 8000 | 5000 | 8000 | 6 | 6 | 0 | 5000 | -5000 | 0 | 0 | 0.02 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 98.4 | 92.4 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 12 | 2 | 5 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 80 | 0 | [6 empty] | 0.01089 | 0.03021 | 0.57 | 100 | 0 | 0 | 0.44428 | 0.23695 | 99 | 2 | 0 | 20 | 5000 | 5000 | 60 | 75 | 90 | 100 |  | 0 | 20 | 2199 | 4397 | 2.5 | 1.25 | 35 | 45 |  | -2 | -2 | -2 | -2 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -145 | 10 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 4397 | 4397 | 4397 | 4397 | 50 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 |  | 10 | 0 | 150 | 1 | 1 | 102 | 112 | 98 | 91 | 112 | 50 | 65 | 85 | 75 |  | 105 | 120 | 95 | 70 | 140 | 0 | 80 | 0 | 120 | 1 | 20 | 5.55 | 0 | 0 | 120 |  |  | 5 | 4 | 4 | 4 | 4 | 56 | 56 | 56 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [30 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1650 | 10 | 200 | 400 | 2800 | 5 | 10000 | 0 | 3850 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 0 | 1500 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 800 |  | 0.2 | 0.7 | 4 | 98 | 8 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1500 | 6.7 | 0 | 95 | 85 | 85 | 95 | 95 | 9.54 | 9.971 | 720 |  |  | 1.28 | 1.55 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.1 |  |  | 0.58 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | [28 empty] | 1 | 1 | 0 | 2 | 0 | 2 | 1 | 1 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4191 |  |  | 4397 | 0 | 0 | 0 | 0 | 0 | 4397 | 4199 |  |  | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 18.5 | -40.09 | 3.99 |  | 0.70855 | 0 | 0.56 | 4199 | 0 | 0 | 2.2 | 1 | 0 | 1 | 0 | 0 | 378 | 0 | 0 | 141 | 0 | 0 | 31 | 0 | 0 | 577 | 576 | 198 | 0 | 0 | 26 | 0 | 69.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 365 | 0 | 372 | 374 | 370 | 370 | 367 | 372 | 368 | 370 | 371 | 370 | 368 | 371 | 366 | 374 | 0 | 0 | 370 | 362 | 370 | 365 | 371 | 494 | 495 | 495 | 496 | 495 | 496 | 497 | 496 | 497 | 495 | 497 | 496 | 496 | 496 | 497 | 496 | 496 | 495 | 496 | 496 | 493 | 496 | 495 | 500 |  | Sending | 30 | 40 | 40 | 40 | 41 | 39 | 40 | 39 | 39 | 39 | 40 | 39 | 40 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 33.2 | 32.7 | 18.501 | 29.9 | 31.1 | 34.599 | 23.3005 | 27.5008 | 32.7 | 19.3009 | 27.551 | 34.6991 | 29.4 | 26.4005 | 31.716 | 31.299 | 28.599 | 30.05 | 30.651 | 32.7991 | 25.7 | 30.2 | 32.5463 | 32.7214 | 1238 | 1320 | 978 | 1391 | 1126 | 1299 | 1226 | 1139 | 762 | 1495 | 1057 | 928 | 1132 | 1214 | 1390 | 1265 | 1406 | 1051 | 1183 | 1267 | 1459 | 1247 | 1117 | 1068 |  | 0 | 1 | [11 empty] | 67.4 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 253.4 | 0 | 0 | 0 | 1090 | 0 | 0 | 0 | 15.7 | 0 | 0 | 0 | 2.001 |  |  |  | 29.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 | 0 | 7.64 | 0 | 7.43 | 0 | 7.62 | 0 | 7.61 | 0 | 7.35 | 0 | 7.51 | 0 | 7.59 | 0 | -0.32 | 0 | 7.48 | 0 | 7.48 | 0 | 7.57 | 0 | 7.55 | 0 | 7.49 | 0 | 7.37 | 0 | 7.98 | 0 | 7.51 | 0 | 7.48 | 0 | 7.4 | 0 | 7.61 | 0 | 7.64 | 0 | 7.61 | 0 | 7.84 | 0 | 7.35 | 0 | 7.56 | 0 | -0.11 | 0 | -0.07 | 0 | -0.15 | 0 | -0.43 | 0 | -0.41 | 0 | 0.01 | 0 | -0.09 | 0 | -0.03 | 0 | -0.51 | 0 | -0.65 | 0 | -0.38 | 0 | -0.25 | 0 | 0.33 | 0 | -0.47 | 0 | 8.14 | 0 | -0.55 | 0 | -0.32 | 0 | -0.19 | 0 | -0.12 | 0 | 0.08 | 0 | -0.35 | 0 | -0.1 | 0 | 7.78 | 0 | 0.01 | 0 | 7.63 | 0 | 7.59 | 0 | 7.52 | 0 | 7.46 | 0 | 7.42 | 0 | 7.33 | 0 | 7.39 | 0 | 7.68 | 0 | 7.35 | 0 | 7.48 | 0 | 7.6 | 0 | 7.46 | 0 | 7.67 | 0 | 5.36 | 0 | 7.98 | 0 | 7.53 | 0 | 7.43 | 0 | 7.48 | 0 | 7.54 | 0 | 7.99 | 0 | 7.82 | 0 | 7.37 | 0 | 7.57 | 0 | 7.79 | 0 | -0.13 | 0 | -0.24 | 0 | -0.16 | 0 | -0.27 | 0 | -0.45 | 0 | -0.04 | 0 | -0.16 | 0 | -0.33 | 0 | -0.52 | 0 | -0.47 | 0 | -0.51 | 0 | -0.15 | 0 | 0.36 | 0 | -0.29 | 0 | -0.17 | 0 | -0.56 | 0 | -0.05 | 0 | -0.23 | 0 | -0.35 | 0 | 0.01 | 0 | -0.2 | 0 | -0.23 | 0 | -0.39 | 0 | -0.17 |  | 0 | 0 | 1 | 1 | 17 | 0 | 98.8 | 98.2 | 98 | 0 | 0 | 8.3 | 8 | 0 | 8 | 0 | 0 | 0 | 5.57 |  | 0 | 0 | 0 | 0 |  | 98.8 | 98.8 | 98.8 | 98.8 | 8.3 | 8.3 | 8.3 | 8.3 |  | 1500 | 1498 |  | 51.6 |  |  | 0 | 0 | ABINSK
28 |  |  |  |  | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","agent_conn":"Prim-SSL-NoProxy","mon_conn":"Prim-NoSSL-NoProxy","rem_conn":"Back-SSL-NoProxy"} | 0 | 0 | 0 | 0 | 0 | 0 | -0.92 | 5.27 | 0 | 0 | 0 | -1209 | 0 | 6.46 | 0 | 3.99 | 4.1 | -3270 | 0 |  |  |  | 0 | 0 | 0 | 0 | 4.75 | 6.12 | 4.74 | 0 | 0 | 0 | 4.5.1.9 | 5094 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 0 |  | 17249 | 0 | 0 | 0 | 0 | -5334 | 0 | -1303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.02 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 440 | 2440 | 6440 | 497800 | 597800 | 697800 | 797800 | 9560 | 16916 | 16916 |  | 253 |  | 51.4 | 25.8 | 70 | 67.1 | 100 | 68 | 67 | 78 | 20 | -3270 | 0 | 0 | 0 | 0 | 85 | 0 | 100 | 50 | 51.4 | 100 | 82.7 | 82.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [53 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1600851885734 | 0 | 44 | 1 | 0 | 0 | 0 | 0 | 15.53 | 0 |  | 2200 |  |  |  |  | 0 | 0 | 0 | 0 | 40367 | 40433 | 0 | 0 | 0 |  | 0 | 0 | 547 | 554 | 549 | 555 | 556 | 556 | 555 | 558 | 556 | 554 | 553 | 554 | 553 | 554 | 554 | 552 | 554 | 551 | 559 | 556 | 555 | 551 | 555 | 556 | 554 | 553 | 559 | 559 | 547 | 546 | 0 | 0 | 370 | 373 | 371 | 13 | [42 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.4 | 38.9 |  |  | 89.9 | 89.8 | 90.2 | 29.1 |  |  |  |  | 7379 | 1600851885734 |  | 4415 | 0.948 | 50.03 | 0 | 10307 | 5953 | 10280 | 5946 | 10302 | 5936 | 10288 | 5949 | 10284 | 5946 | 10287 | 5936 | 0 | 0 | 0 | 0 | 0 | 0 | 2.15 | -37.5 | 4.01 | 0.74 |  | 0 | 82.7 | 71.8 | 0 | 67.1 | 67 | 67 | 1 | 0 | 0 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.7 | 21.7 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 21.8 | 64.6 | 66.7 | 67.7 | 68.6 | 65.2 | 63.8 | 67.7 | 76 | 75.2 | 63.8 | 61.3 | 67.3 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 9583.4 | 9583.3 | 9583.3 | 9583.3 | 9583.3 | 9583.4 | 9200.1 | 9583.2 | 9583.2 | 9583.3 | 9583.4 | 9583.3 | 2018 | 2018 | 10 | 10 | 2018 | 8 | 10 | 2018 | 8 | 10 | 8 | 10 | 2018 | 8 | 10 | 2018 | 10 | 10 | 2018 | 7 | 9 | 2018 | 8 | 10 | 2018 | 8 | 10 | 2018 | 8 | 10 | 2018 | 10 | 10 | 2018 | 8 | 10 | 43188 | 43263 | 43222 | 43200 | 43187 | 43234 | 42869 | 43208 | 43195 | 43193 | 43264 | 43189 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 34 | 0 | 0 | -9.5 | -9.5 | -9.5 | -9.3 | -9.5 | -9.5 | -9.5 | -9.5 | -5.3 | -9.4 | -9.5 | -9.5 | -9.5 | -9.5 | -9.5 | -8.8 | -8.9 | -9.5 | -9.5 | -9.3 | -9.2 | -9.5 | -9.5 | -9.5 | 317 | 158 | 253 | 174 | 220 | 220 | 174 | 158 | 158 | 126 | 189 | 126 | 205 | 220 | 94 | 284 | 189 | 141 | 284 | 220 | 237 | 158 | 110 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 415 | 317 | 415 | 512 | 622 | 341 | 378 | 378 | 476 | 329 | 439 | 573 | 402 | 402 | 378 | 390 | 500 | 341 | 317 | 500 | 525 | 366 | 512 | 0.009 | 5.3 | 0 | 0 | 0 | 0 | 7.5 | 7.27 | 7.49 | 7.6 | 7.2 | 7.23 | 7.45 | 7.43 | 7.63 | 7.27 | 7.38 | 7.39 | 7.37 | 7.24 | 7.43 | 7.7 | 7.55 | 7.4 | 7.55 | 7.44 | 7.54 | 7.44 | 7.62 | 7.54 | -0.23 | -0.7 | -0.09 | -0.13 | -0.33 | -0.07 | -0.13 | -0.1 | -0.31 | -0.37 | -0.22 | -0.15 | -0.29 | -0.38 | -0.2 | 0.13 | -0.05 | -0.25 | -0.34 | 0.19 | -0.02 | 0.18 | 0.1 | -0.09 | 7.52 | 7.3 | 7.5 | 7.56 | 7.5 | 7.19 | 7.54 | 7.32 | 7.56 | 7.39 | 7.4 | 7.42 | 7.38 | 7.34 | 7.39 | 7.47 | 7.65 | 7.49 | 7.27 | 7.34 | 8.08 | 7.49 | 7.61 | 7.51 | -0.43 | -0.45 | -0.4 | -0.39 | -0.44 | -0.51 | -0.11 | -0.36 | -0.49 | -0.47 | -0.54 | -0.26 | -0.59 | -0.37 | -0.32 | -0.37 | -0.25 | -0.38 | -0.47 | -0.4 | -0.25 | -0.25 | -0.05 | -0.25 | 38156.2 | 0 | 12256.8 | 0 | 247 | 0.02 | 0 | 1380 | 1.1 | 0 | 10293 | 4.5.1.0.1 | 4.5.2.0.3 | 4.5.1.0.6 | 4.5.4.0.2 | 4.5.0.0.0 | 4.5.6.7.3 | 4.9.0.0.9 | 4.5.2.0.9 | 4.5.3.0.2 | 4.5.1.0.8 | 4.5.1.0.0 | 4.5.1.0.0 | 4.5.4.0.3 | 4.5.4.0.0 | 4.5.0.2.4 | 4.5.3.2.0 | 4.5.0.0.3 | 4.5.0.0.0 | 4.5.0.0.0 | 4.5.1.0.0 | 4.5.1.0.6 | 4.5.0.0.0 | 0.0.0.0.0 | 4.5.2.2.5 | 4.5.0.0.0 | 4.5.2.0.9 | 4.5.1.0.2 | 4.5.0.0.0 | 4.5.1.0.0 | 4.4.0.0.0 | M10 | 20.9 | 21.1 | 19.8 | 21.2 | 21 | 20.2 | 19.4 | 21.2 | 18.6 | 20.7 | 20.9 | 21.4 | 20.8 | 20.2 | 20.2 | 20.9 | 22.3 | 20.7 | 25.4 | 21.5 | 20.9 | 21.6 | 21.4 | 22.3 | 19.6 | 25.4 | 18.6 | 1574 | [31 empty] | 0 |  |  | 0 |  | 0 |  | 1653 | 0 |  |  | 1 | 1607212800000 |  | 0 | 385952 |  | 5.8 | 4 |  | 2 | 11 |  | 1 | 0 | 6 |  | 0 | 500 | 12 | 275 | 0 |  | 1 |  | 2 | 2.28 | 3.31 |  | 0 |  | 9064 |  | 13.86 | 121.9 | 0 | 359 |  |  |  |  | Running | 50 |  |  |  |  | 37.91 | 2 | 2 | 50.03 | 50.01 | 0 | 50.01 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 1 | 0 | 970 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 1 | 0 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 300 | 30 | 1 | 1.4 | 60 | 1.5 | 80 | 14 | 6 | 11 | 1 | 0 | 0 | 0 | 0 | 7 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 30 | [5 empty] | 0 | 0 | 1 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 200 | -1000 |  | -200 | -1700 | 10 | 0 | 50 | 1500 | 5.6 | 6.7 | 6.9 | 0.1 | 2.7 | 0.1 | 0 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 5.4 |  | 0 | 0 | 0.2 | 0 |  | 10 | 0 |  |  |  | 0 |  | 5 | 5 | 5 | 5 | 5 | 60 | 28 | 40 | 30 | 50 | 180 | 28 | 40 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 0 | 0 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | [479 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 5 | 0 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 35 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 |  |  | 60 | -27 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | [12 empty] | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 1 | 1 | 40 | 0 | 30 | 30 | 10 | 10 | 10 | 3 | 1 | 10500 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 5 | 5 | 0.05 | 0.05 | 0.2 | 0.2 | 1 | 0.56 | 0 | 0.56 | 1 | 30 | 1 | 0 | 0 | 439.7 | 439.7 | 4.4 | 50 | 50 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 5000 | -5000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 47.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 0 | 110 | 90 | 35 | 8 | 0 | 0 | 1 | -0.2 | 50 | 110 | 80 | 0 | 0 | 301 | 200 | 1 | 105 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10000 | 0 | 0 | 0 | 0 | 10500 | 120 | 95 | 45 | 0 | 10 | 0 | 0 | 0 | -0.4 | 50 | 110 | 80 | 0 | 1 | 400 | 200 | 0 | 100 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 90 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30 | 30 | 70 | 490 | 490 | 300 | 0 | 120 | 30 |  | 1 |  | 0 | 1 | 0 | 0 | 0 |  | 0 |  | 0 |  |  |  | 1 | 1 |  |  |  | 0 | 0 |  | 1 |  | 1 | 1 | 0 |  | 0 | 1 | [8 empty] | 0 | 1 |  | 0 | 0 |  |  | 0 |  | 0 | 0 | 1 | 0 |  | 1 | 1 | 0 | 0 |  | 0 |  |  |  | 12.5 |  | 624 |  |  |  |  | 11 | 0 | 336 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.8 | 100 | 0.02 | 100 | 41 | 0 | 1 | 8 | 100 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 30 | 0 | 100 | 5 | 0 | 0 | -5 | 15 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 35 | 30 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 210 | 168 | 75 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 65 | 3 | 0 | 0 | 0 | -2.5 | 10 | 1 | 20 | 15 | 1 | 2 | 1 | 1.82 | 0.6 | 0.6 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0.05 | 0 | 0 | 0 | 15 | 30 | 0.01 | 0.4 | 0 | 60 | 30 | 0 | 0 | 0 | 0 | 1200 | 1400 | 0 | 0.5 | 450 | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 0.2 | 0.05 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1.2 | 0.1 | 280 | 280 | 280 | 280 | 0 | 50 | 50 | 50 | 50 | 50 | 120 | 1 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.3 | 1 | 25 | 5 | 100 | 0 | 10 | 0.01 | 0.5 | 1 | 3 | 60 | 2 | 25 | 10 | 250 | 3 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 | 0 | 1 | 4000 | 2000 | 20000 | 10000 | 4397 | 2198 | 0 | 0 | 2 | 0 | 30 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 |  |  | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 0 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 |  | 1 | 650 | 700 | 1 | 0 | 0 | 0 | [66 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 1 | 1 | 1200 | 38000 |  |  |  | 44800 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 100 | 1000 | 680 | 640 |  | 650 |  |  | 640 | 5 | 650 | 5 | [7 empty] | 5 | 450 |  |  | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | -0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 20 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 10 | 20 | 5 | 0 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | [15 empty] | 5468 | 88 | 90 | 2.16 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 1 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 75 | 90 | 75 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 44.3 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 45 | 300 |  | 75 | 1.2 | 0 | 0 | 0 |  | 0.1 | 0.84 | 60 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 930 | 0 | 5000 | 50 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 500 | 1000 |  |  |  | 0 | 1 | 1 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 0 | 20 | 0.9 | -0.95 | 0.95 |  | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 10500 |  |  | 1 | 0 | 2 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -1476 | 3280 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 0 | 1 | 1 | -0.9 | -3400 | 3400 | 10 | 0 | 100 | 0 | 100 | 0 | 800 | -20 | 800 | -20 | 600 | 0 | 10 | 3.3 | 0.2 | 3.1 | 0.05 | 1.5 | 1.7 | 0.05 | 0.05 | 120 | 5 | 120 | 5 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 30 |  |  | 20 |  |  |  | 3 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.6 | 0.2 | 0.5 | 500 | 1500 | 3.5 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1.5 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 120 | 2 | 120 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 1 | 0 | 75 | 120 | 2 | 2 | 0 | 1 | 0 | 75 | 120 | 2 | 2 | 1 | 62 | 2 | 1 |  | 75 | 120 | 0.5 | 0.5 | 0 | 0 | 0 | 99 | 200 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 84 | 0 | 0 | 0 | 5 | 20 | 0 | 2 | 30 | 90 | 0 | 0 | 0 | 200 | -200 | 0 | -70 | 100 | -100 | 0 | 0 | 0 | 200 | -200 | 20 | 30 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 50 | 100 | 1 | 9.5 | 10 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 10 | 0 | 0 | 1 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 18 | 18 | 18 | 18 | [5 empty] | 4 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 924 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 1 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 0 | 0 | 20 | 4000 | 4000 |  | 850 | 30 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 2 | 3 | 3 | 3 | -5 | -5 | -5 | -5 | 13 | 13 | 13 | 13 | 4.5 |  | 45 | 270 | 70 | -144 | 0 | 80 | 350 | [24 empty] | 0 | 4 | 500 | 30 |  | 4000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 380 | 1 | -30 | -9 | 4300 | 1300 | 10 | 4300 | 2600 | 60 | 0 | 0 | [6 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4392 | 2204 | 5511 | 2838 | 1499 | 1499 |  | 51.7 | 51.6 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4900 | 2150 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4900 | 2150 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4900 | 2150 | 1500 | 1500 |  | 50 | 50 |  | 660 |  | 0 | 1000 | 300 | 48 | -1.6 | -4 | 100 | 10 | 0 | 1 | 10 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 |  | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 10 | 0 | 0.5 | 0 | 0 | 60000 | 0 | 60000 | 0 |  | 4 | 0 | 1 | 0 |  |  |  | 80 |  | 48 | [14 empty] | 52 | 53 | 53 | 53 | [10 empty] | 0 | 0 | 1 | 3 | 57 | 59 | 2 | 2 | 60 |  | 48 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 350 | 105 | 105 | 105 | [8 empty] | -1225 | 4900 |  | 0.2 | 100 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.4 |  |  | 100 | 0.2 |  | 100 |  | 100 | 100 | [11 empty] | 0.2 | 100 | 200 | [43 empty] | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 65 | 70 | 100 | 100 | 0 | 0 | 1 | 100 | 0.02 | 100 | 49 | 0 | 1 | 7 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 45 | 67 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 1.5 | 0.003 | 1 | 1 | 10 | 0.6 | 0 | 1 | 12 | 1 | 1 | 1 | 1 | 0 | 0 | 1.1 | 0.7 | 1 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | 0 | 0.1 | 0.5 | 0.5 | 100 | 40 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 50 | 0 | 100 | 10 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | [42 empty] | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 1 | 0 | 10 | 10 | 10 | 2 | 5 | 0 | 48 | 50 | 1 | 5000 | 8000 | 5000 | 8000 | 6 | 6 | 0 | 5000 | -5000 | 0 | 0 | 0.02 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 98.4 | 92.4 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 12 | 2 | 5 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 80 | 0 | [6 empty] | 0.01 | 0.06 | 0.674 | 100 | 0 | 0 | 0.44428 | 0.23695 | 98 | 2 | 0 | 20 | 5000 | 5000 | 60 | 75 | 90 | 100 |  | 0 | 20 | 2198 | 4397 | 2.5 | 1.25 | 35 | 45 |  | -2 | -2 | -2 | -2 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -145 | 10 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 4397 | 4397 | 4397 | 4397 | 50 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 |  | 10 | 0 | 150 | 1 | 1 | 102 | 112 | 98 | 91 | 112 | 50 | 65 | 85 | 75 |  | 105 | 120 | 95 | 70 | 140 | 0 | 80 | 0 | 120 | 1 | 20 | 5.55 | 0 | 0 | 120 |  |  | 5 | 4 | 4 | 4 | 4 | 56 | 56 | 56 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [30 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1650 | 10 | 200 | 400 | 2800 | 5 | 10000 | 0 | 3850 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 0 | 1500 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 800 |  | 0.2 | 0.7 | 4 | 98 | 8 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1500 | 6.7 | 0 | 95 | 85 | 85 | 95 | 95 | 9.54 | 9.971 | 720 |  |  | 1.28 | 1.55 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.1 |  |  | 0.58 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | [28 empty] | 1 | 1 | 0 | 2 | 0 | 2 | 1 | 1 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4202 |  |  | 4397 | 0 | 0 | 0 | 0 | 0 | 4397 | 4203 |  |  | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183.7 | 20.9 | -37.5 | 3.997 |  | 0.74136 | 0 | 0.56 | 4203 | 0 | 0 | 2.21 | 1 | 0 | 1 | 0 | 0 | 259 | 0 | 0 | 260 | 0 | 0 | 27 | 0 | 0 | 576 | 576 | 316 | 0 | 0 | 30 | 0 | 70.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 371 | 0 | 375 | 373 | 371 | 372 | 374 | 372 | 375 | 374 | 373 | 370 | 372 | 378 | 370 | 373 | 371 | 372 | 372 | 372 | 372 | 0 | 368 | 497 | 496 | 494 | 496 | 497 | 496 | 496 | 496 | 496 | 496 | 496 | 495 | 494 | 497 | 496 | 495 | 496 | 496 | 496 | 497 | 496 | 497 | 494 | 496 |  | Sending | 30 | 42 | 41 | 43 | 41 | 43 | 43 | 42 | 42 | 41 | 41 | 41 | 42 | 41 | 41 | 41 | 43 | 41 | 40 | 41 | 43 | 18.2058 | 34.3994 | 25.62 | 23.2997 | 27.5909 | 29.1895 | 18.8981 | 22.6028 | 26.2974 | 18.1013 | 19.5987 | 22.3963 | 21.1937 | 24.1919 | 29.788 | 25.6955 | 25.3967 | 25.2907 | 26.7977 | 28.0985 | 29.7 | 29.8964 | 23.2484 | 27.497 | 1431 | 1115 | 1557 | 3008 | 3151 | 1158 | 1602 | 1233 | 922 | 3081 | 1512 | 3150 | 3151 | 3294 | 3007 | 1431 | 3054 | 847 | 3008 | 3008 | 1515 | 1557 | 1476 | 1118 |  | 0 | 1 | [11 empty] | 68.1 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | 249.5 | 0 | 0 | 0 | 1095 | 0 | 0 | 0 | 16.1 | 0 | 0 | 0 | 1.928 |  |  |  | 28.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 5 | 9471 | 1 | 9471 | 1 | 9471 | 1 | 9471 | 1 | 9471 | 1 | 9471 | 1 | 9471 | 1 | 9471 | 1 | 9471 | 1 | 9471 | 1 | 9471 | 1 | 9471 | 1 | 9471 | 1 | 9471 | 1 | 9471 | 1 | 9471 | 1 | 9471 | 1 | 9471 | 1 | 9471 | 1 | 9471 | 1 | 9471 | 1 | 9471 | 1 | 9471 | 1 | 9471 | 1 | 0 | 7.5 | 0 | 7.27 | 0 | 7.49 | 0 | 7.6 | 0 | 7.2 | 0 | 7.23 | 0 | 7.45 | 0 | 7.43 | 0 | 7.63 | 0 | 7.27 | 0 | 7.38 | 0 | 7.39 | 0 | 7.37 | 0 | 7.24 | 0 | 7.43 | 0 | 7.7 | 0 | 7.55 | 0 | 7.4 | 0 | 7.55 | 0 | 7.44 | 0 | 7.54 | 0 | 7.44 | 0 | 7.62 | 0 | 7.54 | 0 | -0.23 | 0 | -0.7 | 0 | -0.09 | 0 | -0.13 | 0 | -0.33 | 0 | -0.07 | 0 | -0.13 | 0 | -0.1 | 0 | -0.31 | 0 | -0.37 | 0 | -0.22 | 0 | -0.15 | 0 | -0.29 | 0 | -0.38 | 0 | -0.2 | 0 | 0.13 | 0 | -0.05 | 0 | -0.25 | 0 | -0.34 | 0 | 0.19 | 0 | -0.02 | 0 | 0.18 | 0 | 0.1 | 0 | -0.09 | 0 | 7.52 | 0 | 7.3 | 0 | 7.5 | 0 | 7.56 | 0 | 7.5 | 0 | 7.19 | 0 | 7.54 | 0 | 7.32 | 0 | 7.56 | 0 | 7.39 | 0 | 7.4 | 0 | 7.42 | 0 | 7.38 | 0 | 7.34 | 0 | 7.39 | 0 | 7.47 | 0 | 7.65 | 0 | 7.49 | 0 | 7.27 | 0 | 7.34 | 0 | 8.08 | 0 | 7.49 | 0 | 7.61 | 0 | 7.51 | 0 | -0.43 | 0 | -0.45 | 0 | -0.4 | 0 | -0.39 | 0 | -0.44 | 0 | -0.51 | 0 | -0.11 | 0 | -0.36 | 0 | -0.49 | 0 | -0.47 | 0 | -0.54 | 0 | -0.26 | 0 | -0.59 | 0 | -0.37 | 0 | -0.32 | 0 | -0.37 | 0 | -0.25 | 0 | -0.38 | 0 | -0.47 | 0 | -0.4 | 0 | -0.25 | 0 | -0.25 | 0 | -0.05 | 0 | -0.25 |  | 0 | 1 | 1 | 1 | 17 | 0 | 98 | 97.6 | 97.1 | 0 | 0 | 12 | 11.8 | 0 | 11.8 | 0 | 0 | 0 | 5.32 |  | 0 | 0 | 0 | 0 |  | 98 | 98 | 98 | 98 | 12 | 12 | 12 | 12 |  | 1500 | 1499 |  | 51.4 |  |  | 0 | 0 | ABINSK
29 |  |  |  |  | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","rem_conn":"Prim-SSL-NoProxy","dataItems":"5088/10864","agent_conn":"Back-SSL-NoProxy","mon_conn":"Back-NoSSL-NoProxy"} | 0 | 0 | 0 | 1887 | 0 | 0 | -0.92 | 3.68 | 16.2 | 377 | 0 | -158 | 0 | 6.55 | 0 | 2.7 | 3.75 | -3270 | 0 |  |  |  | 0 | 0 | 0 | 0 | 4.97 | 0 | 4.94 | 0 | 0 | 0 | 4.5.1.6 | 1372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 0 |  | 13125 | 0 | 0 | 0 | 0 | -4033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.44 | 0.69 |  |  |  |  | 8175632 | 0 | 9423067 | 37310586 | 0 | 0 | 0 | 0 | 0 | 0 | 1880 | 1880 | 1880 | 481 | 1527 | 6472 | 694391 | 794391 | 13528 | 13528 | 13528 |  | 370 |  | 59.8 | 66.3 | 70 | 69.7 | 90.6 | 68 | 68.2 | 32.1 | 20 | -3270 | 0 | 0 | 0 | 0 | 89 | 88.9 | 29.9 | 59.8 | 59.8 | 0 | 86.7 | 86.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [53 empty] | 2 | 51 | 2 | 51 | 2 | 51 | 51 | 51 | 2 | 51 | 51 | 51 | 2 | 2 | 2 | 2 | 51 | 2 | 51 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 4.62 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1608948111956 | 0 | 41 | 1.182 | 0 | 0 | 0 | 0 | 37.28 | 0 |  | 5609 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 560 | 564 | 563 | 565 | 571 | 567 | 559 | 565 | 563 | 564 | 567 | 565 | 567 | 568 | 568 | 566 | 565 | 568 | 571 | 560 | 0 | 0 | 0 | 0 | 565 | 566 | 571 | 573 | 559 | 561 | 0 | 0 | 0 | 395 | 394 | 12 | [42 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 9383149 | 5482589 |  |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.5 | 51.3 |  |  | 60.5 | 59 | 58.5 | 24.1 |  |  |  |  | 1 | 1606665482062 |  | 3044 | 0.934 | 49.9 | 0 | 11019 | 6361 | 11006 | 6368 | 11015 | 6347 | 11021 | 6364 | 11016 | 6366 | 11008 | 6350 | 0 | 8443 | 2814 | 3 | 0.031 | 300 | 2.31 | -19.9 | 4.12 | 0.82 |  | 0 | 86.7 | 73.1 | 0 | 0 | 68.2 | 69.7 | 4 | 0 | 0 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 0 | 0 | 0 | 0 | 45.2 | 52.5 | 0 | 0 | 47.6 | 49.7 | 53.7 | 55.1 | 48.3 | 49.2 | 49.5 | 58.1 | 1.26 | 1.26 | 0 | 0 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 88 | 88 | 0 | 0 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 13546.8 | 13546.8 | 0 | 0 | 13546.8 | 13546.8 | 13546.8 | 13546.8 | 13546.8 | 13546.9 | 13546.9 | 13546.8 | 2018 | 2018 | 14 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 9 | 2018 | 10 | 9 | 2018 | 13 | 9 | 2018 | 14 | 9 | 2018 | 14 | 9 | 2018 | 14 | 9 | 2018 | 14 | 9 | 2018 | 14 | 9 | 2018 | 10 | 9 | 42961 | 42925 | 0 | 0 | 42902 | 42921 | 42965 | 42960 | 42966 | 42964 | 42963 | 42908 | 7.73 | 7.73 | 0 | 0 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | -16.3 | -16.3 | -16.3 | -16.3 | -16.3 | -16.3 | -16.3 | -16.3 | -16.3 | -16.3 | -16.3 | -16.3 | -16.3 | -16.3 | -16.3 | -16.3 | -16.3 | -16.3 | -16.3 | -16.3 | 0 | 0 | 0 | 0 | 141 | 110 | 189 | 110 | 62 | 94 | 94 | 126 | 94 | 62 | 126 | 141 | 141 | 110 | 126 | 110 | 189 | 110 | 141 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 231 | 219 | 244 | 305 | 293 | 280 | 268 | 256 | 293 | 378 | 293 | 280 | 354 | 219 | 231 | 268 | 305 | 231 | 329 | 0 | 0 | 0 | 0 | 0.004 | 3.91 | 0 | 0 | 0 | 0 | 7.51 | 7.47 | 7.62 | 7.35 | 7.28 | 7.45 | 7.28 | 7.59 | 7.11 | 7.26 | 7.48 | 7.11 | 7.2 | 7.63 | 7.35 | 7.4 | 7.27 | 7.4 | 7.26 | 7.25 |  |  |  |  | -0.32 | -0.14 | -0.38 | -0.17 | -0.29 | -0.27 | -0.33 | -0.27 | -0.58 | -0.47 | -0.24 | -0.34 | -0.27 | -0.2 | -0.13 | -0.42 | -0.43 | -0.29 | -0.57 | -0.39 |  |  |  |  | 7.28 | 7.38 | 7.53 | 7.38 | 7.42 | 7.51 | 7.45 | 7.66 | 7.54 | 7.49 | 7.48 | 7.29 | 7.14 | 7.5 | 7.63 | 7.51 | 7.34 | 7.72 | 7.12 | 7.82 |  |  |  |  | -0.24 | -0.28 | -0.35 | -0.3 | -0.74 | -0.55 | -0.58 | -0.38 | -0.59 | -0.64 | -0.33 | -0.46 | -0.65 | -0.45 | -0.42 | -0.59 | -0.6 | -0.37 | -0.55 | -0.72 |  |  |  |  | 37310.8 | 0 | 13912.2 | 0.1 | 162 | 0.02 | 0 | 1063 | 1.04 | 0 | 11016 | 4.5.1.0.1 | 4.5.2.0.3 | 4.5.1.0.6 | 4.5.4.0.2 | 4.5.0.0.0 | 4.5.6.5.3 | 4.7.1.0.0 | 4.5.2.0.6 | 4.5.3.0.2 | 4.5.1.0.4 | 4.5.1.0.0 | 4.5.1.0.0 | 4.5.4.0.3 | 4.5.4.0.0 | 4.5.0.0.4 | 4.5.3.1.0 | 4.5.0.0.3 | 4.5.0.0.0 | 4.5.0.0.0 | 4.5.1.0.0 | 4.5.1.0.6 | 4.5.0.0.0 | 0.0.0.0.0 | 4.5.2.0.5 | 4.5.0.0.0 | 4.5.2.0.6 | 4.5.1.0.2 | 4.5.0.0.0 | 4.5.1.0.0 | 4.4.0.0.0 | M01 (4) | 12.1 | 11.5 | 12.3 | 12.6 | 11.9 | 12.4 | 11.3 | 12.5 | 12.7 | 12.4 | 12.3 | 13.1 | 11.9 | 10 | 13.3 | 10.9 | 12.7 | 12.5 | 12.3 | 12.1 | 12.9 | 0 | 0 | 0 | 0 | 13.3 | 10 | 1369 | [82 empty] | Running | 50 |  |  |  |  | 36.47 | 2 | 1 | 49.9 | 49.9 | 0 | 49.9 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 0 | 0 | 970 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 1 | 0 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 30 | 30 | 0 | 1.4 | 20 | 1.5 | 80 | 1 | 0 | 11 | 3 | 0 | 0 | 0 | 0 | 7 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 2 | 2 | 20 | 25 | 40 | [5 empty] | 0 | 0 | 1 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 300 | -100 |  | -100 | -400 | 6 | 0 | 50 | 1500 | 5.8 | 6.7 | 6.9 | 0.1 | 4.4 | 0.1 | 1 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 4.25 |  | 0 | 0 | 0.2 | 0 |  | 10 | 0 |  |  |  | 0 |  | 5 | 5 | 5 | 5 | 5 | 60 | 28 | 40 | 30 | 50 | 180 | 28 | 40 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 0 | 0 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | [479 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 10 | 0 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 32 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 |  |  | 60 | -27 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | [12 empty] | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 1 | 40 | 0 | 30 | 30 | 10 | 10 | 10 | 3 | 1 | 11000 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 4 | 4 | 0.01 | 0.01 | 0.2 | 0.2 | 1 | 0.84 | 1 | 0.84 | 1 | 30 | 0 | 0 | 0 | 100 | 100 | 10 | 50 | 50 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 5000 | -5000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 51.5 | 47.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 1 | 115 | 85 | 35 | 10 | 0 | 0 | 1 | -0.2 | 50 | 110 | 80 | 1 | 0 | 219 | 200 | 1 | 110 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 11000 | 20 | 10 | 5 | 11000 | 0 | 0 | 0 | 0 | 11000 | 120 | 90 | 45 | 0 | 10 | 0 | 0 | 0 | -0.4 | 50 | 110 | 80 | 0 | 0 | 400 | 200 | 0 | 100 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 90 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30 | 30 | 70 | 490 | 490 | 300 | 0 | 120 | 30 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 |  |  |  | 1 | 1 |  |  |  | 1 | 0 |  | 1 |  | 1 | 1 | 0 |  | 1 | 0 | [8 empty] | 1 | 1 |  | 0 | 0 |  |  | 0 |  | 0 | 1 | 1 | 1 |  | 0 | 0 | 0 | 0 |  | 0 |  |  |  | 11.5 |  | 620 |  |  |  |  | 11 | 0 | 290 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.3 | 0.1 | 0.1 | 100 | 35 | 0 | 1 | 4 | 100 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 30 | 0 | 100 | 8 | 0 | 0 | -5 | 15 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 55 | 30 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 200 | 168 | 75 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 1 | 65 | 1 | 0 | 0 | 0 | -4.5 | 10 | 1 | 60 | 55 | 0 | 2 | 1.65 | 1.82 | 0.6 | 0.6 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0 | 0 | 0 | 0 | 15 | 30 | 0.01 | 0.4 | 0 | 60 | 30 | 0 | 0 | 0 | 0 | 1200 | 1400 | 0 | 0.5 | 360 | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 0.3 | 0.1 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 0.2 | 300 | 300 | 300 | 300 | 0 | 50 | 50 | 50 | 50 | 50 | 120 | 1 | 0.0005 | 0.0005 | 0 | 80 | 80 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.3 | 1 | 25 | 5 | 100 | 0 | 10 | 0 | 0.5 | 0 | 4 | 50 | 0 | 25 | 10 | 250 | 3 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 | 0 | 1 | 4000 | 2000 | 20000 | 10000 | 3356 | 1678 | 0 | 0 | 2 | 0 | 30 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 60 | 0 | 200 | 2 | 0 | 200 | 200 | 200 | 2 | 200 | 0 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 |  | 1 | 650 | 700 | 0 | 0 | 0 | 0 | [66 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 1 | 1 | 1200 | 1000 |  |  |  | 1000 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 50 | 1000 | 680 | 640 |  | 650 |  |  | 640 | 5 | 680 | 5 | [7 empty] | 5 | 1000 |  |  | 100 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 1 | 0 | 80 | 20 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 20 | 5 | 7 | 5 | 10 | 5 | 10 | 5 | 10 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | [15 empty] | 4169 | 88 | 90 | 1.55 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 0 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 85 | 90 | 85 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 40.6 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 45 | 300 |  | 75 | 0.868 | 0 | 0 | 0 |  | 0.1 | 0.84 | 60 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 0 | 930 | 0 | 5000 | 50 | 5 | 0 | 90 | 80 | 70 | 60 | 55 | 4 | 20 | 500 | 1000 |  |  |  | 1 | 1 | 1 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 0 | 20 | 0.8 | -0.95 | 0.95 |  | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 11000 |  |  | 0 | 0 | 1 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | -100 | 100 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 0 | 0 | 1 | -0.9 | -100 | 100 | 10 | 0 | 100 | 0 | 100 | 0 | 800 | -20 | 800 | -20 | 600 | 0 | 10 | 2.5 | 0.2 | 3.1 | 0.05 | 1.5 | 1.7 | 0.05 | 0.05 | 120 | 5 | 120 | 5 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 30 |  |  | 20 |  |  |  | 3 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.5 | 0.1 | 0.5 | 500 | 1500 | 4.6 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 1.5 | 2 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 120 | 2 | 120 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 0 | 0 | 75 | 120 | 2 | 2 | 0 | 1 | 0 | 76 | 120 | 2 | 0.5 | 0 | 62 | 2 | 1 |  | 80 | 120 | 2 | 0.5 | 0 | 1 | 0 | 97 | 200 | 2 | 2 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 82 | 0 | 0 | 0 | 5 | 20 | 0 | 2 | 30 | 90 | 0 | 0 | 0 | 200 | -200 | 0 | -50 | 100 | -100 | 0 | 0 | 0 | 200 | -200 | 20 | 30 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 9.5 | 10 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 1 | 1 | 90 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 18 | 18 | 18 | 18 | [5 empty] | 15 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 462 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 1 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 90.9 | 0 | 0 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 | 0 | 100 | 4 | 0 | 20 | 4000 | 4000 |  | 700 | 30 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 4 | 4 | 4 | 4 | -5 | -5 | -5 | -5 | 15 | 15 | 15 | 15 | 4.5 |  | 45 | 270 | 70 | -144 | 0 | 80 | 370 | [24 empty] | 0 | 4 | 500 | 30 |  | 2000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 320 | 0 | -24 | -13 | 2717 | 1600 | 10 | 2717 | 1600 | 40 | 0 | 0 | [6 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 3352 | 1678 | 4485 | 2330 | 1500 | 1500 |  | 60 | 59.7 |  | 500 | [7 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2733 | 1362 | 3050 | 1650 | 1500 | 1500 |  | 50 | 45 |  | 500 | [7 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2733 | 1362 | 3050 | 1650 | 1500 | 1500 |  | 50 | 45 |  | 500 | [7 empty] | 0 | 0.19531 |  | 0.0039 | 2.5 | 1.1 | [5 empty] | 2733 | 1362 | 3050 | 1650 | 1500 | 1500 |  | 50 | 45 |  | 500 |  | 0 | 1000 | 300 | 48 | -1.6 | -4 | 100 | 6 | 0 | 1 | 6 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 6 | 0 | 0.5 | 0 | 0 | 120000 | 0 | 120000 | 0 |  | 4 | 0 | 0 | 0 |  |  |  | 75 |  | 40 | [14 empty] | 60 | 60 | 60 | 60 | [10 empty] | 0 | 0 | 1 | 3 | 57 | 59 | 2 | 2 | 67 |  | 50 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.2 |  |  | 100 | 0.2 |  | 300 | 110 | 110 | 110 | [8 empty] | -925 | 3700 |  | 0.2 | 100 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.4 |  |  | 100 | 0.2 |  | 100 |  | 100 | 100 | [11 empty] | 0.2 | 100 | 200 | [43 empty] | 0 | 0.1 | 100 | 100 | 100 | 50 | 0 | 1 | 2.3 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 76 | 68 | 70 | 0 | 100 | 30 | 0 | 0.1 | 100 | 100 | 100 | 35 | 0 | 0 | 2 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 76 | 65 | 68 | 100 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 1.5 | 0.003 | 1 | 1 | 10 | 0.6 | 0 | 1 | 12 | 1 | 1 | 1 | 1 | 0 | 0 | 1.1 | 0.7 | 1 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 50 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 89 | 0 | 100 | 0 | 0 | 0.1 | 0.5 | 0.5 | 100 | 40 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 50 | 0 | 100 | 10 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | [42 empty] | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 0 | 0 | 10 | 150 | 150 | 100 | 205 | 0 | 48 | 50 | 0 | 3000 | 6000 | 3000 | 6000 | 6 | 6 | 0 | 5000 | -5000 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 88 | 82 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 12 | 2 | 5 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 80 | 0 | [6 empty] | 0.07 | 0.6 | 0.9 | 100 | 0 | 0.02843 | 0.74047 | 0.4739 | 100 | 0 | 4 | 20 | 1515 | 3030 | 60 | 75 | 90 | 100 |  | 0 | 20 | 1678 | 3356 | 2 | 2 | 55 | 55 |  | -6 | -6 | -6 | -6 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -145 | 10 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 3356 | 3356 | 3356 | 3356 | 50 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 |  | 10 | 0 | 150 | 1 | 1 | 102 | 112 | 98 | 91 | 112 | 50 | 65 | 85 | 75 |  | 105 | 120 | 95 | 70 | 140 | 0 | 80 | 0 | 120 | 1 | 22.7 | 3.85 | 0 | 0 | 120 |  |  | 10 | 4 | 4 | 4 | 4 | 63 | 63 | 63 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [30 empty] | 0 | 15.5 | 1013.25 | 1013.25 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.6 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 1 | 0 | 0 | 1450 | 10 | 200 | 400 | 2800 | 5 | 6000 | 0 | 3450 | 1 | 5 | 5 | 55 | 10 | 100 | 0 | 1 | 999 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 900 |  | 0.15 | 0.64 | 7.7 | 100 | 0 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1500 | 6.7 | 0 | 95 | 85 | 85 | 95 | 95 | 9.37 | 9.78 | 788 |  |  | 1.45 | 1.6 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.1 |  |  | 0.74 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [28 empty] | 1 | 1 | 0 | 2 | 0 | 2 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2856 |  |  | 3356 | 0 | 0 | 0 | 0 | 0 | 3356 | 2835 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290.2 | 9.1 | -18.16 | 4.119 | 0.1315 | 0.83245 | 0 | 0.63 | 1678 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 854 | 0 | 0 | 71 | 0 | 0 | 30 | 0 | 0 | 992 | 992 | 137 | 0 | 0 | 37 | 300 | 50.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 392 | 383 | 390 | 390 | 390 | 0 | 377 | 383 | 389 | 382 | 390 | 389 | 0 | 0 | 0 | 0 | 384 | 383 | 396 | 390 | 384 | 389 | 387 | 0 | 522 | 521 | 523 | 517 | 524 | 524 | 517 | 518 | 522 | 520 | 523 | 527 | 0 | 0 | 0 | 0 | 0 | 516 | 520 | 520 | 521 | 0 | 518 |  | Sending | 30 | 43 | 44 | 44 | 45 | 45 | 45 | 45 | 44 | 44 | 45 | 46 | 44 | 43 | 44 | 43 | 46 | 44 | 47 | 46 | 46 | [24 empty] | 2181 | 2198 | 2074 | 2272 | 2258 | 2301 | 2197 | 2508 | 2747 | 2367 | 2046 | 2062 | 2438 | 1937 | 2172 | 2146 | 2196 | 2147 | 2198 | 2021 | [5 empty] | 0 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 0 | 168.2 | 0 | 0 | 0 | 1176 | 0 | 0 | 0 | 14.9 | 0 | 0 | 0 | 1.885 |  |  |  | 52.7 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 | [8 empty] | 0 | 7.51 | 0 | 7.47 | 0 | 7.62 | 0 | 7.35 | 0 | 7.28 | 0 | 7.45 | 0 | 7.28 | 0 | 7.59 | 0 | 7.11 | 0 | 7.26 | 0 | 7.48 | 0 | 7.11 | 0 | 7.2 | 0 | 7.63 | 0 | 7.35 | 0 | 7.4 | 0 | 7.27 | 0 | 7.4 | 0 | 7.26 | 0 | 7.25 | [8 empty] | 0 | -0.32 | 0 | -0.14 | 0 | -0.38 | 0 | -0.17 | 0 | -0.29 | 0 | -0.27 | 0 | -0.33 | 0 | -0.27 | 0 | -0.58 | 0 | -0.47 | 0 | -0.24 | 0 | -0.34 | 0 | -0.27 | 0 | -0.2 | 0 | -0.13 | 0 | -0.42 | 0 | -0.43 | 0 | -0.29 | 0 | -0.57 | 0 | -0.39 | [8 empty] | 0 | 7.28 | 0 | 7.38 | 0 | 7.53 | 0 | 7.38 | 0 | 7.42 | 0 | 7.51 | 0 | 7.45 | 0 | 7.66 | 0 | 7.54 | 0 | 7.49 | 0 | 7.48 | 0 | 7.29 | 0 | 7.14 | 0 | 7.5 | 0 | 7.63 | 0 | 7.51 | 0 | 7.34 | 0 | 7.72 | 0 | 7.12 | 0 | 7.82 | [8 empty] | 0 | -0.24 | 0 | -0.28 | 0 | -0.35 | 0 | -0.3 | 0 | -0.74 | 0 | -0.55 | 0 | -0.58 | 0 | -0.38 | 0 | -0.59 | 0 | -0.64 | 0 | -0.33 | 0 | -0.46 | 0 | -0.65 | 0 | -0.45 | 0 | -0.42 | 0 | -0.59 | 0 | -0.6 | 0 | -0.37 | 0 | -0.55 | 0 | -0.72 | [9 empty] | 0 | 0 | 1 | 1 | 26 | 0 | 100 | 0 | 0 | 0 | 0 | 34.4 | 0 | 0 | 0 | 0 | 0 | 0 | 3.91 |  | 0 | 0 | 0 | 0 |  | 100 | 100 | 100 | 100 | 34.4 | 34.4 | 34.4 | 34.4 |  | 1497 | 1497 |  | 59.8 |  |  | 0 | 0 | BLESSED TEXTILE
30 |  |  |  |  | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","agent_conn":"Back-SSL-NoProxy","mon_conn":"Back-SSL-NoProxy","rem_conn":"Back-NoSSL-NoProxy"} | 0 | 0 | 0 | 0 | 0 | 0 | -0.92 | 5.6 | 0 | 0 | 0 | -1183 | 0 | 6.87 | 0 | 4.25 | 4.41 | 25 | 0 |  |  |  | 0 | 0 | 0 | 0 | 4.86 | 0 | 4.86 | 0 | 0 | 0 | 4.7.0.5 | 6683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 |  | 18803 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 |  |  |  |  | 2001 | 0 | 2000 | 4000 | 10000 | 0 | 0 | 0 | 0 | 0 | -306 | 1694 | -306 | 1694 | 498565 | 598565 | 698565 | 798565 | 8306 | 8306 | 8306 |  | 1110 |  | 56.8 | 36.5 | 57 | 56 | 71.8 | 0 | 0 | 0 | 25 | 25 | 30.2 | 0.7 | 0 | 0 | 95 | 94.7 | 91.7 | 56.8 | 56.8 | 0 | 84.1 | 84.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [53 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 6.87 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1608978882828 | 0 | 63 | 1 | 0 | 0 | 0 | 0 | 14.76 | 0 |  | 1435 |  |  |  |  | 0 | 0 | 0 | 0 | 41409 | 41434 | 0 | 0 | 0 |  | 375 | 0 | 542 | 546 | 545 | 547 | 545 | 547 | 550 | 551 | 548 | 548 | 550 | 545 | 545 | 545 | 545 | 546 | 543 | 546 | 551 | 551 | 548 | 550 | 550 | 546 | 547 | 547 | 551 | 551 | 542 | 542 | 0 | 349 | 0 | 350 | 348 | 9 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49.1 | 41 |  |  | 58.3 | 50.3 | 51.6 | 30.7 |  |  |  |  | 1 | 1606698814587 |  | 4480 | 0.999 | 50 | 0 | 15356 | 8863 | 15326 | 8858 | 15332 | 8846 | 10357 | 5950 | 10348 | 5972 | 10362 | 6029 | 0 | 12925 | 4308 | 3 | 0.006 | 100 | 2.53 | -45.3 | 4.02 | 0.84 |  | 0 | 84.1 | 80.3 | 0 | 56 | 0 | 77.5 | 0 | 0 | 0 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 77.5 | 81.2 | 85.6 | 81.2 | 72.5 | 70.1 | 70.2 | 74.3 | 75.2 | 65.8 | 71.6 | 78.7 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 8347.7 | 8347.6 | 8347.7 | 8347.7 | 8347.7 | 8347.7 | 8347.7 | 8347.8 | 8347.6 | 8347.6 | 8347.6 | 8347.7 | 2019 | 2019 | 5 | 3 | 2019 | 5 | 3 | 2019 | 5 | 3 | 5 | 3 | 2019 | 5 | 3 | 2019 | 5 | 3 | 2019 | 14 | 2 | 2019 | 5 | 3 | 2019 | 5 | 3 | 2019 | 5 | 3 | 2019 | 5 | 3 | 2019 | 15 | 2 | 45004 | 45002 | 45011 | 45019 | 45005 | 45018 | 44631 | 45013 | 45001 | 45006 | 45000 | 44706 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.1 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | -25.2 | 237 | 220 | 189 | 253 | 141 | 141 | 237 | 412 | 126 | 79 | 158 | 94 | 269 | 332 | 205 | 110 | 205 | 126 | 189 | 220 | 126 | 253 | 62 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 329 | 378 | 329 | 354 | 293 | 305 | 305 | 305 | 293 | 378 | 390 | 244 | 317 | 305 | 402 | 317 | 512 | 329 | 366 | 280 | 463 | 305 | 329 | -0.002 | 5.6 | 0 | 0 | 0 | 0 | 7.41 | 7.54 | 7.52 | 7.67 | 7.23 | 7.22 | 7.26 | 7.37 | 7.35 | 7.37 | 7.41 | 7.3 | 7.34 | 7.35 | 7.34 | 7.22 | 7.42 | 6.97 | 7.35 | 7.24 | 7.48 | 7.36 | 7.3 | 7.37 | -0.19 | 0 | -0.45 | -0.29 | -0.47 | -0.38 | -0.4 | -0.41 | -0.59 | -0.34 | -0.5 | -0.25 | -0.39 | -0.44 | -0.47 | -0.4 | -0.56 | -0.75 | -0.57 | -0.48 | -0.66 | -0.48 | -0.57 | -0.68 | 7.39 | 7.71 | 8.02 | 7.49 | 7.42 | 7.49 | 7.6 | 7.49 | 7.71 | 7.32 | 7.69 | 7.48 | 7.54 | 7.17 | 7.31 | 7.5 | 7.26 | 7.06 | 7.53 | 7.45 | 7.55 | 7.44 | 7.47 | 7.28 | -0.19 | -0.47 | -0.36 | -0.48 | -0.4 | -0.82 | -0.56 | -0.47 | -0.52 | -0.66 | -0.45 | -0.58 | -0.56 | -0.5 | -0.49 | -0.47 | -0.66 | -0.6 | -0.77 | -0.58 | -0.44 | -0.52 | -0.62 | -0.63 | 35993.6 | 0 | 257.3 | 0 | 251 | 0.02 | 0 | 1 | 1.1 | 0 | 10359 | 4.7.1.0.0 | 4.7.1.1.5 | 4.7.1.0.2 | 4.7.1.1.0 | 4.7.0.0.1 | 4.7.1.4.1 | 4.9.0.0.0 | 4.7.0.0.5 | 4.7.1.0.0 | 4.7.0.0.5 | 4.5.1.0.0 | 4.7.1.0.0 | 4.7.2.0.1 | 4.7.0.0.1 | 4.7.0.0.4 | 4.7.3.1.5 | 4.7.0.1.1 | 4.7.0.0.0 | 4.7.0.0.0 | 4.6.0.0.0 | 4.7.0.0.2 | 4.7.0.0.0 | 0.0.0.0.0 | 4.7.5.0.5 | 4.7.0.0.0 | 4.7.0.0.3 | 4.7.0.0.1 | 4.7.0.0.0 | 4.7.0.1.1 | 4.7.0.0.0 | M01 | 20.9 | 20.9 | 18.9 | 19.4 | 23.2 | 19.9 | 22.6 | 20.2 | 17.5 | 19.2 | 18.7 | 20.6 | 22.8 | 18.4 | 20.6 | 18.5 | 21.2 | 20 | 21 | 20.5 | 21 | 27.3 | 22.9 | 25 | 22.9 | 27.3 | 17.5 | 1385 | [30 empty] | -1 | 5 | 1 | NaN | 0.0001 | 1607965525000 | 1 | 1 | 0.2049 | 1 | NaN | 3055 | 1 | 1607299200000 | NaN | NaN | NaN | 0.02 | 5.66 | 10 | 1415365 | 2 | 0.0008 | 1 | 1 | 1 | 1 |  | 0 | 964 | 14 | 0.0292 | 1 | 1607962200000 | 2 | 1 | 3 | 2.62 | 4.5 | 1017197 | 1 | 1 | 7845 | 1 | 14.3 | 128 | 0.05 | 0.036 |  |  |  |  | Running | 50 |  |  |  |  | 7.19 | 2 | 2 | 50 | 50 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 0 | 0 | 970 | 40 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 9 | 0 | 0 | 1 | 0 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 30 | 30 | 0 | 1.4 | 20 | 1.5 | 80 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 400 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 1 | 2 | 2 | 20 | 25 | 35 | [5 empty] | 1700 | 800 | 1 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 300 | -700 |  | -200 | -1400 | 10 | 0 | 50 | 1500 | 5.6 | 6.7 | 6.9 | 0.1 | 2.7 | 0.1 | 0 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 3.5 |  | 0 | 0 | 0.2 | 0 |  | 10 | 0 |  |  |  | 0 |  | 5 | 5 | 3 | 3 | 5 | 60 | 25 | 38 | 26 | 50 | 180 | 25 | 38 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 0 | 0 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | [479 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 5 | 0 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 35 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 |  |  | 60 | -27 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | [12 empty] | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 1 | 40 | 0 | 30 | 30 | 1 | 1 | 10 | 3 | 1 | 10500 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 4 | 4 | 0.01 | 0.01 | 0.2 | 0.2 | 1 | 0.84 | 1 | 0.84 | 1 | 30 | 0 | 0 | 0 | 100 | 100 | 10 | 50 | 50 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 5000 | -5000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 47.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 0 | 110 | 90 | 35 | 10 | 0 | 0 | 1 | -0.1 | 50 | 110 | 80 | 1 | 0 | 307 | 200 | 1 | 140 | 10 | 2 | 0.8 | 3 | 4 | 10 | 0.5 | 4 | 15600 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 15600 | 120 | 88 | 45 | 0 | 10 | 0 | 0 | 0 | -0.4 | 50 | 110 | 80 | 0 | 1 | 400 | 200 | 0 | 100 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 90 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 20 | 100 | 50 | 80 | 250 | 100 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 5 | 30 | 30 | 70 | 490 | 490 | 300 | 30 | 120 | 30 |  | 1 |  | 0 | 0 | 1 | 1 | 0 |  | 0 |  | 0 |  |  |  | 1 | 1 |  |  |  | 1 | 0 |  | 1 |  | 1 | 0 | 1 |  | 1 | 0 | [8 empty] | 0 | 1 |  | 0 | 0 |  |  | 1 |  | 0 | 0 | 1 | 0 |  | 1 | 1 | 0 | 0 |  | 0 |  |  |  | 12.5 |  | 624 |  |  |  |  | 11 | 0 | 536 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.5 | 0.1 | 0.05 | 100 | 41 | 0 | 1 | 3 | 100 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 65 | 40 | 0 | 100 | 2 | 0 | 0 | -5 | 15 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 30 | 30 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 200 | 168 | 75 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 65 | 1 | 0 | 0 | 0 | -2.5 | 10 |  | 20 | 15 | 0 | 2 | 1 | 1.82 | 0.6 | 0.6 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0.1 | 0 | 0 | 0 | 15 | 30 | 0.01 | 0.4 | 0 | 60 | 30 | 0.2 | 0 | 0 | 0 | 1200 | 1400 | 0 | 0.5 |  | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 0.2 | 0.05 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 1 | 0 | [10 empty] | 1 | 50 | 60 | 70 | 80 | 90 |  | 1 | 0.0005 | 0.0005 | 0 | 80 | 80 | 1 | 0 | 1 | 4 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.3 | 1 | 25 | 5 | 100 | 0 | 4 | 0.1 | 0.5 | 1 | 7 | 100 | 0 | 25 | 10 | 250 | 0 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 | 0 | 1 | 4000 | 2000 | 20000 | 10000 | 4497 | 2249 | 8 | 4 | 2 | 1 | 30 | 150 | 20 | 120 | 0 | 1 | 1 | 1 | 1 | 0 |  |  | 0 |  | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 60 | 60 | 0 | 200 | 2 | 1 | 50 | 30 | 40 | 0.1 | 0 | 0 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 | 1.5 | 1 | 650 | 700 | 1 | 0 | 0 | 0 | [66 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 1 | 1 | 1200 | 40500 |  |  |  | 45120 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 100 | 1000 | 680 | 640 |  | 650 |  |  | 640 | 5 | 650 | 5 | [7 empty] | 5 | 1000 |  |  | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 20 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 10 | 20 | 5 | 8 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | [15 empty] | 5579 | 88 | 90 | 2.19 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 0 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 85 | 90 | 85 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 60.2 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 45 | 300 |  | 75 | 2.043 | 1 | 0 | 1 |  | 0.1 | 0.84 | 60 | 0 | 75.6 | 80 | 70 | 60 | 55 | 4 | 20 | 2249 | 4497 | 0 | 5000 | 60 | 5 | 0 | 50 | 80 | 70 | 60 | 55 | 4 | 20 | 2249 | 4497 |  |  |  | 0 | 1 | 0 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 0 | 20 | 0.8 | -0.95 | 1 |  | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 10500 |  |  | 1 | 0 | 2 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | 0 | 1440 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 0 | 1 | 1 | -0.9 | -3600 | 3600 | 10 | 0 | 100 | 0 | 100 | 0 | 800 | -20 | 800 | -20 | 600 | 0 | 10 | 3.3 | 0.2 | 3.1 | 0.05 | 1.5 | 1.55 | 0.05 | 0.05 | 120 | 5 | 120 | 5 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 30 |  |  | 20 |  |  |  | 3 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.6 | 0.2 | 0.5 | 500 | 1500 | 3.5 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 2 | 2.5 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 120 | 2 | 120 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 1 | 0 | 62 | 120 | 2 | 2 | 0 | 0 | 0 | 120 | 120 | 2 | 2 | 1 | 61 | 2 | 1 |  | 81 | 120 | 0.5 | 0.5 | 0 | 1 | 0 | 99 | 101 | 2 | 2 | 1 | 2 | 100 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 84 | 0 | 0 | 0 | 5 | 20 | 0 | 2 | 30 | 90 | 0 | 0 | 0 | 200 | -200 | 0 | -70 | 100 | -100 | 0 | 0 | 0 | 200 | -200 | 20 | 30 | 1 | 2 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 9.5 | 10 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 10 | 0 | 0 | 1 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 18 | 18 | 18 | 18 | [5 empty] | 4 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 924 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 1 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 |  | 100 | 0 | 0 | 20 | 4000 | 4000 |  | 367 | 30 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 5 | 5 | 5 | 5 | -5 | -5 | -5 | -5 | 8 | 8 | 8 | 8 | 4.5 |  | 45 | 270 | 70 | -144 | 0 | 80 | 350 | [24 empty] | 0 | 4 | 500 | 30 |  | 4000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 380 | 1 | -30 | -9 | 4497 | 2249 | 10 | 4497 | 2249 | 60 | 0 | 0 | [6 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4475 | 2249 | 5434 | 2789 | 1498 | 1500 |  | 56.8 | 53 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4909 | 2154 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4909 | 2154 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4909 | 2154 | 1500 | 1500 |  | 50 | 50 |  | 660 |  | 0 | 1000 | 600 | 50 | -0.5 | -5 | 120 | 10 | 0 | 1 | 10 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 |  | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 10 | 0 | 0.5 | 0 | 0 | 60000 | 0 | 60000 | 0 |  | 4 | 0 | 1 | 0 |  |  |  | 80 |  | 52 | [14 empty] | 57 | 57 | 57 | 57 | [10 empty] | 0 | 0 | 1 | 3 | 59 | 61 | 2 | 2 | 64 |  | 52 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.1 |  |  | 100 | 0.2 |  | 351 | 140 | 140 | 100 | [8 empty] | -1250 | 5000 |  | 0.2 | 80 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.4 |  |  | 100 | 0.2 |  | 100 |  | 100 | 100 | [11 empty] | 0.2 | 100 | 200 | [43 empty] | 0 | 0.1 | 0.1 | 0.01 | 100 | 120 | 0 | 1 | 1.8 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 65 | 45 | 57 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 70 | 70 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 2 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 25 | 10 | 100 | 20 | 1.5 | 0.003 | 1 | 1 | 10 | 0.6 | 0 | 1 | 12 | 1 | 1 | 1 | 1 | 0 | 0 | 1.1 | 0.7 | 1 | 0 | 100 | 0 | 0 | 0.1 | 0.1 | 0.01 | 100 | 150 | 0 | 1 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 80 | 95 | 0 | 100 | 50 | 0 | 0.1 | 0.5 | 0.5 | 100 | 40 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 50 | 0 | 100 | 10 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | [42 empty] | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 0 | 0 | 10 | 10 | 10 | 2 | 5 | 0 | 48 | 50 | 1 | 5000 | 8000 | 5000 | 8000 | 6 | 6 | 1 | 5000 | -5000 | 1 | 0 | 0.02 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 75.6 | 72.6 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 |  |  |  |  | 12 | 2 | 5 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 80 | 0 | [6 empty] | 0.01421 | 0.29619 | 0.88857 | 100 | 0 | 0 | 0.44428 | 0.23695 | 100 | 2 | 0 | 20 | 5000 | 5000 | 70 | 75 | 70 | 100 |  | 0 | 20 | 2249 | 4497 | 2.5 | 2 | 35 | 45 |  | -2 | -2 | -2 | -2 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -145 | 10 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 4497 | 4497 | 4497 | 4497 | 70 | 0.72 | 0.72 | 0.72 | 0.72 | 0.3 | 0.72 | 0.72 | 0.72 |  | 10 | 10 | 95 | 1 | 1 | 100.4 | 102.9 | 98 | 91 | 102.9 | 50 | 65 | 85 | 75 |  | 105 | 120 | 95 | 70 | 140 | 0 | 70 | 20 | 82 | 1 | 20 | 5.55 | 1 | 10 | 63 |  |  | 5 | 4 | 4 | 4 | 4 | 60 | 60 | 60 | 60 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [30 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.3 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1650 | 10 | 200 | 400 | 2800 | 5 | 10000 | 0 | 3850 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 0 | 1500 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 800 |  | 0.2 | 0.7 | 4 | 100 | 0 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1500 | 6.7 | 0 | 95 | 85 | 85 | 95 | 95 | 8.89 | 9.27 | 804 |  |  | 1.55 | 1.65 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.1 |  |  | 0.61 | [13 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [28 empty] | 1 | 1 | 1 | 2 | 0 | 2 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4480 |  |  | 4497 | 0 | 0 | 0 | 0 | 0 | 4497 | 4497 |  |  | 2.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.1 | 9.8 | -45.23 | 4.006 | 0.016 | 0.831 | 0 | 0.3 | 4497 | 0 | 0 | 2.21 | 55 | 349 | 0 | 0 | 298 | 297 | 176 | 184 | 121 | 33 | 32 | 31 | 566 | 573 | 473 | 473 | 176 | 57 | 59 | 24 | 0 | 75.71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387 | 382 | 382 | 388 | 383 | 384 | 380 | 386 | 380 | 383 | 386 | 387 | 384 | 378 | 385 | 380 | 0 | 386 | 385 | 390 | 385 | 382 | 372 | 381 | 507 | 507 | 503 | 508 | 507 | 507 | 508 | 508 | 506 | 510 | 507 | 507 | 496 | 508 | 509 | 500 | 506 | 506 | 505 | 0 | 506 | 508 | 504 | 505 |  | Sending | 30 | 62 | 61 | 61 | 62 | 62 | 61 | 62 | 61 | 62 | 63 | 61 | 61 | 62 | 61 | 61 | 62 | 62 | 62 | 61 | 60 | [24 empty] | 1423 | 1124 | 3151 | 1175 | 3093 | 1263 | 3007 | 1329 | 1056 | 1150 | 2944 | 1262 | 1057 | 1476 | 1138 | 1430 | 3007 | 1493 | 1556 | 1513 | 672 | 1174 | 886 | 1224 |  | 74 | 1 | [11 empty] | 77.7 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 286.9 | 0 | 0 | 0 | 1031 | 0 | 0 | 0 | 6.8 | 0 | 0 | 0 | 1.912 |  |  |  | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 | 7646 | 1 | 7646 | 1 |  | 1 |  | 1 | 0 | 7.41 | 0 | 7.54 | 0 | 7.52 | 0 | 7.67 | 0 | 7.23 | 0 | 7.22 | 0 | 7.26 | 0 | 7.37 | 0 | 7.35 | 0 | 7.37 | 0 | 7.41 | 0 | 7.3 | 0 | 7.34 | 0 | 7.35 | 0 | 7.34 | 0 | 7.22 | 0 | 7.42 | 0 | 6.97 | 0 | 7.35 | 0 | 7.24 | 0 | 7.5 | 0 | 7.3 | 0 | 7.3 | 0 | 7.37 | 0 | -0.19 | 0 | 0 | 0 | -0.45 | 0 | -0.29 | 0 | -0.47 | 0 | -0.38 | 0 | -0.4 | 0 | -0.41 | 0 | -0.59 | 0 | -0.34 | 0 | -0.5 | 0 | -0.25 | 0 | -0.39 | 0 | -0.44 | 0 | -0.47 | 0 | -0.4 | 0 | -0.56 | 0 | -0.75 | 0 | -0.57 | 0 | -0.48 | 0 | -0.5 | 0 | -0.5 | 0 | -0.57 | 0 | -0.68 | 0 | 7.39 | 0 | 7.71 | 0 | 8.02 | 0 | 7.49 | 0 | 7.42 | 0 | 7.49 | 0 | 7.6 | 0 | 7.49 | 0 | 7.71 | 0 | 7.32 | 0 | 7.69 | 0 | 7.48 | 0 | 7.54 | 0 | 7.17 | 0 | 7.31 | 0 | 7.5 | 0 | 7.26 | 0 | 7.06 | 0 | 7.53 | 0 | 7.45 | 0 | 7.6 | 0 | 7.4 | 0 | 7.47 | 0 | 7.28 | 0 | -0.19 | 0 | -0.47 | 0 | -0.36 | 0 | -0.48 | 0 | -0.4 | 0 | -0.82 | 0 | -0.56 | 0 | -0.47 | 0 | -0.52 | 0 | -0.66 | 0 | -0.45 | 0 | -0.58 | 0 | -0.56 | 0 | -0.5 | 0 | -0.49 | 0 | -0.47 | 0 | -0.66 | 0 | -0.6 | 0 | -0.77 | 0 | -0.58 | 0 | -0.5 | 0 | -0.6 | 0 | -0.62 | 0 | -0.63 |  | 0 | 1 | 1 | 1 | 17 | 0 | 100 | 99.4 | 99.5 | 0 | 0 | 12.1 | 11.9 | 0 | 12.6 | 0 | 0 | 0 | 5.6 |  | 0 | 0 | 0 | 0 |  | 100 | 100 | 100 | 100 | 12.1 | 12.1 | 12.1 | 12.1 |  | 1500 | 1499 |  | 56.8 |  |  | 0 | 0 | Salmmeir 1
31 |  |  |  |  | {"pendingUploads":"0/0","dataItemsValid":"true","edge":"true","agent_conn":"Prim-SSL-NoProxy","mon_conn":"Prim-NoSSL-NoProxy","rem_conn":"Back-NoSSL-NoProxy"} | 0 | 0 | 0 | 0 | 0 | 0 | -0.92 | 5.5 | 0 | 0 | 0 | -1121 | 0 | 6.9 | 0 | 4.17 | 4.39 | 21.6 | 0 |  |  |  | 0 | 0 | 0 | 0 | 4.75 | 0 | 4.74 | 0 | 0 | 0 | 4.7.0.5 | 5245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | NL Zuid | 18499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 |  |  |  |  | 2000 | 0 | 2000 | 4000 | 10000 | 0 | 0 | 0 | 0 | 0 | -405 | 2175 | -405 | 1595 | 498619 | 598619 | 698619 | 798619 | 8405 | 8405 | 8405 |  | 793 |  | 56.9 | 40.9 | 57 | 56 | 71.2 | 0 | 0 | 0 | 25 | 21.6 | 20 | 0.7 | 0 | 0 | 95 | 94.6 | 92.2 | 56.9 | 56.9 | 0 | 83.5 | 83.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [53 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 6.9 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1608981278459 | 0 | 63 | 1 | 0 | 0 | 0 | 0 | 15.57 | 0 |  | 1381 |  |  |  |  | 0 | 0 | 0 | 0 | 41858 | 41755 | 0 | 0 | 0 |  | 355 | 0 | 551 | 553 | 552 | 551 | 548 | 549 | 554 | 557 | 559 | 554 | 551 | 553 | 549 | 552 | 552 | 551 | 550 | 550 | 556 | 555 | 554 | 551 | 553 | 554 | 552 | 552 | 559 | 559 | 548 | 547 | 0 | 352 | 0 | 354 | 349 | 12 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52.5 | 43.2 |  |  | 60.3 | 56.6 | 54.5 | 30.4 |  |  |  |  | 10 | 1606702483995 |  | 4505 | 0.999 | 50 | 0 | 15370 | 8870 | 15338 | 8868 | 15350 | 8854 | 10348 | 5979 | 10360 | 5977 | 10358 | 5979 | 0 | 13546 | 4515 | 3 | 0.006 | 100 | 2.5 | -43.8 | 4.02 | 0.72 |  | 0 | 83.5 | 79.3 | 0 | 56 | 0 | 77.8 | 0 | 0 | 0 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 71.6 | 70.7 | 70.2 | 78.7 | 78 | 82.4 | 84.6 | 86.2 | 83.5 | 78 | 71.6 | 72.2 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1.26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 8438.7 | 8438.8 | 8438.7 | 8438.8 | 8438.7 | 8438.8 | 8438.8 | 8438.8 | 8438.8 | 8438.7 | 8438.7 | 8438.7 | 2019 | 2019 | 11 | 3 | 2019 | 11 | 3 | 2019 | 11 | 3 | 11 | 3 | 2019 | 11 | 3 | 2019 | 11 | 3 | 2019 | 11 | 3 | 2019 | 11 | 3 | 2019 | 11 | 3 | 2019 | 4 | 3 | 2019 | 5 | 3 | 2019 | 27 | 2 | 45032 | 45031 | 45035 | 45036 | 45034 | 45040 | 45027 | 45041 | 45033 | 44992 | 45009 | 44895 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 7.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | -25.3 | -25.3 | -25.3 | -25.3 | -25.3 | -25.3 | -25.3 | -25.3 | -25.3 | -25.3 | -25.3 | -25.3 | -25.3 | -25.3 | -25.3 | -25.3 | -25.3 | -25.3 | -25.3 | -25.3 | -25.3 | -25.3 | -25.3 | -25.3 | 174 | 126 | 237 | 158 | 189 | 126 | 269 | 141 | 237 | 237 | 110 | 94 | 189 | 174 | 174 | 110 | 141 | 141 | 126 | 110 | 126 | 141 | 158 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 415 | 402 | 402 | 378 | 476 | 512 | 463 | 341 | 500 | 329 | 341 | 354 | 293 | 378 | 256 | 341 | 476 | 476 | 341 | 366 | 366 | 366 | 329 | 415 | 0.001 | 5.51 | 0 | 0 | 0 | 0 | 7.54 | 7.67 | 7.73 | 7.67 | 8.01 | 7.76 | 7.86 | 7.94 | 7.57 | 7.55 | 7.59 | 7.66 | 7.7 | 7.81 | 7.52 | 7.66 | 7.54 | 8.16 | 7.53 | 7.52 | 7.68 | 7.53 | 7.65 | 7.61 | 0.2 | -0.42 | -0.46 | -0.23 | -0.4 | -0.41 | -0.38 | 0.16 | -0.35 | -0.26 | -0.02 | -0.29 | -0.26 | -0.29 | -0.23 | -0.12 | -0.28 | -0.03 | -0.25 | -0.29 | -0.17 | -0.34 | -0.28 | -0.18 | 7.83 | 7.65 | 7.79 | 7.63 | 7.65 | 7.66 | 7.68 | 7.5 | 7.55 | 7.82 | 7.56 | 7.56 | 7.83 | 7.52 | 7.62 | 7.54 | 7.59 | 7.79 | 7.75 | 7.58 | 7.95 | 7.98 | 8.02 | 7.81 | 0.3 | -0.38 | -0.5 | -0.46 | -0.29 | -0.38 | -0.36 | -0.32 | -0.4 | -0.32 | -0.35 | 0.02 | -0.4 | -0.23 | -0.19 | -0.46 | -0.27 | -0.43 | -0.3 | -0.34 | -0.18 | -0.34 | -0.32 | -0.39 | 36994 | 0 | 220.2 | 0 | 251 | 0.02 | 0 | 0 | 1.1 | 0 | 10355 | 4.7.1.0.0 | 4.7.1.1.5 | 4.7.1.0.2 | 4.7.1.1.0 | 4.7.0.0.1 | 4.7.1.4.1 | 4.9.0.0.0 | 4.7.0.0.5 | 4.7.1.0.0 | 4.7.0.0.5 | 4.5.1.0.0 | 4.7.1.0.0 | 4.7.2.0.1 | 4.7.0.0.1 | 4.7.0.0.4 | 4.7.3.1.5 | 4.7.0.1.1 | 4.7.0.0.0 | 4.7.0.0.0 | 4.6.0.0.0 | 4.7.0.0.2 | 4.7.0.0.0 | 0.0.0.0.0 | 4.7.5.0.5 | 4.7.0.0.0 | 4.7.0.0.3 | 4.7.0.0.1 | 4.7.0.0.0 | 4.7.0.1.1 | 4.7.0.0.0 | M02 | 19.3 | 18.7 | 19.3 | 20.7 | 18 | 21.2 | 19.9 | 20.5 | 17.9 | 17.4 | 20.2 | 19.1 | 22.5 | 17.6 | 17.1 | 18.9 | 22.9 | 19 | 18.9 | 18 | 18.1 | 20.3 | 21.3 | 20.9 | 17.1 | 22.9 | 17.1 | 1600 | [30 empty] | -1 | 5 | 1 | NaN | 0.0001 | 1607965563000 | 1 | 1 | 0.2103 | 1 | NaN | 2896 | 1 | 1607299200000 | NaN | NaN | NaN | 0.02 | 4.92 | 16 | NaN | 3 | 0.0008 | 1 | 1 | 1 | 3 |  | 0 | 1385 | 17 | 0.0294 | 1 | 1607962200000 | 2 | 1 | 4 | 3.43 | 3.4 | 1017198 | 1 | 1 | 7965 | 1 | 14.4 | 131 | 0.05 | 0.0369 |  |  |  |  | Running | 50 |  |  |  |  | 10.29 | 2 | 2 | 50 | 50 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | [6 empty] | 0 | 0 | 12 | 5 | 16 | 0 | 0 | 8 | 40 | 0 |  | 20 | 0 | 0 | 970 | 40 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 9 | 0 | 0 | 1 | 0 | 1.4 | 1.5 | 20 | 80 | 60 | 30 | 30 | 60 | 30 | 30 | 0 | 1.4 | 20 | 1.5 | 80 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 400 |  |  |  |  | 500 | 7000 | 300 | 1150 |  | 1800 | [9 empty] | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 25 | 0 | 1 | 2 | 2 | 20 | 25 | 35 | [5 empty] | 1700 | 800 | 1 | 120 | 0 | 2 | 2 | 2 | 2 | 60 | 60 | 60 | 60 | 1 | 50 | 50 |  | 300 | -700 |  | -200 | -1400 | 10 | 0 | 50 | 1500 | 5.6 | 6.7 | 6.9 | 0.1 | 2.7 | 0.1 | 0 | 1 | 0 | 500 | 7000 | 70 | -500 |  |  | 3.5 |  | 0 | 0 | 0.2 | 0 |  | 10 | 0 |  |  |  | 0 |  | 5 | 5 | 5 | 3 | 5 | 60 | 25 | 38 | 26 | 50 | 180 | 25 | 38 | 0 | 100 | 0 | 0 | 100 | 0 | 20 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 10 | 0 | 10 | 2 | 0 | 0 | 0 | 100 | 10 | -100 | 10 | 250 | -250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | [479 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 118 | 10 | 122 | 10 | 0 | 115 | 118 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 5 | 0 | 10 | 48 | 60 | 13 | 100 | 33 | 75 | 17 | 50 | 17 | 30 | 13 | 10 | 1 | 30 | 700 | 10 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 15000 | 4000 | 0 | 0 | 30 | 8 | 10 | 35 | 30 | 30 | 30 | 25 | 1 | 1 | 0 | 0 | 1.5 | 1.5 | 0 | 2 | 1 | 50 | 3 | 3 | 8 | 8 | 1 | 0 | 0.03 | 1 | 235 | 100 | 2000 | 180 | -1.15 | 3000 | 30 | 200 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 130 | 100 | 100 | 100 | 100 | 130 | 100 | 0.5 | 0.3 | 1 | 1000 | 200 | 70 | 20 | 80 | 2 | 0 | 0 | 0 | 0 | 11 | -8 | 3 | 2 | 0 | 200 | 300 | 20 | 7 | 5 | 30 | 133 | 5 | 100 | 3 | 0 | 15 | 60 |  |  | 60 | -27 | 5 | 9 | 12 | 14 | 18 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.9 | 0.9 | 0.9 | 0.95 | 1 | 105 | 95 | [12 empty] | 0 | 0 | 0 | 0 | 0.5 | 1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 1 | 40 | 0 | 30 | 30 | 1 | 1 | 10 | 3 | 1 | 10500 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0.2 | 0.3 | 30 | 60 | 65 | 0 | 4 | 4 | 0.01 | 0.01 | 0.2 | 0.2 | 1 | 0.84 | 1 | 0.84 | 1 | 30 | 0 | 0 | 0 | 100 | 100 | 10 | 50 | 50 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 14400 | 300 | 86400 | 300 | 1200 | 5000 | -5000 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 47.5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1400 | 0 | 1 | 0 | 0 | 300 | 30 | 8 | 0 | 110 | 90 | 35 | 10 | 0 | 0 | 1 | -0.1 | 50 | 110 | 80 | 1 | 0 | 307 | 200 | 1 | 140 | 10 | 2 | 0.8 | 3 | 4 | 10 | 0.5 | 4 | 15600 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 15600 | 120 | 88 | 45 | 0 | 10 | 0 | 0 | 0 | -0.4 | 50 | 110 | 80 | 0 | 1 | 400 | 200 | 0 | 100 | 100 | 10 | 2 | 0.3 | 3 | 4 | 10 | 0.5 | 4 | 10500 | 20 | 10 | 5 | 10500 | 0 | 0 | 0 | 0 | 10500 | 120 | 90 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6000 | 20 | 100 | 50 | 80 | 250 | 100 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 1 | 0 | 5 | 30 | 30 | 70 | 490 | 490 | 300 | 30 | 120 | 30 |  | 1 |  | 0 | 0 | 1 | 1 | 0 |  | 0 |  | 0 |  |  |  | 1 | 1 |  |  |  | 1 | 0 |  | 1 |  | 1 | 0 | 1 |  | 1 | 0 | [8 empty] | 0 | 1 |  | 0 | 0 |  |  | 1 |  | 0 | 0 | 1 | 0 |  | 1 | 1 | 0 | 0 |  | 0 |  |  |  | 12.5 |  | 624 |  |  |  |  | 12 | 0 | 536 |  | 1 | 1 | 1 | [9 empty] | 0 | 0.5 | 0.1 | 0.05 | 100 | 41 | 0 | 1 | 5 | 100 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 65 | 45 | 0 | 100 | 0 | 0 | 0 | -5 | 15 | 80 | 100 | 100 | 0 | 0 | 100 | -100 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 1 | 30 | 30 | 0 | 0 | 9600 | 2 | 11 | 111 | 11 | 1 | 9600 | 2 | 12 | 112 | 12 | 1 | 192 | 200 | 168 | 75 | 502 | 1 | 255 | 0 | 255 | 255 | 1 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 65 | 1 | 0 | 0 | 0 | -2.5 | 10 |  | 20 | 15 | 0 | 2 | 1 | 1.82 | 0.6 | 0.6 | 1 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 300 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 0 | 1 | 0.1 | 100 | 0 | 560 | 560 | 560 | 560 | 20 | 3 | 0.1 | 0 | 0 | 0 | 15 | 30 | 0.01 | 0.4 | 0 | 60 | 30 | 0.2 | 0 | 0 | 0 | 1200 | 1400 | 0 | 0.5 |  | 0 | 0 | 1000 | 1 | 2 | 0 | 0.1 | 30 | 12.5 | 0.2 | 0.05 | 2.2 | 12.5 | 0 | 12 | 0 | 0 | 1 | 0 | [10 empty] | 1 | 50 | 60 | 70 | 80 | 90 |  | 1 | 0.0005 | 0.0005 | 0 | 80 | 80 | 1 | 0 | 1 | 4 | 1 | 0 | 0 | 0 | 0 | 100 | 0 | 0.3 | 1 | 25 | 5 | 100 | 0 | 4 | 0.1 | 0.5 | 1 | 7 | 100 | 0 | 25 | 10 | 250 | 0 | 0.1 | 0.1 | 1 | 2 | 0.1 | 1 | 10 | 0.1 | 1 | 10 | 0.1 | 1 | 0 | 1 | 4000 | 2000 | 20000 | 10000 | 4497 | 2249 | 8 | 4 | 2 | 1 | 30 | 150 | 20 | 120 | 0 | 1 | 1 | 1 | 1 | 0 |  |  | 0 |  | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 60 | 60 | 0 | 200 | 2 | 1 | 50 | 30 | 40 | 0.1 | 0 | 0 | 5 | 5 | 1000 | 1000 | 5 | 5 | 1000 | 1000 | 250 | 100 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 20 |  | 180 | 360 | 720 | 700 | 630 | 630 | 625 | 20 | 40 | 0 | 0 | 20 | 20 | 720 | 0 | 0 | 600 | 3600 | 210 | 1.5 | 1 | 650 | 700 | 1 | 0 | 0 | 0 | [66 empty] | 0 | 0 | 0 | 0 |  |  |  |  | 1 | 1 | 1200 | 40500 |  |  |  | 45120 | [5 empty] | 5 | 250 | 250 |  |  | 100 | 100 | 1000 | 680 | 640 |  | 650 |  |  | 640 | 5 | 650 | 5 | [7 empty] | 5 | 1000 |  |  | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1.3169 | 10.18 | 9.75 | 0.762 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 1.3169 | 10 | 9.54 | 0.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | -20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 300 | 1 | 500 | 7000 | 30 | 50 | 0 | 10000 | 0 | 30 | 5 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0.3 | 0 | 0 | 0 | 25 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 20 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 40 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 100 | 100 | 0 | 10 | 3 | 100 | 35 | 0 | 5 | 40 | 60 | 10 | 0 | 0 | 0 | [16 empty] | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 20 | 30 | 0 | 0 |  |  | 0 | 0 | 30 | 75 | 10 | 20 | 5 | 9 | 5 | 0 | 5 | 0 | 5 | 0 |  |  | 120 | 0 | 30000 | 30000 | 17500 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 0 | 40 | 40 | 40 | 1410 | 1410 | 1410 | 400 | 400 | 60000 | 60000 | 100 | 30 | [15 empty] | 5579 | 88 | 90 | 2.19 | [19 empty] | 1 | -10 | 10 | [6 empty] | 0.5 | 0 | 0 | [6 empty] | 4 | 5 | 135 | 1 | 1 |  | 0 | 0 |  | 1 | 1 | 0 |  |  |  |  | 150 | 200 | 85 | 90 | 85 | 90 | 5 | 5 | 10 | 10 | 140 | 145 | 140 | 145 | 140 | 145 | 140 | 5 | 175 | 5 | 5 | 1 | 57.5 | 1 |  |  |  | 150 | 1000 | 80 | 60 | 45 | 300 |  | 75 | 2.043 | 1 | 0 | 1 |  | 0.1 | 0.84 | 60 | 0 | 70 | 80 | 70 | 60 | 55 | 4 | 20 | 2249 | 4497 | 0 | 5000 | 50 | 5 | 0 | 99 | 80 | 70 | 60 | 55 | 4 | 20 | 2249 | 4497 |  |  |  | 0 | 1 | 0 | 0.95 | 0.98 | 1 | -0.98 | -0.95 | 0 | 20 | 0.8 | -0.95 | 1 |  | 0 | 100 | 1 | 100 | 4 | 20 | 90 | 110 | 10500 |  |  | 1 | 0 | 2 | 100 | 50 | 25 | -25 | -50 | 4 | 20 | 0 | 1440 | 0 | 0 | 4 | 20 | -100 | 100 | 5000 | 0 | 1 | 1 | -0.9 | -3600 | 3600 | 10 | 0 | 100 | 0 | 100 | 0 | 800 | -20 | 800 | -20 | 600 | 0 | 10 | 3.3 | 0.2 | 3.1 | 0.05 | 1.5 | 1.55 | 0.05 | 0.05 | 120 | 5 | 120 | 5 | 55 | 5 | 97 | 0.1 | 37 | 3 | 60 | 4 |  |  | 1 | 30 |  |  | 20 |  |  |  | 3 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.75 | 0.1 | 0.55 | 0.1 | 3 | 0.05 | 10 | 0.5 | 5.2 |  | 0.01 | 0.3 | 0.1 | 0.6 | 0.2 | 0.5 | 500 | 1500 | 3.5 | 0.1 | 0.3 | 0.1 | 1.2 | 0.1 | 0.3 | 1 | 0.1 | 500 | 1500 | 5 | 2 | 2.5 | 3 | 180 | 180 | 180 | 60 | 10 | 0 | 1 | 120 | 2 | 120 | 2 | 38 | 3 | 0 | 0 | 83 | 0.1 | 0 | 0 | 1 | 0 | 1 | 0 | 62 | 120 | 2 | 2 | 0 | 0 | 0 | 120 | 120 | 2 | 2 | 1 | 61 | 2 | 1 |  | 81 | 120 | 0.5 | 0.5 | 0 | 1 | 0 | 99 | 101 | 2 | 2 | 1 | 2 | 100 | 0 | 2 | 0 | 0 | 100 | 0 | 10 | 0 | 0 | 0 | 2 | 84 | 0 | 0 | 0 | 5 | 20 | 0 | 2 | 30 | 90 | 0 | 0 | 0 | 200 | -200 | 0 | -70 | 100 | -100 | 0 | 0 | 0 | 200 | -200 | 20 | 30 | 1 | 2 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 10 | 0 | 16 | 0 | 0 | 10 | 0 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 18 | 12 | 35 | 0 | 0 | 55 | 45 | 100 | 0 | 0 | 15 | 0 | 250 | 0 | 0 | 80 | 20 | 100 | -25 | 0 | 60 | 100 | -25 | 3600 | 2 | 0 | 10 | 0 | 0 | 9 | 16 | 0 | 0 | 4 | 10 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 9.5 | 10 | 0.3 | 0 | 10 | 0 | 0 | 500 | 0 | 10 | 0 | 150 | -50 | 1000 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 10 | 0 | 0 | 1 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 0 | 2 | 120 | 1 | 100 | [9 empty] | 18 | 18 | 18 | 18 | [5 empty] | 4 | 4 | 20 | 7.5 | 22.5 |  | 1 | 12 | 30 | 7 | 48 | 650 | 950 | 4000 | 30 | 6 |  | 3 | 42 |  | 924 | [11 empty] | 1 | 250 | 40 | 80 | 3 | 15 | 1800 | 50 | 300 |  |  |  |  | 1800 | 1800 | 0 | 50 | 50 | [5 empty] | 1 | 0 | 990 | -950 | -650 |  | 1000 | 10 | [10 empty] | 1 | 1 | 1 | 1 | -5 | -2 | 2 | 2 | 95 | 100 | 10 | 30 | 0 | 0 | 10 | 10000 | 1400 | 100 | 20 |  | 100 | 0 | 0 | 20 | 4000 | 4000 |  | 367 | 30 | 0 | 400 | -1 | 4 | 3 | 10 | 60 | 120 | 5 | 5 | 5 | 5 | -5 | -5 | -5 | -5 | 8 | 8 | 8 | 8 | 4.5 |  | 45 | 270 | 70 | -144 | 0 | 80 | 350 | [24 empty] | 0 | 4 | 500 | 30 |  | 4000 | [7 empty] | 1.2 |  | 50 | 0 |  | 100 | 100 |  | 100 | 50 | 10 | 25 | 2500 | 1 |  |  | 0 | 380 | 1 | -30 | -9 | 4497 | 2249 | 10 | 4497 | 2249 | 60 | 0 | 0 | [6 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4491 | 2247 | 5355 | 2784 | 1500 | 1500 |  | 56.9 | 56.7 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4909 | 2154 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4909 | 2154 | 1500 | 1500 |  | 50 | 50 |  | 660 | [7 empty] | 0 | 0.39062 |  | 0.05859 | 2.5 | 1.1 | [5 empty] | 4750 | 2000 | 4909 | 2154 | 1500 | 1500 |  | 50 | 50 |  | 660 |  | 0 | 1000 | 600 | 50 | -0.5 | -5 | 120 | 10 | 0 | 1 | 10 | 0 | [6 empty] | 100 | 50 | 100 | 12000 | 100 | -100 | 0 | 0 | -25 |  | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 10 | 0 | 0.5 | 0 | 0 | 60000 | 0 | 60000 | 0 |  | 4 | 0 | 1 | 0 |  |  |  | 80 |  | 52 | [14 empty] | 57 | 57 | 57 | 57 | [10 empty] | 0 | 0 | 1 | 3 | 59 | 61 | 2 | 2 | 64 |  | 52 | [15 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.1 |  |  | 100 | 0.2 |  | 351 | 140 | 140 | 100 | [8 empty] | -1250 | 5000 |  | 0.2 | 80 | 200 | [21 empty] | 20 | 30 | 1 |  |  |  |  | 110 | 0.4 |  |  | 100 | 0.2 |  | 100 |  | 100 | 100 | [11 empty] | 0.2 | 100 | 200 | [43 empty] | 0 | 0.1 | 0.1 | 0.01 | 100 | 120 | 0 | 1 | 1.8 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 65 | 45 | 57 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 0 | 100 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 70 | 70 | 70 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 2 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 25 | 10 | 100 | 20 | 1.5 | 0.003 | 1 | 1 | 10 | 0.6 | 0 | 1 | 12 | 1 | 1 | 1 | 1 | 0 | 0 | 1.1 | 0.7 | 1 | 0 | 100 | 0 | 0 | 0.1 | 0.1 | 0.01 | 100 | 150 | 0 | 1 | 4.5 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 75 | 95 | 0 | 100 | 50 | 0 | 0.1 | 0.5 | 0.5 | 100 | 40 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 50 | 0 | 100 | 10 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 1 | 10 | 10 | 10 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 95 | 75 | 75 | 0 | 100 | 0 | 0 | 0 | 1 | 1 | 100 | 0.01 | 0 | 1 | 3 | 1 | 1 | 1 | 1 | 0 | 0 | 20 | -20 | -3 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 90 | 50 | 50 | 20 | 100 | 20 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 2 | 100 | 100 | 100 | 0.05 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 780 | 720 | 740 | 0 | 100 | -100 | 0 | 1 | 320 | 320 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 400 | 0 | 0 | 0 | 100 | 0 | 0.001 | 0.1 | 100 | 100 | 100 | 70 | 0 | 1 | 6 | 1 | 1 | 1 | 1 | 0 | 0 | 80 | 30 | 80 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 30 | 15 | 25 | 0 | 100 | 0 | 0 | 0.1 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 99 | 85 | 90 | 0 | 100 | 0 | [42 empty] | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.2 | 100 | 100 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 40 | 20 | 28 | 0 | 100 | 0 | 0 | 0 | 50 | 50 | 100 | 205 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 100 | 0 | 50 | 0 | 100 | 0 | 0 | 1000 | -1000 | 0 | 0 | 10 | 10 | 10 | 2 | 5 | 0 | 48 | 50 | 1 | 5000 | 8000 | 5000 | 8000 | 6 | 6 | 1 | 5000 | -5000 | 1 | 0 | 0.02 | 1 | 1 | 1 | 1 | 0 | 0 | 3000 | -3000 | 0 | 50 | 100 | 97.1 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0.1 | 100 | 205 | 0 | 0 | 1 | 20 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 120 | 0 | 100 | 100 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 0 |  |  |  |  | 12 | 2 | 5 | [9 empty] | 235 | 235 | 40 | 25 | 232 | 1 | 100 |  | 70 | 327 | 327 | 1 | 10 |  |  | 0 | 0 | 0 |  |  |  |  | 3 | 0.1 | 10 | 0.5 | 80 | 0 | [6 empty] | 0.01421 | 0.29619 | 0.88857 | 100 | 0 | 0 | 0.44428 | 0.23695 | 100 | 2 | 0 | 20 | 5000 | 5000 | 70 | 75 | 90 | 100 |  | 0 | 20 | 2249 | 4497 | 2.5 | 2 | 35 | 45 |  | -2 | -2 | -2 | -2 |  | 50 | 0.1 |  |  |  |  | 20 | 300 |  |  | 50 | 0.3 | -145 | 10 | 10 | 0.5 | 105 | 0.5 | 0.5 | 0 | 2 | 4497 | 4497 | 4497 | 4497 | 75.6 | 0.72 | 0.72 | 0.72 | 0.72 | 0.3 | 0.72 | 0.72 | 0.72 |  | 10 | 10 | 95 | 1 | 1 | 100.4 | 102.9 | 98 | 91 | 102.9 | 50 | 65 | 85 | 75 |  | 105 | 120 | 95 | 70 | 140 | 0 | 70 | 20 | 82 | 1 | 20 | 5.55 | 1 | 10 | 63 |  |  | 5 | 4 | 4 | 4 | 4 | 60 | 60 | 60 | 60 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [30 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [90 empty] | 1 | 1 |  |  | 1 |  | 0 | 0 |  | 48.2 |  | 0 |  | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.8 | 50 | 10 | 1 | 1 | 9.5 | 10 | 1 | 10 | 9 | 0 | 0 | 0 | 0 | 0 | 30 | 80 | 50 | 27 | 0.5 | 0.5 | 27 | 100 | 0 | 30 | 27 | 0 | 0 | 0 | 0 | 1650 | 10 | 200 | 400 | 2800 | 5 | 10000 | 0 | 3850 | 0 | 5 | 5 | 50 | 10 | 100 | 0 | 0 | 1500 | 0 |  |  | 0 |  | 1 | 90 | 3 | 35 |  |  | 200 | 0 |  |  |  |  | 0 | 0 | 100 | 3 | 500 | 15 | 60 | 60 | 3 | 30 |  |  | 0 |  | 0 | 0 | 0.5 | 6 | 25 | 0 | 0 | 0 | -150 | 5 | 5 | -150 | -10 | -150 | 0 | -100 | 0 | 0 | 800 |  | 0.2 | 0.7 | 4 | 100 | 0 | 0 | 20 | 0 | 1500 |  |  | 0 | 0 | 1740 | 10 | 800 | 10 |  |  |  |  | 100 | 2 | 1502 | 6.7 | 0 | 95 | 85 | 85 | 95 | 95 | 8.89 | 9.27 | 804 |  |  | 1.55 | 1.65 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | 9.54 | 9.971 | 720 |  |  | 1.55 | 1.75 | 30 | 75 | [16 empty] | 1.1 |  |  | 0.61 | [13 empty] | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | [28 empty] | 1 | 1 | 1 | 2 | 0 | 2 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | [49 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4505 |  |  | 4497 | 0 | 0 | 0 | 0 | 0 | 4497 | 4497 |  |  | 2.67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44.1 | 9.8 | -43.79 | 4.022 | 0.0115 | 0.73 | 0 | 0.3 | 4497 | 0 | 0 | 2.16 | 55 | 352 | 0 | 0 | 299 | 299 | 175 | 161 | 121 | 38 | 38 | 32 | 542 | 521 | 482 | 482 | 183 | 31 | 29 | 31 | 0 | 77.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 385 | 373 | 390 | 388 | 387 | 385 | 379 | 390 | 384 | 382 | 387 | 390 | 0 | 382 | 387 | 376 | 387 | 387 | 0 | 389 | 370 | 0 | 0 | 379 | 487 | 506 | 511 | 493 | 508 | 509 | 508 | 507 | 509 | 509 | 496 | 494 | 496 | 507 | 509 | 496 | 508 | 506 | 508 | 0 | 0 | 509 | 487 | 499 |  | Sending | 30 | 61 | 62 | 61 | 62 | 61 | 63 | 61 | 61 | 63 | 62 | 62 | 61 | 61 | 61 | 61 | 62 | 61 | 60 | 60 | 60 | [24 empty] | 1185 | 1117 | 1512 | 1330 | 1479 | 1056 | 3150 | 1343 | 1735 | 3151 | 1125 | 1264 | 1284 | 1391 | 1116 | 1174 | 1119 | 1200 | 1310 | 1251 | 3150 | 1549 | 1516 | 1534 |  | 94 | 1 | [11 empty] | 78.5 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 291.8 | 0 | 0 | 0 | 1024 | 0 | 0 | 0 | 8.3 | 0 | 0 | 0 | 1.86 |  |  |  | 59.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 8342 | 1 | 8342 | 1 | 8342 | 1 | 8342 | 1 | 8342 | 1 | 8342 | 1 | 8342 | 1 | 8342 | 1 | 8342 | 1 | 8342 | 1 | 8342 | 1 | 8342 | 1 | 8342 | 1 | 8342 | 1 | 8342 | 1 | 8342 | 1 | 8342 | 1 | 8342 | 1 | 8342 | 1 | 8342 | 1 | 8342 | 1 | 8342 | 1 | 8342 | 1 | 8342 | 1 | 0 | 7.54 | 0 | 7.67 | 0 | 7.73 | 0 | 7.67 | 0 | 8.01 | 0 | 7.76 | 0 | 7.86 | 0 | 7.94 | 0 | 7.57 | 0 | 7.55 | 0 | 7.59 | 0 | 7.66 | 0 | 7.7 | 0 | 7.81 | 0 | 7.52 | 0 | 7.66 | 0 | 7.54 | 0 | 8.16 | 0 | 7.53 | 0 | 7.52 | 0 | 7.68 | 0 | 7.53 | 0 | 7.65 | 0 | 7.61 | 0 | 0.2 | 0 | -0.42 | 0 | -0.46 | 0 | -0.23 | 0 | -0.4 | 0 | -0.41 | 0 | -0.38 | 0 | 0.16 | 0 | -0.35 | 0 | -0.26 | 0 | -0.02 | 0 | -0.29 | 0 | -0.26 | 0 | -0.29 | 0 | -0.23 | 0 | -0.12 | 0 | -0.28 | 0 | -0.03 | 0 | -0.25 | 0 | -0.29 | 0 | -0.17 | 0 | -0.34 | 0 | -0.28 | 0 | -0.18 | 0 | 7.83 | 0 | 7.65 | 0 | 7.79 | 0 | 7.63 | 0 | 7.65 | 0 | 7.66 | 0 | 7.68 | 0 | 7.5 | 0 | 7.55 | 0 | 7.82 | 0 | 7.56 | 0 | 7.56 | 0 | 7.83 | 0 | 7.52 | 0 | 7.62 | 0 | 7.54 | 0 | 7.59 | 0 | 7.79 | 0 | 7.75 | 0 | 7.58 | 0 | 7.95 | 0 | 7.98 | 0 | 8.02 | 0 | 7.81 | 0 | 0.3 | 0 | -0.38 | 0 | -0.5 | 0 | -0.46 | 0 | -0.29 | 0 | -0.38 | 0 | -0.36 | 0 | -0.32 | 0 | -0.4 | 0 | -0.32 | 0 | -0.35 | 0 | 0.02 | 0 | -0.4 | 0 | -0.23 | 0 | -0.19 | 0 | -0.46 | 0 | -0.27 | 0 | -0.43 | 0 | -0.3 | 0 | -0.34 | 0 | -0.18 | 0 | -0.34 | 0 | -0.32 | 0 | -0.39 |  | 0 | 1 | 1 | 1 | 17 | 0 | 99.9 | 99.1 | 99.8 | 0 | 0 | 12.6 | 11.7 | 0 | 12.3 | 0 | 0 | 0 | 5.51 |  | 0 | 0 | 0 | 0 |  | 99.9 | 99.9 | 99.9 | 99.9 | 12.6 | 12.6 | 12.6 | 12.6 |  | 1502 | 1499 |  | 56.9 |  |  | 0 | 0 | Salmmeir 2

## Weibulls
|  | f | s | beta | eta | R@30k 90%CL | Comment
J624 | G2 | 29 | 907 | 1.49 | 161801 | 92.2% | T23 with LKZ OCR
J620 | G2 | 19 | 404 | 1.374 | 204017 | 93% | T23 with LKZ OCR
J616 | G2 | 19 | 506 | 0.791 | 1294700 | 95% | T23 with LKZ OCR
J612 | G2 | 9 | 317 | 0.83 | 1088700 | 95% | T23 with LKZ OCR
J6xx | G2 | 76 | 2134 | 1.115 | 359656 | 92.92% | T23 with LKZ OCR
J624 | G3 | 35 | 849 | 1.11 | 115347 | 80% | T23 with flat OCR
J620 | G3 | 23 | 422 | 1.162 | 90955 | 75% | T23 with flat OCR
J616 | G3 | 24 | 576 | 0.719 | 878362 | 91.5% | T23 with LKZ OCR
J612 | G3 | 13 | 264 | 1.244 | 92255 | 79% | T23 with LKZ OCR
J6xx | G3 | 95 | 2111 | 0.97 | 195372 | 82.12% | T23 with LKZ OCR
J6xx | all | 251 | 8341 | 0.984 | 574741 | 94.2% | Source - cleaned by Maciej 2020-05_25
J612 | all | 69 | 1681 | 1.061 | 336753 | 91.32% | Source - cleaned by Maciej 2020-05_25
J616 | all | 75 | 2166 | 0.964 | 509948 | 92.61% | Source - cleaned by Maciej 2020-05_25
J620 | all | 82 | 3104 | 0.919 | 882599 | 94.94% | Source - cleaned by Maciej 2020-05_25
J624 | all | 88 | 2533 | 0.899 | 571055 | 92.1% | Source - cleaned by Maciej 2020-05_25
J612 | all w/o Pak | 59 | 1537 | 1.123 | 316497 | 91.86% | Source - cleaned by Maciej 2020-05_25
J616 | all w/o Pak | 54 | 1683 | 1.006 | 503236 | 92.17% | Source - cleaned by Maciej 2020-05_25
J620 | all w/o Pak | 60 | 2900 | 1.11 | 589239 | 95.72% | Source - cleaned by Maciej 2020-05_25
J624 | all w/o Pak | 78 | 2221 | 0.857 | 688030 | 93.41% | Source - cleaned by Maciej 2020-05_25
|  | beta | 1.49 | max
|  |  | 0.719 | min
|  |  | 1.0383 | mittel
|  |  | 1.006 | median